## Objective_stages
case_name | Method | Objective_equation | solver_status | termination_condition | objective_value_solver_raw_W_sum | objective_value_normalized | objective_power_base_W | objective_value | objective_value_raw_W_sum | initial_objective_raw_W_sum | objective_improvement_fraction | PV_available_energy_kWh | PV_curtailment_fraction | BESS_SOC_swing_pu | dead_BESS_rejection_guard_passed | PV_curtailment_power_sum_kW | PV_curtailment_energy_kWh_reported | BESS_throughput_power_sum_kW | BESS_throughput_energy_kWh_reported | worst_interval_curtailment_fraction | Battery_throughput_penalty | No_net_discharge_during_PV_surplus | PV_surplus_gate_violation_count | Night_only_discharge_gate_enabled | Night_PV_to_demand_ratio_threshold | Night_discharge_gate_violation_count | method_signature
Case_C_balanced | One-stage weighted power-sum objective | sum_t[(PV_available-PV_command)+1e-3*¦Q_PV¦] + 0.0001*sum_t(P_BESS_charge+P_BESS_discharge) | ok | optimal | 141742.9513 | 0.60063 | 235990.3088 | 141742.9517 | 141742.9517 | 1713200.5968 | 0.91726 | 1750.2726 | 0.040402 | 0.78383 | TRUE | 141.4295 | 70.7147 | 3134.7501 | 1567.375 | 1 | 0.0001 | TRUE | 0 | TRUE | 1e-06 | 0 | LOCATION_MULTISTART_feeder2_1818_S4_STRONG

## Existing_metrics
case_name | scenario_id | PV_architecture | BESS_enabled | size_label | control_mode | BESS_energy_kWh | BESS_power_kW | BESS_C_rate | Objective_mode | solver_status | termination_condition | objective_value_solver_raw_W_sum | objective_value_normalized | objective_power_base_W | objective_value | objective_value_raw_W_sum | initial_objective_raw_W_sum | objective_improvement_fraction | PV_available_energy_kWh | PV_curtailment_fraction | BESS_SOC_swing_pu | dead_BESS_rejection_guard_passed | Battery_throughput_penalty | Night_only_discharge_gate_enabled | Night_PV_to_demand_ratio_threshold | Net_injection_smoothing_penalty | Objective_equation | Time_sim_interval_minutes | Number_of_time_steps | delta_t_hours_from_time_grid | Cold_start | Warm_started_from_Case_C | Manual_initialization_in_main_script | Forced_no_discharge_time_min | PV_command_energy_kWh | PV_curtailment_energy_kWh | PV_curtailment_percent | PV_whole_horizon_curtailment_fraction_guard | PV_max_single_interval_curtailment_fraction | PV_max_single_interval_time_min | PV_curtailment_reporting_interval_h | BESS_charge_energy_kWh | BESS_discharge_energy_kWh | BESS_throughput_kWh | BESS_equivalent_full_cycles_over_horizon | BESS_cycle_limit_enabled | BESS_cycle_limit_over_horizon | BESS_cycle_limit_margin | BESS_SOC_min_observed | BESS_SOC_max_observed | BESS_DOD_observed_pu | BESS_initial_SOC | BESS_last_state_SOC | BESS_terminal_SOC_target | BESS_terminal_SOC_estimate | BESS_terminal_SOC_error | BESS_max_exclusivity_product_pu2 | BESS_cross_phase_opposite_direction_interval_count | BESS_SOC_balance_max_abs_error_pu | Voltage_violation_rows_OPF_or_DSS | Max_voltage_violation_pu_OPF_or_DSS | Total_voltage_violation_pu_OPF_or_DSS | Max_OPF_network_voltage_range_pu | Max_DSS_network_voltage_range_pu | Max_OPF_VUF2_percent | Max_DSS_VUF2_percent | Max_OPF_VUF0_percent | Max_DSS_VUF0_percent | OPF_total_line_losses_kWh | Max_OPF_line_loading_percent | Max_DSS_line_loading_percent
Case_C_balanced | C | central | TRUE | E1000kWh_P250kW | balanced | 1000 | 250 | 0.25 | one_stage_weighted_power_sum | ok | optimal | 141742.9513 | 0.60063 | 235990.3088 | 141742.9517 | 141742.9517 | 1713200.5968 | 0.91726 | 1750.2726 | 0.040402 | 0.78383 | TRUE | 0.0001 | TRUE | 1e-06 | 0 | sum_t[(PV_available-PV_command)+1e-3*¦Q_PV¦] + 0.0001*sum_t(P_BESS_charge+P_BESS_discharge) | 30 | 48 | 0.5 | TRUE | FALSE | TRUE |  | 1679.5579 | 70.7147 | 4.0402 | 0.040402 | 1 | 1230 | 0.5 | 870.9254 | 696.4496 | 1567.375 | 0.78369 | TRUE | 1 | 0.21631 | 0.18959 | 0.97343 | 0.78383 | 0.5 | 0.55164 | 0.5 | 0.51 | 0.01 | 2e-08 | 36 | 2.4425e-15 | 25 | 1.163e-05 | 3.3864e-05 | 0.044494 | 0.04449 | 0.43997 | 0.43998 | 1.6948 | 1.6947 | 34.8238 | 100 | 100.0166

## Additional_metrics
Case | Objective_architecture | Lexicographic_epsilon_policy | Lexicographic_absolute_epsilon_kWh | Lexicographic_absolute_epsilon_Wh | Stage2_PV_curtailment_kWh | Stage2_BESS_throughput_kWh | Stage2_equivalent_full_cycles | Curtailment_and_discharge_overlap_intervals | Curtailment_and_discharge_overlap_hours | Terminal_SOC_pu | Minimum_SOC_pu | Maximum_SOC_pu | Maximum_absolute_phase_BESS_Q_kvar | Maximum_central_bus_voltage_pu | Minimum_central_bus_voltage_pu | Maximum_feeder_phase_current_A | Peak_feeder_import_kW | Peak_feeder_export_kW | Feeder_import_energy_kWh | Feeder_export_energy_kWh | Gross_load_energy_kWh | Feeder_monitor_sign_factor | Feeder_sign_rule
Case_C_balanced | One-stage weighted PV-curtailment and BESS-throughput objective | not_applicable_one_stage | 0 | 0 | 70.7147 | 1567.375 | 0.78369 | 11 | 5.5 | 0.55164 | 0.18959 | 0.97343 | 23.0758 | 1.1 | 1.0359 | 137.3052 | 58.3058 | 63.1637 | 80.6044 | 733.7699 | 748.6474 | 1 | Terminal 1 at secondary: positive import; negative export. Fixed topology sign.

## Stage1_dispatch
Stage | Time_sample | Time_h | PV_available_kW | PV_command_kW | PV_curtailment_kW | SOC_pu | BESS_P_ch_A_kW | BESS_P_dis_A_kW | BESS_P_net_A_kW | BESS_Q_A_kvar | BESS_P_ch_B_kW | BESS_P_dis_B_kW | BESS_P_net_B_kW | BESS_Q_B_kvar | BESS_P_ch_C_kW | BESS_P_dis_C_kW | BESS_P_net_C_kW | BESS_Q_C_kvar | BESS_P_ch_total_kW | BESS_P_dis_total_kW | BESS_P_net_total_kW | BESS_Q_total_kvar | PV_curtailment_energy_kWh | PV_interval_curtailment_fraction
One-stage weighted objective | 30 | 0.5 | 0 | -3.005e-19 | 3.005e-19 | 0.5 | 5.6119e-06 | 24.7492 | 24.7492 | -3.2164 | 5.6119e-06 | 24.7492 | 24.7492 | -3.2164 | 5.6119e-06 | 24.7492 | 24.7492 | -3.2164 | 1.6836e-05 | 74.2475 | 74.2475 | -9.6491 | 1.5025e-19
One-stage weighted objective | 60 | 1 | 0 | -3.0206e-19 | 3.0206e-19 | 0.45875 | 5.5733e-06 | 24.9204 | 24.9204 | -2.3552 | 5.5733e-06 | 24.9204 | 24.9204 | -2.3552 | 5.5733e-06 | 24.9204 | 24.9204 | -2.3552 | 1.672e-05 | 74.7612 | 74.7612 | -7.0657 | 1.5103e-19
One-stage weighted objective | 90 | 1.5 | 0 | -3.0385e-19 | 3.0385e-19 | 0.41722 | 5.534e-06 | 25.0974 | 25.0973 | -0.5501 | 5.534e-06 | 25.0974 | 25.0973 | -0.5501 | 5.534e-06 | 25.0974 | 25.0973 | -0.5501 | 1.6602e-05 | 75.2921 | 75.292 | -1.6503 | 1.5192e-19
One-stage weighted objective | 120 | 2 | 0 | -2.9893e-19 | 2.9893e-19 | 0.37539 | 5.6487e-06 | 24.5878 | 24.5878 | -4.6122 | 5.6487e-06 | 24.5878 | 24.5878 | -4.6122 | 5.6487e-06 | 24.5878 | 24.5878 | -4.6122 | 1.6946e-05 | 73.7634 | 73.7634 | -13.8366 | 1.4946e-19
One-stage weighted objective | 150 | 2.5 | 0 | -3.0294e-19 | 3.0294e-19 | 0.33441 | 5.5539e-06 | 25.0074 | 25.0074 | -2.1312 | 5.5539e-06 | 25.0074 | 25.0074 | -2.1312 | 5.5539e-06 | 25.0074 | 25.0074 | -2.1312 | 1.6662e-05 | 75.0221 | 75.0221 | -6.3937 | 1.5147e-19
One-stage weighted objective | 180 | 3 | 0 | -3.0301e-19 | 3.0301e-19 | 0.29273 | 5.5521e-06 | 25.0157 | 25.0157 | -1.8191 | 5.5521e-06 | 25.0157 | 25.0157 | -1.8191 | 5.5521e-06 | 25.0157 | 25.0157 | -1.8191 | 1.6656e-05 | 75.0471 | 75.0471 | -5.4573 | 1.5151e-19
One-stage weighted objective | 210 | 3.5 | 0 | -3.039e-19 | 3.039e-19 | 0.25104 | 5.5327e-06 | 25.1031 | 25.1031 | 0.44035 | 5.5327e-06 | 25.1031 | 25.1031 | 0.44035 | 5.5327e-06 | 25.1031 | 25.1031 | 0.44035 | 1.6598e-05 | 75.3094 | 75.3094 | 1.3211 | 1.5195e-19
One-stage weighted objective | 240 | 4 | 0.80283 | -9.6439e-12 | 0.80283 | 0.2092 | -9.1131e-12 | 0.80283 | 0.80283 | -23.0758 | -9.1131e-12 | 0.80283 | 0.80283 | -23.0758 | -9.1131e-12 | 0.80283 | 0.80283 | -23.0758 | -2.7339e-11 | 2.4085 | 2.4085 | -69.2275 | 0.40142 | 1
One-stage weighted objective | 270 | 4.5 | 3.3481 | -9.6439e-12 | 3.3481 | 0.20786 | -9.1326e-12 | 3.3481 | 3.3481 | -22.9301 | -9.1326e-12 | 3.3481 | 3.3481 | -22.9301 | -9.1326e-12 | 3.3481 | 3.3481 | -22.9301 | -2.7398e-11 | 10.0444 | 10.0444 | -68.7902 | 1.6741 | 1
One-stage weighted objective | 300 | 5 | 7.6125 | -9.6439e-12 | 7.6125 | 0.20228 | -9.1623e-12 | 7.6125 | 7.6125 | -22.1806 | -9.1623e-12 | 7.6125 | 7.6125 | -22.1806 | -9.1623e-12 | 7.6125 | 7.6125 | -22.1806 | -2.7487e-11 | 22.8375 | 22.8375 | -66.5417 | 3.8062 | 1
One-stage weighted objective | 330 | 5.5 | 16.2147 | 16.2147 | 0 | 0.18959 | 6.8199e-13 | 3.6961e-12 | 3.0141e-12 | -22.6273 | 6.8199e-13 | 3.6961e-12 | 3.0141e-12 | -22.6273 | 6.8199e-13 | 3.6961e-12 | 3.0141e-12 | -22.6273 | 2.046e-12 | 1.1088e-11 | 9.0423e-12 | -67.8818 | 0 | 0
One-stage weighted objective | 360 | 6 | 32.0406 | 32.0406 | 0 | 0.18959 | 6.8196e-13 | 3.6961e-12 | 3.0141e-12 | -21.2057 | 6.8196e-13 | 3.6961e-12 | 3.0141e-12 | -21.2057 | 6.8196e-13 | 3.6961e-12 | 3.0141e-12 | -21.2057 | 2.0459e-12 | 1.1088e-11 | 9.0423e-12 | -63.617 | 0 | 0
One-stage weighted objective | 390 | 6.5 | 67.5412 | 67.5412 | 0 | 0.18959 | 6.8049e-13 | 3.6946e-12 | 3.0141e-12 | -10.4244 | 6.8049e-13 | 3.6946e-12 | 3.0141e-12 | -10.4244 | 6.8049e-13 | 3.6946e-12 | 3.0141e-12 | -10.4244 | 2.0415e-12 | 1.1084e-11 | 9.0424e-12 | -31.2733 | 0 | 0
One-stage weighted objective | 420 | 7 | 81.236 | 81.2359 | 5.191e-05 | 0.18959 | 2.6704 | 5.201e-05 | -2.6704 | -5.4926 | 2.6704 | 5.201e-05 | -2.6704 | -5.4926 | 2.6704 | 5.201e-05 | -2.6704 | -5.4926 | 8.0112 | 0.00015603 | -8.0111 | -16.4777 | 2.5955e-05 | 6.3901e-07
One-stage weighted objective | 450 | 7.5 | 139.7831 | 139.7831 | 6.156e-06 | 0.1932 | 22.201 | 6.256e-06 | -22.201 | -4.7136 | 22.201 | 6.256e-06 | -22.201 | -4.7136 | 22.201 | 6.256e-06 | -22.201 | -4.7136 | 66.6031 | 1.8768e-05 | -66.6031 | -14.1407 | 3.078e-06 | 4.4039e-08
One-stage weighted objective | 480 | 8 | 137.807 | 137.807 | 6.4135e-06 | 0.22317 | 21.3233 | 6.5135e-06 | -21.3233 | -2.2851 | 21.3233 | 6.5135e-06 | -21.3233 | -2.2851 | 21.3233 | 6.5135e-06 | -21.3233 | -2.2851 | 63.9698 | 1.954e-05 | -63.9698 | -6.8553 | 3.2067e-06 | 4.654e-08
One-stage weighted objective | 510 | 8.5 | 157.7864 | 157.7864 | 4.9295e-06 | 0.25196 | 27.6148 | 5.0295e-06 | -27.6148 | -0.31826 | 27.6148 | 5.0295e-06 | -27.6148 | -0.31826 | 27.6148 | 5.0295e-06 | -27.6148 | -0.31826 | 82.8444 | 1.5089e-05 | -82.8444 | -0.95479 | 2.4648e-06 | 3.1242e-08
One-stage weighted objective | 540 | 9 | 172.4435 | 172.4435 | 4.1717e-06 | 0.28924 | 32.5141 | 4.2716e-06 | -32.5141 | -0.5539 | 32.5141 | 4.2716e-06 | -32.5141 | -0.5539 | 32.5141 | 4.2716e-06 | -32.5141 | -0.5539 | 97.5424 | 1.2815e-05 | -97.5424 | -1.6617 | 2.0858e-06 | 2.4191e-08
One-stage weighted objective | 570 | 9.5 | 185.0063 | 185.0063 | 3.5992e-06 | 0.33313 | 37.5456 | 3.6992e-06 | -37.5456 | -5.4419 | 37.5456 | 3.6992e-06 | -37.5456 | -5.4419 | 37.5456 | 3.6992e-06 | -37.5456 | -5.4419 | 112.6369 | 1.1098e-05 | -112.6369 | -16.3258 | 1.7996e-06 | 1.9455e-08
One-stage weighted objective | 600 | 10 | 119.4161 | 119.4161 | 8.337e-06 | 0.38382 | 16.4618 | 8.437e-06 | -16.4618 | -7.1481 | 16.4618 | 8.437e-06 | -16.4618 | -7.1481 | 16.4618 | 8.437e-06 | -16.4618 | -7.1481 | 49.3855 | 2.5311e-05 | -49.3854 | -21.4444 | 4.1685e-06 | 6.9815e-08
One-stage weighted objective | 630 | 10.5 | 229.7457 | 229.7457 | 2.593e-06 | 0.40604 | 51.5736 | 2.693e-06 | -51.5736 | 0.44355 | 51.5736 | 2.693e-06 | -51.5736 | 0.44355 | 51.5736 | 2.693e-06 | -51.5736 | 0.44355 | 154.7207 | 8.0791e-06 | -154.7207 | 1.3307 | 1.2965e-06 | 1.1287e-08
One-stage weighted objective | 660 | 11 | 235.9903 | 235.9903 | 2.4786e-06 | 0.47566 | 53.863 | 2.5786e-06 | -53.863 | 0.43886 | 53.863 | 2.5786e-06 | -53.863 | 0.43886 | 53.863 | 2.5786e-06 | -53.863 | 0.43886 | 161.5891 | 7.7357e-06 | -161.5891 | 1.3166 | 1.2393e-06 | 1.0503e-08
One-stage weighted objective | 690 | 11.5 | 232.5884 | 232.5884 | 2.5395e-06 | 0.54838 | 52.6192 | 2.6395e-06 | -52.6192 | 0.44517 | 52.6192 | 2.6395e-06 | -52.6192 | 0.44517 | 52.6192 | 2.6395e-06 | -52.6192 | 0.44517 | 157.8577 | 7.9185e-06 | -157.8576 | 1.3355 | 1.2698e-06 | 1.0918e-08
One-stage weighted objective | 720 | 12 | 137.6625 | 137.6625 | 6.5691e-06 | 0.61941 | 20.8256 | 6.6691e-06 | -20.8256 | 0.44801 | 20.8256 | 6.6691e-06 | -20.8256 | 0.44801 | 20.8256 | 6.6691e-06 | -20.8256 | 0.44801 | 62.4768 | 2.0007e-05 | -62.4768 | 1.344 | 3.2846e-06 | 4.7719e-08
One-stage weighted objective | 750 | 12.5 | 86.5072 | 86.5072 | 3.4235e-05 | 0.64753 | 4.0452 | 3.4335e-05 | -4.0451 | -1.7667 | 4.0452 | 3.4335e-05 | -4.0451 | -1.7667 | 4.0452 | 3.4335e-05 | -4.0451 | -1.7667 | 12.1355 | 0.000103 | -12.1354 | -5.3 | 1.7117e-05 | 3.9574e-07
One-stage weighted objective | 780 | 13 | 63.4361 | 63.4361 | 0 | 0.65299 | 6.8172e-13 | 3.6958e-12 | 3.0141e-12 | -12.054 | 6.8172e-13 | 3.6958e-12 | 3.0141e-12 | -12.054 | 6.8172e-13 | 3.6958e-12 | 3.0141e-12 | -12.054 | 2.0452e-12 | 1.1088e-11 | 9.0424e-12 | -36.1619 | 0 | 0
One-stage weighted objective | 810 | 13.5 | 220.8431 | 220.8431 | 2.6743e-06 | 0.65299 | 50.0621 | 2.7743e-06 | -50.0621 | -6.65 | 50.0621 | 2.7743e-06 | -50.0621 | -6.65 | 50.0621 | 2.7743e-06 | -50.0621 | -6.65 | 150.1862 | 8.323e-06 | -150.1862 | -19.95 | 1.3372e-06 | 1.211e-08
One-stage weighted objective | 840 | 14 | 219.0145 | 219.0145 | 2.7436e-06 | 0.72057 | 48.8433 | 2.8436e-06 | -48.8433 | -5.561 | 48.8433 | 2.8436e-06 | -48.8433 | -5.561 | 48.8433 | 2.8436e-06 | -48.8433 | -5.561 | 146.5298 | 8.5307e-06 | -146.5298 | -16.683 | 1.3718e-06 | 1.2527e-08
One-stage weighted objective | 870 | 14.5 | 209.1048 | 209.1048 | 2.8689e-06 | 0.78651 | 46.7813 | 2.9689e-06 | -46.7813 | -9.2441 | 46.7813 | 2.9689e-06 | -46.7813 | -9.2441 | 46.7813 | 2.9689e-06 | -46.7813 | -9.2441 | 140.344 | 8.9067e-06 | -140.344 | -27.7322 | 1.4344e-06 | 1.372e-08
One-stage weighted objective | 900 | 15 | 169.5897 | 169.5897 | 4.3036e-06 | 0.84967 | 31.5401 | 4.4036e-06 | -31.5401 | 0.45074 | 31.5401 | 4.4036e-06 | -31.5401 | 0.45074 | 31.5401 | 4.4036e-06 | -31.5401 | 0.45074 | 94.6203 | 1.3211e-05 | -94.6203 | 1.3522 | 2.1518e-06 | 2.5376e-08
One-stage weighted objective | 930 | 15.5 | 108.3862 | 108.3862 | 1.2452e-05 | 0.89225 | 11.0655 | 1.2552e-05 | -11.0655 | 0.16437 | 11.0655 | 1.2552e-05 | -11.0655 | 0.16437 | 11.0655 | 1.2552e-05 | -11.0655 | 0.16437 | 33.1965 | 3.7655e-05 | -33.1965 | 0.4931 | 6.2258e-06 | 1.1488e-07
One-stage weighted objective | 960 | 16 | 167.9718 | 167.9718 | 4.213e-06 | 0.90718 | 32.2024 | 4.313e-06 | -32.2024 | -6.1366 | 32.2024 | 4.313e-06 | -32.2024 | -6.1366 | 32.2024 | 4.313e-06 | -32.2024 | -6.1366 | 96.6073 | 1.2939e-05 | -96.6072 | -18.4097 | 2.1065e-06 | 2.5082e-08
One-stage weighted objective | 990 | 16.5 | 124.5804 | 124.5804 | 8.1356e-06 | 0.95066 | 16.8645 | 8.2356e-06 | -16.8645 | -4.3228 | 16.8645 | 8.2356e-06 | -16.8645 | -4.3228 | 16.8645 | 8.2356e-06 | -16.8645 | -4.3228 | 50.5934 | 2.4707e-05 | -50.5934 | -12.9684 | 4.0678e-06 | 6.5304e-08
One-stage weighted objective | 1020 | 17 | 58.8677 | 33.5578 | 25.3098 | 0.97343 | 1.0169e-05 | 13.6576 | 13.6576 | 0.44079 | 1.0169e-05 | 13.6576 | 13.6576 | 0.44079 | 1.0169e-05 | 13.6576 | 13.6576 | 0.44079 | 3.0508e-05 | 40.9727 | 40.9727 | 1.3224 | 12.6549 | 0.42994
One-stage weighted objective | 1050 | 17.5 | 21.3862 | -9.6439e-12 | 21.3862 | 0.95066 | -9.1951e-12 | 21.3862 | 21.3862 | -11.4678 | -9.1951e-12 | 21.3862 | 21.3862 | -11.4678 | -9.1951e-12 | 21.3862 | 21.3862 | -11.4678 | -2.7585e-11 | 64.1585 | 64.1585 | -34.4035 | 10.6931 | 1
One-stage weighted objective | 1080 | 18 | 35.7263 | 9.9713 | 25.755 | 0.91502 | 6.6889e-06 | 20.764 | 20.764 | -5.1878 | 6.6889e-06 | 20.764 | 20.764 | -5.1878 | 6.6889e-06 | 20.764 | 20.764 | -5.1878 | 2.0067e-05 | 62.292 | 62.292 | -15.5634 | 12.8775 | 0.7209
One-stage weighted objective | 1110 | 18.5 | 34.8805 | 0.89114 | 33.9893 | 0.88041 | 5.6838e-06 | 24.4359 | 24.4359 | 0.44252 | 5.6838e-06 | 24.4359 | 24.4359 | 0.44252 | 5.6838e-06 | 24.4359 | 24.4359 | 0.44252 | 1.7051e-05 | 73.3077 | 73.3077 | 1.3276 | 16.9947 | 0.97445
One-stage weighted objective | 1140 | 19 | 14.6764 | -9.6439e-12 | 14.6764 | 0.83969 | -9.1838e-12 | 14.6764 | 14.6764 | -18.7117 | -9.1838e-12 | 14.6764 | 14.6764 | -18.7117 | -9.1838e-12 | 14.6764 | 14.6764 | -18.7117 | -2.7551e-11 | 44.0291 | 44.0291 | -56.1351 | 7.3382 | 1
One-stage weighted objective | 1170 | 19.5 | 6.5566 | -9.6439e-12 | 6.5566 | 0.81523 | -9.157e-12 | 6.5566 | 6.5566 | -22.256 | -9.157e-12 | 6.5566 | 6.5566 | -22.256 | -9.157e-12 | 6.5566 | 6.5566 | -22.256 | -2.7471e-11 | 19.6699 | 19.6699 | -66.7681 | 3.2783 | 1
One-stage weighted objective | 1200 | 20 | 1.4787 | -9.6439e-12 | 1.4787 | 0.8043 | -9.1141e-12 | 1.4787 | 1.4787 | -22.37 | -9.1141e-12 | 1.4787 | 1.4787 | -22.37 | -9.1141e-12 | 1.4787 | 1.4787 | -22.37 | -2.7342e-11 | 4.4361 | 4.4361 | -67.11 | 0.73936 | 1
One-stage weighted objective | 1230 | 20.5 | 0.51386 | -9.6439e-12 | 0.51386 | 0.80183 | -9.115e-12 | 0.51386 | 0.51386 | -22.4461 | -9.115e-12 | 0.51386 | 0.51386 | -22.4461 | -9.115e-12 | 0.51386 | 0.51386 | -22.4461 | -2.7345e-11 | 1.5416 | 1.5416 | -67.3382 | 0.25693 | 1
One-stage weighted objective | 1260 | 21 | 0 | -3.0443e-19 | 3.0443e-19 | 0.80098 | 5.5412e-06 | 25.0647 | 25.0647 | 0.44548 | 5.5412e-06 | 25.0647 | 25.0647 | 0.44548 | 5.5412e-06 | 25.0647 | 25.0647 | 0.44548 | 1.6624e-05 | 75.1941 | 75.194 | 1.3364 | 1.5221e-19
One-stage weighted objective | 1290 | 21.5 | 0 | -3.0045e-19 | 3.0045e-19 | 0.7592 | 5.6066e-06 | 24.7726 | 24.7726 | 0.074113 | 5.6066e-06 | 24.7726 | 24.7726 | 0.074113 | 5.6066e-06 | 24.7726 | 24.7726 | 0.074113 | 1.682e-05 | 74.3177 | 74.3177 | 0.22234 | 1.5022e-19
One-stage weighted objective | 1320 | 22 | 0 | -3.0525e-19 | 3.0525e-19 | 0.71791 | 5.5378e-06 | 25.0803 | 25.0802 | 0.45222 | 5.5378e-06 | 25.0803 | 25.0802 | 0.45222 | 5.5378e-06 | 25.0803 | 25.0802 | 0.45222 | 1.6613e-05 | 75.2408 | 75.2407 | 1.3567 | 1.5262e-19
One-stage weighted objective | 1350 | 22.5 | 0 | -3.0825e-19 | 3.0825e-19 | 0.67611 | 5.5553e-06 | 25.001 | 25.001 | 0.44562 | 5.5553e-06 | 25.001 | 25.001 | 0.44562 | 5.5553e-06 | 25.001 | 25.001 | 0.44562 | 1.6666e-05 | 75.003 | 75.003 | 1.3369 | 1.5412e-19
One-stage weighted objective | 1380 | 23 | 0 | -2.9983e-19 | 2.9983e-19 | 0.63445 | 5.6201e-06 | 24.7127 | 24.7127 | -1.2171 | 5.6201e-06 | 24.7127 | 24.7127 | -1.2171 | 5.6201e-06 | 24.7127 | 24.7127 | -1.2171 | 1.686e-05 | 74.1381 | 74.1381 | -3.6514 | 1.4992e-19
One-stage weighted objective | 1410 | 23.5 | 0 | -3.0264e-19 | 3.0264e-19 | 0.59326 | 5.5627e-06 | 24.9681 | 24.9681 | -1.1553 | 5.5627e-06 | 24.9681 | 24.9681 | -1.1553 | 5.5627e-06 | 24.9681 | 24.9681 | -1.1553 | 1.6688e-05 | 74.9042 | 74.9042 | -3.4658 | 1.5132e-19
One-stage weighted objective | 1440 | 24 | 0 | -3.0337e-19 | 3.0337e-19 | 0.55164 | 5.5585e-06 | 24.9867 | 24.9867 | 0.44309 | 5.5585e-06 | 24.9867 | 24.9867 | 0.44309 | 5.5585e-06 | 24.9867 | 24.9867 | 0.44309 | 1.6676e-05 | 74.9601 | 74.9601 | 1.3293 | 1.5168e-19

## Stage2_dispatch
Stage | Time_sample | Time_h | PV_available_kW | PV_command_kW | PV_curtailment_kW | SOC_pu | BESS_P_ch_A_kW | BESS_P_dis_A_kW | BESS_P_net_A_kW | BESS_Q_A_kvar | BESS_P_ch_B_kW | BESS_P_dis_B_kW | BESS_P_net_B_kW | BESS_Q_B_kvar | BESS_P_ch_C_kW | BESS_P_dis_C_kW | BESS_P_net_C_kW | BESS_Q_C_kvar | BESS_P_ch_total_kW | BESS_P_dis_total_kW | BESS_P_net_total_kW | BESS_Q_total_kvar | PV_curtailment_energy_kWh | PV_interval_curtailment_fraction
One-stage weighted objective | 30 | 0.5 | 0 | -3.005e-19 | 3.005e-19 | 0.5 | 5.6119e-06 | 24.7492 | 24.7492 | -3.2164 | 5.6119e-06 | 24.7492 | 24.7492 | -3.2164 | 5.6119e-06 | 24.7492 | 24.7492 | -3.2164 | 1.6836e-05 | 74.2475 | 74.2475 | -9.6491 | 1.5025e-19
One-stage weighted objective | 60 | 1 | 0 | -3.0206e-19 | 3.0206e-19 | 0.45875 | 5.5733e-06 | 24.9204 | 24.9204 | -2.3552 | 5.5733e-06 | 24.9204 | 24.9204 | -2.3552 | 5.5733e-06 | 24.9204 | 24.9204 | -2.3552 | 1.672e-05 | 74.7612 | 74.7612 | -7.0657 | 1.5103e-19
One-stage weighted objective | 90 | 1.5 | 0 | -3.0385e-19 | 3.0385e-19 | 0.41722 | 5.534e-06 | 25.0974 | 25.0973 | -0.5501 | 5.534e-06 | 25.0974 | 25.0973 | -0.5501 | 5.534e-06 | 25.0974 | 25.0973 | -0.5501 | 1.6602e-05 | 75.2921 | 75.292 | -1.6503 | 1.5192e-19
One-stage weighted objective | 120 | 2 | 0 | -2.9893e-19 | 2.9893e-19 | 0.37539 | 5.6487e-06 | 24.5878 | 24.5878 | -4.6122 | 5.6487e-06 | 24.5878 | 24.5878 | -4.6122 | 5.6487e-06 | 24.5878 | 24.5878 | -4.6122 | 1.6946e-05 | 73.7634 | 73.7634 | -13.8366 | 1.4946e-19
One-stage weighted objective | 150 | 2.5 | 0 | -3.0294e-19 | 3.0294e-19 | 0.33441 | 5.5539e-06 | 25.0074 | 25.0074 | -2.1312 | 5.5539e-06 | 25.0074 | 25.0074 | -2.1312 | 5.5539e-06 | 25.0074 | 25.0074 | -2.1312 | 1.6662e-05 | 75.0221 | 75.0221 | -6.3937 | 1.5147e-19
One-stage weighted objective | 180 | 3 | 0 | -3.0301e-19 | 3.0301e-19 | 0.29273 | 5.5521e-06 | 25.0157 | 25.0157 | -1.8191 | 5.5521e-06 | 25.0157 | 25.0157 | -1.8191 | 5.5521e-06 | 25.0157 | 25.0157 | -1.8191 | 1.6656e-05 | 75.0471 | 75.0471 | -5.4573 | 1.5151e-19
One-stage weighted objective | 210 | 3.5 | 0 | -3.039e-19 | 3.039e-19 | 0.25104 | 5.5327e-06 | 25.1031 | 25.1031 | 0.44035 | 5.5327e-06 | 25.1031 | 25.1031 | 0.44035 | 5.5327e-06 | 25.1031 | 25.1031 | 0.44035 | 1.6598e-05 | 75.3094 | 75.3094 | 1.3211 | 1.5195e-19
One-stage weighted objective | 240 | 4 | 0.80283 | -9.6439e-12 | 0.80283 | 0.2092 | -9.1131e-12 | 0.80283 | 0.80283 | -23.0758 | -9.1131e-12 | 0.80283 | 0.80283 | -23.0758 | -9.1131e-12 | 0.80283 | 0.80283 | -23.0758 | -2.7339e-11 | 2.4085 | 2.4085 | -69.2275 | 0.40142 | 1
One-stage weighted objective | 270 | 4.5 | 3.3481 | -9.6439e-12 | 3.3481 | 0.20786 | -9.1326e-12 | 3.3481 | 3.3481 | -22.9301 | -9.1326e-12 | 3.3481 | 3.3481 | -22.9301 | -9.1326e-12 | 3.3481 | 3.3481 | -22.9301 | -2.7398e-11 | 10.0444 | 10.0444 | -68.7902 | 1.6741 | 1
One-stage weighted objective | 300 | 5 | 7.6125 | -9.6439e-12 | 7.6125 | 0.20228 | -9.1623e-12 | 7.6125 | 7.6125 | -22.1806 | -9.1623e-12 | 7.6125 | 7.6125 | -22.1806 | -9.1623e-12 | 7.6125 | 7.6125 | -22.1806 | -2.7487e-11 | 22.8375 | 22.8375 | -66.5417 | 3.8062 | 1
One-stage weighted objective | 330 | 5.5 | 16.2147 | 16.2147 | 0 | 0.18959 | 6.8199e-13 | 3.6961e-12 | 3.0141e-12 | -22.6273 | 6.8199e-13 | 3.6961e-12 | 3.0141e-12 | -22.6273 | 6.8199e-13 | 3.6961e-12 | 3.0141e-12 | -22.6273 | 2.046e-12 | 1.1088e-11 | 9.0423e-12 | -67.8818 | 0 | 0
One-stage weighted objective | 360 | 6 | 32.0406 | 32.0406 | 0 | 0.18959 | 6.8196e-13 | 3.6961e-12 | 3.0141e-12 | -21.2057 | 6.8196e-13 | 3.6961e-12 | 3.0141e-12 | -21.2057 | 6.8196e-13 | 3.6961e-12 | 3.0141e-12 | -21.2057 | 2.0459e-12 | 1.1088e-11 | 9.0423e-12 | -63.617 | 0 | 0
One-stage weighted objective | 390 | 6.5 | 67.5412 | 67.5412 | 0 | 0.18959 | 6.8049e-13 | 3.6946e-12 | 3.0141e-12 | -10.4244 | 6.8049e-13 | 3.6946e-12 | 3.0141e-12 | -10.4244 | 6.8049e-13 | 3.6946e-12 | 3.0141e-12 | -10.4244 | 2.0415e-12 | 1.1084e-11 | 9.0424e-12 | -31.2733 | 0 | 0
One-stage weighted objective | 420 | 7 | 81.236 | 81.2359 | 5.191e-05 | 0.18959 | 2.6704 | 5.201e-05 | -2.6704 | -5.4926 | 2.6704 | 5.201e-05 | -2.6704 | -5.4926 | 2.6704 | 5.201e-05 | -2.6704 | -5.4926 | 8.0112 | 0.00015603 | -8.0111 | -16.4777 | 2.5955e-05 | 6.3901e-07
One-stage weighted objective | 450 | 7.5 | 139.7831 | 139.7831 | 6.156e-06 | 0.1932 | 22.201 | 6.256e-06 | -22.201 | -4.7136 | 22.201 | 6.256e-06 | -22.201 | -4.7136 | 22.201 | 6.256e-06 | -22.201 | -4.7136 | 66.6031 | 1.8768e-05 | -66.6031 | -14.1407 | 3.078e-06 | 4.4039e-08
One-stage weighted objective | 480 | 8 | 137.807 | 137.807 | 6.4135e-06 | 0.22317 | 21.3233 | 6.5135e-06 | -21.3233 | -2.2851 | 21.3233 | 6.5135e-06 | -21.3233 | -2.2851 | 21.3233 | 6.5135e-06 | -21.3233 | -2.2851 | 63.9698 | 1.954e-05 | -63.9698 | -6.8553 | 3.2067e-06 | 4.654e-08
One-stage weighted objective | 510 | 8.5 | 157.7864 | 157.7864 | 4.9295e-06 | 0.25196 | 27.6148 | 5.0295e-06 | -27.6148 | -0.31826 | 27.6148 | 5.0295e-06 | -27.6148 | -0.31826 | 27.6148 | 5.0295e-06 | -27.6148 | -0.31826 | 82.8444 | 1.5089e-05 | -82.8444 | -0.95479 | 2.4648e-06 | 3.1242e-08
One-stage weighted objective | 540 | 9 | 172.4435 | 172.4435 | 4.1717e-06 | 0.28924 | 32.5141 | 4.2716e-06 | -32.5141 | -0.5539 | 32.5141 | 4.2716e-06 | -32.5141 | -0.5539 | 32.5141 | 4.2716e-06 | -32.5141 | -0.5539 | 97.5424 | 1.2815e-05 | -97.5424 | -1.6617 | 2.0858e-06 | 2.4191e-08
One-stage weighted objective | 570 | 9.5 | 185.0063 | 185.0063 | 3.5992e-06 | 0.33313 | 37.5456 | 3.6992e-06 | -37.5456 | -5.4419 | 37.5456 | 3.6992e-06 | -37.5456 | -5.4419 | 37.5456 | 3.6992e-06 | -37.5456 | -5.4419 | 112.6369 | 1.1098e-05 | -112.6369 | -16.3258 | 1.7996e-06 | 1.9455e-08
One-stage weighted objective | 600 | 10 | 119.4161 | 119.4161 | 8.337e-06 | 0.38382 | 16.4618 | 8.437e-06 | -16.4618 | -7.1481 | 16.4618 | 8.437e-06 | -16.4618 | -7.1481 | 16.4618 | 8.437e-06 | -16.4618 | -7.1481 | 49.3855 | 2.5311e-05 | -49.3854 | -21.4444 | 4.1685e-06 | 6.9815e-08
One-stage weighted objective | 630 | 10.5 | 229.7457 | 229.7457 | 2.593e-06 | 0.40604 | 51.5736 | 2.693e-06 | -51.5736 | 0.44355 | 51.5736 | 2.693e-06 | -51.5736 | 0.44355 | 51.5736 | 2.693e-06 | -51.5736 | 0.44355 | 154.7207 | 8.0791e-06 | -154.7207 | 1.3307 | 1.2965e-06 | 1.1287e-08
One-stage weighted objective | 660 | 11 | 235.9903 | 235.9903 | 2.4786e-06 | 0.47566 | 53.863 | 2.5786e-06 | -53.863 | 0.43886 | 53.863 | 2.5786e-06 | -53.863 | 0.43886 | 53.863 | 2.5786e-06 | -53.863 | 0.43886 | 161.5891 | 7.7357e-06 | -161.5891 | 1.3166 | 1.2393e-06 | 1.0503e-08
One-stage weighted objective | 690 | 11.5 | 232.5884 | 232.5884 | 2.5395e-06 | 0.54838 | 52.6192 | 2.6395e-06 | -52.6192 | 0.44517 | 52.6192 | 2.6395e-06 | -52.6192 | 0.44517 | 52.6192 | 2.6395e-06 | -52.6192 | 0.44517 | 157.8577 | 7.9185e-06 | -157.8576 | 1.3355 | 1.2698e-06 | 1.0918e-08
One-stage weighted objective | 720 | 12 | 137.6625 | 137.6625 | 6.5691e-06 | 0.61941 | 20.8256 | 6.6691e-06 | -20.8256 | 0.44801 | 20.8256 | 6.6691e-06 | -20.8256 | 0.44801 | 20.8256 | 6.6691e-06 | -20.8256 | 0.44801 | 62.4768 | 2.0007e-05 | -62.4768 | 1.344 | 3.2846e-06 | 4.7719e-08
One-stage weighted objective | 750 | 12.5 | 86.5072 | 86.5072 | 3.4235e-05 | 0.64753 | 4.0452 | 3.4335e-05 | -4.0451 | -1.7667 | 4.0452 | 3.4335e-05 | -4.0451 | -1.7667 | 4.0452 | 3.4335e-05 | -4.0451 | -1.7667 | 12.1355 | 0.000103 | -12.1354 | -5.3 | 1.7117e-05 | 3.9574e-07
One-stage weighted objective | 780 | 13 | 63.4361 | 63.4361 | 0 | 0.65299 | 6.8172e-13 | 3.6958e-12 | 3.0141e-12 | -12.054 | 6.8172e-13 | 3.6958e-12 | 3.0141e-12 | -12.054 | 6.8172e-13 | 3.6958e-12 | 3.0141e-12 | -12.054 | 2.0452e-12 | 1.1088e-11 | 9.0424e-12 | -36.1619 | 0 | 0
One-stage weighted objective | 810 | 13.5 | 220.8431 | 220.8431 | 2.6743e-06 | 0.65299 | 50.0621 | 2.7743e-06 | -50.0621 | -6.65 | 50.0621 | 2.7743e-06 | -50.0621 | -6.65 | 50.0621 | 2.7743e-06 | -50.0621 | -6.65 | 150.1862 | 8.323e-06 | -150.1862 | -19.95 | 1.3372e-06 | 1.211e-08
One-stage weighted objective | 840 | 14 | 219.0145 | 219.0145 | 2.7436e-06 | 0.72057 | 48.8433 | 2.8436e-06 | -48.8433 | -5.561 | 48.8433 | 2.8436e-06 | -48.8433 | -5.561 | 48.8433 | 2.8436e-06 | -48.8433 | -5.561 | 146.5298 | 8.5307e-06 | -146.5298 | -16.683 | 1.3718e-06 | 1.2527e-08
One-stage weighted objective | 870 | 14.5 | 209.1048 | 209.1048 | 2.8689e-06 | 0.78651 | 46.7813 | 2.9689e-06 | -46.7813 | -9.2441 | 46.7813 | 2.9689e-06 | -46.7813 | -9.2441 | 46.7813 | 2.9689e-06 | -46.7813 | -9.2441 | 140.344 | 8.9067e-06 | -140.344 | -27.7322 | 1.4344e-06 | 1.372e-08
One-stage weighted objective | 900 | 15 | 169.5897 | 169.5897 | 4.3036e-06 | 0.84967 | 31.5401 | 4.4036e-06 | -31.5401 | 0.45074 | 31.5401 | 4.4036e-06 | -31.5401 | 0.45074 | 31.5401 | 4.4036e-06 | -31.5401 | 0.45074 | 94.6203 | 1.3211e-05 | -94.6203 | 1.3522 | 2.1518e-06 | 2.5376e-08
One-stage weighted objective | 930 | 15.5 | 108.3862 | 108.3862 | 1.2452e-05 | 0.89225 | 11.0655 | 1.2552e-05 | -11.0655 | 0.16437 | 11.0655 | 1.2552e-05 | -11.0655 | 0.16437 | 11.0655 | 1.2552e-05 | -11.0655 | 0.16437 | 33.1965 | 3.7655e-05 | -33.1965 | 0.4931 | 6.2258e-06 | 1.1488e-07
One-stage weighted objective | 960 | 16 | 167.9718 | 167.9718 | 4.213e-06 | 0.90718 | 32.2024 | 4.313e-06 | -32.2024 | -6.1366 | 32.2024 | 4.313e-06 | -32.2024 | -6.1366 | 32.2024 | 4.313e-06 | -32.2024 | -6.1366 | 96.6073 | 1.2939e-05 | -96.6072 | -18.4097 | 2.1065e-06 | 2.5082e-08
One-stage weighted objective | 990 | 16.5 | 124.5804 | 124.5804 | 8.1356e-06 | 0.95066 | 16.8645 | 8.2356e-06 | -16.8645 | -4.3228 | 16.8645 | 8.2356e-06 | -16.8645 | -4.3228 | 16.8645 | 8.2356e-06 | -16.8645 | -4.3228 | 50.5934 | 2.4707e-05 | -50.5934 | -12.9684 | 4.0678e-06 | 6.5304e-08
One-stage weighted objective | 1020 | 17 | 58.8677 | 33.5578 | 25.3098 | 0.97343 | 1.0169e-05 | 13.6576 | 13.6576 | 0.44079 | 1.0169e-05 | 13.6576 | 13.6576 | 0.44079 | 1.0169e-05 | 13.6576 | 13.6576 | 0.44079 | 3.0508e-05 | 40.9727 | 40.9727 | 1.3224 | 12.6549 | 0.42994
One-stage weighted objective | 1050 | 17.5 | 21.3862 | -9.6439e-12 | 21.3862 | 0.95066 | -9.1951e-12 | 21.3862 | 21.3862 | -11.4678 | -9.1951e-12 | 21.3862 | 21.3862 | -11.4678 | -9.1951e-12 | 21.3862 | 21.3862 | -11.4678 | -2.7585e-11 | 64.1585 | 64.1585 | -34.4035 | 10.6931 | 1
One-stage weighted objective | 1080 | 18 | 35.7263 | 9.9713 | 25.755 | 0.91502 | 6.6889e-06 | 20.764 | 20.764 | -5.1878 | 6.6889e-06 | 20.764 | 20.764 | -5.1878 | 6.6889e-06 | 20.764 | 20.764 | -5.1878 | 2.0067e-05 | 62.292 | 62.292 | -15.5634 | 12.8775 | 0.7209
One-stage weighted objective | 1110 | 18.5 | 34.8805 | 0.89114 | 33.9893 | 0.88041 | 5.6838e-06 | 24.4359 | 24.4359 | 0.44252 | 5.6838e-06 | 24.4359 | 24.4359 | 0.44252 | 5.6838e-06 | 24.4359 | 24.4359 | 0.44252 | 1.7051e-05 | 73.3077 | 73.3077 | 1.3276 | 16.9947 | 0.97445
One-stage weighted objective | 1140 | 19 | 14.6764 | -9.6439e-12 | 14.6764 | 0.83969 | -9.1838e-12 | 14.6764 | 14.6764 | -18.7117 | -9.1838e-12 | 14.6764 | 14.6764 | -18.7117 | -9.1838e-12 | 14.6764 | 14.6764 | -18.7117 | -2.7551e-11 | 44.0291 | 44.0291 | -56.1351 | 7.3382 | 1
One-stage weighted objective | 1170 | 19.5 | 6.5566 | -9.6439e-12 | 6.5566 | 0.81523 | -9.157e-12 | 6.5566 | 6.5566 | -22.256 | -9.157e-12 | 6.5566 | 6.5566 | -22.256 | -9.157e-12 | 6.5566 | 6.5566 | -22.256 | -2.7471e-11 | 19.6699 | 19.6699 | -66.7681 | 3.2783 | 1
One-stage weighted objective | 1200 | 20 | 1.4787 | -9.6439e-12 | 1.4787 | 0.8043 | -9.1141e-12 | 1.4787 | 1.4787 | -22.37 | -9.1141e-12 | 1.4787 | 1.4787 | -22.37 | -9.1141e-12 | 1.4787 | 1.4787 | -22.37 | -2.7342e-11 | 4.4361 | 4.4361 | -67.11 | 0.73936 | 1
One-stage weighted objective | 1230 | 20.5 | 0.51386 | -9.6439e-12 | 0.51386 | 0.80183 | -9.115e-12 | 0.51386 | 0.51386 | -22.4461 | -9.115e-12 | 0.51386 | 0.51386 | -22.4461 | -9.115e-12 | 0.51386 | 0.51386 | -22.4461 | -2.7345e-11 | 1.5416 | 1.5416 | -67.3382 | 0.25693 | 1
One-stage weighted objective | 1260 | 21 | 0 | -3.0443e-19 | 3.0443e-19 | 0.80098 | 5.5412e-06 | 25.0647 | 25.0647 | 0.44548 | 5.5412e-06 | 25.0647 | 25.0647 | 0.44548 | 5.5412e-06 | 25.0647 | 25.0647 | 0.44548 | 1.6624e-05 | 75.1941 | 75.194 | 1.3364 | 1.5221e-19
One-stage weighted objective | 1290 | 21.5 | 0 | -3.0045e-19 | 3.0045e-19 | 0.7592 | 5.6066e-06 | 24.7726 | 24.7726 | 0.074113 | 5.6066e-06 | 24.7726 | 24.7726 | 0.074113 | 5.6066e-06 | 24.7726 | 24.7726 | 0.074113 | 1.682e-05 | 74.3177 | 74.3177 | 0.22234 | 1.5022e-19
One-stage weighted objective | 1320 | 22 | 0 | -3.0525e-19 | 3.0525e-19 | 0.71791 | 5.5378e-06 | 25.0803 | 25.0802 | 0.45222 | 5.5378e-06 | 25.0803 | 25.0802 | 0.45222 | 5.5378e-06 | 25.0803 | 25.0802 | 0.45222 | 1.6613e-05 | 75.2408 | 75.2407 | 1.3567 | 1.5262e-19
One-stage weighted objective | 1350 | 22.5 | 0 | -3.0825e-19 | 3.0825e-19 | 0.67611 | 5.5553e-06 | 25.001 | 25.001 | 0.44562 | 5.5553e-06 | 25.001 | 25.001 | 0.44562 | 5.5553e-06 | 25.001 | 25.001 | 0.44562 | 1.6666e-05 | 75.003 | 75.003 | 1.3369 | 1.5412e-19
One-stage weighted objective | 1380 | 23 | 0 | -2.9983e-19 | 2.9983e-19 | 0.63445 | 5.6201e-06 | 24.7127 | 24.7127 | -1.2171 | 5.6201e-06 | 24.7127 | 24.7127 | -1.2171 | 5.6201e-06 | 24.7127 | 24.7127 | -1.2171 | 1.686e-05 | 74.1381 | 74.1381 | -3.6514 | 1.4992e-19
One-stage weighted objective | 1410 | 23.5 | 0 | -3.0264e-19 | 3.0264e-19 | 0.59326 | 5.5627e-06 | 24.9681 | 24.9681 | -1.1553 | 5.5627e-06 | 24.9681 | 24.9681 | -1.1553 | 5.5627e-06 | 24.9681 | 24.9681 | -1.1553 | 1.6688e-05 | 74.9042 | 74.9042 | -3.4658 | 1.5132e-19
One-stage weighted objective | 1440 | 24 | 0 | -3.0337e-19 | 3.0337e-19 | 0.55164 | 5.5585e-06 | 24.9867 | 24.9867 | 0.44309 | 5.5585e-06 | 24.9867 | 24.9867 | 0.44309 | 5.5585e-06 | 24.9867 | 24.9867 | 0.44309 | 1.6676e-05 | 74.9601 | 74.9601 | 1.3293 | 1.5168e-19

## PV
Time_sample | Time_h | PV_architecture | PV_available_P_W | PV_command_P_W | PV_Q_command_var | PV_curtailment_W | CentralSolar_Available_P_W | CentralSolar_P_command_W | CentralSolar_Q_command_var | CentralSolar_P_curtailment_W
30 | 0.5 | central | 0 | -3.005e-16 | -1.2289e-07 | 3.005e-16 | 0 | -3.005e-16 | -1.2289e-07 | 3.005e-16
60 | 1 | central | 0 | -3.0206e-16 | -1.2648e-07 | 3.0206e-16 | 0 | -3.0206e-16 | -1.2648e-07 | 3.0206e-16
90 | 1.5 | central | 0 | -3.0385e-16 | -1.3192e-07 | 3.0385e-16 | 0 | -3.0385e-16 | -1.3192e-07 | 3.0385e-16
120 | 2 | central | 0 | -2.9893e-16 | -1.1113e-07 | 2.9893e-16 | 0 | -2.9893e-16 | -1.1113e-07 | 2.9893e-16
150 | 2.5 | central | 0 | -3.0294e-16 | -1.2974e-07 | 3.0294e-16 | 0 | -3.0294e-16 | -1.2974e-07 | 3.0294e-16
180 | 3 | central | 0 | -3.0301e-16 | -1.3257e-07 | 3.0301e-16 | 0 | -3.0301e-16 | -1.3257e-07 | 3.0301e-16
210 | 3.5 | central | 0 | -3.039e-16 | -4.8565e-08 | 3.039e-16 | 0 | -3.039e-16 | -4.8565e-08 | 3.039e-16
240 | 4 | central | 802.831 | -9.6439e-09 | 1.0994e-07 | 802.831 | 802.831 | -9.6439e-09 | 1.0994e-07 | 802.831
270 | 4.5 | central | 3348.1315 | -9.6439e-09 | 1.1385e-07 | 3348.1315 | 3348.1315 | -9.6439e-09 | 1.1385e-07 | 3348.1315
300 | 5 | central | 7612.4905 | -9.6439e-09 | 1.1457e-07 | 7612.4905 | 7612.4905 | -9.6439e-09 | 1.1457e-07 | 7612.4905
330 | 5.5 | central | 16214.673 | 16214.6731 | 1.1483e-07 | 0 | 16214.673 | 16214.6731 | 1.1483e-07 | 0
360 | 6 | central | 32040.6263 | 32040.6264 | 1.0272e-07 | 0 | 32040.6263 | 32040.6264 | 1.0272e-07 | 0
390 | 6.5 | central | 67541.1711 | 67541.1712 | -1.9734e-09 | 0 | 67541.1711 | 67541.1712 | -1.9734e-09 | 0
420 | 7 | central | 81235.982 | 81235.9301 | -1.2881e-07 | 0.05191 | 81235.982 | 81235.9301 | -1.2881e-07 | 0.05191
450 | 7.5 | central | 139783.0917 | 139783.0855 | 8.4091e-09 | 0.006156 | 139783.0917 | 139783.0855 | 8.4091e-09 | 0.006156
480 | 8 | central | 137806.9962 | 137806.9898 | -9.9954e-08 | 0.0064135 | 137806.9962 | 137806.9898 | -9.9954e-08 | 0.0064135
510 | 8.5 | central | 157786.3758 | 157786.3708 | -3.1951e-08 | 0.0049295 | 157786.3758 | 157786.3708 | -3.1951e-08 | 0.0049295
540 | 9 | central | 172443.4812 | 172443.4771 | 4.1747e-08 | 0.0041717 | 172443.4812 | 172443.4771 | 4.1747e-08 | 0.0041717
570 | 9.5 | central | 185006.283 | 185006.2794 | -4.1255e-08 | 0.0035992 | 185006.283 | 185006.2794 | -4.1255e-08 | 0.0035992
600 | 10 | central | 119416.0716 | 119416.0633 | 7.9801e-08 | 0.008337 | 119416.0716 | 119416.0633 | 7.9801e-08 | 0.008337
630 | 10.5 | central | 229745.7421 | 229745.7395 | -1.6521e-07 | 0.002593 | 229745.7421 | 229745.7395 | -1.6521e-07 | 0.002593
660 | 11 | central | 235990.3088 | 235990.3063 | 1.6536e-07 | 0.0024786 | 235990.3088 | 235990.3063 | 1.6536e-07 | 0.0024786
690 | 11.5 | central | 232588.4442 | 232588.4416 | -2.3004e-07 | 0.0025395 | 232588.4442 | 232588.4416 | -2.3004e-07 | 0.0025395
720 | 12 | central | 137662.547 | 137662.5404 | 2.086e-07 | 0.0065691 | 137662.547 | 137662.5404 | 2.086e-07 | 0.0065691
750 | 12.5 | central | 86507.1933 | 86507.1591 | -9.0215e-08 | 0.034235 | 86507.1933 | 86507.1591 | -9.0215e-08 | 0.034235
780 | 13 | central | 63436.078 | 63436.0781 | 1.6314e-08 | 0 | 63436.078 | 63436.0781 | 1.6314e-08 | 0
810 | 13.5 | central | 220843.1249 | 220843.1222 | -3.7992e-08 | 0.0026743 | 220843.1249 | 220843.1222 | -3.7992e-08 | 0.0026743
840 | 14 | central | 219014.5042 | 219014.5014 | 1.2742e-08 | 0.0027436 | 219014.5042 | 219014.5014 | 1.2742e-08 | 0.0027436
870 | 14.5 | central | 209104.7846 | 209104.7818 | 7.743e-08 | 0.0028689 | 209104.7846 | 209104.7818 | 7.743e-08 | 0.0028689
900 | 15 | central | 169589.676 | 169589.6717 | -2.0149e-07 | 0.0043036 | 169589.676 | 169589.6717 | -2.0149e-07 | 0.0043036
930 | 15.5 | central | 108386.1781 | 108386.1656 | 1.6015e-07 | 0.012452 | 108386.1781 | 108386.1656 | 1.6015e-07 | 0.012452
960 | 16 | central | 167971.8118 | 167971.8076 | -9.5815e-09 | 0.004213 | 167971.8118 | 167971.8076 | -9.5815e-09 | 0.004213
990 | 16.5 | central | 124580.4462 | 124580.4381 | -8.3968e-08 | 0.0081356 | 124580.4462 | 124580.4381 | -8.3968e-08 | 0.0081356
1020 | 17 | central | 58867.659 | 33557.8497 | -1.7213e-07 | 25309.8093 | 58867.659 | 33557.8497 | -1.7213e-07 | 25309.8093
1050 | 17.5 | central | 21386.1553 | -9.6439e-09 | -4.7855e-09 | 21386.1553 | 21386.1553 | -9.6439e-09 | -4.7855e-09 | 21386.1553
1080 | 18 | central | 35726.2956 | 9971.3271 | -1.713e-08 | 25754.9686 | 35726.2956 | 9971.3271 | -1.713e-08 | 25754.9686
1110 | 18.5 | central | 34880.4892 | 891.1416 | -1.9932e-07 | 33989.3476 | 34880.4892 | 891.1416 | -1.9932e-07 | 33989.3476
1140 | 19 | central | 14676.3552 | -9.6439e-09 | -1.0993e-10 | 14676.3552 | 14676.3552 | -9.6439e-09 | -1.0993e-10 | 14676.3552
1170 | 19.5 | central | 6556.6442 | -9.6439e-09 | 1.1423e-07 | 6556.6442 | 6556.6442 | -9.6439e-09 | 1.1423e-07 | 6556.6442
1200 | 20 | central | 1478.7101 | -9.6439e-09 | 2.0763e-07 | 1478.7101 | 1478.7101 | -9.6439e-09 | 2.0763e-07 | 1478.7101
1230 | 20.5 | central | 513.8622 | -9.6439e-09 | 1.6422e-07 | 513.8622 | 513.8622 | -9.6439e-09 | 1.6422e-07 | 513.8622
1260 | 21 | central | 0 | -3.0443e-16 | -4.1433e-08 | 3.0443e-16 | 0 | -3.0443e-16 | -4.1433e-08 | 3.0443e-16
1290 | 21.5 | central | 0 | -3.0045e-16 | 4.6563e-08 | 3.0045e-16 | 0 | -3.0045e-16 | 4.6563e-08 | 3.0045e-16
1320 | 22 | central | 0 | -3.0525e-16 | -2.8972e-07 | 3.0525e-16 | 0 | -3.0525e-16 | -2.8972e-07 | 3.0525e-16
1350 | 22.5 | central | 0 | -3.0825e-16 | 1.1933e-07 | 3.0825e-16 | 0 | -3.0825e-16 | 1.1933e-07 | 3.0825e-16
1380 | 23 | central | 0 | -2.9983e-16 | -1.287e-07 | 2.9983e-16 | 0 | -2.9983e-16 | -1.287e-07 | 2.9983e-16
1410 | 23.5 | central | 0 | -3.0264e-16 | -1.2767e-07 | 3.0264e-16 | 0 | -3.0264e-16 | -1.2767e-07 | 3.0264e-16
1440 | 24 | central | 0 | -3.0337e-16 | 2.7854e-08 | 3.0337e-16 | 0 | -3.0337e-16 | 2.7854e-08 | 3.0337e-16

## BESS_P_Q_SOC
Time_sample | Time_h | BESS_P_ch_A_W | BESS_P_ch_B_W | BESS_P_ch_C_W | BESS_P_dis_A_W | BESS_P_dis_B_W | BESS_P_dis_C_W | BESS_P_net_A_W | BESS_P_net_B_W | BESS_P_net_C_W | BESS_P_net_total_W | BESS_Q_A_var | BESS_Q_B_var | BESS_Q_C_var | BESS_Q_total_var | BESS_SOC_pu
30 | 0.5 | 0.0056119 | 0.0056119 | 0.0056119 | 24749.1569 | 24749.1569 | 24749.1569 | 24749.1513 | 24749.1513 | 24749.1513 | 74247.4539 | -3216.3592 | -3216.3592 | -3216.3592 | -9649.0777 | 0.5
60 | 1 | 0.0055733 | 0.0055733 | 0.0055733 | 24920.3923 | 24920.3923 | 24920.3923 | 24920.3867 | 24920.3867 | 24920.3867 | 74761.1601 | -2355.2186 | -2355.2186 | -2355.2186 | -7065.6558 | 0.45875
90 | 1.5 | 0.005534 | 0.005534 | 0.005534 | 25097.351 | 25097.351 | 25097.351 | 25097.3455 | 25097.3455 | 25097.3455 | 75292.0364 | -550.0997 | -550.0997 | -550.0997 | -1650.299 | 0.41722
120 | 2 | 0.0056487 | 0.0056487 | 0.0056487 | 24587.8146 | 24587.8146 | 24587.8146 | 24587.809 | 24587.809 | 24587.809 | 73763.4269 | -4612.2139 | -4612.2139 | -4612.2139 | -13836.6418 | 0.37539
150 | 2.5 | 0.0055539 | 0.0055539 | 0.0055539 | 25007.3557 | 25007.3557 | 25007.3557 | 25007.3502 | 25007.3502 | 25007.3502 | 75022.0505 | -2131.2325 | -2131.2325 | -2131.2325 | -6393.6974 | 0.33441
180 | 3 | 0.0055521 | 0.0055521 | 0.0055521 | 25015.6901 | 25015.6901 | 25015.6901 | 25015.6846 | 25015.6846 | 25015.6846 | 75047.0538 | -1819.1103 | -1819.1103 | -1819.1103 | -5457.3309 | 0.29273
210 | 3.5 | 0.0055327 | 0.0055327 | 0.0055327 | 25103.1402 | 25103.1402 | 25103.1402 | 25103.1347 | 25103.1347 | 25103.1347 | 75309.404 | 440.3522 | 440.3522 | 440.3522 | 1321.0567 | 0.25104
240 | 4 | -9.1131e-09 | -9.1131e-09 | -9.1131e-09 | 802.831 | 802.831 | 802.831 | 802.831 | 802.831 | 802.831 | 2408.4931 | -23075.8293 | -23075.8293 | -23075.8293 | -69227.4878 | 0.2092
270 | 4.5 | -9.1326e-09 | -9.1326e-09 | -9.1326e-09 | 3348.1315 | 3348.1315 | 3348.1315 | 3348.1315 | 3348.1315 | 3348.1315 | 10044.3945 | -22930.053 | -22930.053 | -22930.053 | -68790.159 | 0.20786
300 | 5 | -9.1623e-09 | -9.1623e-09 | -9.1623e-09 | 7612.4905 | 7612.4905 | 7612.4905 | 7612.4905 | 7612.4905 | 7612.4905 | 22837.4716 | -22180.5804 | -22180.5804 | -22180.5804 | -66541.7412 | 0.20228
330 | 5.5 | 6.8199e-10 | 6.8199e-10 | 6.8199e-10 | 3.6961e-09 | 3.6961e-09 | 3.6961e-09 | 3.0141e-09 | 3.0141e-09 | 3.0141e-09 | 9.0423e-09 | -22627.2666 | -22627.2666 | -22627.2666 | -67881.7998 | 0.18959
360 | 6 | 6.8196e-10 | 6.8196e-10 | 6.8196e-10 | 3.6961e-09 | 3.6961e-09 | 3.6961e-09 | 3.0141e-09 | 3.0141e-09 | 3.0141e-09 | 9.0423e-09 | -21205.6576 | -21205.6576 | -21205.6576 | -63616.9727 | 0.18959
390 | 6.5 | 6.8049e-10 | 6.8049e-10 | 6.8049e-10 | 3.6946e-09 | 3.6946e-09 | 3.6946e-09 | 3.0141e-09 | 3.0141e-09 | 3.0141e-09 | 9.0424e-09 | -10424.4359 | -10424.4359 | -10424.4359 | -31273.3076 | 0.18959
420 | 7 | 2670.4061 | 2670.4061 | 2670.4061 | 0.05201 | 0.05201 | 0.05201 | -2670.3541 | -2670.3541 | -2670.3541 | -8011.0622 | -5492.5743 | -5492.5743 | -5492.5743 | -16477.7229 | 0.18959
450 | 7.5 | 22201.0333 | 22201.0333 | 22201.0333 | 0.006256 | 0.006256 | 0.006256 | -22201.0271 | -22201.0271 | -22201.0271 | -66603.0812 | -4713.5651 | -4713.5651 | -4713.5651 | -14140.6952 | 0.1932
480 | 8 | 21323.2705 | 21323.2705 | 21323.2705 | 0.0065135 | 0.0065135 | 0.0065135 | -21323.264 | -21323.264 | -21323.264 | -63969.7921 | -2285.1003 | -2285.1003 | -2285.1003 | -6855.3008 | 0.22317
510 | 8.5 | 27614.7986 | 27614.7986 | 27614.7986 | 0.0050295 | 0.0050295 | 0.0050295 | -27614.7936 | -27614.7936 | -27614.7936 | -82844.3808 | -318.2627 | -318.2627 | -318.2627 | -954.7882 | 0.25196
540 | 9 | 32514.1253 | 32514.1253 | 32514.1253 | 0.0042716 | 0.0042716 | 0.0042716 | -32514.1211 | -32514.1211 | -32514.1211 | -97542.3632 | -553.9047 | -553.9047 | -553.9047 | -1661.7141 | 0.28924
570 | 9.5 | 37545.6455 | 37545.6455 | 37545.6455 | 0.0036992 | 0.0036992 | 0.0036992 | -37545.6418 | -37545.6418 | -37545.6418 | -112636.9254 | -5441.9203 | -5441.9203 | -5441.9203 | -16325.761 | 0.33313
600 | 10 | 16461.8231 | 16461.8231 | 16461.8231 | 0.008437 | 0.008437 | 0.008437 | -16461.8146 | -16461.8146 | -16461.8146 | -49385.4439 | -7148.1316 | -7148.1316 | -7148.1316 | -21444.3949 | 0.38382
630 | 10.5 | 51573.5583 | 51573.5583 | 51573.5583 | 0.002693 | 0.002693 | 0.002693 | -51573.5556 | -51573.5556 | -51573.5556 | -154720.6668 | 443.5515 | 443.5515 | 443.5515 | 1330.6544 | 0.40604
660 | 11 | 53863.0315 | 53863.0315 | 53863.0315 | 0.0025786 | 0.0025786 | 0.0025786 | -53863.0289 | -53863.0289 | -53863.0289 | -161589.0866 | 438.857 | 438.857 | 438.857 | 1316.5711 | 0.47566
690 | 11.5 | 52619.2182 | 52619.2182 | 52619.2182 | 0.0026395 | 0.0026395 | 0.0026395 | -52619.2155 | -52619.2155 | -52619.2155 | -157857.6466 | 445.1653 | 445.1653 | 445.1653 | 1335.496 | 0.54838
720 | 12 | 20825.6085 | 20825.6085 | 20825.6085 | 0.0066691 | 0.0066691 | 0.0066691 | -20825.6019 | -20825.6019 | -20825.6019 | -62476.8056 | 448.0104 | 448.0104 | 448.0104 | 1344.0312 | 0.61941
750 | 12.5 | 4045.1634 | 4045.1634 | 4045.1634 | 0.034335 | 0.034335 | 0.034335 | -4045.129 | -4045.129 | -4045.129 | -12135.3871 | -1766.6806 | -1766.6806 | -1766.6806 | -5300.0418 | 0.64753
780 | 13 | 6.8172e-10 | 6.8172e-10 | 6.8172e-10 | 3.6958e-09 | 3.6958e-09 | 3.6958e-09 | 3.0141e-09 | 3.0141e-09 | 3.0141e-09 | 9.0424e-09 | -12053.9725 | -12053.9725 | -12053.9725 | -36161.9176 | 0.65299
810 | 13.5 | 50062.0747 | 50062.0747 | 50062.0747 | 0.0027743 | 0.0027743 | 0.0027743 | -50062.072 | -50062.072 | -50062.072 | -150186.2159 | -6649.9979 | -6649.9979 | -6649.9979 | -19949.9936 | 0.65299
840 | 14 | 48843.2611 | 48843.2611 | 48843.2611 | 0.0028436 | 0.0028436 | 0.0028436 | -48843.2583 | -48843.2583 | -48843.2583 | -146529.7748 | -5561.0064 | -5561.0064 | -5561.0064 | -16683.0192 | 0.72057
870 | 14.5 | 46781.3269 | 46781.3269 | 46781.3269 | 0.0029689 | 0.0029689 | 0.0029689 | -46781.3239 | -46781.3239 | -46781.3239 | -140343.9717 | -9244.0679 | -9244.0679 | -9244.0679 | -27732.2037 | 0.78651
900 | 15 | 31540.1057 | 31540.1057 | 31540.1057 | 0.0044036 | 0.0044036 | 0.0044036 | -31540.1013 | -31540.1013 | -31540.1013 | -94620.3039 | 450.74 | 450.74 | 450.74 | 1352.2201 | 0.84967
930 | 15.5 | 11065.5075 | 11065.5075 | 11065.5075 | 0.012552 | 0.012552 | 0.012552 | -11065.4949 | -11065.4949 | -11065.4949 | -33196.4847 | 164.3673 | 164.3673 | 164.3673 | 493.1019 | 0.89225
960 | 16 | 32202.4198 | 32202.4198 | 32202.4198 | 0.004313 | 0.004313 | 0.004313 | -32202.4155 | -32202.4155 | -32202.4155 | -96607.2465 | -6136.5779 | -6136.5779 | -6136.5779 | -18409.7336 | 0.90718
990 | 16.5 | 16864.4787 | 16864.4787 | 16864.4787 | 0.0082356 | 0.0082356 | 0.0082356 | -16864.4705 | -16864.4705 | -16864.4705 | -50593.4115 | -4322.7991 | -4322.7991 | -4322.7991 | -12968.3974 | 0.95066
1020 | 17 | 0.010169 | 0.010169 | 0.010169 | 13657.5776 | 13657.5776 | 13657.5776 | 13657.5674 | 13657.5674 | 13657.5674 | 40972.7023 | 440.7915 | 440.7915 | 440.7915 | 1322.3746 | 0.97343
1050 | 17.5 | -9.1951e-09 | -9.1951e-09 | -9.1951e-09 | 21386.1554 | 21386.1554 | 21386.1554 | 21386.1554 | 21386.1554 | 21386.1554 | 64158.4661 | -11467.8407 | -11467.8407 | -11467.8407 | -34403.5221 | 0.95066
1080 | 18 | 0.0066889 | 0.0066889 | 0.0066889 | 20764.0121 | 20764.0121 | 20764.0121 | 20764.0054 | 20764.0054 | 20764.0054 | 62292.0161 | -5187.797 | -5187.797 | -5187.797 | -15563.391 | 0.91502
1110 | 18.5 | 0.0056838 | 0.0056838 | 0.0056838 | 24435.8967 | 24435.8967 | 24435.8967 | 24435.891 | 24435.891 | 24435.891 | 73307.6731 | 442.518 | 442.518 | 442.518 | 1327.5541 | 0.88041
1140 | 19 | -9.1838e-09 | -9.1838e-09 | -9.1838e-09 | 14676.3553 | 14676.3553 | 14676.3553 | 14676.3553 | 14676.3553 | 14676.3553 | 44029.0659 | -18711.6906 | -18711.6906 | -18711.6906 | -56135.0718 | 0.83969
1170 | 19.5 | -9.157e-09 | -9.157e-09 | -9.157e-09 | 6556.6443 | 6556.6443 | 6556.6443 | 6556.6443 | 6556.6443 | 6556.6443 | 19669.9329 | -22256.02 | -22256.02 | -22256.02 | -66768.0599 | 0.81523
1200 | 20 | -9.1141e-09 | -9.1141e-09 | -9.1141e-09 | 1478.7101 | 1478.7101 | 1478.7101 | 1478.7101 | 1478.7101 | 1478.7101 | 4436.1304 | -22370.0095 | -22370.0095 | -22370.0095 | -67110.0285 | 0.8043
1230 | 20.5 | -9.115e-09 | -9.115e-09 | -9.115e-09 | 513.8622 | 513.8622 | 513.8622 | 513.8622 | 513.8622 | 513.8622 | 1541.5865 | -22446.0534 | -22446.0534 | -22446.0534 | -67338.1601 | 0.80183
1260 | 21 | 0.0055412 | 0.0055412 | 0.0055412 | 25064.6865 | 25064.6865 | 25064.6865 | 25064.6809 | 25064.6809 | 25064.6809 | 75194.0428 | 445.4751 | 445.4751 | 445.4751 | 1336.4252 | 0.80098
1290 | 21.5 | 0.0056066 | 0.0056066 | 0.0056066 | 24772.5815 | 24772.5815 | 24772.5815 | 24772.5759 | 24772.5759 | 24772.5759 | 74317.7276 | 74.1129 | 74.1129 | 74.1129 | 222.3387 | 0.7592
1320 | 22 | 0.0055378 | 0.0055378 | 0.0055378 | 25080.2514 | 25080.2514 | 25080.2514 | 25080.2459 | 25080.2459 | 25080.2459 | 75240.7376 | 452.2216 | 452.2216 | 452.2216 | 1356.6647 | 0.71791
1350 | 22.5 | 0.0055553 | 0.0055553 | 0.0055553 | 25001.011 | 25001.011 | 25001.011 | 25001.0055 | 25001.0055 | 25001.0055 | 75003.0164 | 445.6248 | 445.6248 | 445.6248 | 1336.8745 | 0.67611
1380 | 23 | 0.0056201 | 0.0056201 | 0.0056201 | 24712.6947 | 24712.6947 | 24712.6947 | 24712.6891 | 24712.6891 | 24712.6891 | 74138.0673 | -1217.1257 | -1217.1257 | -1217.1257 | -3651.3772 | 0.63445
1410 | 23.5 | 0.0055627 | 0.0055627 | 0.0055627 | 24968.0728 | 24968.0728 | 24968.0728 | 24968.0673 | 24968.0673 | 24968.0673 | 74904.2018 | -1155.2633 | -1155.2633 | -1155.2633 | -3465.7899 | 0.59326
1440 | 24 | 0.0055585 | 0.0055585 | 0.0055585 | 24986.6906 | 24986.6906 | 24986.6906 | 24986.685 | 24986.685 | 24986.685 | 74960.0551 | 443.0861 | 443.0861 | 443.0861 | 1329.2584 | 0.55164

## Gross_load
Time_sample | Time_h | Load_P_A_kW | Load_P_B_kW | Load_P_C_kW | Load_P_total_kW | Load_Q_A_kvar | Load_Q_B_kvar | Load_Q_C_kvar | Load_Q_total_kvar
30 | 0.5 | 6.775 | 3.133 | 5.756 | 15.664 | 1.3204 | 2.1718 | 2.3865 | 5.8786
60 | 1 | 4.538 | 3.063 | 3.909 | 11.51 | 1.4445 | 2.3671 | 0.72966 | 4.5412
90 | 1.5 | 4.498 | 3.333 | 2.547 | 10.378 | 1.3938 | 2.7087 | 1.5902 | 5.6928
120 | 2 | 4.798 | 2.203 | 4.027 | 11.028 | 1.7734 | 1.2787 | 3.4631 | 6.5153
150 | 2.5 | 4.468 | 2.313 | 2.657 | 9.438 | 1.3559 | 1.418 | 1.7294 | 4.5032
180 | 3 | 4.548 | 3.263 | 2.197 | 10.008 | 1.4571 | 2.6202 | 1.1473 | 5.2245
210 | 3.5 | 4.868 | 3.853 | 3.917 | 12.638 | 1.8621 | 3.3668 | 3.3239 | 8.5528
240 | 4 | 4.058 | 3.143 | 3.207 | 10.408 | 0.837 | 2.4683 | 2.4254 | 5.7307
270 | 4.5 | 4.788 | 2.913 | 1.597 | 9.298 | 1.7608 | 2.1772 | 0.38797 | 4.326
300 | 5 | 4.998 | 2.593 | 2.847 | 10.438 | 2.0266 | 1.7723 | 1.9698 | 5.7687
330 | 5.5 | 4.758 | 3.343 | 3.287 | 11.388 | 1.7228 | 2.7214 | 2.5267 | 6.9709
360 | 6 | 2.033 | 3.223 | 6.205 | 11.461 | 1.2546 | 2.6075 | 1.6028 | 5.465
390 | 6.5 | 6.7234 | 3.063 | 2.537 | 12.3234 | 1.7581 | 2.405 | 1.8053 | 5.9684
420 | 7 | 7.1512 | 4.409 | 2.24 | 13.8002 | 1.7449 | 2.2264 | 0.85054 | 4.8218
450 | 7.5 | 3.593 | 3.923 | 10.0461 | 17.5621 | 1.2181 | 2.3777 | 1.9475 | 5.5432
480 | 8 | 7.721 | 6.845 | 15.9545 | 30.5205 | 1.4863 | 2.4348 | 3.5644 | 7.4855
510 | 8.5 | 7.788 | 5.53 | 10.0135 | 23.3315 | 1.9794 | 1.9955 | 2.02 | 5.995
540 | 9 | 10.8782 | 12.8862 | 11.283 | 35.0474 | 2.1381 | 2.7218 | 3.081 | 7.9408
570 | 9.5 | 9.5751 | 15.5691 | 14.327 | 39.4712 | 2.0312 | 5.0343 | 1.8787 | 8.9442
600 | 10 | 9.5641 | 10.1356 | 19.795 | 39.4947 | 1.2172 | 2.3869 | 2.1623 | 5.7663
630 | 10.5 | 15.6601 | 14.2976 | 12.958 | 42.9157 | 1.4742 | 1.687 | 1.2818 | 4.443
660 | 11 | 21.833 | 16.3095 | 11.908 | 50.0505 | 2.7126 | 1.8769 | 2.0759 | 6.6654
690 | 11.5 | 11.078 | 12.3535 | 9 | 32.4315 | 1.3743 | 3.1469 | 2.4264 | 6.9476
720 | 12 | 8.631 | 8.175 | 6.597 | 23.403 | 2.2513 | 2.5673 | 1.8946 | 6.7132
750 | 12.5 | 12.625 | 6.751 | 5.71 | 25.086 | 1.5686 | 2.0723 | 3.2609 | 6.9018
780 | 13 | 13.977 | 19.161 | 12.795 | 45.933 | 1.3981 | 3.6862 | 1.7488 | 6.8331
810 | 13.5 | 10.973 | 18.6495 | 6.462 | 36.0845 | 2.8153 | 2.8039 | 1.6396 | 7.2588
840 | 14 | 17.657 | 15.4425 | 7.937 | 41.0365 | 2.278 | 2.7179 | 2.7962 | 7.7921
870 | 14.5 | 16.914 | 13.333 | 4.956 | 35.203 | 2.5403 | 2.6265 | 2.1787 | 7.3456
900 | 15 | 15.948 | 13.766 | 9.496 | 39.21 | 1.757 | 3.8163 | 2.3896 | 7.9629
930 | 15.5 | 10.829 | 8.084 | 7.0115 | 25.9245 | 1.7979 | 1.6523 | 1.751 | 5.2011
960 | 16 | 17.599 | 19.7 | 7.951 | 45.25 | 0.72461 | 2.7144 | 1.2898 | 4.7288
990 | 16.5 | 19.767 | 10.8465 | 11.079 | 41.6925 | 1.3098 | 2.0389 | 2.6227 | 5.9715
1020 | 17 | 22.562 | 16.272 | 21.8271 | 60.6611 | 1.9223 | 3.6665 | 2.9859 | 8.5747
1050 | 17.5 | 23.5674 | 23.0585 | 13.754 | 60.3799 | 0.98357 | 2.2826 | 2.3508 | 5.617
1080 | 18 | 29.3454 | 12.047 | 9.219 | 50.6114 | 2.2778 | 2.0299 | 1.4388 | 5.7465
1110 | 18.5 | 24.223 | 21.301 | 16.263 | 61.787 | 1.0162 | 3.9074 | 2.513 | 7.4365
1140 | 19 | 14.979 | 16.617 | 17.9025 | 49.4985 | 1.4078 | 2.858 | 1.4769 | 5.7426
1170 | 19.5 | 15.8125 | 9.124 | 15.4985 | 40.435 | 2.0975 | 0.70568 | 3.0132 | 5.8164
1200 | 20 | 15.6635 | 19.309 | 21.427 | 56.3995 | 1.8603 | 2.2009 | 2.329 | 6.3902
1230 | 20.5 | 12.8425 | 18.8375 | 15.719 | 47.399 | 2.004 | 2.6921 | 2.2048 | 6.9009
1260 | 21 | 12.1055 | 11.478 | 10.5285 | 34.112 | 1.1207 | 1.5563 | 1.6423 | 4.3193
1290 | 21.5 | 15.135 | 18.5825 | 11.3285 | 45.046 | 2.2166 | 2.9888 | 2.0799 | 7.2853
1320 | 22 | 15.3522 | 12.551 | 11.381 | 39.2842 | 0.54529 | 3.4741 | 1.7075 | 5.7269
1350 | 22.5 | 11.6285 | 11.489 | 10.959 | 34.0765 | 1.4247 | 1.0862 | 1.3822 | 3.8931
1380 | 23 | 9.0495 | 14.848 | 11.0385 | 34.936 | 1.8655 | 1.7882 | 1.274 | 4.9277
1410 | 23.5 | 10.472 | 6.5255 | 9.089 | 26.0865 | 0.73307 | 1.8673 | 1.3155 | 3.9159
1440 | 24 | 9.898 | 6.9875 | 10.268 | 27.1535 | 2.184 | 3.3179 | 1.9283 | 7.4302

## Central_bus_voltage
Time_sample | Time_h | Bus | DSS_V_A_V | DSS_V_B_V | DSS_V_C_V | DSS_angle_A_deg | DSS_angle_B_deg | DSS_angle_C_deg | DSS_V_A_pu | DSS_V_B_pu | DSS_V_C_pu | DSS_V_max_pu | DSS_V_min_pu
30 | 0.5 | feeder2_1818 | 252.8549 | 254.034 | 252.0945 | -29.1249 | -148.7112 | 91.2332 | 1.0949 | 1.1 | 1.0916 | 1.1 | 1.0916
60 | 1 | feeder2_1818 | 254.0342 | 253.6533 | 252.842 | -29.0144 | -148.6776 | 91.0242 | 1.1 | 1.0984 | 1.0948 | 1.1 | 1.0948
90 | 1.5 | feeder2_1818 | 253.9794 | 253.5692 | 254.0337 | -28.9901 | -148.8875 | 91.0267 | 1.0998 | 1.098 | 1.1 | 1.1 | 1.098
120 | 2 | feeder2_1818 | 252.0981 | 254.0332 | 252.6944 | -28.8537 | -148.8211 | 91.517 | 1.0916 | 1.1 | 1.0942 | 1.1 | 1.0916
150 | 2.5 | feeder2_1818 | 253.2538 | 254.0314 | 253.8127 | -28.9293 | -148.9032 | 91.2304 | 1.0966 | 1.1 | 1.099 | 1.1 | 1.0966
180 | 3 | feeder2_1818 | 253.771 | 253.3478 | 254.0368 | -28.8985 | -148.836 | 91.0809 | 1.0989 | 1.097 | 1.1 | 1.1 | 1.097
210 | 3.5 | feeder2_1818 | 253.9703 | 254.0352 | 253.603 | -29.1272 | -148.9362 | 91.0544 | 1.0997 | 1.1 | 1.0981 | 1.1 | 1.0981
240 | 4 | feeder2_1818 | 243.4441 | 243.4863 | 243.0064 | -28.6744 | -148.4829 | 91.5079 | 1.0541 | 1.0543 | 1.0522 | 1.0543 | 1.0522
270 | 4.5 | feeder2_1818 | 243.8496 | 243.6192 | 244.9118 | -28.3872 | -148.4752 | 91.493 | 1.0559 | 1.0549 | 1.0605 | 1.0605 | 1.0549
300 | 5 | feeder2_1818 | 244.753 | 245.5492 | 245.6132 | -28.344 | -148.3779 | 91.7567 | 1.0598 | 1.0633 | 1.0635 | 1.0635 | 1.0598
330 | 5.5 | feeder2_1818 | 244.2686 | 244.6955 | 244.6416 | -28.4335 | -148.3886 | 91.682 | 1.0577 | 1.0596 | 1.0593 | 1.0596 | 1.0577
360 | 6 | feeder2_1818 | 247.4523 | 246.1455 | 245.1896 | -28.3708 | -147.9926 | 91.5607 | 1.0715 | 1.0658 | 1.0617 | 1.0715 | 1.0617
390 | 6.5 | feeder2_1818 | 250.6886 | 251.593 | 251.7226 | -28.5504 | -148.5016 | 91.6587 | 1.0855 | 1.0894 | 1.09 | 1.09 | 1.0855
420 | 7 | feeder2_1818 | 250.5879 | 252.7125 | 254.0341 | -28.7572 | -148.9684 | 91.4676 | 1.0851 | 1.0943 | 1.1 | 1.1 | 1.0851
450 | 7.5 | feeder2_1818 | 254.0313 | 253.1721 | 250.9556 | -28.9766 | -148.4303 | 91.0201 | 1.1 | 1.0963 | 1.0867 | 1.1 | 1.0867
480 | 8 | feeder2_1818 | 253.8826 | 254.034 | 249.6802 | -29.386 | -148.5571 | 90.8603 | 1.0993 | 1.1 | 1.0811 | 1.1 | 1.0811
510 | 8.5 | feeder2_1818 | 253.9361 | 254.0335 | 252.3495 | -29.2468 | -148.8439 | 90.8352 | 1.0996 | 1.1 | 1.0927 | 1.1 | 1.0927
540 | 9 | feeder2_1818 | 254.0346 | 252.2549 | 252.5002 | -29.0729 | -149.0377 | 90.7067 | 1.1 | 1.0923 | 1.0934 | 1.1 | 1.0923
570 | 9.5 | feeder2_1818 | 254.0336 | 249.7925 | 250.736 | -28.7994 | -148.5412 | 90.6378 | 1.1 | 1.0816 | 1.0857 | 1.1 | 1.0816
600 | 10 | feeder2_1818 | 254.0349 | 252.6032 | 246.5999 | -29.385 | -148.0548 | 90.7646 | 1.1 | 1.0938 | 1.0678 | 1.1 | 1.0678
630 | 10.5 | feeder2_1818 | 252.0904 | 252.9041 | 252.6493 | -29.4582 | -149.3681 | 90.6982 | 1.0916 | 1.0951 | 1.094 | 1.0951 | 1.0916
660 | 11 | feeder2_1818 | 251.1143 | 250.5476 | 253.9324 | -29.2064 | -149.7899 | 90.5668 | 1.0874 | 1.0849 | 1.0996 | 1.0996 | 1.0849
690 | 11.5 | feeder2_1818 | 253.7223 | 251.6606 | 253.479 | -29.1307 | -149.2592 | 90.6335 | 1.0986 | 1.0897 | 1.0976 | 1.0986 | 1.0897
720 | 12 | feeder2_1818 | 253.9351 | 253.1907 | 253.3032 | -29.1129 | -149.0339 | 90.7923 | 1.0996 | 1.0963 | 1.0968 | 1.0996 | 1.0963
750 | 12.5 | feeder2_1818 | 250.5069 | 253.921 | 254.0352 | -29.2209 | -149.362 | 91.4521 | 1.0847 | 1.0995 | 1.1 | 1.1 | 1.0847
780 | 13 | feeder2_1818 | 248.8705 | 247.0236 | 250.7333 | -28.5288 | -148.9809 | 91.152 | 1.0776 | 1.0696 | 1.0857 | 1.0857 | 1.0696
810 | 13.5 | feeder2_1818 | 251.6252 | 247.204 | 254.0321 | -28.2514 | -149.3158 | 90.8079 | 1.0896 | 1.0704 | 1.1 | 1.1 | 1.0704
840 | 14 | feeder2_1818 | 248.6447 | 250.4377 | 254.0334 | -28.7911 | -149.5327 | 91.3494 | 1.0767 | 1.0844 | 1.1 | 1.1 | 1.0767
870 | 14.5 | feeder2_1818 | 246.9244 | 249.6372 | 254.0341 | -28.5604 | -149.48 | 91.6936 | 1.0692 | 1.081 | 1.1 | 1.1 | 1.0692
900 | 15 | feeder2_1818 | 250.7643 | 252.4653 | 253.7701 | -29.4264 | -149.5281 | 90.9758 | 1.0858 | 1.0932 | 1.0989 | 1.0989 | 1.0858
930 | 15.5 | feeder2_1818 | 252.5602 | 253.1701 | 254.0339 | -29.1299 | -149.2904 | 90.9108 | 1.0936 | 1.0963 | 1.1 | 1.1 | 1.0936
960 | 16 | feeder2_1818 | 250.0941 | 248.1509 | 254.0307 | -28.6462 | -149.524 | 90.9807 | 1.0829 | 1.0745 | 1.1 | 1.1 | 1.0745
990 | 16.5 | feeder2_1818 | 246.7236 | 254.0348 | 252.911 | -29.5143 | -149.5646 | 91.7228 | 1.0683 | 1.1 | 1.0951 | 1.1 | 1.0683
1020 | 17 | feeder2_1818 | 249.9135 | 252.4072 | 250.9848 | -29.8839 | -149.4851 | 90.6638 | 1.0822 | 1.093 | 1.0868 | 1.093 | 1.0822
1050 | 17.5 | feeder2_1818 | 248.1702 | 246.2095 | 251.2841 | -28.583 | -149.3567 | 91.1104 | 1.0746 | 1.0661 | 1.0881 | 1.0881 | 1.0661
1080 | 18 | feeder2_1818 | 246.276 | 253.1598 | 254.0333 | -29.345 | -149.6569 | 91.7161 | 1.0664 | 1.0962 | 1.1 | 1.1 | 1.0664
1110 | 18.5 | feeder2_1818 | 251.9386 | 249.8663 | 252.8782 | -29.3974 | -149.6107 | 90.4114 | 1.0909 | 1.082 | 1.095 | 1.095 | 1.082
1140 | 19 | feeder2_1818 | 246.7185 | 246.2149 | 244.967 | -28.7773 | -148.3982 | 91.2523 | 1.0683 | 1.0661 | 1.0607 | 1.0683 | 1.0607
1170 | 19.5 | feeder2_1818 | 242.7426 | 245.5824 | 242.495 | -28.9488 | -148.6031 | 91.585 | 1.0511 | 1.0634 | 1.05 | 1.0634 | 1.05
1200 | 20 | feeder2_1818 | 243.0396 | 240.2356 | 240.7013 | -28.9127 | -148.86 | 90.6954 | 1.0524 | 1.0403 | 1.0423 | 1.0524 | 1.0403
1230 | 20.5 | feeder2_1818 | 242.8364 | 239.2352 | 242.1353 | -28.6586 | -148.9621 | 90.7277 | 1.0515 | 1.0359 | 1.0485 | 1.0515 | 1.0359
1260 | 21 | feeder2_1818 | 252.4407 | 253.4531 | 253.2209 | -29.328 | -149.3245 | 90.841 | 1.0931 | 1.0975 | 1.0965 | 1.0975 | 1.0931
1290 | 21.5 | feeder2_1818 | 252.1844 | 250.2297 | 254.0315 | -29.001 | -149.6125 | 90.5685 | 1.092 | 1.0835 | 1.1 | 1.1 | 1.0835
1320 | 22 | feeder2_1818 | 250.759 | 253.3752 | 253.626 | -29.5633 | -149.4361 | 91.0296 | 1.0858 | 1.0971 | 1.0982 | 1.0982 | 1.0858
1350 | 22.5 | feeder2_1818 | 253.1312 | 252.5772 | 253.3516 | -29.1873 | -149.3175 | 90.6504 | 1.0961 | 1.0937 | 1.097 | 1.097 | 1.0937
1380 | 23 | feeder2_1818 | 254.035 | 249.9273 | 253.743 | -28.7509 | -149.2742 | 90.4339 | 1.1 | 1.0822 | 1.0987 | 1.1 | 1.0822
1410 | 23.5 | feeder2_1818 | 252.7495 | 254.0325 | 252.4756 | -29.3369 | -148.9844 | 91.0253 | 1.0944 | 1.1 | 1.0933 | 1.1 | 1.0933
1440 | 24 | feeder2_1818 | 253.5383 | 253.6839 | 252.432 | -29.3496 | -148.9203 | 90.7879 | 1.0979 | 1.0985 | 1.0931 | 1.0985 | 1.0931

## Feeder_head_PQI
Time_sample | Time_h | Feeder_line | DSS_P_A_kW_raw | DSS_P_B_kW_raw | DSS_P_C_kW_raw | DSS_Q_A_kvar_raw | DSS_Q_B_kvar_raw | DSS_Q_C_kvar_raw | DSS_I_A_A | DSS_I_B_A | DSS_I_C_A | DSS_P_total_kW_raw | DSS_Q_total_kvar_raw | Feeder_P_A_kW_import_positive | Feeder_Q_A_kvar_import_positive | Feeder_P_B_kW_import_positive | Feeder_Q_B_kvar_import_positive | Feeder_P_C_kW_import_positive | Feeder_Q_C_kvar_import_positive | Feeder_P_total_kW_import_positive | Feeder_Q_total_kvar_import_positive | Feeder_import_kW | Feeder_export_kW
30 | 0.5 | feeder2_line1 | -16.6617 | -20.8379 | -18.0479 | 4.9623 | 6.0967 | 6.2752 | 70.0343 | 87.4645 | 76.9855 | -55.5475 | 17.3342 | -16.6617 | 4.9623 | -20.8379 | 6.0967 | -18.0479 | 6.2752 | -55.5475 | 17.3342 | 0 | 55.5475
60 | 1 | feeder2_line1 | -19.316 | -21.1414 | -20.0694 | 4.2985 | 5.4988 | 3.4855 | 79.7015 | 87.9927 | 82.0307 | -60.5268 | 13.2828 | -19.316 | 4.2985 | -21.1414 | 5.4988 | -20.0694 | 3.4855 | -60.5268 | 13.2828 | 0 | 60.5268
90 | 1.5 | feeder2_line1 | -19.5631 | -21.0876 | -21.8459 | 2.4907 | 4.0493 | 2.7302 | 79.4078 | 86.4767 | 88.6435 | -62.4966 | 9.2701 | -19.5631 | 2.4907 | -21.0876 | 4.0493 | -21.8459 | 2.7302 | -62.4966 | 9.2701 | 0 | 62.4966
120 | 2 | feeder2_line1 | -18.8535 | -21.6389 | -19.8009 | 6.9673 | 6.3967 | 9.03 | 80.9878 | 90.9024 | 87.7121 | -60.2933 | 22.394 | -18.8535 | 6.9673 | -21.6389 | 6.3967 | -19.8009 | 9.03 | -60.2933 | 22.394 | 0 | 60.2933
150 | 2.5 | feeder2_line1 | -19.5489 | -21.9859 | -21.6289 | 4.017 | 4.1031 | 4.5058 | 80.3773 | 90.0692 | 88.9791 | -63.1637 | 12.6259 | -19.5489 | 4.017 | -21.9859 | 4.1031 | -21.6289 | 4.5058 | -63.1637 | 12.6259 | 0 | 63.1637
180 | 3 | feeder2_line1 | -19.4278 | -21.072 | -22.1082 | 3.8389 | 5.2067 | 3.4763 | 79.7559 | 87.4293 | 90.118 | -62.608 | 12.5218 | -19.4278 | 3.8389 | -21.072 | 5.2067 | -22.1082 | 3.4763 | -62.608 | 12.5218 | 0 | 62.608
210 | 3.5 | feeder2_line1 | -19.2096 | -20.5369 | -20.4846 | 2.0147 | 3.8213 | 3.7544 | 77.7683 | 84.1256 | 83.869 | -60.2311 | 9.5904 | -19.2096 | 2.0147 | -20.5369 | 3.8213 | -20.4846 | 3.7544 | -60.2311 | 9.5904 | 0 | 60.2311
240 | 4 | feeder2_line1 | 4.1872 | 3.1061 | 3.1768 | 24.3726 | 26.1925 | 26.1942 | 99.9851 | 106.6659 | 106.7071 | 10.4701 | 76.7592 | 4.1872 | 24.3726 | 3.1061 | 26.1925 | 3.1768 | 26.1942 | 10.4701 | 76.7592 | 10.4701 | 0
270 | 4.5 | feeder2_line1 | 2.4832 | 0.27335 | -1.1054 | 25.2722 | 25.7724 | 23.6771 | 102.6778 | 104.2133 | 95.8048 | 1.6511 | 74.7217 | 2.4832 | 25.2722 | 0.27335 | 25.7724 | -1.1054 | 23.6771 | 1.6511 | 74.7217 | 1.6511 | 0
300 | 5 | feeder2_line1 | -1.6121 | -4.3406 | -4.0022 | 24.8546 | 24.528 | 24.7509 | 100.6868 | 100.6808 | 101.3451 | -9.9549 | 74.1336 | -1.6121 | 24.8546 | -4.3406 | 24.528 | -4.0022 | 24.7509 | -9.9549 | 74.1336 | 0 | 9.9549
330 | 5.5 | feeder2_line1 | 0.3416 | -1.3313 | -1.3467 | 24.9431 | 26.0452 | 25.833 | 100.8515 | 105.4455 | 104.5885 | -2.3365 | 76.8213 | 0.3416 | 24.9431 | -1.3313 | 26.0452 | -1.3467 | 25.833 | -2.3365 | 76.8213 | 0 | 2.3365
360 | 6 | feeder2_line1 | -7.9833 | -6.6142 | -3.3657 | 22.8997 | 24.5551 | 23.4243 | 97.9851 | 102.779 | 95.6394 | -17.9632 | 70.8791 | -7.9833 | 22.8997 | -6.6142 | 24.5551 | -3.3657 | 23.4243 | -17.9632 | 70.8791 | 0 | 17.9632
390 | 6.5 | feeder2_line1 | -14.5538 | -18.7396 | -19.239 | 12.7717 | 13.5196 | 12.8832 | 78.0987 | 93.1966 | 93.3748 | -52.5323 | 39.1746 | -14.5538 | 12.7717 | -18.7396 | 13.5196 | -19.239 | 12.8832 | -52.5323 | 39.1746 | 0 | 52.5323
420 | 7 | feeder2_line1 | -16.0508 | -19.1195 | -21.3765 | 7.7874 | 8.2909 | 6.8663 | 71.8997 | 83.9849 | 90.4568 | -56.5468 | 22.9446 | -16.0508 | 7.7874 | -19.1195 | 8.2909 | -21.3765 | 6.8663 | -56.5468 | 22.9446 | 0 | 56.5468
450 | 7.5 | feeder2_line1 | -19.9526 | -19.646 | -12.8414 | 6.3592 | 7.8931 | 7.2101 | 84.3687 | 85.3188 | 59.3553 | -52.4401 | 21.4623 | -19.9526 | 6.3592 | -19.646 | 7.8931 | -12.8414 | 7.2101 | -52.4401 | 21.4623 | 0 | 52.4401
480 | 8 | feeder2_line1 | -15.4903 | -16.5513 | -6.8382 | 4.1677 | 5.5283 | 6.5067 | 64.6162 | 70.3031 | 38.0477 | -38.8798 | 16.2027 | -15.4903 | 4.1677 | -16.5513 | 5.5283 | -6.8382 | 6.5067 | -38.8798 | 16.2027 | 0 | 38.8798
510 | 8.5 | feeder2_line1 | -15.7837 | -18.3871 | -13.4004 | 2.8502 | 3.0244 | 2.8825 | 64.5945 | 75.0405 | 55.2076 | -47.5712 | 8.7571 | -15.7837 | 2.8502 | -18.3871 | 3.0244 | -13.4004 | 2.8825 | -47.5712 | 8.7571 | 0 | 47.5712
540 | 9 | feeder2_line1 | -12.348 | -10.1381 | -12.3611 | 3.3143 | 3.9552 | 4.1871 | 51.4997 | 43.843 | 52.5775 | -34.8471 | 11.4566 | -12.348 | 3.3143 | -10.1381 | 3.9552 | -12.3611 | 4.1871 | -34.8471 | 11.4566 | 0 | 34.8471
570 | 9.5 | feeder2_line1 | -12.9423 | -6.8396 | -7.7825 | 8.0614 | 11.4869 | 7.7414 | 61.4603 | 53.9273 | 44.2535 | -27.5644 | 27.2897 | -12.9423 | 8.0614 | -6.8396 | 11.4869 | -7.7825 | 7.7414 | -27.5644 | 27.2897 | 0 | 27.5644
600 | 10 | feeder2_line1 | -12.198 | -11.5672 | -1.299 | 8.5873 | 10.3557 | 9.812 | 60.1362 | 62.605 | 39.9233 | -25.0642 | 28.755 | -12.198 | 8.5873 | -11.5672 | 10.3557 | -1.299 | 9.812 | -25.0642 | 28.755 | 0 | 25.0642
630 | 10.5 | feeder2_line1 | -6.9354 | -8.4555 | -10.0327 | 1.4264 | 1.7022 | 1.216 | 28.5192 | 34.74 | 40.6996 | -25.4236 | 4.3446 | -6.9354 | 1.4264 | -8.4555 | 1.7022 | -10.0327 | 1.216 | -25.4236 | 4.3446 | 0 | 25.4236
660 | 11 | feeder2_line1 | -0.20796 | -6.1753 | -10.8824 | 2.875 | 1.8137 | 2.1024 | 11.6158 | 25.9256 | 44.6409 | -17.2657 | 6.7912 | -0.20796 | 2.875 | -6.1753 | 1.8137 | -10.8824 | 2.1024 | -17.2657 | 6.7912 | 0 | 17.2657
690 | 11.5 | feeder2_line1 | -12.1552 | -11.2074 | -14.8555 | 1.3983 | 3.3588 | 2.5409 | 49.2722 | 47.1308 | 60.6963 | -38.2181 | 7.298 | -12.1552 | 1.3983 | -11.2074 | 3.3588 | -14.8555 | 2.5409 | -38.2181 | 7.298 | 0 | 38.2181
720 | 12 | feeder2_line1 | -15.0582 | -15.6478 | -17.4644 | 2.4428 | 2.8222 | 1.9919 | 61.435 | 64.0357 | 70.7776 | -48.1703 | 7.2569 | -15.0582 | 2.4428 | -15.6478 | 2.8222 | -17.4644 | 1.9919 | -48.1703 | 7.2569 | 0 | 48.1703
750 | 12.5 | feeder2_line1 | -10.4664 | -16.9355 | -18.2774 | 3.7832 | 4.3247 | 5.9629 | 44.8358 | 70.4058 | 77.4557 | -45.6793 | 14.0708 | -10.4664 | 3.7832 | -16.9355 | 4.3247 | -18.2774 | 5.9629 | -45.6793 | 14.0708 | 0 | 45.6793
780 | 13 | feeder2_line1 | -5.1529 | 0.026651 | -6.5931 | 13.8808 | 16.4346 | 14.2224 | 59.7504 | 66.3592 | 63.2609 | -11.7193 | 44.5379 | -5.1529 | 13.8808 | 0.026651 | 16.4346 | -6.5931 | 14.2224 | -11.7193 | 44.5379 | 0 | 11.7193
810 | 13.5 | feeder2_line1 | -11.0834 | -2.9823 | -15.9606 | 10.2053 | 10.0081 | 8.6265 | 60.7527 | 42.1216 | 73.1281 | -30.0264 | 28.8399 | -11.0834 | 10.2053 | -2.9823 | 10.0081 | -15.9606 | 8.6265 | -30.0264 | 28.8399 | 0 | 30.0264
840 | 14 | feeder2_line1 | -4.4764 | -7.0021 | -14.9174 | 8.3876 | 8.757 | 9.0525 | 38.3367 | 45.2094 | 70.34 | -26.3959 | 26.1971 | -4.4764 | 8.3876 | -7.0021 | 8.757 | -14.9174 | 9.0525 | -26.3959 | 26.1971 | 0 | 26.3959
870 | 14.5 | feeder2_line1 | -4.2697 | -8.2455 | -16.9278 | 12.4208 | 12.3156 | 12.0766 | 52.9928 | 59.7888 | 83.8545 | -29.443 | 36.813 | -4.2697 | 12.4208 | -8.2455 | 12.3156 | -16.9278 | 12.0766 | -29.443 | 36.813 | 0 | 29.443
900 | 15 | feeder2_line1 | -7.1975 | -9.9211 | -14.2094 | 1.6878 | 4.056 | 2.5813 | 29.7775 | 43.1828 | 58.1638 | -31.328 | 8.3252 | -7.1975 | 1.6878 | -9.9211 | 4.056 | -14.2094 | 2.5813 | -31.328 | 8.3252 | 0 | 31.328
930 | 15.5 | feeder2_line1 | -12.7485 | -16.013 | -16.9139 | 2.1781 | 1.9556 | 2.1351 | 52.0872 | 64.9598 | 68.6485 | -45.6754 | 6.2688 | -12.7485 | 2.1781 | -16.013 | 1.9556 | -16.9139 | 2.1351 | -45.6754 | 6.2688 | 0 | 45.6754
960 | 16 | feeder2_line1 | -3.7863 | -1.981 | -14.3367 | 7.2222 | 9.3531 | 7.7908 | 32.8769 | 38.5604 | 65.7642 | -20.104 | 24.3661 | -3.7863 | 7.2222 | -1.981 | 9.3531 | -14.3367 | 7.7908 | -20.104 | 24.3661 | 0 | 20.104
990 | 16.5 | feeder2_line1 | -2.7553 | -12.4132 | -11.8693 | 5.9521 | 6.6919 | 7.7666 | 26.4398 | 56.8328 | 57.1753 | -27.0378 | 20.4106 | -2.7553 | 5.9521 | -12.4132 | 6.6919 | -11.8693 | 7.7666 | -27.0378 | 20.4106 | 0 | 27.0378
1020 | 17 | feeder2_line1 | 0.38835 | -6.6314 | -0.36702 | 1.8373 | 3.8761 | 3.0459 | 7.5663 | 30.9497 | 12.3631 | -6.6101 | 8.7593 | 0.38835 | 1.8373 | -6.6314 | 3.8761 | -0.36702 | 3.0459 | -6.6101 | 8.7593 | 0 | 6.6101
1050 | 17.5 | feeder2_line1 | 5.22 | 4.0787 | -5.9703 | 12.8333 | 14.264 | 14.2134 | 55.9217 | 59.8928 | 62.2132 | 3.3284 | 41.3106 | 5.22 | 12.8333 | 4.0787 | 14.264 | -5.9703 | 14.2134 | 3.3284 | 41.3106 | 3.3284 | 0
1080 | 18 | feeder2_line1 | 8.0925 | -11.0813 | -13.5434 | 7.9106 | 7.5141 | 7.2225 | 45.6503 | 53.967 | 61.8597 | -16.5322 | 22.6472 | 8.0925 | 7.9106 | -11.0813 | 7.5141 | -13.5434 | 7.2225 | -16.5322 | 22.6472 | 0 | 16.5322
1110 | 18.5 | feeder2_line1 | 2.7689 | -1.2483 | -6.3113 | 0.89796 | 4.076 | 2.5511 | 11.728 | 17.1802 | 27.424 | -4.7906 | 7.525 | 2.7689 | 0.89796 | -1.2483 | 4.076 | -6.3113 | 2.5511 | -4.7906 | 7.525 | 0 | 4.7906
1140 | 19 | feeder2_line1 | 2.1087 | 3.9426 | 5.3572 | 20.537 | 22.2176 | 20.7224 | 83.4165 | 91.202 | 86.495 | 11.4086 | 63.477 | 2.1087 | 20.537 | 3.9426 | 22.2176 | 5.3572 | 20.7224 | 11.4086 | 63.477 | 11.4086 | 0
1170 | 19.5 | feeder2_line1 | 10.7778 | 3.5934 | 10.7831 | 25.0405 | 23.2867 | 26.0003 | 110.26 | 95.248 | 113.8607 | 25.1543 | 74.3275 | 10.7778 | 25.0405 | 3.5934 | 23.2867 | 10.7831 | 26.0003 | 25.1543 | 74.3275 | 25.1543 | 0
1200 | 20 | feeder2_line1 | 15.9527 | 19.9848 | 22.3682 | 24.7539 | 25.2686 | 25.514 | 119.126 | 130.3506 | 137.3052 | 58.3058 | 75.5365 | 15.9527 | 24.7539 | 19.9848 | 25.2686 | 22.3682 | 25.514 | 58.3058 | 75.5365 | 58.3058 | 0
1230 | 20.5 | feeder2_line1 | 13.8023 | 20.3283 | 16.76 | 24.9244 | 25.9908 | 25.3401 | 115.2438 | 133.5227 | 122.9114 | 50.8906 | 76.2553 | 13.8023 | 24.9244 | 20.3283 | 25.9908 | 16.76 | 25.3401 | 50.8906 | 76.2553 | 50.8906 | 0
1260 | 21 | feeder2_line1 | -11.5681 | -12.247 | -13.1258 | 1.0626 | 1.5624 | 1.6842 | 46.7798 | 49.7197 | 53.2917 | -36.9409 | 4.3092 | -11.5681 | 1.0626 | -12.247 | 1.5624 | -13.1258 | 1.6842 | -36.9409 | 4.3092 | 0 | 36.9409
1290 | 21.5 | feeder2_line1 | -7.8866 | -4.3875 | -11.9413 | 2.7007 | 3.3926 | 2.479 | 33.5819 | 22.3475 | 49.1213 | -24.2154 | 8.5723 | -7.8866 | 2.7007 | -4.3875 | 3.3926 | -11.9413 | 2.479 | -24.2154 | 8.5723 | 0 | 24.2154
1320 | 22 | feeder2_line1 | -7.8202 | -11.1878 | -12.0784 | 0.28318 | 3.7071 | 1.8192 | 31.5128 | 47.48 | 49.1916 | -31.0864 | 5.8094 | -7.8202 | 0.28318 | -11.1878 | 3.7071 | -12.0784 | 1.8192 | -31.0864 | 5.8094 | 0 | 31.0864
1350 | 22.5 | feeder2_line1 | -11.9559 | -12.2309 | -12.584 | 1.4462 | 1.0121 | 1.364 | 48.4984 | 49.4196 | 50.9719 | -36.7709 | 3.8223 | -11.9559 | 1.4462 | -12.2309 | 1.0121 | -12.584 | 1.364 | -36.7709 | 3.8223 | 0 | 36.7709
1380 | 23 | feeder2_line1 | -14.3307 | -7.9604 | -11.9613 | 3.7177 | 3.453 | 2.8059 | 59.6358 | 34.9586 | 49.4867 | -34.2524 | 9.9766 | -14.3307 | 3.7177 | -7.9604 | 3.453 | -11.9613 | 2.8059 | -34.2524 | 9.9766 | 0 | 34.2524
1410 | 23.5 | feeder2_line1 | -13.0029 | -17.4863 | -14.608 | 2.2013 | 3.6341 | 2.9676 | 53.1127 | 71.9316 | 60.0364 | -45.0972 | 8.8029 | -13.0029 | 2.2013 | -17.4863 | 3.6341 | -14.608 | 2.9676 | -45.0972 | 8.8029 | 0 | 45.0972
1440 | 24 | feeder2_line1 | -13.6436 | -17.1278 | -13.4177 | 2.2913 | 3.749 | 2.0067 | 55.7166 | 70.6181 | 54.6366 | -44.1891 | 8.0469 | -13.6436 | 2.2913 | -17.1278 | 3.749 | -13.4177 | 2.0067 | -44.1891 | 8.0469 | 0 | 44.1891

## Curt_dis_overlap
Stage | Time_sample | Time_h | PV_available_kW | PV_command_kW | PV_curtailment_kW | SOC_pu | BESS_P_ch_A_kW | BESS_P_dis_A_kW | BESS_P_net_A_kW | BESS_Q_A_kvar | BESS_P_ch_B_kW | BESS_P_dis_B_kW | BESS_P_net_B_kW | BESS_Q_B_kvar | BESS_P_ch_C_kW | BESS_P_dis_C_kW | BESS_P_net_C_kW | BESS_Q_C_kvar | BESS_P_ch_total_kW | BESS_P_dis_total_kW | BESS_P_net_total_kW | BESS_Q_total_kvar | PV_curtailment_energy_kWh | PV_interval_curtailment_fraction
One-stage weighted objective | 240 | 4 | 0.80283 | -9.6439e-12 | 0.80283 | 0.2092 | -9.1131e-12 | 0.80283 | 0.80283 | -23.0758 | -9.1131e-12 | 0.80283 | 0.80283 | -23.0758 | -9.1131e-12 | 0.80283 | 0.80283 | -23.0758 | -2.7339e-11 | 2.4085 | 2.4085 | -69.2275 | 0.40142 | 1
One-stage weighted objective | 270 | 4.5 | 3.3481 | -9.6439e-12 | 3.3481 | 0.20786 | -9.1326e-12 | 3.3481 | 3.3481 | -22.9301 | -9.1326e-12 | 3.3481 | 3.3481 | -22.9301 | -9.1326e-12 | 3.3481 | 3.3481 | -22.9301 | -2.7398e-11 | 10.0444 | 10.0444 | -68.7902 | 1.6741 | 1
One-stage weighted objective | 300 | 5 | 7.6125 | -9.6439e-12 | 7.6125 | 0.20228 | -9.1623e-12 | 7.6125 | 7.6125 | -22.1806 | -9.1623e-12 | 7.6125 | 7.6125 | -22.1806 | -9.1623e-12 | 7.6125 | 7.6125 | -22.1806 | -2.7487e-11 | 22.8375 | 22.8375 | -66.5417 | 3.8062 | 1
One-stage weighted objective | 1020 | 17 | 58.8677 | 33.5578 | 25.3098 | 0.97343 | 1.0169e-05 | 13.6576 | 13.6576 | 0.44079 | 1.0169e-05 | 13.6576 | 13.6576 | 0.44079 | 1.0169e-05 | 13.6576 | 13.6576 | 0.44079 | 3.0508e-05 | 40.9727 | 40.9727 | 1.3224 | 12.6549 | 0.42994
One-stage weighted objective | 1050 | 17.5 | 21.3862 | -9.6439e-12 | 21.3862 | 0.95066 | -9.1951e-12 | 21.3862 | 21.3862 | -11.4678 | -9.1951e-12 | 21.3862 | 21.3862 | -11.4678 | -9.1951e-12 | 21.3862 | 21.3862 | -11.4678 | -2.7585e-11 | 64.1585 | 64.1585 | -34.4035 | 10.6931 | 1
One-stage weighted objective | 1080 | 18 | 35.7263 | 9.9713 | 25.755 | 0.91502 | 6.6889e-06 | 20.764 | 20.764 | -5.1878 | 6.6889e-06 | 20.764 | 20.764 | -5.1878 | 6.6889e-06 | 20.764 | 20.764 | -5.1878 | 2.0067e-05 | 62.292 | 62.292 | -15.5634 | 12.8775 | 0.7209
One-stage weighted objective | 1110 | 18.5 | 34.8805 | 0.89114 | 33.9893 | 0.88041 | 5.6838e-06 | 24.4359 | 24.4359 | 0.44252 | 5.6838e-06 | 24.4359 | 24.4359 | 0.44252 | 5.6838e-06 | 24.4359 | 24.4359 | 0.44252 | 1.7051e-05 | 73.3077 | 73.3077 | 1.3276 | 16.9947 | 0.97445
One-stage weighted objective | 1140 | 19 | 14.6764 | -9.6439e-12 | 14.6764 | 0.83969 | -9.1838e-12 | 14.6764 | 14.6764 | -18.7117 | -9.1838e-12 | 14.6764 | 14.6764 | -18.7117 | -9.1838e-12 | 14.6764 | 14.6764 | -18.7117 | -2.7551e-11 | 44.0291 | 44.0291 | -56.1351 | 7.3382 | 1
One-stage weighted objective | 1170 | 19.5 | 6.5566 | -9.6439e-12 | 6.5566 | 0.81523 | -9.157e-12 | 6.5566 | 6.5566 | -22.256 | -9.157e-12 | 6.5566 | 6.5566 | -22.256 | -9.157e-12 | 6.5566 | 6.5566 | -22.256 | -2.7471e-11 | 19.6699 | 19.6699 | -66.7681 | 3.2783 | 1
One-stage weighted objective | 1200 | 20 | 1.4787 | -9.6439e-12 | 1.4787 | 0.8043 | -9.1141e-12 | 1.4787 | 1.4787 | -22.37 | -9.1141e-12 | 1.4787 | 1.4787 | -22.37 | -9.1141e-12 | 1.4787 | 1.4787 | -22.37 | -2.7342e-11 | 4.4361 | 4.4361 | -67.11 | 0.73936 | 1
One-stage weighted objective | 1230 | 20.5 | 0.51386 | -9.6439e-12 | 0.51386 | 0.80183 | -9.115e-12 | 0.51386 | 0.51386 | -22.4461 | -9.115e-12 | 0.51386 | 0.51386 | -22.4461 | -9.115e-12 | 0.51386 | 0.51386 | -22.4461 | -2.7345e-11 | 1.5416 | 1.5416 | -67.3382 | 0.25693 | 1

## Voltage_violations
Time_sample | Time_h | Bus | Phase | Low_limit_pu | High_limit_pu | OPF_V_pu | DSS_V_pu | OPF_violation_pu | DSS_violation_pu | Voltage_violation_pu
30 | 0.5 | feeder2_1818 | 2 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
60 | 1 | feeder2_1818 | 1 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 5.2948e-07 | 5.2948e-07
90 | 1.5 | feeder2_1818 | 3 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
120 | 2 | feeder2_1818 | 2 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
150 | 2.5 | feeder2_1818 | 2 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
180 | 3 | feeder2_1818 | 3 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 1.163e-05 | 1.163e-05
210 | 3.5 | feeder2_1818 | 2 | 0.9 | 1.1 | 1.1 | 1.1 | 5.4995e-09 | 4.4938e-06 | 4.4938e-06
420 | 7 | feeder2_1818 | 3 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 9.046e-10 | 5.5e-09
450 | 7.5 | feeder2_1818 | 1 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
480 | 8 | feeder2_1818 | 2 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
510 | 8.5 | feeder2_1818 | 2 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
540 | 9 | feeder2_1818 | 1 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 2.1813e-06 | 2.1813e-06
570 | 9.5 | feeder2_1818 | 1 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
600 | 10 | feeder2_1818 | 1 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 3.5688e-06 | 3.5688e-06
750 | 12.5 | feeder2_1818 | 3 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 4.7581e-06 | 4.7581e-06
810 | 13.5 | feeder2_1818 | 3 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
840 | 14 | feeder2_1818 | 3 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
870 | 14.5 | feeder2_1818 | 3 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
930 | 15.5 | feeder2_1818 | 3 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
960 | 16 | feeder2_1818 | 3 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
990 | 16.5 | feeder2_1818 | 2 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 2.7759e-06 | 2.7759e-06
1080 | 18 | feeder2_1818 | 3 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
1290 | 21.5 | feeder2_1818 | 3 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09
1380 | 23 | feeder2_1818 | 1 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 3.8331e-06 | 3.8331e-06
1410 | 23.5 | feeder2_1818 | 2 | 0.9 | 1.1 | 1.1 | 1.1 | 5.5e-09 | 0 | 5.5e-09

## Voltage_KPI_time
Time_sample | Time_h | OPF_network_voltage_range_pu | DSS_network_voltage_range_pu | Max_OPF_VUF2_percent | Max_OPF_VUF0_percent | Max_DSS_VUF2_percent | Max_DSS_VUF0_percent
30 | 0.5 | 0.025264 | 0.025263 | 0.087543 | 0.45421 | 0.087542 | 0.45407
60 | 1 | 0.025018 | 0.025019 | 0.082277 | 0.33093 | 0.082296 | 0.33114
90 | 1.5 | 0.024792 | 0.02479 | 0.093504 | 0.10016 | 0.093467 | 0.10006
120 | 2 | 0.025627 | 0.025624 | 0.041746 | 0.45328 | 0.041745 | 0.45315
150 | 2.5 | 0.024848 | 0.024837 | 0.0645 | 0.23378 | 0.064435 | 0.23375
180 | 3 | 0.024975 | 0.024987 | 0.099435 | 0.10549 | 0.099444 | 0.10557
210 | 3.5 | 0.024778 | 0.024783 | 0.065877 | 0.2206 | 0.065702 | 0.22111
240 | 4 | 0.018737 | 0.018736 | 0.06122 | 0.20843 | 0.061246 | 0.20836
270 | 4.5 | 0.016725 | 0.016723 | 0.11903 | 0.21643 | 0.11893 | 0.21711
300 | 5 | 0.012854 | 0.012849 | 0.073253 | 0.2439 | 0.073354 | 0.24372
330 | 5.5 | 0.014125 | 0.014122 | 0.062918 | 0.1847 | 0.062907 | 0.18456
360 | 6 | 0.01223 | 0.01223 | 0.081754 | 0.54405 | 0.081714 | 0.54397
390 | 6.5 | 0.018398 | 0.018397 | 0.13896 | 0.36085 | 0.13891 | 0.36067
420 | 7 | 0.025581 | 0.025581 | 0.21407 | 0.60633 | 0.21397 | 0.60606
450 | 7.5 | 0.028109 | 0.028097 | 0.14868 | 0.84079 | 0.14857 | 0.8406
480 | 8 | 0.032374 | 0.032371 | 0.21206 | 1.1382 | 0.21202 | 1.1379
510 | 8.5 | 0.024915 | 0.024913 | 0.10764 | 0.46198 | 0.10767 | 0.46216
540 | 9 | 0.026425 | 0.026427 | 0.12955 | 0.44371 | 0.12952 | 0.44385
570 | 9.5 | 0.033741 | 0.033735 | 0.17426 | 1.1801 | 0.17421 | 1.1799
600 | 10 | 0.042573 | 0.042578 | 0.29034 | 1.664 | 0.29037 | 1.6642
630 | 10.5 | 0.02111 | 0.021116 | 0.11059 | 0.20714 | 0.11066 | 0.20755
660 | 11 | 0.033676 | 0.033659 | 0.22017 | 0.82819 | 0.2201 | 0.82759
690 | 11.5 | 0.023735 | 0.023728 | 0.15932 | 0.3961 | 0.15929 | 0.39551
720 | 12 | 0.02439 | 0.024387 | 0.056258 | 0.18918 | 0.056272 | 0.18901
750 | 12.5 | 0.028466 | 0.028468 | 0.18592 | 0.933 | 0.18582 | 0.93257
780 | 13 | 0.024353 | 0.024327 | 0.25676 | 0.67929 | 0.25666 | 0.67784
810 | 13.5 | 0.038708 | 0.038697 | 0.3143 | 1.3927 | 0.31421 | 1.3922
840 | 14 | 0.031693 | 0.031689 | 0.27428 | 1.0928 | 0.27427 | 1.0925
870 | 14.5 | 0.038172 | 0.038168 | 0.36077 | 1.4693 | 0.36071 | 1.4691
900 | 15 | 0.024092 | 0.024096 | 0.26268 | 0.6141 | 0.26284 | 0.61502
930 | 15.5 | 0.024831 | 0.02483 | 0.098107 | 0.36919 | 0.098134 | 0.36926
960 | 16 | 0.036957 | 0.036943 | 0.38444 | 1.134 | 0.38429 | 1.1332
990 | 16.5 | 0.037643 | 0.037643 | 0.31884 | 1.6188 | 0.31883 | 1.6186
1020 | 17 | 0.022044 | 0.022038 | 0.21557 | 0.55741 | 0.21553 | 0.5571
1050 | 17.5 | 0.029001 | 0.029005 | 0.35715 | 0.98105 | 0.3572 | 0.9813
1080 | 18 | 0.044494 | 0.04449 | 0.43997 | 1.6948 | 0.43998 | 1.6947
1110 | 18.5 | 0.025186 | 0.025195 | 0.29949 | 0.49299 | 0.29954 | 0.49338
1140 | 19 | 0.016404 | 0.016398 | 0.066183 | 0.59695 | 0.066048 | 0.59626
1170 | 19.5 | 0.023613 | 0.023609 | 0.18147 | 0.81695 | 0.18151 | 0.81651
1200 | 20 | 0.0307 | 0.030692 | 0.1589 | 0.64124 | 0.15868 | 0.64205
1230 | 20.5 | 0.034585 | 0.034587 | 0.18677 | 0.85279 | 0.1867 | 0.85307
1260 | 21 | 0.022245 | 0.022238 | 0.050331 | 0.24268 | 0.050301 | 0.24219
1290 | 21.5 | 0.027568 | 0.027556 | 0.20546 | 0.77688 | 0.20534 | 0.77628
1320 | 22 | 0.023355 | 0.023366 | 0.26836 | 0.62381 | 0.26844 | 0.62405
1350 | 22.5 | 0.021797 | 0.021792 | 0.047952 | 0.24948 | 0.047896 | 0.24916
1380 | 23 | 0.031575 | 0.031574 | 0.24691 | 1.054 | 0.24679 | 1.0537
1410 | 23.5 | 0.02488 | 0.024874 | 0.1199 | 0.50628 | 0.11988 | 0.50569
1440 | 24 | 0.023401 | 0.023386 | 0.11421 | 0.54223 | 0.1141 | 0.54174

## Voltage_KPI_bus
Time_sample | Time_h | Bus | OPF_VUF2_percent | OPF_VUF0_percent | DSS_VUF2_percent | DSS_VUF0_percent
30 | 0.5 | secondary | 0.01452 | 0.023535 | 0.014517 | 0.023532
30 | 0.5 | feeder2_44 | 0.027016 | 0.12272 | 0.027018 | 0.12272
30 | 0.5 | feeder2_45 | 0.027437 | 0.12664 | 0.027433 | 0.12665
30 | 0.5 | feeder2_46 | 0.028233 | 0.1215 | 0.028232 | 0.1215
30 | 0.5 | feeder2_51 | 0.028183 | 0.13354 | 0.028185 | 0.13355
30 | 0.5 | feeder2_48 | 0.0274 | 0.126 | 0.0274 | 0.126
30 | 0.5 | feeder2_52 | 0.024692 | 0.13758 | 0.024688 | 0.13758
30 | 0.5 | feeder2_68 | 0.030591 | 0.15149 | 0.030587 | 0.15149
30 | 0.5 | feeder2_69 | 0.030756 | 0.15158 | 0.030756 | 0.15159
30 | 0.5 | feeder2_71 | 0.030909 | 0.15386 | 0.030907 | 0.15387
30 | 0.5 | feeder2_72 | 0.030872 | 0.15361 | 0.030871 | 0.15361
30 | 0.5 | feeder2_73 | 0.031907 | 0.16132 | 0.031903 | 0.16132
30 | 0.5 | feeder2_74 | 0.031806 | 0.16139 | 0.031809 | 0.16139
30 | 0.5 | feeder2_77 | 0.032766 | 0.1677 | 0.032773 | 0.1677
30 | 0.5 | feeder2_79 | 0.033117 | 0.16787 | 0.033111 | 0.16788
30 | 0.5 | feeder2_81 | 0.034094 | 0.1777 | 0.034097 | 0.1777
30 | 0.5 | feeder2_82 | 0.034038 | 0.17709 | 0.034039 | 0.17709
30 | 0.5 | feeder2_116 | 0.040153 | 0.2232 | 0.040153 | 0.22319
30 | 0.5 | feeder2_119 | 0.037916 | 0.22552 | 0.037917 | 0.22552
30 | 0.5 | feeder2_120 | 0.042642 | 0.23882 | 0.042645 | 0.23882
30 | 0.5 | feeder2_248 | 0.040472 | 0.24105 | 0.040474 | 0.24105
30 | 0.5 | feeder2_124 | 0.044344 | 0.24756 | 0.044348 | 0.24756
30 | 0.5 | feeder2_282 | 0.04431 | 0.24741 | 0.044309 | 0.24741
30 | 0.5 | feeder2_275 | 0.044227 | 0.24763 | 0.044227 | 0.24763
30 | 0.5 | feeder2_151 | 0.047325 | 0.26284 | 0.047323 | 0.26283
30 | 0.5 | feeder2_295 | 0.047422 | 0.26289 | 0.047421 | 0.26289
30 | 0.5 | feeder2_311 | 0.047603 | 0.26299 | 0.047606 | 0.26298
30 | 0.5 | feeder2_201 | 0.052178 | 0.28797 | 0.052185 | 0.28797
30 | 0.5 | feeder2_314 | 0.052138 | 0.28785 | 0.052138 | 0.28785
30 | 0.5 | feeder2_342 | 0.059106 | 0.32392 | 0.059104 | 0.32392
30 | 0.5 | feeder2_368 | 0.060877 | 0.32803 | 0.060878 | 0.32803
30 | 0.5 | feeder2_347 | 0.060089 | 0.334 | 0.060092 | 0.334
30 | 0.5 | feeder2_353 | 0.060604 | 0.33923 | 0.060609 | 0.33922
30 | 0.5 | feeder2_518 | 0.060029 | 0.33372 | 0.060028 | 0.33371
30 | 0.5 | feeder2_365 | 0.06119 | 0.34499 | 0.06119 | 0.34498
30 | 0.5 | feeder2_653 | 0.060366 | 0.33941 | 0.060364 | 0.3394
30 | 0.5 | feeder2_377 | 0.060836 | 0.34643 | 0.060841 | 0.34642
30 | 0.5 | feeder2_622 | 0.07296 | 0.3509 | 0.072961 | 0.3509
30 | 0.5 | feeder2_451 | 0.060824 | 0.32777 | 0.060827 | 0.32777
30 | 0.5 | feeder2_383 | 0.063774 | 0.33505 | 0.063774 | 0.33505
30 | 0.5 | feeder2_385 | 0.060425 | 0.34815 | 0.060424 | 0.34813
30 | 0.5 | feeder2_621 | 0.06094 | 0.34648 | 0.060944 | 0.34647
30 | 0.5 | feeder2_611 | 0.063611 | 0.33515 | 0.063616 | 0.33516
30 | 0.5 | feeder2_405 | 0.063957 | 0.33549 | 0.06396 | 0.33549
30 | 0.5 | feeder2_461 | 0.059254 | 0.35349 | 0.059256 | 0.35346
30 | 0.5 | feeder2_594 | 0.059006 | 0.34962 | 0.059006 | 0.3496
30 | 0.5 | feeder2_732 | 0.061232 | 0.33832 | 0.061235 | 0.33833
30 | 0.5 | feeder2_417 | 0.065502 | 0.33822 | 0.065502 | 0.33823
30 | 0.5 | feeder2_663 | 0.065655 | 0.33833 | 0.065656 | 0.33834
30 | 0.5 | feeder2_444 | 0.066664 | 0.34029 | 0.066663 | 0.3403
30 | 0.5 | feeder2_759 | 0.068603 | 0.3384 | 0.068608 | 0.33841
30 | 0.5 | feeder2_842 | 0.087543 | 0.35311 | 0.087542 | 0.35312
30 | 0.5 | feeder2_459 | 0.066683 | 0.34034 | 0.066687 | 0.34035
30 | 0.5 | feeder2_702 | 0.06667 | 0.34028 | 0.066673 | 0.34029
30 | 0.5 | feeder2_493 | 0.066761 | 0.34055 | 0.066767 | 0.34056
30 | 0.5 | feeder2_651 | 0.059452 | 0.35357 | 0.059457 | 0.35354
30 | 0.5 | feeder2_684 | 0.058287 | 0.3587 | 0.058287 | 0.35865
30 | 0.5 | feeder2_674 | 0.066726 | 0.34057 | 0.066729 | 0.34059
30 | 0.5 | feeder2_696 | 0.067011 | 0.34112 | 0.067015 | 0.34112
30 | 0.5 | feeder2_681 | 0.066668 | 0.3406 | 0.066671 | 0.34061
30 | 0.5 | feeder2_682 | 0.066671 | 0.34061 | 0.066671 | 0.34062
30 | 0.5 | feeder2_728 | 0.058153 | 0.35874 | 0.05815 | 0.3587
30 | 0.5 | feeder2_724 | 0.057612 | 0.36475 | 0.057608 | 0.36469
30 | 0.5 | feeder2_703 | 0.067653 | 0.34151 | 0.067658 | 0.34152
30 | 0.5 | feeder2_704 | 0.067149 | 0.3412 | 0.067154 | 0.34121
30 | 0.5 | feeder2_754 | 0.057522 | 0.36447 | 0.057524 | 0.36441
30 | 0.5 | feeder2_747 | 0.057374 | 0.36759 | 0.057374 | 0.36753
30 | 0.5 | feeder2_828 | 0.058119 | 0.35878 | 0.058123 | 0.35874
30 | 0.5 | feeder2_763 | 0.057962 | 0.35877 | 0.057966 | 0.35873
30 | 0.5 | feeder2_836 | 0.058177 | 0.36666 | 0.058174 | 0.3666
30 | 0.5 | feeder2_758 | 0.057039 | 0.3705 | 0.057036 | 0.37043
30 | 0.5 | feeder2_788 | 0.057744 | 0.36969 | 0.057744 | 0.36963
30 | 0.5 | feeder2_812 | 0.056087 | 0.38122 | 0.056091 | 0.38114
30 | 0.5 | feeder2_947 | 0.057786 | 0.35814 | 0.057789 | 0.3581
30 | 0.5 | feeder2_868 | 0.058258 | 0.35833 | 0.058257 | 0.35829
30 | 0.5 | feeder2_785 | 0.057855 | 0.35927 | 0.057854 | 0.35923
30 | 0.5 | feeder2_1176 | 0.05833 | 0.35945 | 0.058329 | 0.3594
30 | 0.5 | feeder2_846 | 0.056993 | 0.36017 | 0.056996 | 0.36013
30 | 0.5 | feeder2_911 | 0.057838 | 0.35916 | 0.057837 | 0.35912
30 | 0.5 | feeder2_1107 | 0.055679 | 0.38298 | 0.055676 | 0.3829
30 | 0.5 | feeder2_920 | 0.055946 | 0.38387 | 0.055948 | 0.38379
30 | 0.5 | feeder2_926 | 0.055744 | 0.38782 | 0.055745 | 0.38773
30 | 0.5 | feeder2_1239 | 0.055941 | 0.384 | 0.055941 | 0.38391
30 | 0.5 | feeder2_933 | 0.05566 | 0.38973 | 0.055661 | 0.38963
30 | 0.5 | feeder2_1146 | 0.055729 | 0.38727 | 0.055727 | 0.38718
30 | 0.5 | feeder2_1124 | 0.05581 | 0.38976 | 0.055803 | 0.38966
30 | 0.5 | feeder2_942 | 0.055427 | 0.39459 | 0.055425 | 0.39449
30 | 0.5 | feeder2_952 | 0.055361 | 0.40161 | 0.055356 | 0.4015
30 | 0.5 | feeder2_965 | 0.055395 | 0.39463 | 0.055394 | 0.39453
30 | 0.5 | feeder2_961 | 0.055364 | 0.40247 | 0.055361 | 0.40236
30 | 0.5 | feeder2_963 | 0.05536 | 0.40159 | 0.055351 | 0.40148
30 | 0.5 | feeder2_973 | 0.055393 | 0.40702 | 0.055385 | 0.4069
30 | 0.5 | feeder2_1128 | 0.055364 | 0.40251 | 0.055357 | 0.4024
30 | 0.5 | feeder2_1113 | 0.055575 | 0.40143 | 0.055567 | 0.40132
30 | 0.5 | feeder2_1143 | 0.055304 | 0.40087 | 0.055303 | 0.40076
30 | 0.5 | feeder2_1238 | 0.059236 | 0.39289 | 0.059238 | 0.39279
30 | 0.5 | feeder2_979 | 0.055354 | 0.39488 | 0.055353 | 0.39478
30 | 0.5 | feeder2_1236 | 0.055255 | 0.41458 | 0.055245 | 0.41446
30 | 0.5 | feeder2_989 | 0.055395 | 0.40701 | 0.055393 | 0.4069
30 | 0.5 | feeder2_1196 | 0.054364 | 0.39592 | 0.054357 | 0.39581
30 | 0.5 | feeder2_1158 | 0.056173 | 0.40611 | 0.056167 | 0.406
30 | 0.5 | feeder2_1122 | 0.055392 | 0.38388 | 0.055391 | 0.3838
30 | 0.5 | feeder2_1258 | 0.056219 | 0.38267 | 0.056217 | 0.3826
30 | 0.5 | feeder2_1303 | 0.055331 | 0.38375 | 0.055328 | 0.38367
30 | 0.5 | feeder2_1138 | 0.055174 | 0.38462 | 0.055174 | 0.38454
30 | 0.5 | feeder2_1304 | 0.053607 | 0.38632 | 0.053604 | 0.38623
30 | 0.5 | feeder2_1212 | 0.054922 | 0.38484 | 0.054922 | 0.38476
30 | 0.5 | feeder2_1311 | 0.055371 | 0.38362 | 0.055367 | 0.38354
30 | 0.5 | feeder2_1290 | 0.054723 | 0.38624 | 0.054723 | 0.38616
30 | 0.5 | feeder2_1325 | 0.055108 | 0.42495 | 0.055099 | 0.42482
30 | 0.5 | feeder2_1248 | 0.055256 | 0.41458 | 0.055247 | 0.41446
30 | 0.5 | feeder2_1249 | 0.059583 | 0.39272 | 0.05958 | 0.39262
30 | 0.5 | feeder2_1250 | 0.061354 | 0.39215 | 0.061361 | 0.39204
30 | 0.5 | feeder2_1366 | 0.055434 | 0.41462 | 0.055429 | 0.4145
30 | 0.5 | feeder2_1266 | 0.056284 | 0.3827 | 0.056284 | 0.38262
30 | 0.5 | feeder2_1372 | 0.05461 | 0.38595 | 0.054605 | 0.38587
30 | 0.5 | feeder2_1363 | 0.054588 | 0.38816 | 0.054582 | 0.38808
30 | 0.5 | feeder2_1446 | 0.055543 | 0.42459 | 0.055537 | 0.42446
30 | 0.5 | feeder2_1502 | 0.055163 | 0.43735 | 0.055144 | 0.43721
30 | 0.5 | feeder2_1428 | 0.054288 | 0.38856 | 0.054286 | 0.38848
30 | 0.5 | feeder2_1380 | 0.054448 | 0.3899 | 0.054442 | 0.38981
30 | 0.5 | feeder2_1550 | 0.054422 | 0.38984 | 0.054422 | 0.38975
30 | 0.5 | feeder2_1386 | 0.054388 | 0.39078 | 0.054387 | 0.3907
30 | 0.5 | feeder2_1551 | 0.054316 | 0.39089 | 0.05431 | 0.39081
30 | 0.5 | feeder2_1400 | 0.05436 | 0.39118 | 0.054358 | 0.3911
30 | 0.5 | feeder2_1552 | 0.052484 | 0.39314 | 0.052476 | 0.39306
30 | 0.5 | feeder2_1408 | 0.054472 | 0.39099 | 0.054472 | 0.3909
30 | 0.5 | feeder2_1553 | 0.054276 | 0.39126 | 0.054267 | 0.39118
30 | 0.5 | feeder2_1416 | 0.054532 | 0.39083 | 0.054529 | 0.39074
30 | 0.5 | feeder2_1530 | 0.054425 | 0.39059 | 0.054424 | 0.39051
30 | 0.5 | feeder2_1425 | 0.05467 | 0.39066 | 0.054663 | 0.39058
30 | 0.5 | feeder2_1589 | 0.05453 | 0.39085 | 0.054521 | 0.39077
30 | 0.5 | feeder2_1435 | 0.054698 | 0.39061 | 0.054698 | 0.39053
30 | 0.5 | feeder2_1621 | 0.055631 | 0.38974 | 0.055624 | 0.38966
30 | 0.5 | feeder2_1564 | 0.054694 | 0.39086 | 0.05469 | 0.39078
30 | 0.5 | feeder2_1704 | 0.056138 | 0.43648 | 0.056122 | 0.43634
30 | 0.5 | feeder2_1525 | 0.055103 | 0.44084 | 0.055092 | 0.4407
30 | 0.5 | feeder2_1716 | 0.057095 | 0.43861 | 0.057079 | 0.43847
30 | 0.5 | feeder2_1537 | 0.054955 | 0.44507 | 0.054936 | 0.44493
30 | 0.5 | feeder2_1645 | 0.050711 | 0.45421 | 0.050689 | 0.45407
30 | 0.5 | feeder2_1561 | 0.054793 | 0.44507 | 0.054775 | 0.44492
30 | 0.5 | feeder2_1657 | 0.054708 | 0.44494 | 0.054692 | 0.44479
30 | 0.5 | feeder2_1570 | 0.054731 | 0.44511 | 0.054714 | 0.44496
30 | 0.5 | feeder2_1756 | 0.054797 | 0.4432 | 0.054783 | 0.44305
30 | 0.5 | feeder2_1588 | 0.0547 | 0.44528 | 0.054681 | 0.44513
30 | 0.5 | feeder2_1628 | 0.05459 | 0.44511 | 0.054575 | 0.44496
30 | 0.5 | feeder2_1598 | 0.054671 | 0.44556 | 0.054659 | 0.44541
30 | 0.5 | feeder2_1816 | 0.055029 | 0.44564 | 0.055013 | 0.44549
30 | 0.5 | feeder2_1765 | 0.055174 | 0.44561 | 0.055163 | 0.44546
30 | 0.5 | feeder2_1641 | 0.054474 | 0.44682 | 0.054459 | 0.44666
30 | 0.5 | feeder2_1689 | 0.054342 | 0.44807 | 0.054323 | 0.44791
30 | 0.5 | feeder2_1744 | 0.054406 | 0.44672 | 0.054393 | 0.44657
30 | 0.5 | feeder2_1817 | 0.054345 | 0.44813 | 0.054328 | 0.44798
30 | 0.5 | feeder2_1779 | 0.054382 | 0.44807 | 0.054365 | 0.44791
30 | 0.5 | feeder2_1800 | 0.052696 | 0.44973 | 0.052681 | 0.44958
30 | 0.5 | feeder2_1818 | 0.056453 | 0.44593 | 0.056447 | 0.44576
30 | 0.5 | feeder2_1753 | 0.054288 | 0.44655 | 0.054276 | 0.44639
30 | 0.5 | feeder2_1754 | 0.054384 | 0.44668 | 0.054368 | 0.44653
60 | 1 | secondary | 0.015717 | 0.0061296 | 0.015723 | 0.0061404
60 | 1 | feeder2_44 | 0.029235 | 0.031953 | 0.029244 | 0.031998
60 | 1 | feeder2_45 | 0.0297 | 0.033271 | 0.029708 | 0.033313
60 | 1 | feeder2_46 | 0.029891 | 0.028117 | 0.0299 | 0.028159
60 | 1 | feeder2_51 | 0.030465 | 0.035395 | 0.030475 | 0.035443
60 | 1 | feeder2_48 | 0.032413 | 0.034895 | 0.032418 | 0.034939
60 | 1 | feeder2_52 | 0.030274 | 0.035628 | 0.030278 | 0.03567
60 | 1 | feeder2_68 | 0.032646 | 0.04134 | 0.032648 | 0.041387
60 | 1 | feeder2_69 | 0.032797 | 0.041245 | 0.032803 | 0.041296
60 | 1 | feeder2_71 | 0.032934 | 0.042136 | 0.032941 | 0.042189
60 | 1 | feeder2_72 | 0.032937 | 0.042008 | 0.032945 | 0.042061
60 | 1 | feeder2_73 | 0.033841 | 0.04465 | 0.033846 | 0.044702
60 | 1 | feeder2_74 | 0.033727 | 0.044792 | 0.03374 | 0.04485
60 | 1 | feeder2_77 | 0.034624 | 0.046789 | 0.034629 | 0.046843
60 | 1 | feeder2_79 | 0.035034 | 0.044427 | 0.035043 | 0.044486
60 | 1 | feeder2_81 | 0.035741 | 0.051046 | 0.035747 | 0.051104
60 | 1 | feeder2_82 | 0.037435 | 0.051759 | 0.03744 | 0.051816
60 | 1 | feeder2_116 | 0.040649 | 0.06988 | 0.040661 | 0.069962
60 | 1 | feeder2_119 | 0.03997 | 0.070722 | 0.039982 | 0.070802
60 | 1 | feeder2_120 | 0.04253 | 0.076445 | 0.042542 | 0.07653
60 | 1 | feeder2_248 | 0.042115 | 0.076957 | 0.04212 | 0.077035
60 | 1 | feeder2_124 | 0.043708 | 0.080288 | 0.043719 | 0.080378
60 | 1 | feeder2_282 | 0.043695 | 0.080192 | 0.043705 | 0.080278
60 | 1 | feeder2_275 | 0.043571 | 0.080477 | 0.043581 | 0.080563
60 | 1 | feeder2_151 | 0.045782 | 0.086939 | 0.045793 | 0.087034
60 | 1 | feeder2_295 | 0.045873 | 0.086903 | 0.045887 | 0.086999
60 | 1 | feeder2_311 | 0.046043 | 0.086821 | 0.046049 | 0.086912
60 | 1 | feeder2_201 | 0.04913 | 0.098192 | 0.049144 | 0.098299
60 | 1 | feeder2_314 | 0.049105 | 0.098101 | 0.049115 | 0.098203
60 | 1 | feeder2_342 | 0.053932 | 0.11439 | 0.053947 | 0.11452
60 | 1 | feeder2_368 | 0.055887 | 0.112 | 0.055898 | 0.11212
60 | 1 | feeder2_347 | 0.053455 | 0.12762 | 0.053462 | 0.12774
60 | 1 | feeder2_353 | 0.053237 | 0.13462 | 0.053243 | 0.13475
60 | 1 | feeder2_518 | 0.053429 | 0.12746 | 0.053441 | 0.12759
60 | 1 | feeder2_365 | 0.053012 | 0.1424 | 0.053029 | 0.14254
60 | 1 | feeder2_653 | 0.052973 | 0.13496 | 0.052987 | 0.13509
60 | 1 | feeder2_377 | 0.052888 | 0.14671 | 0.052906 | 0.14685
60 | 1 | feeder2_622 | 0.053046 | 0.14239 | 0.053055 | 0.14251
60 | 1 | feeder2_451 | 0.057075 | 0.11222 | 0.057086 | 0.11234
60 | 1 | feeder2_383 | 0.058898 | 0.10912 | 0.058914 | 0.10924
60 | 1 | feeder2_385 | 0.052738 | 0.15174 | 0.052748 | 0.15187
60 | 1 | feeder2_621 | 0.052987 | 0.14666 | 0.052995 | 0.14679
60 | 1 | feeder2_611 | 0.057479 | 0.11045 | 0.057488 | 0.11056
60 | 1 | feeder2_405 | 0.059108 | 0.10892 | 0.05912 | 0.10904
60 | 1 | feeder2_461 | 0.052181 | 0.17211 | 0.052201 | 0.17226
60 | 1 | feeder2_594 | 0.052481 | 0.15208 | 0.052495 | 0.15221
60 | 1 | feeder2_732 | 0.058834 | 0.10926 | 0.058843 | 0.10937
60 | 1 | feeder2_417 | 0.060706 | 0.10749 | 0.060719 | 0.10761
60 | 1 | feeder2_663 | 0.061357 | 0.10515 | 0.061373 | 0.10527
60 | 1 | feeder2_444 | 0.061801 | 0.10729 | 0.061812 | 0.10741
60 | 1 | feeder2_759 | 0.061773 | 0.10715 | 0.061787 | 0.10727
60 | 1 | feeder2_842 | 0.082277 | 0.10709 | 0.082296 | 0.1072
60 | 1 | feeder2_459 | 0.061821 | 0.1073 | 0.061827 | 0.10742
60 | 1 | feeder2_702 | 0.061811 | 0.10725 | 0.061819 | 0.10737
60 | 1 | feeder2_493 | 0.061896 | 0.10736 | 0.061905 | 0.10748
60 | 1 | feeder2_651 | 0.052368 | 0.17198 | 0.052379 | 0.17212
60 | 1 | feeder2_684 | 0.051682 | 0.1893 | 0.051696 | 0.18945
60 | 1 | feeder2_674 | 0.061859 | 0.10741 | 0.061875 | 0.10753
60 | 1 | feeder2_696 | 0.062145 | 0.10735 | 0.062162 | 0.10747
60 | 1 | feeder2_681 | 0.061796 | 0.10749 | 0.061811 | 0.1076
60 | 1 | feeder2_682 | 0.0618 | 0.10748 | 0.061816 | 0.1076
60 | 1 | feeder2_728 | 0.051688 | 0.1902 | 0.051701 | 0.19035
60 | 1 | feeder2_724 | 0.051298 | 0.20512 | 0.051313 | 0.20528
60 | 1 | feeder2_703 | 0.062769 | 0.10728 | 0.062777 | 0.1074
60 | 1 | feeder2_704 | 0.06228 | 0.10733 | 0.062288 | 0.10745
60 | 1 | feeder2_754 | 0.052268 | 0.20588 | 0.052278 | 0.20604
60 | 1 | feeder2_747 | 0.051121 | 0.21128 | 0.051135 | 0.21143
60 | 1 | feeder2_828 | 0.051648 | 0.19025 | 0.05166 | 0.1904
60 | 1 | feeder2_763 | 0.051712 | 0.19145 | 0.05173 | 0.1916
60 | 1 | feeder2_836 | 0.051666 | 0.2096 | 0.051681 | 0.20975
60 | 1 | feeder2_758 | 0.050856 | 0.21733 | 0.050872 | 0.21749
60 | 1 | feeder2_788 | 0.050802 | 0.21722 | 0.050818 | 0.21737
60 | 1 | feeder2_812 | 0.050126 | 0.23616 | 0.050144 | 0.23633
60 | 1 | feeder2_947 | 0.051646 | 0.19123 | 0.05166 | 0.19137
60 | 1 | feeder2_868 | 0.052116 | 0.19172 | 0.052133 | 0.19186
60 | 1 | feeder2_785 | 0.051705 | 0.19211 | 0.051717 | 0.19225
60 | 1 | feeder2_1176 | 0.052151 | 0.19179 | 0.052159 | 0.19193
60 | 1 | feeder2_846 | 0.050844 | 0.19267 | 0.050862 | 0.19282
60 | 1 | feeder2_911 | 0.051929 | 0.19294 | 0.051938 | 0.19308
60 | 1 | feeder2_1107 | 0.049853 | 0.23826 | 0.049873 | 0.23843
60 | 1 | feeder2_920 | 0.050002 | 0.24087 | 0.050017 | 0.24103
60 | 1 | feeder2_926 | 0.049832 | 0.24773 | 0.049846 | 0.2479
60 | 1 | feeder2_1239 | 0.049991 | 0.24105 | 0.050004 | 0.24122
60 | 1 | feeder2_933 | 0.049762 | 0.25079 | 0.049781 | 0.25096
60 | 1 | feeder2_1146 | 0.049808 | 0.24766 | 0.049828 | 0.24783
60 | 1 | feeder2_1124 | 0.05016 | 0.24974 | 0.050178 | 0.24991
60 | 1 | feeder2_942 | 0.049425 | 0.25952 | 0.049442 | 0.25969
60 | 1 | feeder2_952 | 0.04916 | 0.2708 | 0.049179 | 0.27098
60 | 1 | feeder2_965 | 0.049396 | 0.25972 | 0.049415 | 0.25991
60 | 1 | feeder2_961 | 0.049133 | 0.27198 | 0.049154 | 0.27217
60 | 1 | feeder2_963 | 0.04916 | 0.27081 | 0.049185 | 0.27099
60 | 1 | feeder2_973 | 0.048994 | 0.27822 | 0.049015 | 0.2784
60 | 1 | feeder2_1128 | 0.04913 | 0.27204 | 0.049147 | 0.27222
60 | 1 | feeder2_1113 | 0.049138 | 0.27078 | 0.049159 | 0.27097
60 | 1 | feeder2_1143 | 0.049178 | 0.2715 | 0.049198 | 0.27168
60 | 1 | feeder2_1238 | 0.051374 | 0.26158 | 0.051393 | 0.26176
60 | 1 | feeder2_979 | 0.049349 | 0.25987 | 0.049369 | 0.26004
60 | 1 | feeder2_1236 | 0.048771 | 0.2876 | 0.048798 | 0.2878
60 | 1 | feeder2_989 | 0.048994 | 0.27822 | 0.049015 | 0.2784
60 | 1 | feeder2_1196 | 0.048357 | 0.26037 | 0.048372 | 0.26054
60 | 1 | feeder2_1158 | 0.049139 | 0.27813 | 0.049162 | 0.27832
60 | 1 | feeder2_1122 | 0.049695 | 0.23923 | 0.049715 | 0.2394
60 | 1 | feeder2_1258 | 0.050145 | 0.23806 | 0.050161 | 0.23822
60 | 1 | feeder2_1303 | 0.049655 | 0.23918 | 0.049668 | 0.23934
60 | 1 | feeder2_1138 | 0.049578 | 0.24002 | 0.049595 | 0.24019
60 | 1 | feeder2_1304 | 0.049155 | 0.24059 | 0.049171 | 0.24076
60 | 1 | feeder2_1212 | 0.049363 | 0.24121 | 0.049379 | 0.24138
60 | 1 | feeder2_1311 | 0.050218 | 0.24198 | 0.050236 | 0.24215
60 | 1 | feeder2_1290 | 0.049067 | 0.24214 | 0.049087 | 0.24231
60 | 1 | feeder2_1325 | 0.048432 | 0.30062 | 0.048458 | 0.30082
60 | 1 | feeder2_1248 | 0.048772 | 0.2876 | 0.048798 | 0.2878
60 | 1 | feeder2_1249 | 0.051974 | 0.26214 | 0.051994 | 0.26232
60 | 1 | feeder2_1250 | 0.051362 | 0.26157 | 0.051383 | 0.26174
60 | 1 | feeder2_1366 | 0.048948 | 0.28749 | 0.048968 | 0.28767
60 | 1 | feeder2_1266 | 0.050208 | 0.23802 | 0.050223 | 0.23818
60 | 1 | feeder2_1372 | 0.049007 | 0.24205 | 0.049023 | 0.24221
60 | 1 | feeder2_1363 | 0.048816 | 0.24331 | 0.048836 | 0.24348
60 | 1 | feeder2_1446 | 0.048386 | 0.30057 | 0.048413 | 0.30077
60 | 1 | feeder2_1502 | 0.048114 | 0.31533 | 0.048137 | 0.31553
60 | 1 | feeder2_1428 | 0.048443 | 0.24383 | 0.048465 | 0.24401
60 | 1 | feeder2_1380 | 0.04857 | 0.2439 | 0.048593 | 0.24407
60 | 1 | feeder2_1550 | 0.048555 | 0.24388 | 0.048576 | 0.24405
60 | 1 | feeder2_1386 | 0.048457 | 0.24421 | 0.048482 | 0.24438
60 | 1 | feeder2_1551 | 0.048359 | 0.24438 | 0.048378 | 0.24455
60 | 1 | feeder2_1400 | 0.048405 | 0.24431 | 0.048419 | 0.24448
60 | 1 | feeder2_1552 | 0.048277 | 0.24454 | 0.048301 | 0.24471
60 | 1 | feeder2_1408 | 0.0483 | 0.24442 | 0.048321 | 0.24459
60 | 1 | feeder2_1553 | 0.048051 | 0.24479 | 0.048069 | 0.24495
60 | 1 | feeder2_1416 | 0.04825 | 0.24439 | 0.048267 | 0.24456
60 | 1 | feeder2_1530 | 0.048185 | 0.24431 | 0.048206 | 0.24448
60 | 1 | feeder2_1425 | 0.048175 | 0.24441 | 0.048199 | 0.24458
60 | 1 | feeder2_1589 | 0.048 | 0.24466 | 0.048021 | 0.24483
60 | 1 | feeder2_1435 | 0.048161 | 0.24439 | 0.048183 | 0.24456
60 | 1 | feeder2_1621 | 0.04887 | 0.24285 | 0.048886 | 0.24301
60 | 1 | feeder2_1564 | 0.047694 | 0.24586 | 0.047718 | 0.24603
60 | 1 | feeder2_1704 | 0.048398 | 0.31511 | 0.048427 | 0.31532
60 | 1 | feeder2_1525 | 0.048015 | 0.31918 | 0.048035 | 0.31939
60 | 1 | feeder2_1716 | 0.048219 | 0.31904 | 0.048244 | 0.31925
60 | 1 | feeder2_1537 | 0.047902 | 0.32352 | 0.047925 | 0.32373
60 | 1 | feeder2_1645 | 0.043296 | 0.33093 | 0.04333 | 0.33114
60 | 1 | feeder2_1561 | 0.04796 | 0.32422 | 0.047982 | 0.32443
60 | 1 | feeder2_1657 | 0.04845 | 0.32478 | 0.048478 | 0.32499
60 | 1 | feeder2_1570 | 0.047986 | 0.32441 | 0.048007 | 0.32462
60 | 1 | feeder2_1756 | 0.049427 | 0.32601 | 0.049451 | 0.32622
60 | 1 | feeder2_1588 | 0.04801 | 0.3245 | 0.048034 | 0.32471
60 | 1 | feeder2_1628 | 0.047953 | 0.32445 | 0.047983 | 0.32467
60 | 1 | feeder2_1598 | 0.048049 | 0.32463 | 0.048075 | 0.32484
60 | 1 | feeder2_1816 | 0.048414 | 0.3244 | 0.048442 | 0.32462
60 | 1 | feeder2_1765 | 0.048543 | 0.32426 | 0.048566 | 0.32447
60 | 1 | feeder2_1641 | 0.048172 | 0.32549 | 0.048196 | 0.32571
60 | 1 | feeder2_1689 | 0.048266 | 0.3255 | 0.048292 | 0.32572
60 | 1 | feeder2_1744 | 0.048646 | 0.32602 | 0.048667 | 0.32624
60 | 1 | feeder2_1817 | 0.048263 | 0.32559 | 0.048287 | 0.32581
60 | 1 | feeder2_1779 | 0.048304 | 0.32547 | 0.048332 | 0.32569
60 | 1 | feeder2_1800 | 0.04823 | 0.32555 | 0.048256 | 0.32578
60 | 1 | feeder2_1818 | 0.049774 | 0.32384 | 0.049798 | 0.32408
60 | 1 | feeder2_1753 | 0.048575 | 0.32595 | 0.048606 | 0.32617
60 | 1 | feeder2_1754 | 0.048993 | 0.3264 | 0.049014 | 0.32661
90 | 1.5 | secondary | 0.017212 | 0.0040449 | 0.017203 | 0.0040379
90 | 1.5 | feeder2_44 | 0.032009 | 0.021082 | 0.032001 | 0.021052
90 | 1.5 | feeder2_45 | 0.032555 | 0.021679 | 0.032547 | 0.021646
90 | 1.5 | feeder2_46 | 0.032181 | 0.021782 | 0.032173 | 0.021753
90 | 1.5 | feeder2_51 | 0.033499 | 0.022799 | 0.033491 | 0.022766
90 | 1.5 | feeder2_48 | 0.032995 | 0.021103 | 0.032984 | 0.021073
90 | 1.5 | feeder2_52 | 0.032524 | 0.025718 | 0.032512 | 0.02569
90 | 1.5 | feeder2_68 | 0.036386 | 0.025006 | 0.036375 | 0.024969
90 | 1.5 | feeder2_69 | 0.036443 | 0.025176 | 0.03643 | 0.025141
90 | 1.5 | feeder2_71 | 0.036769 | 0.025292 | 0.036759 | 0.025252
90 | 1.5 | feeder2_72 | 0.036922 | 0.025082 | 0.036911 | 0.025044
90 | 1.5 | feeder2_73 | 0.037969 | 0.026213 | 0.037959 | 0.026172
90 | 1.5 | feeder2_74 | 0.03784 | 0.026204 | 0.037829 | 0.026167
90 | 1.5 | feeder2_77 | 0.039005 | 0.027012 | 0.038991 | 0.02697
90 | 1.5 | feeder2_79 | 0.039116 | 0.027375 | 0.039103 | 0.027335
90 | 1.5 | feeder2_81 | 0.040625 | 0.028134 | 0.040614 | 0.02809
90 | 1.5 | feeder2_82 | 0.041015 | 0.027616 | 0.041003 | 0.027572
90 | 1.5 | feeder2_116 | 0.047924 | 0.033723 | 0.047911 | 0.033667
90 | 1.5 | feeder2_119 | 0.047161 | 0.03368 | 0.047148 | 0.033624
90 | 1.5 | feeder2_120 | 0.050738 | 0.035895 | 0.050722 | 0.035836
90 | 1.5 | feeder2_248 | 0.050253 | 0.035831 | 0.050238 | 0.035772
90 | 1.5 | feeder2_124 | 0.052512 | 0.037291 | 0.052498 | 0.037224
90 | 1.5 | feeder2_282 | 0.052596 | 0.037175 | 0.052579 | 0.037112
90 | 1.5 | feeder2_275 | 0.052325 | 0.037227 | 0.052308 | 0.037162
90 | 1.5 | feeder2_151 | 0.055627 | 0.039868 | 0.055612 | 0.039796
90 | 1.5 | feeder2_295 | 0.055671 | 0.039969 | 0.055656 | 0.039896
90 | 1.5 | feeder2_311 | 0.055745 | 0.040158 | 0.055727 | 0.040088
90 | 1.5 | feeder2_201 | 0.060732 | 0.043714 | 0.060715 | 0.043633
90 | 1.5 | feeder2_314 | 0.060787 | 0.043636 | 0.060767 | 0.043559
90 | 1.5 | feeder2_342 | 0.067999 | 0.049409 | 0.06798 | 0.049318
90 | 1.5 | feeder2_368 | 0.069109 | 0.056636 | 0.069091 | 0.056545
90 | 1.5 | feeder2_347 | 0.069701 | 0.038778 | 0.069677 | 0.038684
90 | 1.5 | feeder2_353 | 0.070548 | 0.033583 | 0.070529 | 0.033477
90 | 1.5 | feeder2_518 | 0.069857 | 0.038581 | 0.069835 | 0.038484
90 | 1.5 | feeder2_365 | 0.071523 | 0.027886 | 0.071497 | 0.027783
90 | 1.5 | feeder2_653 | 0.070227 | 0.033492 | 0.070204 | 0.03339
90 | 1.5 | feeder2_377 | 0.072054 | 0.024601 | 0.072032 | 0.024493
90 | 1.5 | feeder2_622 | 0.070709 | 0.028541 | 0.070689 | 0.028433
90 | 1.5 | feeder2_451 | 0.069247 | 0.056454 | 0.069224 | 0.056364
90 | 1.5 | feeder2_383 | 0.070933 | 0.068467 | 0.070915 | 0.068374
90 | 1.5 | feeder2_385 | 0.072661 | 0.020784 | 0.072637 | 0.020675
90 | 1.5 | feeder2_621 | 0.072102 | 0.02471 | 0.072083 | 0.024603
90 | 1.5 | feeder2_611 | 0.070026 | 0.069302 | 0.070003 | 0.069211
90 | 1.5 | feeder2_405 | 0.071068 | 0.069169 | 0.071047 | 0.069077
90 | 1.5 | feeder2_461 | 0.075251 | 0.0055818 | 0.075227 | 0.0054737
90 | 1.5 | feeder2_594 | 0.072344 | 0.020698 | 0.072324 | 0.020591
90 | 1.5 | feeder2_732 | 0.06919 | 0.071144 | 0.069167 | 0.071054
90 | 1.5 | feeder2_417 | 0.072254 | 0.074106 | 0.072233 | 0.074014
90 | 1.5 | feeder2_663 | 0.071814 | 0.074737 | 0.071793 | 0.074644
90 | 1.5 | feeder2_444 | 0.073169 | 0.077649 | 0.07315 | 0.077556
90 | 1.5 | feeder2_759 | 0.075563 | 0.075136 | 0.075546 | 0.075042
90 | 1.5 | feeder2_842 | 0.0858 | 0.10016 | 0.085782 | 0.10006
90 | 1.5 | feeder2_459 | 0.073181 | 0.077718 | 0.073162 | 0.077622
90 | 1.5 | feeder2_702 | 0.073207 | 0.07768 | 0.073191 | 0.077584
90 | 1.5 | feeder2_493 | 0.073225 | 0.077992 | 0.0732 | 0.0779
90 | 1.5 | feeder2_651 | 0.075329 | 0.0057776 | 0.075301 | 0.0056728
90 | 1.5 | feeder2_684 | 0.077337 | 0.0073199 | 0.077308 | 0.0074451
90 | 1.5 | feeder2_674 | 0.073174 | 0.077969 | 0.073157 | 0.077876
90 | 1.5 | feeder2_696 | 0.07341 | 0.0789 | 0.073394 | 0.078804
90 | 1.5 | feeder2_681 | 0.073085 | 0.077928 | 0.073067 | 0.077836
90 | 1.5 | feeder2_682 | 0.073097 | 0.07794 | 0.07308 | 0.077847
90 | 1.5 | feeder2_728 | 0.077268 | 0.0070387 | 0.07724 | 0.0071627
90 | 1.5 | feeder2_724 | 0.079554 | 0.020882 | 0.079524 | 0.021015
90 | 1.5 | feeder2_703 | 0.073746 | 0.079595 | 0.073728 | 0.079502
90 | 1.5 | feeder2_704 | 0.073481 | 0.07905 | 0.073457 | 0.078961
90 | 1.5 | feeder2_754 | 0.079727 | 0.021036 | 0.079703 | 0.021173
90 | 1.5 | feeder2_747 | 0.080461 | 0.026347 | 0.080437 | 0.026485
90 | 1.5 | feeder2_828 | 0.077216 | 0.0070614 | 0.077188 | 0.0071814
90 | 1.5 | feeder2_763 | 0.077189 | 0.0067901 | 0.077163 | 0.0069079
90 | 1.5 | feeder2_836 | 0.08054 | 0.026118 | 0.080509 | 0.026255
90 | 1.5 | feeder2_758 | 0.081228 | 0.031151 | 0.081199 | 0.031289
90 | 1.5 | feeder2_788 | 0.082797 | 0.032763 | 0.082771 | 0.032906
90 | 1.5 | feeder2_812 | 0.083241 | 0.043927 | 0.083211 | 0.044073
90 | 1.5 | feeder2_947 | 0.077562 | 0.0072874 | 0.077533 | 0.0074035
90 | 1.5 | feeder2_868 | 0.077314 | 0.006955 | 0.077286 | 0.0070678
90 | 1.5 | feeder2_785 | 0.077117 | 0.0065512 | 0.077087 | 0.006663
90 | 1.5 | feeder2_1176 | 0.075424 | 0.0067532 | 0.075399 | 0.0068131
90 | 1.5 | feeder2_846 | 0.076861 | 0.006581 | 0.076836 | 0.0066984
90 | 1.5 | feeder2_911 | 0.077125 | 0.0066277 | 0.077096 | 0.0067376
90 | 1.5 | feeder2_1107 | 0.083385 | 0.048391 | 0.083358 | 0.048542
90 | 1.5 | feeder2_920 | 0.083768 | 0.04629 | 0.083737 | 0.046438
90 | 1.5 | feeder2_926 | 0.084584 | 0.049732 | 0.084552 | 0.049883
90 | 1.5 | feeder2_1239 | 0.083732 | 0.046391 | 0.083699 | 0.046539
90 | 1.5 | feeder2_933 | 0.084826 | 0.050626 | 0.0848 | 0.050781
90 | 1.5 | feeder2_1146 | 0.085151 | 0.052714 | 0.085121 | 0.052867
90 | 1.5 | feeder2_1124 | 0.084877 | 0.050468 | 0.084844 | 0.05062
90 | 1.5 | feeder2_942 | 0.085415 | 0.053039 | 0.085384 | 0.053195
90 | 1.5 | feeder2_952 | 0.086722 | 0.057461 | 0.086689 | 0.057621
90 | 1.5 | feeder2_965 | 0.085358 | 0.052938 | 0.085328 | 0.053093
90 | 1.5 | feeder2_961 | 0.086814 | 0.057679 | 0.086783 | 0.057839
90 | 1.5 | feeder2_963 | 0.086732 | 0.057518 | 0.086701 | 0.057682
90 | 1.5 | feeder2_973 | 0.087309 | 0.058835 | 0.087276 | 0.058996
90 | 1.5 | feeder2_1128 | 0.086802 | 0.057712 | 0.086772 | 0.057876
90 | 1.5 | feeder2_1113 | 0.087959 | 0.058809 | 0.087928 | 0.05897
90 | 1.5 | feeder2_1143 | 0.086744 | 0.057678 | 0.086711 | 0.057839
90 | 1.5 | feeder2_1238 | 0.085485 | 0.05304 | 0.085455 | 0.053198
90 | 1.5 | feeder2_979 | 0.085283 | 0.052802 | 0.085251 | 0.052961
90 | 1.5 | feeder2_1236 | 0.088024 | 0.060753 | 0.08799 | 0.060916
90 | 1.5 | feeder2_989 | 0.087309 | 0.058834 | 0.087276 | 0.058996
90 | 1.5 | feeder2_1196 | 0.084527 | 0.05212 | 0.084499 | 0.052281
90 | 1.5 | feeder2_1158 | 0.087377 | 0.058682 | 0.087344 | 0.058845
90 | 1.5 | feeder2_1122 | 0.083418 | 0.050877 | 0.083385 | 0.051024
90 | 1.5 | feeder2_1258 | 0.082997 | 0.04758 | 0.08297 | 0.047731
90 | 1.5 | feeder2_1303 | 0.084974 | 0.052484 | 0.084944 | 0.052629
90 | 1.5 | feeder2_1138 | 0.083336 | 0.052302 | 0.083308 | 0.052451
90 | 1.5 | feeder2_1304 | 0.082789 | 0.052626 | 0.082761 | 0.052772
90 | 1.5 | feeder2_1212 | 0.083261 | 0.055073 | 0.083233 | 0.055223
90 | 1.5 | feeder2_1311 | 0.084921 | 0.056758 | 0.084895 | 0.056905
90 | 1.5 | feeder2_1290 | 0.082905 | 0.057245 | 0.082874 | 0.05739
90 | 1.5 | feeder2_1325 | 0.088988 | 0.064355 | 0.088956 | 0.064529
90 | 1.5 | feeder2_1248 | 0.088021 | 0.060749 | 0.087987 | 0.060913
90 | 1.5 | feeder2_1249 | 0.085507 | 0.053057 | 0.085478 | 0.053217
90 | 1.5 | feeder2_1250 | 0.08552 | 0.05307 | 0.08549 | 0.053227
90 | 1.5 | feeder2_1366 | 0.088096 | 0.060564 | 0.088061 | 0.060733
90 | 1.5 | feeder2_1266 | 0.082541 | 0.047036 | 0.08251 | 0.04718
90 | 1.5 | feeder2_1372 | 0.083099 | 0.057355 | 0.08307 | 0.0575
90 | 1.5 | feeder2_1363 | 0.082508 | 0.059605 | 0.08248 | 0.059751
90 | 1.5 | feeder2_1446 | 0.090495 | 0.065934 | 0.090459 | 0.066105
90 | 1.5 | feeder2_1502 | 0.089692 | 0.066379 | 0.089654 | 0.066554
90 | 1.5 | feeder2_1428 | 0.082013 | 0.059958 | 0.081986 | 0.060104
90 | 1.5 | feeder2_1380 | 0.082198 | 0.062029 | 0.082168 | 0.062169
90 | 1.5 | feeder2_1550 | 0.08224 | 0.062046 | 0.082207 | 0.062187
90 | 1.5 | feeder2_1386 | 0.082046 | 0.063261 | 0.082019 | 0.063404
90 | 1.5 | feeder2_1551 | 0.081886 | 0.063399 | 0.081857 | 0.063542
90 | 1.5 | feeder2_1400 | 0.081982 | 0.063824 | 0.081958 | 0.063969
90 | 1.5 | feeder2_1552 | 0.081768 | 0.064011 | 0.081741 | 0.064152
90 | 1.5 | feeder2_1408 | 0.081871 | 0.06491 | 0.081839 | 0.065048
90 | 1.5 | feeder2_1553 | 0.081 | 0.064978 | 0.080971 | 0.065117
90 | 1.5 | feeder2_1416 | 0.081888 | 0.065437 | 0.081859 | 0.065578
90 | 1.5 | feeder2_1530 | 0.083955 | 0.06737 | 0.083927 | 0.067516
90 | 1.5 | feeder2_1425 | 0.081709 | 0.065488 | 0.081677 | 0.065625
90 | 1.5 | feeder2_1589 | 0.080864 | 0.065466 | 0.080836 | 0.065603
90 | 1.5 | feeder2_1435 | 0.081707 | 0.065488 | 0.081681 | 0.065631
90 | 1.5 | feeder2_1621 | 0.081797 | 0.0652 | 0.081769 | 0.065339
90 | 1.5 | feeder2_1564 | 0.081633 | 0.065797 | 0.081603 | 0.065936
90 | 1.5 | feeder2_1704 | 0.089121 | 0.065675 | 0.089085 | 0.065852
90 | 1.5 | feeder2_1525 | 0.089867 | 0.067205 | 0.089836 | 0.067387
90 | 1.5 | feeder2_1716 | 0.089944 | 0.066993 | 0.089907 | 0.067173
90 | 1.5 | feeder2_1537 | 0.090056 | 0.068162 | 0.090021 | 0.068342
90 | 1.5 | feeder2_1645 | 0.089954 | 0.068221 | 0.089917 | 0.068403
90 | 1.5 | feeder2_1561 | 0.090282 | 0.069208 | 0.090243 | 0.069387
90 | 1.5 | feeder2_1657 | 0.091219 | 0.070189 | 0.091184 | 0.070379
90 | 1.5 | feeder2_1570 | 0.090336 | 0.06942 | 0.090299 | 0.069605
90 | 1.5 | feeder2_1756 | 0.093504 | 0.072738 | 0.093467 | 0.072924
90 | 1.5 | feeder2_1588 | 0.090347 | 0.069406 | 0.090311 | 0.069592
90 | 1.5 | feeder2_1628 | 0.09047 | 0.069537 | 0.090434 | 0.069726
90 | 1.5 | feeder2_1598 | 0.09036 | 0.069355 | 0.090325 | 0.069542
90 | 1.5 | feeder2_1816 | 0.088342 | 0.067658 | 0.088304 | 0.067842
90 | 1.5 | feeder2_1765 | 0.090528 | 0.068838 | 0.09049 | 0.069027
90 | 1.5 | feeder2_1641 | 0.090392 | 0.070006 | 0.090354 | 0.070204
90 | 1.5 | feeder2_1689 | 0.090198 | 0.069359 | 0.090163 | 0.069563
90 | 1.5 | feeder2_1744 | 0.091125 | 0.070775 | 0.091087 | 0.070968
90 | 1.5 | feeder2_1817 | 0.08996 | 0.068718 | 0.089921 | 0.068922
90 | 1.5 | feeder2_1779 | 0.090211 | 0.069318 | 0.090175 | 0.069522
90 | 1.5 | feeder2_1800 | 0.090144 | 0.06938 | 0.090106 | 0.069584
90 | 1.5 | feeder2_1818 | 0.089812 | 0.068803 | 0.089769 | 0.069017
90 | 1.5 | feeder2_1753 | 0.093362 | 0.07312 | 0.093322 | 0.073316
90 | 1.5 | feeder2_1754 | 0.091146 | 0.070797 | 0.091112 | 0.070993
120 | 2 | secondary | 0.0046809 | 0.023966 | 0.0046753 | 0.023963
120 | 2 | feeder2_44 | 0.008709 | 0.12497 | 0.0086957 | 0.12494
120 | 2 | feeder2_45 | 0.0088624 | 0.12883 | 0.0088533 | 0.1288
120 | 2 | feeder2_46 | 0.0090529 | 0.12556 | 0.0090413 | 0.12554
120 | 2 | feeder2_51 | 0.0091461 | 0.13562 | 0.0091317 | 0.1356
120 | 2 | feeder2_48 | 0.0082675 | 0.1282 | 0.0082562 | 0.12818
120 | 2 | feeder2_52 | 0.0092879 | 0.13566 | 0.0092785 | 0.13564
120 | 2 | feeder2_68 | 0.0099327 | 0.15477 | 0.0099224 | 0.15474
120 | 2 | feeder2_69 | 0.0099876 | 0.15492 | 0.0099775 | 0.15488
120 | 2 | feeder2_71 | 0.010038 | 0.1573 | 0.010025 | 0.15726
120 | 2 | feeder2_72 | 0.0098108 | 0.15706 | 0.0097999 | 0.15703
120 | 2 | feeder2_73 | 0.010372 | 0.16524 | 0.010359 | 0.16521
120 | 2 | feeder2_74 | 0.010463 | 0.16526 | 0.01045 | 0.16523
120 | 2 | feeder2_77 | 0.010655 | 0.17205 | 0.010641 | 0.17202
120 | 2 | feeder2_79 | 0.012151 | 0.17216 | 0.012139 | 0.17213
120 | 2 | feeder2_81 | 0.01103 | 0.18271 | 0.011016 | 0.18267
120 | 2 | feeder2_82 | 0.010477 | 0.18213 | 0.010463 | 0.18209
120 | 2 | feeder2_116 | 0.012863 | 0.23107 | 0.012849 | 0.23102
120 | 2 | feeder2_119 | 0.013302 | 0.23295 | 0.013293 | 0.23291
120 | 2 | feeder2_120 | 0.013382 | 0.24805 | 0.013369 | 0.248
120 | 2 | feeder2_248 | 0.013653 | 0.24992 | 0.013641 | 0.24987
120 | 2 | feeder2_124 | 0.013598 | 0.2578 | 0.013583 | 0.25775
120 | 2 | feeder2_282 | 0.01346 | 0.25766 | 0.013444 | 0.25761
120 | 2 | feeder2_275 | 0.013667 | 0.26081 | 0.013657 | 0.26075
120 | 2 | feeder2_151 | 0.013805 | 0.27302 | 0.013788 | 0.27297
120 | 2 | feeder2_295 | 0.013827 | 0.27311 | 0.013809 | 0.27306
120 | 2 | feeder2_311 | 0.013883 | 0.27327 | 0.013865 | 0.27321
120 | 2 | feeder2_201 | 0.01423 | 0.298 | 0.014206 | 0.29794
120 | 2 | feeder2_314 | 0.012699 | 0.29604 | 0.012677 | 0.29597
120 | 2 | feeder2_342 | 0.015867 | 0.3379 | 0.015844 | 0.33783
120 | 2 | feeder2_368 | 0.015938 | 0.34343 | 0.015911 | 0.34337
120 | 2 | feeder2_347 | 0.017384 | 0.34722 | 0.01736 | 0.34715
120 | 2 | feeder2_353 | 0.018243 | 0.35199 | 0.01822 | 0.35192
120 | 2 | feeder2_518 | 0.01712 | 0.34696 | 0.017096 | 0.34689
120 | 2 | feeder2_365 | 0.019208 | 0.35728 | 0.019188 | 0.3572
120 | 2 | feeder2_653 | 0.018482 | 0.35203 | 0.018457 | 0.35195
120 | 2 | feeder2_377 | 0.019753 | 0.36014 | 0.019733 | 0.36007
120 | 2 | feeder2_622 | 0.019213 | 0.35731 | 0.019191 | 0.35724
120 | 2 | feeder2_451 | 0.015683 | 0.34319 | 0.015654 | 0.34313
120 | 2 | feeder2_383 | 0.01655 | 0.35262 | 0.016518 | 0.35256
120 | 2 | feeder2_385 | 0.020399 | 0.36341 | 0.020379 | 0.36333
120 | 2 | feeder2_621 | 0.019763 | 0.36024 | 0.019741 | 0.36016
120 | 2 | feeder2_611 | 0.016633 | 0.35263 | 0.016601 | 0.35257
120 | 2 | feeder2_405 | 0.016604 | 0.3532 | 0.016574 | 0.35313
120 | 2 | feeder2_461 | 0.022784 | 0.37479 | 0.022766 | 0.3747
120 | 2 | feeder2_594 | 0.020653 | 0.36457 | 0.020634 | 0.36449
120 | 2 | feeder2_732 | 0.015766 | 0.35487 | 0.015734 | 0.3548
120 | 2 | feeder2_417 | 0.017098 | 0.35721 | 0.017065 | 0.35714
120 | 2 | feeder2_663 | 0.017185 | 0.35736 | 0.017152 | 0.3573
120 | 2 | feeder2_444 | 0.017551 | 0.36022 | 0.017515 | 0.36017
120 | 2 | feeder2_759 | 0.017395 | 0.36008 | 0.01736 | 0.36001
120 | 2 | feeder2_842 | 0.037056 | 0.37936 | 0.037021 | 0.3793
120 | 2 | feeder2_459 | 0.017537 | 0.36012 | 0.017505 | 0.36006
120 | 2 | feeder2_702 | 0.017133 | 0.35855 | 0.017102 | 0.35849
120 | 2 | feeder2_493 | 0.017594 | 0.36039 | 0.017563 | 0.36032
120 | 2 | feeder2_651 | 0.022793 | 0.37496 | 0.022773 | 0.37487
120 | 2 | feeder2_684 | 0.024839 | 0.38383 | 0.024822 | 0.38373
120 | 2 | feeder2_674 | 0.01761 | 0.36038 | 0.017577 | 0.36032
120 | 2 | feeder2_696 | 0.017723 | 0.36119 | 0.017691 | 0.36112
120 | 2 | feeder2_681 | 0.017641 | 0.36038 | 0.017605 | 0.36032
120 | 2 | feeder2_682 | 0.01763 | 0.36038 | 0.017596 | 0.36032
120 | 2 | feeder2_728 | 0.024824 | 0.3836 | 0.024805 | 0.38351
120 | 2 | feeder2_724 | 0.027008 | 0.3936 | 0.026988 | 0.39351
120 | 2 | feeder2_703 | 0.01825 | 0.36178 | 0.018214 | 0.36172
120 | 2 | feeder2_704 | 0.017837 | 0.36131 | 0.017804 | 0.36125
120 | 2 | feeder2_754 | 0.026779 | 0.39334 | 0.026762 | 0.39324
120 | 2 | feeder2_747 | 0.02792 | 0.39773 | 0.0279 | 0.39763
120 | 2 | feeder2_828 | 0.024871 | 0.3836 | 0.024852 | 0.38351
120 | 2 | feeder2_763 | 0.02478 | 0.38327 | 0.024761 | 0.38318
120 | 2 | feeder2_836 | 0.030154 | 0.39784 | 0.030135 | 0.39774
120 | 2 | feeder2_758 | 0.028628 | 0.40112 | 0.028606 | 0.40101
120 | 2 | feeder2_788 | 0.028337 | 0.40077 | 0.028318 | 0.40067
120 | 2 | feeder2_812 | 0.030919 | 0.41199 | 0.030901 | 0.41187
120 | 2 | feeder2_947 | 0.024264 | 0.38269 | 0.024244 | 0.38259
120 | 2 | feeder2_868 | 0.024606 | 0.38307 | 0.024585 | 0.38298
120 | 2 | feeder2_785 | 0.024804 | 0.38332 | 0.024783 | 0.38323
120 | 2 | feeder2_1176 | 0.024787 | 0.38374 | 0.024764 | 0.38364
120 | 2 | feeder2_846 | 0.025033 | 0.38334 | 0.025012 | 0.38325
120 | 2 | feeder2_911 | 0.024787 | 0.38323 | 0.024769 | 0.38314
120 | 2 | feeder2_1107 | 0.032428 | 0.41882 | 0.032412 | 0.41871
120 | 2 | feeder2_920 | 0.031167 | 0.41318 | 0.031148 | 0.41306
120 | 2 | feeder2_926 | 0.031415 | 0.41443 | 0.031395 | 0.41432
120 | 2 | feeder2_1239 | 0.03131 | 0.41379 | 0.031295 | 0.41368
120 | 2 | feeder2_933 | 0.031527 | 0.41501 | 0.031511 | 0.4149
120 | 2 | feeder2_1146 | 0.031409 | 0.41431 | 0.031392 | 0.4142
120 | 2 | feeder2_1124 | 0.031501 | 0.41514 | 0.031481 | 0.41503
120 | 2 | feeder2_942 | 0.031829 | 0.41637 | 0.031808 | 0.41625
120 | 2 | feeder2_952 | 0.032225 | 0.41848 | 0.032205 | 0.41836
120 | 2 | feeder2_965 | 0.031835 | 0.41636 | 0.031819 | 0.41624
120 | 2 | feeder2_961 | 0.03227 | 0.41874 | 0.03225 | 0.41862
120 | 2 | feeder2_963 | 0.032224 | 0.41847 | 0.032207 | 0.41836
120 | 2 | feeder2_973 | 0.032501 | 0.42012 | 0.032484 | 0.42
120 | 2 | feeder2_1128 | 0.032282 | 0.41873 | 0.032264 | 0.41861
120 | 2 | feeder2_1113 | 0.032183 | 0.41842 | 0.032161 | 0.4183
120 | 2 | feeder2_1143 | 0.032202 | 0.4182 | 0.032182 | 0.41808
120 | 2 | feeder2_1238 | 0.03168 | 0.41615 | 0.031665 | 0.41604
120 | 2 | feeder2_979 | 0.031845 | 0.41636 | 0.031826 | 0.41624
120 | 2 | feeder2_1236 | 0.032867 | 0.42206 | 0.032848 | 0.42194
120 | 2 | feeder2_989 | 0.0325 | 0.42012 | 0.032483 | 0.42
120 | 2 | feeder2_1196 | 0.032014 | 0.41637 | 0.031996 | 0.41626
120 | 2 | feeder2_1158 | 0.032455 | 0.42026 | 0.032434 | 0.42014
120 | 2 | feeder2_1122 | 0.033036 | 0.42128 | 0.033023 | 0.42116
120 | 2 | feeder2_1258 | 0.033016 | 0.41902 | 0.032999 | 0.41891
120 | 2 | feeder2_1303 | 0.032962 | 0.42117 | 0.032948 | 0.42105
120 | 2 | feeder2_1138 | 0.033529 | 0.42328 | 0.033515 | 0.42316
120 | 2 | feeder2_1304 | 0.034477 | 0.42454 | 0.034466 | 0.42442
120 | 2 | feeder2_1212 | 0.034338 | 0.42663 | 0.034329 | 0.42651
120 | 2 | feeder2_1311 | 0.034243 | 0.42649 | 0.034231 | 0.42636
120 | 2 | feeder2_1290 | 0.035385 | 0.43099 | 0.035376 | 0.43087
120 | 2 | feeder2_1325 | 0.033335 | 0.42438 | 0.033312 | 0.42425
120 | 2 | feeder2_1248 | 0.032871 | 0.42206 | 0.032852 | 0.42194
120 | 2 | feeder2_1249 | 0.031652 | 0.41612 | 0.031634 | 0.416
120 | 2 | feeder2_1250 | 0.031637 | 0.4161 | 0.031622 | 0.41599
120 | 2 | feeder2_1366 | 0.032826 | 0.42223 | 0.032803 | 0.42211
120 | 2 | feeder2_1266 | 0.032995 | 0.41908 | 0.032978 | 0.41897
120 | 2 | feeder2_1372 | 0.034084 | 0.42977 | 0.034074 | 0.42964
120 | 2 | feeder2_1363 | 0.036888 | 0.43759 | 0.036878 | 0.43746
120 | 2 | feeder2_1446 | 0.032401 | 0.42346 | 0.032381 | 0.42334
120 | 2 | feeder2_1502 | 0.034113 | 0.42823 | 0.034091 | 0.4281
120 | 2 | feeder2_1428 | 0.037927 | 0.43892 | 0.037917 | 0.43879
120 | 2 | feeder2_1380 | 0.038221 | 0.44373 | 0.038215 | 0.44359
120 | 2 | feeder2_1550 | 0.038182 | 0.44367 | 0.038179 | 0.44353
120 | 2 | feeder2_1386 | 0.038884 | 0.44678 | 0.038879 | 0.44665
120 | 2 | feeder2_1551 | 0.04042 | 0.44961 | 0.040417 | 0.44948
120 | 2 | feeder2_1400 | 0.039071 | 0.44762 | 0.039067 | 0.44748
120 | 2 | feeder2_1552 | 0.039286 | 0.44763 | 0.039279 | 0.44749
120 | 2 | feeder2_1408 | 0.039441 | 0.44935 | 0.039435 | 0.44921
120 | 2 | feeder2_1553 | 0.041746 | 0.45328 | 0.041745 | 0.45315
120 | 2 | feeder2_1416 | 0.039455 | 0.44942 | 0.039452 | 0.44929
120 | 2 | feeder2_1530 | 0.037769 | 0.44793 | 0.03776 | 0.44779
120 | 2 | feeder2_1425 | 0.039644 | 0.45039 | 0.039637 | 0.45025
120 | 2 | feeder2_1589 | 0.040759 | 0.45224 | 0.040758 | 0.4521
120 | 2 | feeder2_1435 | 0.039645 | 0.45042 | 0.039639 | 0.45028
120 | 2 | feeder2_1621 | 0.039525 | 0.45065 | 0.039523 | 0.45051
120 | 2 | feeder2_1564 | 0.039716 | 0.45046 | 0.039713 | 0.45032
120 | 2 | feeder2_1704 | 0.03407 | 0.42849 | 0.034045 | 0.42836
120 | 2 | feeder2_1525 | 0.034328 | 0.42913 | 0.034306 | 0.429
120 | 2 | feeder2_1716 | 0.037852 | 0.42936 | 0.037825 | 0.42923
120 | 2 | feeder2_1537 | 0.03453 | 0.43003 | 0.034511 | 0.4299
120 | 2 | feeder2_1645 | 0.035073 | 0.43153 | 0.035053 | 0.43139
120 | 2 | feeder2_1561 | 0.034606 | 0.43027 | 0.034585 | 0.43014
120 | 2 | feeder2_1657 | 0.0345 | 0.43014 | 0.034478 | 0.43001
120 | 2 | feeder2_1570 | 0.034642 | 0.43041 | 0.034616 | 0.43027
120 | 2 | feeder2_1756 | 0.034436 | 0.43015 | 0.034417 | 0.43001
120 | 2 | feeder2_1588 | 0.034675 | 0.43055 | 0.034656 | 0.43042
120 | 2 | feeder2_1628 | 0.033817 | 0.4297 | 0.033794 | 0.42956
120 | 2 | feeder2_1598 | 0.034768 | 0.43099 | 0.034747 | 0.43085
120 | 2 | feeder2_1816 | 0.037406 | 0.43139 | 0.037379 | 0.43126
120 | 2 | feeder2_1765 | 0.034677 | 0.43143 | 0.034653 | 0.4313
120 | 2 | feeder2_1641 | 0.035207 | 0.43267 | 0.035188 | 0.43253
120 | 2 | feeder2_1689 | 0.035591 | 0.43424 | 0.035571 | 0.4341
120 | 2 | feeder2_1744 | 0.035136 | 0.43258 | 0.035115 | 0.43244
120 | 2 | feeder2_1817 | 0.03581 | 0.43532 | 0.035789 | 0.43518
120 | 2 | feeder2_1779 | 0.035583 | 0.43428 | 0.035563 | 0.43413
120 | 2 | feeder2_1800 | 0.035964 | 0.4353 | 0.035942 | 0.43515
120 | 2 | feeder2_1818 | 0.036321 | 0.43205 | 0.036289 | 0.4319
120 | 2 | feeder2_1753 | 0.035025 | 0.43243 | 0.035005 | 0.43229
120 | 2 | feeder2_1754 | 0.035112 | 0.43255 | 0.035091 | 0.43241
150 | 2.5 | secondary | 0.0096094 | 0.013454 | 0.0096023 | 0.01345
150 | 2.5 | feeder2_44 | 0.017872 | 0.070126 | 0.01785 | 0.070101
150 | 2.5 | feeder2_45 | 0.018154 | 0.072202 | 0.018135 | 0.072174
150 | 2.5 | feeder2_46 | 0.017896 | 0.071231 | 0.017865 | 0.071216
150 | 2.5 | feeder2_51 | 0.018648 | 0.075885 | 0.018628 | 0.075857
150 | 2.5 | feeder2_48 | 0.018363 | 0.071654 | 0.018348 | 0.071625
150 | 2.5 | feeder2_52 | 0.01844 | 0.075863 | 0.018422 | 0.075829
150 | 2.5 | feeder2_68 | 0.020055 | 0.086257 | 0.020037 | 0.086219
150 | 2.5 | feeder2_69 | 0.02018 | 0.086432 | 0.020158 | 0.086398
150 | 2.5 | feeder2_71 | 0.020239 | 0.087621 | 0.020218 | 0.087582
150 | 2.5 | feeder2_72 | 0.0203 | 0.087417 | 0.02028 | 0.08738
150 | 2.5 | feeder2_73 | 0.020819 | 0.09191 | 0.020795 | 0.09187
150 | 2.5 | feeder2_74 | 0.019525 | 0.093364 | 0.019507 | 0.093319
150 | 2.5 | feeder2_77 | 0.021377 | 0.095384 | 0.021359 | 0.095336
150 | 2.5 | feeder2_79 | 0.021636 | 0.095752 | 0.021618 | 0.095708
150 | 2.5 | feeder2_81 | 0.022229 | 0.10073 | 0.022212 | 0.10068
150 | 2.5 | feeder2_82 | 0.02241 | 0.10021 | 0.02239 | 0.10016
150 | 2.5 | feeder2_116 | 0.026092 | 0.12519 | 0.026066 | 0.12513
150 | 2.5 | feeder2_119 | 0.025338 | 0.12516 | 0.02531 | 0.12509
150 | 2.5 | feeder2_120 | 0.027595 | 0.13432 | 0.027568 | 0.13425
150 | 2.5 | feeder2_248 | 0.027126 | 0.13428 | 0.027102 | 0.1342
150 | 2.5 | feeder2_124 | 0.028548 | 0.13998 | 0.028522 | 0.1399
150 | 2.5 | feeder2_282 | 0.028576 | 0.13986 | 0.028548 | 0.13978
150 | 2.5 | feeder2_275 | 0.026017 | 0.1425 | 0.026001 | 0.14242
150 | 2.5 | feeder2_151 | 0.030674 | 0.14842 | 0.030651 | 0.14834
150 | 2.5 | feeder2_295 | 0.030751 | 0.14851 | 0.030719 | 0.14845
150 | 2.5 | feeder2_311 | 0.03089 | 0.1487 | 0.030863 | 0.14863
150 | 2.5 | feeder2_201 | 0.034106 | 0.16204 | 0.034077 | 0.16197
150 | 2.5 | feeder2_314 | 0.034845 | 0.16118 | 0.03482 | 0.16111
150 | 2.5 | feeder2_342 | 0.038787 | 0.18334 | 0.038752 | 0.18327
150 | 2.5 | feeder2_368 | 0.04048 | 0.1903 | 0.040449 | 0.19023
150 | 2.5 | feeder2_347 | 0.038484 | 0.18088 | 0.038448 | 0.18079
150 | 2.5 | feeder2_353 | 0.038345 | 0.17976 | 0.038317 | 0.17967
150 | 2.5 | feeder2_518 | 0.038541 | 0.18066 | 0.03851 | 0.18057
150 | 2.5 | feeder2_365 | 0.038218 | 0.17858 | 0.038192 | 0.17848
150 | 2.5 | feeder2_653 | 0.038037 | 0.17971 | 0.038005 | 0.17963
150 | 2.5 | feeder2_377 | 0.038148 | 0.17793 | 0.03812 | 0.17783
150 | 2.5 | feeder2_622 | 0.038246 | 0.17862 | 0.038212 | 0.17852
150 | 2.5 | feeder2_451 | 0.040522 | 0.1901 | 0.040487 | 0.19004
150 | 2.5 | feeder2_383 | 0.04327 | 0.20176 | 0.043233 | 0.2017
150 | 2.5 | feeder2_385 | 0.03806 | 0.17714 | 0.03803 | 0.17704
150 | 2.5 | feeder2_621 | 0.038229 | 0.17803 | 0.038203 | 0.17793
150 | 2.5 | feeder2_611 | 0.043068 | 0.20171 | 0.043027 | 0.20166
150 | 2.5 | feeder2_405 | 0.043449 | 0.20248 | 0.043407 | 0.20243
150 | 2.5 | feeder2_461 | 0.037796 | 0.17411 | 0.037771 | 0.17399
150 | 2.5 | feeder2_594 | 0.037755 | 0.17709 | 0.037722 | 0.17699
150 | 2.5 | feeder2_732 | 0.043134 | 0.20241 | 0.043096 | 0.20235
150 | 2.5 | feeder2_417 | 0.044814 | 0.20795 | 0.044779 | 0.20789
150 | 2.5 | feeder2_663 | 0.044899 | 0.20849 | 0.044853 | 0.20844
150 | 2.5 | feeder2_444 | 0.045813 | 0.21192 | 0.045774 | 0.21186
150 | 2.5 | feeder2_759 | 0.045823 | 0.2118 | 0.045787 | 0.21174
150 | 2.5 | feeder2_842 | 0.0645 | 0.23378 | 0.064435 | 0.23375
150 | 2.5 | feeder2_459 | 0.045817 | 0.21201 | 0.045775 | 0.21196
150 | 2.5 | feeder2_702 | 0.047021 | 0.21061 | 0.046984 | 0.21056
150 | 2.5 | feeder2_493 | 0.045729 | 0.21291 | 0.045688 | 0.21286
150 | 2.5 | feeder2_651 | 0.03794 | 0.17431 | 0.037909 | 0.17419
150 | 2.5 | feeder2_684 | 0.037544 | 0.17143 | 0.037517 | 0.1713
150 | 2.5 | feeder2_674 | 0.045303 | 0.21322 | 0.045259 | 0.21317
150 | 2.5 | feeder2_696 | 0.046074 | 0.2143 | 0.046035 | 0.21425
150 | 2.5 | feeder2_681 | 0.044731 | 0.21362 | 0.044688 | 0.21357
150 | 2.5 | feeder2_682 | 0.04441 | 0.21392 | 0.044366 | 0.21387
150 | 2.5 | feeder2_728 | 0.037684 | 0.17027 | 0.037658 | 0.17013
150 | 2.5 | feeder2_724 | 0.037167 | 0.1714 | 0.037142 | 0.17125
150 | 2.5 | feeder2_703 | 0.046622 | 0.21498 | 0.046579 | 0.21494
150 | 2.5 | feeder2_704 | 0.046174 | 0.2146 | 0.046133 | 0.21455
150 | 2.5 | feeder2_754 | 0.03724 | 0.17117 | 0.037214 | 0.17103
150 | 2.5 | feeder2_747 | 0.037021 | 0.1715 | 0.036998 | 0.17135
150 | 2.5 | feeder2_828 | 0.037635 | 0.17026 | 0.037608 | 0.17012
150 | 2.5 | feeder2_763 | 0.037914 | 0.16857 | 0.037892 | 0.16843
150 | 2.5 | feeder2_836 | 0.037176 | 0.17171 | 0.037148 | 0.17157
150 | 2.5 | feeder2_758 | 0.036875 | 0.17149 | 0.036846 | 0.17134
150 | 2.5 | feeder2_788 | 0.036977 | 0.17119 | 0.03695 | 0.17104
150 | 2.5 | feeder2_812 | 0.036451 | 0.17182 | 0.036423 | 0.17165
150 | 2.5 | feeder2_947 | 0.03809 | 0.16806 | 0.038068 | 0.16793
150 | 2.5 | feeder2_868 | 0.038503 | 0.16785 | 0.038483 | 0.16771
150 | 2.5 | feeder2_785 | 0.037967 | 0.16817 | 0.037948 | 0.16802
150 | 2.5 | feeder2_1176 | 0.038305 | 0.16864 | 0.038283 | 0.16849
150 | 2.5 | feeder2_846 | 0.037209 | 0.16869 | 0.037186 | 0.16855
150 | 2.5 | feeder2_911 | 0.038334 | 0.16649 | 0.038312 | 0.16634
150 | 2.5 | feeder2_1107 | 0.035557 | 0.17341 | 0.035527 | 0.17322
150 | 2.5 | feeder2_920 | 0.036579 | 0.17149 | 0.036555 | 0.17131
150 | 2.5 | feeder2_926 | 0.036793 | 0.17103 | 0.036767 | 0.17086
150 | 2.5 | feeder2_1239 | 0.036553 | 0.17145 | 0.036527 | 0.17127
150 | 2.5 | feeder2_933 | 0.036855 | 0.1711 | 0.036829 | 0.17093
150 | 2.5 | feeder2_1146 | 0.036945 | 0.16978 | 0.036916 | 0.16961
150 | 2.5 | feeder2_1124 | 0.036963 | 0.17125 | 0.036939 | 0.17108
150 | 2.5 | feeder2_942 | 0.036984 | 0.17114 | 0.036954 | 0.17097
150 | 2.5 | feeder2_952 | 0.037071 | 0.17243 | 0.037042 | 0.17227
150 | 2.5 | feeder2_965 | 0.036997 | 0.17098 | 0.036967 | 0.17082
150 | 2.5 | feeder2_961 | 0.037069 | 0.1727 | 0.037044 | 0.17254
150 | 2.5 | feeder2_963 | 0.037073 | 0.17241 | 0.037042 | 0.17225
150 | 2.5 | feeder2_973 | 0.037159 | 0.17382 | 0.037129 | 0.17367
150 | 2.5 | feeder2_1128 | 0.036897 | 0.17322 | 0.036868 | 0.17305
150 | 2.5 | feeder2_1113 | 0.037543 | 0.17188 | 0.03751 | 0.17172
150 | 2.5 | feeder2_1143 | 0.037055 | 0.17218 | 0.037027 | 0.17202
150 | 2.5 | feeder2_1238 | 0.039101 | 0.16866 | 0.039073 | 0.16849
150 | 2.5 | feeder2_979 | 0.036991 | 0.17097 | 0.036966 | 0.1708
150 | 2.5 | feeder2_1236 | 0.037187 | 0.17503 | 0.037151 | 0.17488
150 | 2.5 | feeder2_989 | 0.03716 | 0.17383 | 0.037132 | 0.17367
150 | 2.5 | feeder2_1196 | 0.036817 | 0.17094 | 0.03679 | 0.17078
150 | 2.5 | feeder2_1158 | 0.037077 | 0.17428 | 0.037044 | 0.17413
150 | 2.5 | feeder2_1122 | 0.035156 | 0.1738 | 0.035124 | 0.17361
150 | 2.5 | feeder2_1258 | 0.035778 | 0.17371 | 0.035753 | 0.17352
150 | 2.5 | feeder2_1303 | 0.035171 | 0.17371 | 0.035145 | 0.17352
150 | 2.5 | feeder2_1138 | 0.034844 | 0.17415 | 0.034815 | 0.17395
150 | 2.5 | feeder2_1304 | 0.034301 | 0.17412 | 0.03427 | 0.17391
150 | 2.5 | feeder2_1212 | 0.034254 | 0.17499 | 0.034226 | 0.17478
150 | 2.5 | feeder2_1311 | 0.034276 | 0.17486 | 0.034251 | 0.17465
150 | 2.5 | feeder2_1290 | 0.033538 | 0.17616 | 0.033505 | 0.17593
150 | 2.5 | feeder2_1325 | 0.036944 | 0.17536 | 0.036917 | 0.17519
150 | 2.5 | feeder2_1248 | 0.037185 | 0.17503 | 0.037149 | 0.17488
150 | 2.5 | feeder2_1249 | 0.039106 | 0.16863 | 0.039082 | 0.16846
150 | 2.5 | feeder2_1250 | 0.040573 | 0.16711 | 0.04055 | 0.16694
150 | 2.5 | feeder2_1366 | 0.036841 | 0.17619 | 0.03679 | 0.17606
150 | 2.5 | feeder2_1266 | 0.03583 | 0.17377 | 0.035804 | 0.17358
150 | 2.5 | feeder2_1372 | 0.033614 | 0.1759 | 0.033587 | 0.17568
150 | 2.5 | feeder2_1363 | 0.032793 | 0.1778 | 0.032766 | 0.17756
150 | 2.5 | feeder2_1446 | 0.036984 | 0.17523 | 0.036957 | 0.17507
150 | 2.5 | feeder2_1502 | 0.036688 | 0.17589 | 0.036656 | 0.17572
150 | 2.5 | feeder2_1428 | 0.032301 | 0.17779 | 0.032275 | 0.17754
150 | 2.5 | feeder2_1380 | 0.032013 | 0.17995 | 0.031987 | 0.1797
150 | 2.5 | feeder2_1550 | 0.032029 | 0.17989 | 0.032002 | 0.17964
150 | 2.5 | feeder2_1386 | 0.031635 | 0.18105 | 0.031606 | 0.18079
150 | 2.5 | feeder2_1551 | 0.030688 | 0.18194 | 0.030658 | 0.18168
150 | 2.5 | feeder2_1400 | 0.031513 | 0.18138 | 0.031484 | 0.18112
150 | 2.5 | feeder2_1552 | 0.029987 | 0.18289 | 0.029966 | 0.18263
150 | 2.5 | feeder2_1408 | 0.031471 | 0.18136 | 0.03144 | 0.1811
150 | 2.5 | feeder2_1553 | 0.031133 | 0.18135 | 0.031106 | 0.18109
150 | 2.5 | feeder2_1416 | 0.031461 | 0.18136 | 0.031429 | 0.1811
150 | 2.5 | feeder2_1530 | 0.031518 | 0.18114 | 0.031492 | 0.18088
150 | 2.5 | feeder2_1425 | 0.031451 | 0.18147 | 0.031419 | 0.1812
150 | 2.5 | feeder2_1589 | 0.031216 | 0.18147 | 0.031189 | 0.1812
150 | 2.5 | feeder2_1435 | 0.031452 | 0.18149 | 0.031419 | 0.18123
150 | 2.5 | feeder2_1621 | 0.031665 | 0.18176 | 0.031634 | 0.18149
150 | 2.5 | feeder2_1564 | 0.031399 | 0.18145 | 0.031369 | 0.18118
150 | 2.5 | feeder2_1704 | 0.036891 | 0.17618 | 0.036861 | 0.176
150 | 2.5 | feeder2_1525 | 0.0366 | 0.17592 | 0.036574 | 0.17574
150 | 2.5 | feeder2_1716 | 0.03642 | 0.1766 | 0.03638 | 0.17644
150 | 2.5 | feeder2_1537 | 0.036475 | 0.17582 | 0.036449 | 0.17564
150 | 2.5 | feeder2_1645 | 0.035869 | 0.17631 | 0.035843 | 0.17612
150 | 2.5 | feeder2_1561 | 0.036424 | 0.17548 | 0.036399 | 0.17529
150 | 2.5 | feeder2_1657 | 0.036461 | 0.17537 | 0.036436 | 0.17518
150 | 2.5 | feeder2_1570 | 0.036404 | 0.17535 | 0.03638 | 0.17516
150 | 2.5 | feeder2_1756 | 0.036452 | 0.17514 | 0.036429 | 0.17494
150 | 2.5 | feeder2_1588 | 0.036387 | 0.17525 | 0.036361 | 0.17505
150 | 2.5 | feeder2_1628 | 0.03644 | 0.1751 | 0.036416 | 0.17491
150 | 2.5 | feeder2_1598 | 0.036369 | 0.17516 | 0.036343 | 0.17497
150 | 2.5 | feeder2_1816 | 0.036658 | 0.17554 | 0.036635 | 0.17534
150 | 2.5 | feeder2_1765 | 0.036723 | 0.17566 | 0.036693 | 0.17546
150 | 2.5 | feeder2_1641 | 0.03621 | 0.17438 | 0.036182 | 0.17416
150 | 2.5 | feeder2_1689 | 0.035898 | 0.17514 | 0.035876 | 0.17491
150 | 2.5 | feeder2_1744 | 0.037 | 0.1735 | 0.036981 | 0.17328
150 | 2.5 | feeder2_1817 | 0.035885 | 0.17511 | 0.03586 | 0.17488
150 | 2.5 | feeder2_1779 | 0.035925 | 0.17518 | 0.035904 | 0.17495
150 | 2.5 | feeder2_1800 | 0.03467 | 0.17642 | 0.034654 | 0.17619
150 | 2.5 | feeder2_1818 | 0.035538 | 0.17431 | 0.035544 | 0.17406
150 | 2.5 | feeder2_1753 | 0.037028 | 0.17338 | 0.037008 | 0.17317
150 | 2.5 | feeder2_1754 | 0.037541 | 0.17292 | 0.037521 | 0.1727
180 | 3 | secondary | 0.019715 | 0.0038344 | 0.019713 | 0.0038487
180 | 3 | feeder2_44 | 0.036667 | 0.019986 | 0.036661 | 0.020061
180 | 3 | feeder2_45 | 0.037298 | 0.020316 | 0.03729 | 0.020394
180 | 3 | feeder2_46 | 0.035175 | 0.023372 | 0.035164 | 0.023463
180 | 3 | feeder2_51 | 0.0383 | 0.02135 | 0.038291 | 0.021426
180 | 3 | feeder2_48 | 0.040576 | 0.017225 | 0.040569 | 0.017323
180 | 3 | feeder2_52 | 0.038086 | 0.021181 | 0.038076 | 0.021263
180 | 3 | feeder2_68 | 0.041148 | 0.024351 | 0.041139 | 0.02443
180 | 3 | feeder2_69 | 0.041221 | 0.024536 | 0.041215 | 0.024609
180 | 3 | feeder2_71 | 0.041524 | 0.024741 | 0.041518 | 0.024817
180 | 3 | feeder2_72 | 0.04166 | 0.024676 | 0.041653 | 0.024751
180 | 3 | feeder2_73 | 0.042705 | 0.025969 | 0.042692 | 0.026048
180 | 3 | feeder2_74 | 0.04189 | 0.026429 | 0.041882 | 0.026491
180 | 3 | feeder2_77 | 0.043772 | 0.026995 | 0.043759 | 0.027075
180 | 3 | feeder2_79 | 0.043916 | 0.027402 | 0.043904 | 0.02748
180 | 3 | feeder2_81 | 0.045438 | 0.028466 | 0.045427 | 0.028552
180 | 3 | feeder2_82 | 0.045789 | 0.028262 | 0.045782 | 0.028345
180 | 3 | feeder2_116 | 0.052943 | 0.035214 | 0.052933 | 0.035306
180 | 3 | feeder2_119 | 0.052171 | 0.03469 | 0.052157 | 0.034776
180 | 3 | feeder2_120 | 0.055827 | 0.038043 | 0.055814 | 0.03814
180 | 3 | feeder2_248 | 0.055338 | 0.037702 | 0.055328 | 0.037796
180 | 3 | feeder2_124 | 0.057642 | 0.039935 | 0.057633 | 0.040039
180 | 3 | feeder2_282 | 0.057716 | 0.039895 | 0.057704 | 0.040002
180 | 3 | feeder2_275 | 0.056866 | 0.040087 | 0.056854 | 0.04018
180 | 3 | feeder2_151 | 0.060972 | 0.043252 | 0.060959 | 0.043374
180 | 3 | feeder2_295 | 0.061023 | 0.043353 | 0.061012 | 0.043474
180 | 3 | feeder2_311 | 0.061112 | 0.043549 | 0.061103 | 0.043667
180 | 3 | feeder2_201 | 0.066432 | 0.048345 | 0.066416 | 0.048497
180 | 3 | feeder2_314 | 0.066478 | 0.048334 | 0.066467 | 0.048485
180 | 3 | feeder2_342 | 0.074207 | 0.055671 | 0.074194 | 0.055857
180 | 3 | feeder2_368 | 0.075347 | 0.062146 | 0.075331 | 0.062303
180 | 3 | feeder2_347 | 0.076142 | 0.048207 | 0.076132 | 0.04849
180 | 3 | feeder2_353 | 0.077107 | 0.045116 | 0.07709 | 0.045459
180 | 3 | feeder2_518 | 0.07628 | 0.048202 | 0.076266 | 0.048491
180 | 3 | feeder2_365 | 0.078209 | 0.04248 | 0.078196 | 0.042893
180 | 3 | feeder2_653 | 0.076784 | 0.044812 | 0.07677 | 0.045151
180 | 3 | feeder2_377 | 0.078802 | 0.040941 | 0.078789 | 0.041392
180 | 3 | feeder2_622 | 0.077522 | 0.044116 | 0.07751 | 0.044526
180 | 3 | feeder2_451 | 0.075469 | 0.062081 | 0.075449 | 0.062244
180 | 3 | feeder2_383 | 0.077215 | 0.073054 | 0.077194 | 0.073174
180 | 3 | feeder2_385 | 0.079477 | 0.03946 | 0.079468 | 0.039953
180 | 3 | feeder2_621 | 0.078858 | 0.041014 | 0.078846 | 0.041461
180 | 3 | feeder2_611 | 0.076996 | 0.072902 | 0.07698 | 0.073016
180 | 3 | feeder2_405 | 0.077336 | 0.073758 | 0.077318 | 0.073869
180 | 3 | feeder2_461 | 0.082335 | 0.038154 | 0.082325 | 0.038801
180 | 3 | feeder2_594 | 0.079158 | 0.03913 | 0.079145 | 0.039625
180 | 3 | feeder2_732 | 0.075267 | 0.074464 | 0.075253 | 0.074556
180 | 3 | feeder2_417 | 0.078428 | 0.078999 | 0.078407 | 0.079107
180 | 3 | feeder2_663 | 0.078041 | 0.080081 | 0.078021 | 0.080192
180 | 3 | feeder2_444 | 0.07926 | 0.08265 | 0.079236 | 0.082748
180 | 3 | feeder2_759 | 0.079324 | 0.082597 | 0.079303 | 0.082699
180 | 3 | feeder2_842 | 0.092835 | 0.10549 | 0.092791 | 0.10557
180 | 3 | feeder2_459 | 0.079265 | 0.082617 | 0.079243 | 0.082715
180 | 3 | feeder2_702 | 0.080616 | 0.081228 | 0.080597 | 0.081321
180 | 3 | feeder2_493 | 0.07915 | 0.083031 | 0.079132 | 0.083119
180 | 3 | feeder2_651 | 0.081867 | 0.039412 | 0.081858 | 0.040055
180 | 3 | feeder2_684 | 0.08462 | 0.041056 | 0.084611 | 0.041753
180 | 3 | feeder2_674 | 0.078825 | 0.083146 | 0.078808 | 0.083231
180 | 3 | feeder2_696 | 0.079346 | 0.083929 | 0.079327 | 0.084015
180 | 3 | feeder2_681 | 0.078383 | 0.083279 | 0.078363 | 0.083362
180 | 3 | feeder2_682 | 0.078161 | 0.083434 | 0.078142 | 0.083515
180 | 3 | feeder2_728 | 0.084611 | 0.041161 | 0.084603 | 0.041858
180 | 3 | feeder2_724 | 0.087016 | 0.047881 | 0.08701 | 0.04857
180 | 3 | feeder2_703 | 0.079719 | 0.084636 | 0.0797 | 0.084721
180 | 3 | feeder2_704 | 0.079425 | 0.084082 | 0.0794 | 0.084173
180 | 3 | feeder2_754 | 0.088511 | 0.048782 | 0.088509 | 0.049461
180 | 3 | feeder2_747 | 0.08786 | 0.050887 | 0.087855 | 0.051565
180 | 3 | feeder2_828 | 0.084559 | 0.041118 | 0.08455 | 0.041817
180 | 3 | feeder2_763 | 0.08462 | 0.041377 | 0.084618 | 0.04207
180 | 3 | feeder2_836 | 0.08796 | 0.050786 | 0.087957 | 0.051466
180 | 3 | feeder2_758 | 0.08857 | 0.053737 | 0.08857 | 0.054406
180 | 3 | feeder2_788 | 0.090117 | 0.054886 | 0.090114 | 0.05555
180 | 3 | feeder2_812 | 0.090425 | 0.061703 | 0.090425 | 0.062354
180 | 3 | feeder2_947 | 0.084949 | 0.041965 | 0.084948 | 0.042659
180 | 3 | feeder2_868 | 0.085843 | 0.041799 | 0.08584 | 0.042491
180 | 3 | feeder2_785 | 0.084396 | 0.041027 | 0.084387 | 0.041729
180 | 3 | feeder2_1176 | 0.083 | 0.043908 | 0.082989 | 0.044609
180 | 3 | feeder2_846 | 0.08343 | 0.039442 | 0.083426 | 0.04014
180 | 3 | feeder2_911 | 0.084401 | 0.041127 | 0.084394 | 0.041827
180 | 3 | feeder2_1107 | 0.091063 | 0.065781 | 0.091063 | 0.0664
180 | 3 | feeder2_920 | 0.090769 | 0.062969 | 0.09077 | 0.063622
180 | 3 | feeder2_926 | 0.091312 | 0.064921 | 0.091311 | 0.065582
180 | 3 | feeder2_1239 | 0.090736 | 0.062914 | 0.090736 | 0.06357
180 | 3 | feeder2_933 | 0.091553 | 0.065762 | 0.091554 | 0.066423
180 | 3 | feeder2_1146 | 0.091309 | 0.06506 | 0.091312 | 0.065719
180 | 3 | feeder2_1124 | 0.09162 | 0.065662 | 0.091624 | 0.066327
180 | 3 | feeder2_942 | 0.092137 | 0.068013 | 0.092138 | 0.068678
180 | 3 | feeder2_952 | 0.092812 | 0.070328 | 0.092812 | 0.071013
180 | 3 | feeder2_965 | 0.092161 | 0.068146 | 0.09216 | 0.068812
180 | 3 | feeder2_961 | 0.092885 | 0.070546 | 0.09289 | 0.071235
180 | 3 | feeder2_963 | 0.092812 | 0.070335 | 0.092812 | 0.071019
180 | 3 | feeder2_973 | 0.093362 | 0.072151 | 0.093366 | 0.07285
180 | 3 | feeder2_1128 | 0.092731 | 0.069781 | 0.092733 | 0.070466
180 | 3 | feeder2_1113 | 0.092839 | 0.070395 | 0.092845 | 0.071079
180 | 3 | feeder2_1143 | 0.092816 | 0.070642 | 0.09282 | 0.071327
180 | 3 | feeder2_1238 | 0.094866 | 0.070279 | 0.094865 | 0.070928
180 | 3 | feeder2_979 | 0.092153 | 0.068135 | 0.092152 | 0.068803
180 | 3 | feeder2_1236 | 0.094049 | 0.074663 | 0.094055 | 0.075379
180 | 3 | feeder2_989 | 0.093362 | 0.07215 | 0.093366 | 0.072849
180 | 3 | feeder2_1196 | 0.091973 | 0.068071 | 0.091978 | 0.068735
180 | 3 | feeder2_1158 | 0.093445 | 0.072033 | 0.093449 | 0.072731
180 | 3 | feeder2_1122 | 0.091265 | 0.067494 | 0.091263 | 0.068094
180 | 3 | feeder2_1258 | 0.090791 | 0.065826 | 0.090789 | 0.066457
180 | 3 | feeder2_1303 | 0.092822 | 0.068743 | 0.09282 | 0.069338
180 | 3 | feeder2_1138 | 0.091324 | 0.068415 | 0.091322 | 0.069008
180 | 3 | feeder2_1304 | 0.090766 | 0.068235 | 0.090765 | 0.068822
180 | 3 | feeder2_1212 | 0.09154 | 0.070545 | 0.091539 | 0.071115
180 | 3 | feeder2_1311 | 0.092999 | 0.071797 | 0.093002 | 0.072363
180 | 3 | feeder2_1290 | 0.091593 | 0.072169 | 0.091593 | 0.072724
180 | 3 | feeder2_1325 | 0.094938 | 0.078339 | 0.094942 | 0.079071
180 | 3 | feeder2_1248 | 0.09405 | 0.074662 | 0.094056 | 0.075378
180 | 3 | feeder2_1249 | 0.094883 | 0.070321 | 0.094887 | 0.07097
180 | 3 | feeder2_1250 | 0.096718 | 0.071704 | 0.096721 | 0.072343
180 | 3 | feeder2_1366 | 0.094142 | 0.074526 | 0.094143 | 0.075238
180 | 3 | feeder2_1266 | 0.090424 | 0.06604 | 0.090418 | 0.066675
180 | 3 | feeder2_1372 | 0.091757 | 0.072458 | 0.091759 | 0.073014
180 | 3 | feeder2_1363 | 0.091642 | 0.073595 | 0.09164 | 0.074127
180 | 3 | feeder2_1446 | 0.096443 | 0.07957 | 0.09645 | 0.080295
180 | 3 | feeder2_1502 | 0.095582 | 0.080763 | 0.09559 | 0.081528
180 | 3 | feeder2_1428 | 0.091136 | 0.073487 | 0.091134 | 0.074014
180 | 3 | feeder2_1380 | 0.091863 | 0.075513 | 0.091866 | 0.076028
180 | 3 | feeder2_1550 | 0.091899 | 0.075574 | 0.091901 | 0.076089
180 | 3 | feeder2_1386 | 0.091971 | 0.076441 | 0.091972 | 0.076943
180 | 3 | feeder2_1551 | 0.09181 | 0.07644 | 0.09181 | 0.076944
180 | 3 | feeder2_1400 | 0.092028 | 0.076883 | 0.092028 | 0.077381
180 | 3 | feeder2_1552 | 0.091815 | 0.076887 | 0.09182 | 0.077386
180 | 3 | feeder2_1408 | 0.092168 | 0.077795 | 0.092171 | 0.078289
180 | 3 | feeder2_1553 | 0.091816 | 0.07775 | 0.091814 | 0.078242
180 | 3 | feeder2_1416 | 0.092256 | 0.078275 | 0.092261 | 0.078768
180 | 3 | feeder2_1530 | 0.094321 | 0.080193 | 0.094323 | 0.080677
180 | 3 | feeder2_1425 | 0.092229 | 0.07814 | 0.092231 | 0.078629
180 | 3 | feeder2_1589 | 0.091987 | 0.078103 | 0.091988 | 0.078589
180 | 3 | feeder2_1435 | 0.092228 | 0.078114 | 0.092229 | 0.078605
180 | 3 | feeder2_1621 | 0.092358 | 0.077868 | 0.092355 | 0.078359
180 | 3 | feeder2_1564 | 0.092158 | 0.078105 | 0.092155 | 0.078592
180 | 3 | feeder2_1704 | 0.095142 | 0.080862 | 0.095143 | 0.081639
180 | 3 | feeder2_1525 | 0.095729 | 0.081401 | 0.095734 | 0.082167
180 | 3 | feeder2_1716 | 0.095828 | 0.081247 | 0.095834 | 0.082018
180 | 3 | feeder2_1537 | 0.095889 | 0.082143 | 0.095895 | 0.082918
180 | 3 | feeder2_1645 | 0.095788 | 0.08214 | 0.095793 | 0.082912
180 | 3 | feeder2_1561 | 0.096078 | 0.082983 | 0.096086 | 0.083763
180 | 3 | feeder2_1657 | 0.096157 | 0.083126 | 0.096166 | 0.083904
180 | 3 | feeder2_1570 | 0.09616 | 0.083312 | 0.09617 | 0.084096
180 | 3 | feeder2_1756 | 0.098946 | 0.085658 | 0.098953 | 0.086423
180 | 3 | feeder2_1588 | 0.096204 | 0.083462 | 0.096214 | 0.084247
180 | 3 | feeder2_1628 | 0.096311 | 0.083651 | 0.096316 | 0.084438
180 | 3 | feeder2_1598 | 0.096259 | 0.083598 | 0.096264 | 0.084388
180 | 3 | feeder2_1816 | 0.09646 | 0.083298 | 0.096469 | 0.084086
180 | 3 | feeder2_1765 | 0.096479 | 0.083232 | 0.096488 | 0.084024
180 | 3 | feeder2_1641 | 0.096465 | 0.084554 | 0.096476 | 0.085359
180 | 3 | feeder2_1689 | 0.096434 | 0.084307 | 0.096444 | 0.08513
180 | 3 | feeder2_1744 | 0.097195 | 0.085185 | 0.097205 | 0.085989
180 | 3 | feeder2_1817 | 0.096417 | 0.084296 | 0.096424 | 0.085122
180 | 3 | feeder2_1779 | 0.096451 | 0.084278 | 0.096461 | 0.085103
180 | 3 | feeder2_1800 | 0.096379 | 0.084293 | 0.09639 | 0.085118
180 | 3 | feeder2_1818 | 0.09583 | 0.083459 | 0.095869 | 0.084323
180 | 3 | feeder2_1753 | 0.099435 | 0.08705 | 0.099444 | 0.087838
180 | 3 | feeder2_1754 | 0.097213 | 0.085219 | 0.09722 | 0.086023
210 | 3.5 | secondary | 0.011115 | 0.011104 | 0.011089 | 0.011116
210 | 3.5 | feeder2_44 | 0.020672 | 0.057876 | 0.020627 | 0.057925
210 | 3.5 | feeder2_45 | 0.021059 | 0.059791 | 0.021014 | 0.059842
210 | 3.5 | feeder2_46 | 0.017878 | 0.056355 | 0.017838 | 0.056393
210 | 3.5 | feeder2_51 | 0.021617 | 0.06346 | 0.021568 | 0.063512
210 | 3.5 | feeder2_48 | 0.023965 | 0.05799 | 0.02392 | 0.058047
210 | 3.5 | feeder2_52 | 0.022808 | 0.069233 | 0.022758 | 0.069282
210 | 3.5 | feeder2_68 | 0.023394 | 0.071647 | 0.023342 | 0.071706
210 | 3.5 | feeder2_69 | 0.023375 | 0.071727 | 0.023323 | 0.071788
210 | 3.5 | feeder2_71 | 0.02363 | 0.072728 | 0.023578 | 0.07279
210 | 3.5 | feeder2_72 | 0.023843 | 0.072477 | 0.023792 | 0.072539
210 | 3.5 | feeder2_73 | 0.024367 | 0.076139 | 0.024314 | 0.076204
210 | 3.5 | feeder2_74 | 0.02426 | 0.076221 | 0.024206 | 0.076288
210 | 3.5 | feeder2_77 | 0.025005 | 0.079055 | 0.02495 | 0.079124
210 | 3.5 | feeder2_79 | 0.023187 | 0.07802 | 0.023133 | 0.07808
210 | 3.5 | feeder2_81 | 0.026096 | 0.083972 | 0.026042 | 0.084048
210 | 3.5 | feeder2_82 | 0.026622 | 0.083371 | 0.026566 | 0.083448
210 | 3.5 | feeder2_116 | 0.030919 | 0.10665 | 0.03085 | 0.10676
210 | 3.5 | feeder2_119 | 0.030454 | 0.10903 | 0.030387 | 0.10914
210 | 3.5 | feeder2_120 | 0.032911 | 0.11378 | 0.03284 | 0.11389
210 | 3.5 | feeder2_248 | 0.032584 | 0.11604 | 0.032514 | 0.11616
210 | 3.5 | feeder2_124 | 0.034266 | 0.11726 | 0.034191 | 0.11738
210 | 3.5 | feeder2_282 | 0.034394 | 0.1171 | 0.034323 | 0.11723
210 | 3.5 | feeder2_275 | 0.034093 | 0.11735 | 0.034022 | 0.11747
210 | 3.5 | feeder2_151 | 0.036651 | 0.12337 | 0.036575 | 0.12349
210 | 3.5 | feeder2_295 | 0.036652 | 0.12341 | 0.036574 | 0.12354
210 | 3.5 | feeder2_311 | 0.036643 | 0.12349 | 0.036568 | 0.12362
210 | 3.5 | feeder2_201 | 0.04059 | 0.13327 | 0.040506 | 0.13341
210 | 3.5 | feeder2_314 | 0.041879 | 0.13252 | 0.041799 | 0.13267
210 | 3.5 | feeder2_342 | 0.045595 | 0.14914 | 0.045501 | 0.1493
210 | 3.5 | feeder2_368 | 0.046555 | 0.15327 | 0.046466 | 0.15342
210 | 3.5 | feeder2_347 | 0.046371 | 0.14944 | 0.046273 | 0.14963
210 | 3.5 | feeder2_353 | 0.04675 | 0.14984 | 0.046648 | 0.15005
210 | 3.5 | feeder2_518 | 0.046608 | 0.14916 | 0.04651 | 0.14935
210 | 3.5 | feeder2_365 | 0.047213 | 0.15025 | 0.047112 | 0.15048
210 | 3.5 | feeder2_653 | 0.046474 | 0.15006 | 0.046375 | 0.15027
210 | 3.5 | feeder2_377 | 0.047548 | 0.15097 | 0.047443 | 0.15121
210 | 3.5 | feeder2_622 | 0.044562 | 0.14828 | 0.044463 | 0.14851
210 | 3.5 | feeder2_451 | 0.048187 | 0.15222 | 0.048098 | 0.15237
210 | 3.5 | feeder2_383 | 0.047799 | 0.16118 | 0.047709 | 0.16131
210 | 3.5 | feeder2_385 | 0.047936 | 0.15183 | 0.047829 | 0.15209
210 | 3.5 | feeder2_621 | 0.04755 | 0.15101 | 0.047443 | 0.15125
210 | 3.5 | feeder2_611 | 0.047407 | 0.16269 | 0.047318 | 0.16282
210 | 3.5 | feeder2_405 | 0.047892 | 0.16161 | 0.047799 | 0.16173
210 | 3.5 | feeder2_461 | 0.04991 | 0.1533 | 0.049795 | 0.15362
210 | 3.5 | feeder2_594 | 0.047659 | 0.15332 | 0.047553 | 0.15357
210 | 3.5 | feeder2_732 | 0.047243 | 0.16447 | 0.047151 | 0.1646
210 | 3.5 | feeder2_417 | 0.048712 | 0.16427 | 0.048623 | 0.16438
210 | 3.5 | feeder2_663 | 0.04876 | 0.16437 | 0.048674 | 0.16449
210 | 3.5 | feeder2_444 | 0.049349 | 0.16631 | 0.049259 | 0.16641
210 | 3.5 | feeder2_759 | 0.053255 | 0.16382 | 0.05317 | 0.16394
210 | 3.5 | feeder2_842 | 0.056351 | 0.17881 | 0.056284 | 0.17887
210 | 3.5 | feeder2_459 | 0.049341 | 0.16645 | 0.049253 | 0.16655
210 | 3.5 | feeder2_702 | 0.049385 | 0.16639 | 0.049296 | 0.1665
210 | 3.5 | feeder2_493 | 0.049309 | 0.16699 | 0.049223 | 0.1671
210 | 3.5 | feeder2_651 | 0.049893 | 0.15335 | 0.049781 | 0.15366
210 | 3.5 | feeder2_684 | 0.051532 | 0.15507 | 0.051413 | 0.15543
210 | 3.5 | feeder2_674 | 0.049215 | 0.16724 | 0.049127 | 0.16735
210 | 3.5 | feeder2_696 | 0.04942 | 0.16752 | 0.049332 | 0.16763
210 | 3.5 | feeder2_681 | 0.049009 | 0.16789 | 0.04892 | 0.168
210 | 3.5 | feeder2_682 | 0.049141 | 0.16727 | 0.049054 | 0.16738
210 | 3.5 | feeder2_728 | 0.051554 | 0.15489 | 0.051433 | 0.15526
210 | 3.5 | feeder2_724 | 0.053203 | 0.15785 | 0.053078 | 0.15827
210 | 3.5 | feeder2_703 | 0.049518 | 0.16788 | 0.049433 | 0.16799
210 | 3.5 | feeder2_704 | 0.049439 | 0.1676 | 0.049353 | 0.1677
210 | 3.5 | feeder2_754 | 0.054583 | 0.15736 | 0.054457 | 0.15779
210 | 3.5 | feeder2_747 | 0.053715 | 0.15947 | 0.053588 | 0.15991
210 | 3.5 | feeder2_828 | 0.05151 | 0.15493 | 0.051388 | 0.1553
210 | 3.5 | feeder2_763 | 0.051608 | 0.15458 | 0.05149 | 0.15495
210 | 3.5 | feeder2_836 | 0.052374 | 0.15829 | 0.052245 | 0.15873
210 | 3.5 | feeder2_758 | 0.054231 | 0.16139 | 0.054099 | 0.16185
210 | 3.5 | feeder2_788 | 0.055676 | 0.16088 | 0.055545 | 0.16135
210 | 3.5 | feeder2_812 | 0.055411 | 0.1684 | 0.055273 | 0.16891
210 | 3.5 | feeder2_947 | 0.052164 | 0.15398 | 0.052046 | 0.15435
210 | 3.5 | feeder2_868 | 0.051796 | 0.15438 | 0.051675 | 0.15475
210 | 3.5 | feeder2_785 | 0.051584 | 0.15467 | 0.051463 | 0.15504
210 | 3.5 | feeder2_1176 | 0.051543 | 0.15476 | 0.051423 | 0.15513
210 | 3.5 | feeder2_846 | 0.051374 | 0.15488 | 0.051253 | 0.15525
210 | 3.5 | feeder2_911 | 0.051604 | 0.15457 | 0.051482 | 0.15494
210 | 3.5 | feeder2_1107 | 0.055145 | 0.17796 | 0.055006 | 0.17848
210 | 3.5 | feeder2_920 | 0.05583 | 0.16778 | 0.055691 | 0.16831
210 | 3.5 | feeder2_926 | 0.056485 | 0.16675 | 0.056344 | 0.1673
210 | 3.5 | feeder2_1239 | 0.055793 | 0.16793 | 0.055652 | 0.16845
210 | 3.5 | feeder2_933 | 0.056699 | 0.16639 | 0.056559 | 0.16694
210 | 3.5 | feeder2_1146 | 0.056844 | 0.16636 | 0.056704 | 0.1669
210 | 3.5 | feeder2_1124 | 0.05584 | 0.16559 | 0.055696 | 0.16614
210 | 3.5 | feeder2_942 | 0.057337 | 0.16617 | 0.057191 | 0.16673
210 | 3.5 | feeder2_952 | 0.058223 | 0.16469 | 0.058071 | 0.16528
210 | 3.5 | feeder2_965 | 0.057344 | 0.16632 | 0.057202 | 0.16689
210 | 3.5 | feeder2_961 | 0.058285 | 0.16458 | 0.058135 | 0.16518
210 | 3.5 | feeder2_963 | 0.05823 | 0.16467 | 0.05808 | 0.16527
210 | 3.5 | feeder2_973 | 0.058624 | 0.16397 | 0.05847 | 0.16459
210 | 3.5 | feeder2_1128 | 0.058273 | 0.16463 | 0.058121 | 0.16523
210 | 3.5 | feeder2_1113 | 0.058834 | 0.16459 | 0.058685 | 0.16519
210 | 3.5 | feeder2_1143 | 0.058271 | 0.16438 | 0.058119 | 0.16498
210 | 3.5 | feeder2_1238 | 0.059189 | 0.16601 | 0.059043 | 0.16658
210 | 3.5 | feeder2_979 | 0.057316 | 0.16657 | 0.05717 | 0.16713
210 | 3.5 | feeder2_1236 | 0.059115 | 0.16305 | 0.058957 | 0.16368
210 | 3.5 | feeder2_989 | 0.058624 | 0.16397 | 0.058471 | 0.16459
210 | 3.5 | feeder2_1196 | 0.057277 | 0.16756 | 0.057131 | 0.16812
210 | 3.5 | feeder2_1158 | 0.058624 | 0.16399 | 0.058469 | 0.1646
210 | 3.5 | feeder2_1122 | 0.055039 | 0.18165 | 0.054903 | 0.18217
210 | 3.5 | feeder2_1258 | 0.055093 | 0.17797 | 0.054955 | 0.17849
210 | 3.5 | feeder2_1303 | 0.055146 | 0.18154 | 0.055007 | 0.18206
210 | 3.5 | feeder2_1138 | 0.054958 | 0.18461 | 0.054819 | 0.18513
210 | 3.5 | feeder2_1304 | 0.054778 | 0.18628 | 0.054641 | 0.1868
210 | 3.5 | feeder2_1212 | 0.054977 | 0.18951 | 0.054841 | 0.19003
210 | 3.5 | feeder2_1311 | 0.057424 | 0.18921 | 0.057285 | 0.18975
210 | 3.5 | feeder2_1290 | 0.054483 | 0.19607 | 0.054347 | 0.19659
210 | 3.5 | feeder2_1325 | 0.059761 | 0.16174 | 0.0596 | 0.1624
210 | 3.5 | feeder2_1248 | 0.059115 | 0.16305 | 0.058957 | 0.16368
210 | 3.5 | feeder2_1249 | 0.059709 | 0.16595 | 0.059561 | 0.16652
210 | 3.5 | feeder2_1250 | 0.059241 | 0.16596 | 0.059097 | 0.16653
210 | 3.5 | feeder2_1366 | 0.059106 | 0.16306 | 0.05895 | 0.16369
210 | 3.5 | feeder2_1266 | 0.055089 | 0.17798 | 0.054952 | 0.1785
210 | 3.5 | feeder2_1372 | 0.054762 | 0.19581 | 0.054626 | 0.19633
210 | 3.5 | feeder2_1363 | 0.053926 | 0.2035 | 0.053788 | 0.20402
210 | 3.5 | feeder2_1446 | 0.060893 | 0.16158 | 0.060731 | 0.16225
210 | 3.5 | feeder2_1502 | 0.060117 | 0.16065 | 0.059952 | 0.16134
210 | 3.5 | feeder2_1428 | 0.053896 | 0.20515 | 0.05376 | 0.20567
210 | 3.5 | feeder2_1380 | 0.053585 | 0.20983 | 0.05345 | 0.21035
210 | 3.5 | feeder2_1550 | 0.054388 | 0.20971 | 0.054253 | 0.21023
210 | 3.5 | feeder2_1386 | 0.053314 | 0.21303 | 0.05318 | 0.21355
210 | 3.5 | feeder2_1551 | 0.053696 | 0.21488 | 0.05356 | 0.21539
210 | 3.5 | feeder2_1400 | 0.05322 | 0.21411 | 0.053083 | 0.21463
210 | 3.5 | feeder2_1552 | 0.053056 | 0.21429 | 0.052919 | 0.21481
210 | 3.5 | feeder2_1408 | 0.053051 | 0.21627 | 0.052915 | 0.21679
210 | 3.5 | feeder2_1553 | 0.053531 | 0.21884 | 0.053395 | 0.21935
210 | 3.5 | feeder2_1416 | 0.05301 | 0.21681 | 0.052874 | 0.21732
210 | 3.5 | feeder2_1530 | 0.053247 | 0.21659 | 0.05311 | 0.2171
210 | 3.5 | feeder2_1425 | 0.052912 | 0.21795 | 0.052776 | 0.21847
210 | 3.5 | feeder2_1589 | 0.052759 | 0.21817 | 0.052624 | 0.21869
210 | 3.5 | feeder2_1435 | 0.052897 | 0.21816 | 0.052761 | 0.21868
210 | 3.5 | feeder2_1621 | 0.052802 | 0.21817 | 0.052667 | 0.21869
210 | 3.5 | feeder2_1564 | 0.052708 | 0.2206 | 0.052571 | 0.22111
210 | 3.5 | feeder2_1704 | 0.059078 | 0.15965 | 0.058912 | 0.16034
210 | 3.5 | feeder2_1525 | 0.060251 | 0.16071 | 0.060082 | 0.1614
210 | 3.5 | feeder2_1716 | 0.057731 | 0.15823 | 0.057561 | 0.15893
210 | 3.5 | feeder2_1537 | 0.060451 | 0.16113 | 0.060283 | 0.16184
210 | 3.5 | feeder2_1645 | 0.060569 | 0.16299 | 0.0604 | 0.1637
210 | 3.5 | feeder2_1561 | 0.06079 | 0.16054 | 0.06062 | 0.16127
210 | 3.5 | feeder2_1657 | 0.06162 | 0.16041 | 0.061446 | 0.16114
210 | 3.5 | feeder2_1570 | 0.060887 | 0.16034 | 0.060716 | 0.16107
210 | 3.5 | feeder2_1756 | 0.065877 | 0.16015 | 0.065702 | 0.16091
210 | 3.5 | feeder2_1588 | 0.060896 | 0.16021 | 0.060721 | 0.16094
210 | 3.5 | feeder2_1628 | 0.061069 | 0.16005 | 0.060897 | 0.16078
210 | 3.5 | feeder2_1598 | 0.0609 | 0.16009 | 0.060724 | 0.16083
210 | 3.5 | feeder2_1816 | 0.060896 | 0.16013 | 0.060721 | 0.16086
210 | 3.5 | feeder2_1765 | 0.06083 | 0.16007 | 0.060655 | 0.16081
210 | 3.5 | feeder2_1641 | 0.06089 | 0.15949 | 0.060711 | 0.16026
210 | 3.5 | feeder2_1689 | 0.060862 | 0.15915 | 0.060677 | 0.15992
210 | 3.5 | feeder2_1744 | 0.060981 | 0.1594 | 0.060802 | 0.16016
210 | 3.5 | feeder2_1817 | 0.060843 | 0.15922 | 0.060659 | 0.16
210 | 3.5 | feeder2_1779 | 0.060266 | 0.15856 | 0.06008 | 0.15933
210 | 3.5 | feeder2_1800 | 0.060818 | 0.1592 | 0.060633 | 0.15997
210 | 3.5 | feeder2_1818 | 0.061363 | 0.15862 | 0.061145 | 0.15944
210 | 3.5 | feeder2_1753 | 0.061129 | 0.15924 | 0.060949 | 0.15999
210 | 3.5 | feeder2_1754 | 0.061012 | 0.15937 | 0.060833 | 0.16013
240 | 4 | secondary | 0.01038 | 0.010926 | 0.010383 | 0.010927
240 | 4 | feeder2_44 | 0.019398 | 0.057223 | 0.019404 | 0.057241
240 | 4 | feeder2_45 | 0.019736 | 0.059 | 0.019744 | 0.059017
240 | 4 | feeder2_46 | 0.019145 | 0.057427 | 0.019149 | 0.057444
240 | 4 | feeder2_51 | 0.020307 | 0.062187 | 0.020313 | 0.062206
240 | 4 | feeder2_48 | 0.020329 | 0.058371 | 0.020337 | 0.058388
240 | 4 | feeder2_52 | 0.022401 | 0.068521 | 0.022411 | 0.068542
240 | 4 | feeder2_68 | 0.022101 | 0.068796 | 0.022109 | 0.068818
240 | 4 | feeder2_69 | 0.022062 | 0.06886 | 0.022069 | 0.068884
240 | 4 | feeder2_71 | 0.022341 | 0.069668 | 0.022347 | 0.069689
240 | 4 | feeder2_72 | 0.022568 | 0.069415 | 0.022574 | 0.069437
240 | 4 | feeder2_73 | 0.023093 | 0.07243 | 0.0231 | 0.072451
240 | 4 | feeder2_74 | 0.023456 | 0.074648 | 0.023463 | 0.074671
240 | 4 | feeder2_77 | 0.023773 | 0.074452 | 0.023779 | 0.074473
240 | 4 | feeder2_79 | 0.023682 | 0.074568 | 0.023689 | 0.074594
240 | 4 | feeder2_81 | 0.024849 | 0.07759 | 0.024856 | 0.077616
240 | 4 | feeder2_82 | 0.025394 | 0.076996 | 0.0254 | 0.077022
240 | 4 | feeder2_116 | 0.029726 | 0.092345 | 0.029733 | 0.092372
240 | 4 | feeder2_119 | 0.029123 | 0.092936 | 0.02913 | 0.092964
240 | 4 | feeder2_120 | 0.031675 | 0.097543 | 0.031681 | 0.097575
240 | 4 | feeder2_248 | 0.031272 | 0.097884 | 0.031278 | 0.097914
240 | 4 | feeder2_124 | 0.032927 | 0.10062 | 0.032934 | 0.10066
240 | 4 | feeder2_282 | 0.03306 | 0.10047 | 0.03307 | 0.1005
240 | 4 | feeder2_275 | 0.032752 | 0.10073 | 0.032761 | 0.10076
240 | 4 | feeder2_151 | 0.035139 | 0.10605 | 0.035146 | 0.10608
240 | 4 | feeder2_295 | 0.035139 | 0.10609 | 0.035143 | 0.10613
240 | 4 | feeder2_311 | 0.035126 | 0.10616 | 0.035134 | 0.10619
240 | 4 | feeder2_201 | 0.038803 | 0.11486 | 0.038811 | 0.11491
240 | 4 | feeder2_314 | 0.040826 | 0.1138 | 0.040834 | 0.11384
240 | 4 | feeder2_342 | 0.043077 | 0.13019 | 0.043084 | 0.13024
240 | 4 | feeder2_368 | 0.043816 | 0.13379 | 0.04382 | 0.13385
240 | 4 | feeder2_347 | 0.043762 | 0.13141 | 0.043772 | 0.13146
240 | 4 | feeder2_353 | 0.044103 | 0.13233 | 0.044114 | 0.13237
240 | 4 | feeder2_518 | 0.044005 | 0.13113 | 0.044014 | 0.13117
240 | 4 | feeder2_365 | 0.044529 | 0.13335 | 0.04454 | 0.13339
240 | 4 | feeder2_653 | 0.043825 | 0.13256 | 0.043838 | 0.1326
240 | 4 | feeder2_377 | 0.044808 | 0.13419 | 0.044819 | 0.13422
240 | 4 | feeder2_622 | 0.043171 | 0.13232 | 0.04318 | 0.13236
240 | 4 | feeder2_451 | 0.044032 | 0.13351 | 0.044039 | 0.13358
240 | 4 | feeder2_383 | 0.045099 | 0.14025 | 0.045103 | 0.14032
240 | 4 | feeder2_385 | 0.045131 | 0.13519 | 0.045143 | 0.13523
240 | 4 | feeder2_621 | 0.044807 | 0.13423 | 0.044819 | 0.13426
240 | 4 | feeder2_611 | 0.044893 | 0.14037 | 0.044896 | 0.14044
240 | 4 | feeder2_405 | 0.045188 | 0.14067 | 0.045191 | 0.14074
240 | 4 | feeder2_461 | 0.04663 | 0.13946 | 0.046647 | 0.13947
240 | 4 | feeder2_594 | 0.044862 | 0.13544 | 0.044874 | 0.13546
240 | 4 | feeder2_732 | 0.044459 | 0.14356 | 0.044466 | 0.14363
240 | 4 | feeder2_417 | 0.045979 | 0.14324 | 0.045982 | 0.14332
240 | 4 | feeder2_663 | 0.046031 | 0.14335 | 0.046034 | 0.14343
240 | 4 | feeder2_444 | 0.046597 | 0.14523 | 0.046598 | 0.14531
240 | 4 | feeder2_759 | 0.050989 | 0.14234 | 0.050988 | 0.14241
240 | 4 | feeder2_842 | 0.054197 | 0.15829 | 0.054184 | 0.15839
240 | 4 | feeder2_459 | 0.046568 | 0.14535 | 0.046571 | 0.14543
240 | 4 | feeder2_702 | 0.046612 | 0.14529 | 0.046613 | 0.14537
240 | 4 | feeder2_493 | 0.046457 | 0.14586 | 0.046459 | 0.14594
240 | 4 | feeder2_651 | 0.046604 | 0.13949 | 0.046621 | 0.13951
240 | 4 | feeder2_684 | 0.047903 | 0.14348 | 0.047925 | 0.14348
240 | 4 | feeder2_674 | 0.046338 | 0.14617 | 0.04634 | 0.14626
240 | 4 | feeder2_696 | 0.046401 | 0.14598 | 0.046401 | 0.14606
240 | 4 | feeder2_681 | 0.046247 | 0.14621 | 0.04625 | 0.14629
240 | 4 | feeder2_682 | 0.045998 | 0.14744 | 0.046001 | 0.14752
240 | 4 | feeder2_728 | 0.047929 | 0.14331 | 0.047949 | 0.14331
240 | 4 | feeder2_724 | 0.049245 | 0.14853 | 0.049268 | 0.14851
240 | 4 | feeder2_703 | 0.046522 | 0.14637 | 0.046521 | 0.14645
240 | 4 | feeder2_704 | 0.046067 | 0.14586 | 0.046066 | 0.14595
240 | 4 | feeder2_754 | 0.049511 | 0.14826 | 0.049534 | 0.14825
240 | 4 | feeder2_747 | 0.049787 | 0.15087 | 0.04981 | 0.15085
240 | 4 | feeder2_828 | 0.047885 | 0.14335 | 0.047903 | 0.14335
240 | 4 | feeder2_763 | 0.047989 | 0.143 | 0.048007 | 0.143
240 | 4 | feeder2_836 | 0.048379 | 0.14964 | 0.048401 | 0.14962
240 | 4 | feeder2_758 | 0.050341 | 0.15346 | 0.050367 | 0.15343
240 | 4 | feeder2_788 | 0.050688 | 0.15313 | 0.050713 | 0.1531
240 | 4 | feeder2_812 | 0.052029 | 0.1623 | 0.052054 | 0.16225
240 | 4 | feeder2_947 | 0.048569 | 0.14239 | 0.048593 | 0.1424
240 | 4 | feeder2_868 | 0.048185 | 0.14279 | 0.048204 | 0.14279
240 | 4 | feeder2_785 | 0.047964 | 0.14309 | 0.047982 | 0.14309
240 | 4 | feeder2_1176 | 0.047898 | 0.14316 | 0.047916 | 0.14316
240 | 4 | feeder2_846 | 0.047757 | 0.14331 | 0.047779 | 0.14331
240 | 4 | feeder2_911 | 0.047985 | 0.14298 | 0.048004 | 0.14298
240 | 4 | feeder2_1107 | 0.05237 | 0.16812 | 0.052397 | 0.16806
240 | 4 | feeder2_920 | 0.052422 | 0.16328 | 0.05245 | 0.16323
240 | 4 | feeder2_926 | 0.053041 | 0.16463 | 0.053072 | 0.16458
240 | 4 | feeder2_1239 | 0.052384 | 0.16344 | 0.052414 | 0.16339
240 | 4 | feeder2_933 | 0.053313 | 0.16527 | 0.053345 | 0.16522
240 | 4 | feeder2_1146 | 0.05306 | 0.16449 | 0.053091 | 0.16443
240 | 4 | feeder2_1124 | 0.053275 | 0.16526 | 0.053303 | 0.16521
240 | 4 | feeder2_942 | 0.053994 | 0.1669 | 0.054027 | 0.16684
240 | 4 | feeder2_952 | 0.054462 | 0.16738 | 0.054492 | 0.16732
240 | 4 | feeder2_965 | 0.054064 | 0.16716 | 0.054095 | 0.16709
240 | 4 | feeder2_961 | 0.054508 | 0.16747 | 0.05454 | 0.1674
240 | 4 | feeder2_963 | 0.054463 | 0.16738 | 0.054496 | 0.16731
240 | 4 | feeder2_973 | 0.054798 | 0.16738 | 0.054831 | 0.16731
240 | 4 | feeder2_1128 | 0.054428 | 0.16839 | 0.054461 | 0.16833
240 | 4 | feeder2_1113 | 0.054522 | 0.16732 | 0.054556 | 0.16725
240 | 4 | feeder2_1143 | 0.054511 | 0.16709 | 0.054543 | 0.16702
240 | 4 | feeder2_1238 | 0.059914 | 0.16713 | 0.05994 | 0.16706
240 | 4 | feeder2_979 | 0.054026 | 0.16757 | 0.054056 | 0.16751
240 | 4 | feeder2_1236 | 0.05522 | 0.16722 | 0.055256 | 0.16715
240 | 4 | feeder2_989 | 0.054798 | 0.16738 | 0.054831 | 0.16731
240 | 4 | feeder2_1196 | 0.054227 | 0.1692 | 0.054258 | 0.16914
240 | 4 | feeder2_1158 | 0.054781 | 0.16739 | 0.054813 | 0.16732
240 | 4 | feeder2_1122 | 0.052555 | 0.17078 | 0.052585 | 0.17072
240 | 4 | feeder2_1258 | 0.051786 | 0.16762 | 0.051816 | 0.16757
240 | 4 | feeder2_1303 | 0.05267 | 0.17066 | 0.052699 | 0.1706
240 | 4 | feeder2_1138 | 0.052699 | 0.17294 | 0.052731 | 0.17288
240 | 4 | feeder2_1304 | 0.052316 | 0.17348 | 0.052346 | 0.17342
240 | 4 | feeder2_1212 | 0.05311 | 0.17712 | 0.05314 | 0.17706
240 | 4 | feeder2_1311 | 0.054469 | 0.17702 | 0.054498 | 0.17695
240 | 4 | feeder2_1290 | 0.053331 | 0.18258 | 0.053362 | 0.18251
240 | 4 | feeder2_1325 | 0.055776 | 0.16699 | 0.05581 | 0.16691
240 | 4 | feeder2_1248 | 0.05522 | 0.16722 | 0.055257 | 0.16715
240 | 4 | feeder2_1249 | 0.061132 | 0.16717 | 0.061159 | 0.1671
240 | 4 | feeder2_1250 | 0.06122 | 0.16717 | 0.061246 | 0.16709
240 | 4 | feeder2_1366 | 0.055188 | 0.16723 | 0.055223 | 0.16715
240 | 4 | feeder2_1266 | 0.051778 | 0.16762 | 0.051806 | 0.16757
240 | 4 | feeder2_1372 | 0.054445 | 0.18239 | 0.054478 | 0.18231
240 | 4 | feeder2_1363 | 0.05318 | 0.1889 | 0.05321 | 0.18883
240 | 4 | feeder2_1446 | 0.056866 | 0.16688 | 0.056901 | 0.1668
240 | 4 | feeder2_1502 | 0.056025 | 0.16705 | 0.056063 | 0.16697
240 | 4 | feeder2_1428 | 0.05285 | 0.1894 | 0.052884 | 0.18934
240 | 4 | feeder2_1380 | 0.053198 | 0.1958 | 0.05323 | 0.19573
240 | 4 | feeder2_1550 | 0.053996 | 0.1958 | 0.05403 | 0.19573
240 | 4 | feeder2_1386 | 0.053102 | 0.19923 | 0.053137 | 0.19916
240 | 4 | feeder2_1551 | 0.053911 | 0.20199 | 0.053947 | 0.20192
240 | 4 | feeder2_1400 | 0.053101 | 0.20019 | 0.053136 | 0.20012
240 | 4 | feeder2_1552 | 0.052936 | 0.20039 | 0.05297 | 0.20032
240 | 4 | feeder2_1408 | 0.053127 | 0.20208 | 0.053161 | 0.20201
240 | 4 | feeder2_1553 | 0.052901 | 0.20243 | 0.052934 | 0.20236
240 | 4 | feeder2_1416 | 0.053158 | 0.20299 | 0.053191 | 0.20292
240 | 4 | feeder2_1530 | 0.054474 | 0.20286 | 0.054507 | 0.20279
240 | 4 | feeder2_1425 | 0.053024 | 0.20488 | 0.05306 | 0.20482
240 | 4 | feeder2_1589 | 0.054158 | 0.20843 | 0.054193 | 0.20836
240 | 4 | feeder2_1435 | 0.053018 | 0.20491 | 0.053052 | 0.20484
240 | 4 | feeder2_1621 | 0.052907 | 0.20488 | 0.052941 | 0.20481
240 | 4 | feeder2_1564 | 0.052943 | 0.20525 | 0.052979 | 0.20518
240 | 4 | feeder2_1704 | 0.05594 | 0.16702 | 0.05598 | 0.16694
240 | 4 | feeder2_1525 | 0.056084 | 0.16707 | 0.056122 | 0.16699
240 | 4 | feeder2_1716 | 0.056037 | 0.16706 | 0.056077 | 0.16698
240 | 4 | feeder2_1537 | 0.056147 | 0.16709 | 0.056187 | 0.167
240 | 4 | feeder2_1645 | 0.056054 | 0.16718 | 0.056095 | 0.16709
240 | 4 | feeder2_1561 | 0.056232 | 0.16707 | 0.05627 | 0.16698
240 | 4 | feeder2_1657 | 0.056373 | 0.16694 | 0.056411 | 0.16685
240 | 4 | feeder2_1570 | 0.056263 | 0.16709 | 0.056304 | 0.16701
240 | 4 | feeder2_1756 | 0.058922 | 0.16689 | 0.058962 | 0.1668
240 | 4 | feeder2_1588 | 0.056247 | 0.16715 | 0.056286 | 0.16706
240 | 4 | feeder2_1628 | 0.056433 | 0.16698 | 0.056472 | 0.1669
240 | 4 | feeder2_1598 | 0.056219 | 0.16727 | 0.056257 | 0.16718
240 | 4 | feeder2_1816 | 0.056165 | 0.16729 | 0.056205 | 0.1672
240 | 4 | feeder2_1765 | 0.056079 | 0.16722 | 0.05612 | 0.16713
240 | 4 | feeder2_1641 | 0.056055 | 0.16785 | 0.056098 | 0.16776
240 | 4 | feeder2_1689 | 0.055891 | 0.16852 | 0.055935 | 0.16843
240 | 4 | feeder2_1744 | 0.056158 | 0.16775 | 0.056198 | 0.16766
240 | 4 | feeder2_1817 | 0.055781 | 0.16984 | 0.055827 | 0.16975
240 | 4 | feeder2_1779 | 0.055247 | 0.16791 | 0.055288 | 0.16782
240 | 4 | feeder2_1800 | 0.05585 | 0.16857 | 0.055895 | 0.16848
240 | 4 | feeder2_1818 | 0.056367 | 0.16876 | 0.056427 | 0.16866
240 | 4 | feeder2_1753 | 0.056325 | 0.16758 | 0.056369 | 0.16749
240 | 4 | feeder2_1754 | 0.056193 | 0.16772 | 0.056233 | 0.16763
270 | 4.5 | secondary | 0.024123 | 0.010332 | 0.024104 | 0.010367
270 | 4.5 | feeder2_44 | 0.045062 | 0.054092 | 0.045031 | 0.054264
270 | 4.5 | feeder2_45 | 0.045831 | 0.055497 | 0.045793 | 0.055683
270 | 4.5 | feeder2_46 | 0.044461 | 0.057636 | 0.044427 | 0.057808
270 | 4.5 | feeder2_51 | 0.047171 | 0.057903 | 0.047131 | 0.058099
270 | 4.5 | feeder2_48 | 0.046114 | 0.055661 | 0.04608 | 0.055842
270 | 4.5 | feeder2_52 | 0.045684 | 0.056969 | 0.045652 | 0.057163
270 | 4.5 | feeder2_68 | 0.051143 | 0.065172 | 0.051103 | 0.065392
270 | 4.5 | feeder2_69 | 0.051253 | 0.065298 | 0.051217 | 0.065512
270 | 4.5 | feeder2_71 | 0.051669 | 0.066134 | 0.05163 | 0.066358
270 | 4.5 | feeder2_72 | 0.051759 | 0.066223 | 0.051719 | 0.066443
270 | 4.5 | feeder2_73 | 0.053319 | 0.069135 | 0.053276 | 0.06937
270 | 4.5 | feeder2_74 | 0.053187 | 0.068992 | 0.053149 | 0.069224
270 | 4.5 | feeder2_77 | 0.054741 | 0.071737 | 0.054699 | 0.07198
270 | 4.5 | feeder2_79 | 0.054964 | 0.072019 | 0.05492 | 0.072261
270 | 4.5 | feeder2_81 | 0.056964 | 0.075771 | 0.056926 | 0.076024
270 | 4.5 | feeder2_82 | 0.057207 | 0.075959 | 0.057166 | 0.07621
270 | 4.5 | feeder2_116 | 0.06702 | 0.093729 | 0.066974 | 0.094046
270 | 4.5 | feeder2_119 | 0.066243 | 0.092894 | 0.066193 | 0.093213
270 | 4.5 | feeder2_120 | 0.070847 | 0.10089 | 0.070793 | 0.10124
270 | 4.5 | feeder2_248 | 0.07036 | 0.10037 | 0.070307 | 0.10072
270 | 4.5 | feeder2_124 | 0.073239 | 0.10551 | 0.073185 | 0.10587
270 | 4.5 | feeder2_282 | 0.073283 | 0.10558 | 0.073227 | 0.10594
270 | 4.5 | feeder2_275 | 0.07306 | 0.10531 | 0.073003 | 0.10567
270 | 4.5 | feeder2_151 | 0.077432 | 0.11365 | 0.077373 | 0.11404
270 | 4.5 | feeder2_295 | 0.077503 | 0.11371 | 0.077447 | 0.1141
270 | 4.5 | feeder2_311 | 0.077628 | 0.11383 | 0.077575 | 0.11422
270 | 4.5 | feeder2_201 | 0.084327 | 0.12698 | 0.084266 | 0.12741
270 | 4.5 | feeder2_314 | 0.085109 | 0.12663 | 0.08505 | 0.12705
270 | 4.5 | feeder2_342 | 0.093931 | 0.14654 | 0.093864 | 0.14703
270 | 4.5 | feeder2_368 | 0.095916 | 0.15085 | 0.095845 | 0.15135
270 | 4.5 | feeder2_347 | 0.095591 | 0.14861 | 0.095525 | 0.1491
270 | 4.5 | feeder2_353 | 0.096426 | 0.14976 | 0.096355 | 0.15026
270 | 4.5 | feeder2_518 | 0.095674 | 0.14875 | 0.095604 | 0.14925
270 | 4.5 | feeder2_365 | 0.097379 | 0.15137 | 0.097309 | 0.15187
270 | 4.5 | feeder2_653 | 0.096104 | 0.14941 | 0.096029 | 0.14992
270 | 4.5 | feeder2_377 | 0.097896 | 0.1523 | 0.097822 | 0.15281
270 | 4.5 | feeder2_622 | 0.097406 | 0.15138 | 0.097336 | 0.15189
270 | 4.5 | feeder2_451 | 0.095988 | 0.15096 | 0.095915 | 0.15146
270 | 4.5 | feeder2_383 | 0.099156 | 0.15801 | 0.099089 | 0.15852
270 | 4.5 | feeder2_385 | 0.098483 | 0.15342 | 0.098411 | 0.15393
270 | 4.5 | feeder2_621 | 0.097974 | 0.15235 | 0.0979 | 0.15286
270 | 4.5 | feeder2_611 | 0.09894 | 0.15778 | 0.098869 | 0.15829
270 | 4.5 | feeder2_405 | 0.099362 | 0.15848 | 0.09929 | 0.159
270 | 4.5 | feeder2_461 | 0.10096 | 0.15913 | 0.10088 | 0.15965
270 | 4.5 | feeder2_594 | 0.098166 | 0.15308 | 0.098091 | 0.15359
270 | 4.5 | feeder2_732 | 0.099026 | 0.15812 | 0.098959 | 0.15864
270 | 4.5 | feeder2_417 | 0.10094 | 0.16216 | 0.10086 | 0.16268
270 | 4.5 | feeder2_663 | 0.10063 | 0.16488 | 0.10056 | 0.16541
270 | 4.5 | feeder2_444 | 0.10209 | 0.16416 | 0.10202 | 0.16468
270 | 4.5 | feeder2_759 | 0.10369 | 0.16319 | 0.10362 | 0.16371
270 | 4.5 | feeder2_842 | 0.11833 | 0.18056 | 0.11824 | 0.18111
270 | 4.5 | feeder2_459 | 0.10215 | 0.16409 | 0.10208 | 0.16462
270 | 4.5 | feeder2_702 | 0.10376 | 0.16305 | 0.10369 | 0.16358
270 | 4.5 | feeder2_493 | 0.10221 | 0.1642 | 0.10214 | 0.16473
270 | 4.5 | feeder2_651 | 0.1011 | 0.15921 | 0.10102 | 0.15973
270 | 4.5 | feeder2_684 | 0.10293 | 0.16437 | 0.10285 | 0.16488
270 | 4.5 | feeder2_674 | 0.10216 | 0.16415 | 0.10209 | 0.16468
270 | 4.5 | feeder2_696 | 0.10244 | 0.16477 | 0.10237 | 0.1653
270 | 4.5 | feeder2_681 | 0.10208 | 0.16405 | 0.102 | 0.16458
270 | 4.5 | feeder2_682 | 0.10209 | 0.16407 | 0.10201 | 0.16459
270 | 4.5 | feeder2_728 | 0.10309 | 0.16434 | 0.10301 | 0.16485
270 | 4.5 | feeder2_724 | 0.10474 | 0.17024 | 0.10465 | 0.17076
270 | 4.5 | feeder2_703 | 0.10292 | 0.16526 | 0.10285 | 0.16578
270 | 4.5 | feeder2_704 | 0.10254 | 0.16488 | 0.10247 | 0.1654
270 | 4.5 | feeder2_754 | 0.10482 | 0.17045 | 0.10474 | 0.17097
270 | 4.5 | feeder2_747 | 0.10548 | 0.1726 | 0.1054 | 0.17311
270 | 4.5 | feeder2_828 | 0.10304 | 0.16429 | 0.10296 | 0.1648
270 | 4.5 | feeder2_763 | 0.10335 | 0.16439 | 0.10328 | 0.16489
270 | 4.5 | feeder2_836 | 0.10503 | 0.17545 | 0.10494 | 0.17597
270 | 4.5 | feeder2_758 | 0.10602 | 0.17346 | 0.10594 | 0.17397
270 | 4.5 | feeder2_788 | 0.10614 | 0.17374 | 0.10606 | 0.17425
270 | 4.5 | feeder2_812 | 0.10771 | 0.17604 | 0.10762 | 0.17655
270 | 4.5 | feeder2_947 | 0.10355 | 0.16484 | 0.10346 | 0.16534
270 | 4.5 | feeder2_868 | 0.10342 | 0.16454 | 0.10334 | 0.16504
270 | 4.5 | feeder2_785 | 0.10351 | 0.16421 | 0.10343 | 0.1647
270 | 4.5 | feeder2_1176 | 0.10385 | 0.16435 | 0.10377 | 0.16485
270 | 4.5 | feeder2_846 | 0.10325 | 0.16394 | 0.10318 | 0.16443
270 | 4.5 | feeder2_911 | 0.10389 | 0.16409 | 0.10381 | 0.16458
270 | 4.5 | feeder2_1107 | 0.10775 | 0.17469 | 0.10766 | 0.17519
270 | 4.5 | feeder2_920 | 0.10817 | 0.17721 | 0.10808 | 0.17772
270 | 4.5 | feeder2_926 | 0.10901 | 0.17968 | 0.10892 | 0.18018
270 | 4.5 | feeder2_1239 | 0.10799 | 0.1764 | 0.10791 | 0.17691
270 | 4.5 | feeder2_933 | 0.10935 | 0.18074 | 0.10926 | 0.18125
270 | 4.5 | feeder2_1146 | 0.10917 | 0.17985 | 0.10909 | 0.18035
270 | 4.5 | feeder2_1124 | 0.10946 | 0.18077 | 0.10937 | 0.18128
270 | 4.5 | feeder2_942 | 0.11018 | 0.18346 | 0.11009 | 0.18397
270 | 4.5 | feeder2_952 | 0.11145 | 0.18766 | 0.11136 | 0.18818
270 | 4.5 | feeder2_965 | 0.11017 | 0.18345 | 0.11009 | 0.18395
270 | 4.5 | feeder2_961 | 0.11156 | 0.18808 | 0.11147 | 0.18859
270 | 4.5 | feeder2_963 | 0.11146 | 0.18767 | 0.11137 | 0.18819
270 | 4.5 | feeder2_973 | 0.11216 | 0.19032 | 0.11207 | 0.19084
270 | 4.5 | feeder2_1128 | 0.11155 | 0.18802 | 0.11146 | 0.18854
270 | 4.5 | feeder2_1113 | 0.11194 | 0.18771 | 0.11185 | 0.18822
270 | 4.5 | feeder2_1143 | 0.11165 | 0.18804 | 0.11156 | 0.18855
270 | 4.5 | feeder2_1238 | 0.11022 | 0.18366 | 0.11013 | 0.18417
270 | 4.5 | feeder2_979 | 0.11016 | 0.1834 | 0.11008 | 0.18392
270 | 4.5 | feeder2_1236 | 0.11302 | 0.19369 | 0.11293 | 0.19422
270 | 4.5 | feeder2_989 | 0.11216 | 0.19032 | 0.11207 | 0.19084
270 | 4.5 | feeder2_1196 | 0.10998 | 0.18323 | 0.10989 | 0.18374
270 | 4.5 | feeder2_1158 | 0.11228 | 0.19031 | 0.11219 | 0.19083
270 | 4.5 | feeder2_1122 | 0.10771 | 0.17418 | 0.10762 | 0.17466
270 | 4.5 | feeder2_1258 | 0.10796 | 0.17474 | 0.10787 | 0.17523
270 | 4.5 | feeder2_1303 | 0.10773 | 0.17429 | 0.10764 | 0.17478
270 | 4.5 | feeder2_1138 | 0.10768 | 0.17374 | 0.10759 | 0.17422
270 | 4.5 | feeder2_1304 | 0.10712 | 0.17318 | 0.10703 | 0.17366
270 | 4.5 | feeder2_1212 | 0.1077 | 0.17327 | 0.10762 | 0.17373
270 | 4.5 | feeder2_1311 | 0.10899 | 0.17336 | 0.1089 | 0.17382
270 | 4.5 | feeder2_1290 | 0.10757 | 0.17253 | 0.10748 | 0.17299
270 | 4.5 | feeder2_1325 | 0.11414 | 0.19836 | 0.11405 | 0.19891
270 | 4.5 | feeder2_1248 | 0.11302 | 0.19369 | 0.11293 | 0.19422
270 | 4.5 | feeder2_1249 | 0.11022 | 0.1837 | 0.11014 | 0.18421
270 | 4.5 | feeder2_1250 | 0.11023 | 0.18371 | 0.11014 | 0.18422
270 | 4.5 | feeder2_1366 | 0.11316 | 0.19369 | 0.11306 | 0.19423
270 | 4.5 | feeder2_1266 | 0.10801 | 0.17474 | 0.10793 | 0.17523
270 | 4.5 | feeder2_1372 | 0.10767 | 0.17278 | 0.10758 | 0.17324
270 | 4.5 | feeder2_1363 | 0.10745 | 0.17139 | 0.10736 | 0.17185
270 | 4.5 | feeder2_1446 | 0.1142 | 0.1985 | 0.1141 | 0.19905
270 | 4.5 | feeder2_1502 | 0.11542 | 0.20344 | 0.11532 | 0.204
270 | 4.5 | feeder2_1428 | 0.10695 | 0.17089 | 0.10686 | 0.17135
270 | 4.5 | feeder2_1380 | 0.10744 | 0.17079 | 0.10736 | 0.17124
270 | 4.5 | feeder2_1550 | 0.10928 | 0.1708 | 0.1092 | 0.17124
270 | 4.5 | feeder2_1386 | 0.1073 | 0.1704 | 0.10721 | 0.17086
270 | 4.5 | feeder2_1551 | 0.10636 | 0.16929 | 0.10627 | 0.16975
270 | 4.5 | feeder2_1400 | 0.10729 | 0.17049 | 0.10721 | 0.17094
270 | 4.5 | feeder2_1552 | 0.10708 | 0.17029 | 0.107 | 0.17075
270 | 4.5 | feeder2_1408 | 0.10728 | 0.17076 | 0.1072 | 0.17122
270 | 4.5 | feeder2_1553 | 0.10693 | 0.17042 | 0.10685 | 0.17087
270 | 4.5 | feeder2_1416 | 0.10729 | 0.17098 | 0.1072 | 0.17143
270 | 4.5 | feeder2_1530 | 0.10737 | 0.17119 | 0.10728 | 0.17164
270 | 4.5 | feeder2_1425 | 0.10732 | 0.17127 | 0.10723 | 0.17172
270 | 4.5 | feeder2_1589 | 0.10708 | 0.17103 | 0.10699 | 0.17149
270 | 4.5 | feeder2_1435 | 0.10733 | 0.17135 | 0.10724 | 0.17181
270 | 4.5 | feeder2_1621 | 0.10725 | 0.1726 | 0.10716 | 0.17306
270 | 4.5 | feeder2_1564 | 0.10727 | 0.17101 | 0.10718 | 0.17147
270 | 4.5 | feeder2_1704 | 0.11562 | 0.20347 | 0.11552 | 0.20404
270 | 4.5 | feeder2_1525 | 0.11573 | 0.20475 | 0.11563 | 0.20531
270 | 4.5 | feeder2_1716 | 0.11546 | 0.20652 | 0.11536 | 0.2071
270 | 4.5 | feeder2_1537 | 0.11604 | 0.20596 | 0.11594 | 0.20654
270 | 4.5 | feeder2_1645 | 0.11595 | 0.20588 | 0.11585 | 0.20645
270 | 4.5 | feeder2_1561 | 0.11641 | 0.20739 | 0.11631 | 0.20796
270 | 4.5 | feeder2_1657 | 0.11645 | 0.20752 | 0.11635 | 0.20809
270 | 4.5 | feeder2_1570 | 0.11656 | 0.20797 | 0.11646 | 0.20855
270 | 4.5 | feeder2_1756 | 0.11903 | 0.20832 | 0.11893 | 0.20889
270 | 4.5 | feeder2_1588 | 0.11669 | 0.20848 | 0.11659 | 0.20906
270 | 4.5 | feeder2_1628 | 0.11748 | 0.20866 | 0.11737 | 0.20923
270 | 4.5 | feeder2_1598 | 0.11682 | 0.20905 | 0.11672 | 0.20963
270 | 4.5 | feeder2_1816 | 0.11712 | 0.20903 | 0.11702 | 0.20961
270 | 4.5 | feeder2_1765 | 0.11718 | 0.20909 | 0.11707 | 0.20967
270 | 4.5 | feeder2_1641 | 0.11739 | 0.21188 | 0.11728 | 0.21248
270 | 4.5 | feeder2_1689 | 0.11769 | 0.21398 | 0.11758 | 0.2146
270 | 4.5 | feeder2_1744 | 0.11819 | 0.21199 | 0.11808 | 0.21258
270 | 4.5 | feeder2_1817 | 0.11767 | 0.2139 | 0.11756 | 0.21452
270 | 4.5 | feeder2_1779 | 0.11746 | 0.21507 | 0.11735 | 0.2157
270 | 4.5 | feeder2_1800 | 0.11763 | 0.21392 | 0.11752 | 0.21454
270 | 4.5 | feeder2_1818 | 0.11782 | 0.21643 | 0.11771 | 0.21711
270 | 4.5 | feeder2_1753 | 0.11822 | 0.21216 | 0.11812 | 0.21275
270 | 4.5 | feeder2_1754 | 0.11874 | 0.21203 | 0.11864 | 0.21263
300 | 5 | secondary | 0.012192 | 0.013922 | 0.01222 | 0.013913
300 | 5 | feeder2_44 | 0.022764 | 0.072853 | 0.022806 | 0.072793
300 | 5 | feeder2_45 | 0.02312 | 0.074957 | 0.023165 | 0.074893
300 | 5 | feeder2_46 | 0.023422 | 0.074756 | 0.023473 | 0.074687
300 | 5 | feeder2_51 | 0.023748 | 0.078676 | 0.0238 | 0.078608
300 | 5 | feeder2_48 | 0.02321 | 0.074488 | 0.023259 | 0.074423
300 | 5 | feeder2_52 | 0.023552 | 0.078606 | 0.023605 | 0.078538
300 | 5 | feeder2_68 | 0.025532 | 0.089177 | 0.025588 | 0.089102
300 | 5 | feeder2_69 | 0.025683 | 0.089368 | 0.025733 | 0.089293
300 | 5 | feeder2_71 | 0.025767 | 0.090559 | 0.025818 | 0.090488
300 | 5 | feeder2_72 | 0.025779 | 0.090387 | 0.025832 | 0.09031
300 | 5 | feeder2_73 | 0.026505 | 0.094899 | 0.026562 | 0.094822
300 | 5 | feeder2_74 | 0.024971 | 0.096076 | 0.025027 | 0.096
300 | 5 | feeder2_77 | 0.027201 | 0.098469 | 0.027259 | 0.09839
300 | 5 | feeder2_79 | 0.027552 | 0.099586 | 0.027608 | 0.099503
300 | 5 | feeder2_81 | 0.028184 | 0.10361 | 0.028246 | 0.10352
300 | 5 | feeder2_82 | 0.029961 | 0.10114 | 0.030018 | 0.10106
300 | 5 | feeder2_116 | 0.032438 | 0.12931 | 0.032506 | 0.12922
300 | 5 | feeder2_119 | 0.030247 | 0.13038 | 0.030315 | 0.13029
300 | 5 | feeder2_120 | 0.034286 | 0.13841 | 0.034361 | 0.13831
300 | 5 | feeder2_248 | 0.033849 | 0.13828 | 0.033919 | 0.13817
300 | 5 | feeder2_124 | 0.035446 | 0.14409 | 0.035523 | 0.14398
300 | 5 | feeder2_282 | 0.035444 | 0.14399 | 0.035518 | 0.14388
300 | 5 | feeder2_275 | 0.033524 | 0.14536 | 0.033602 | 0.14525
300 | 5 | feeder2_151 | 0.037774 | 0.15335 | 0.037854 | 0.15323
300 | 5 | feeder2_295 | 0.037864 | 0.15346 | 0.037947 | 0.15333
300 | 5 | feeder2_311 | 0.038027 | 0.15365 | 0.038103 | 0.15354
300 | 5 | feeder2_201 | 0.041542 | 0.16832 | 0.04163 | 0.16818
300 | 5 | feeder2_314 | 0.041528 | 0.16825 | 0.041613 | 0.16811
300 | 5 | feeder2_342 | 0.046935 | 0.18983 | 0.047032 | 0.18966
300 | 5 | feeder2_368 | 0.048443 | 0.1977 | 0.048539 | 0.19754
300 | 5 | feeder2_347 | 0.047326 | 0.18576 | 0.047431 | 0.18558
300 | 5 | feeder2_353 | 0.047537 | 0.18383 | 0.047637 | 0.18365
300 | 5 | feeder2_518 | 0.047333 | 0.18558 | 0.047434 | 0.1854
300 | 5 | feeder2_365 | 0.047791 | 0.18177 | 0.047895 | 0.18158
300 | 5 | feeder2_653 | 0.047248 | 0.18371 | 0.047354 | 0.18353
300 | 5 | feeder2_377 | 0.047927 | 0.18064 | 0.048031 | 0.18045
300 | 5 | feeder2_622 | 0.047824 | 0.18181 | 0.047927 | 0.18162
300 | 5 | feeder2_451 | 0.048443 | 0.19753 | 0.048535 | 0.19737
300 | 5 | feeder2_383 | 0.050916 | 0.21058 | 0.051018 | 0.21041
300 | 5 | feeder2_385 | 0.048076 | 0.17931 | 0.048179 | 0.17911
300 | 5 | feeder2_621 | 0.048023 | 0.18076 | 0.048129 | 0.18056
300 | 5 | feeder2_611 | 0.050726 | 0.2105 | 0.050824 | 0.21033
300 | 5 | feeder2_405 | 0.051074 | 0.21139 | 0.051165 | 0.21123
300 | 5 | feeder2_461 | 0.048747 | 0.17419 | 0.04886 | 0.17397
300 | 5 | feeder2_594 | 0.047791 | 0.17919 | 0.047899 | 0.17898
300 | 5 | feeder2_732 | 0.048038 | 0.21316 | 0.048137 | 0.21299
300 | 5 | feeder2_417 | 0.052462 | 0.21716 | 0.052559 | 0.217
300 | 5 | feeder2_663 | 0.052747 | 0.21786 | 0.052849 | 0.21769
300 | 5 | feeder2_444 | 0.053461 | 0.22132 | 0.053561 | 0.22114
300 | 5 | feeder2_759 | 0.053448 | 0.22121 | 0.053541 | 0.22105
300 | 5 | feeder2_842 | 0.073253 | 0.2439 | 0.073354 | 0.24372
300 | 5 | feeder2_459 | 0.053453 | 0.22144 | 0.053549 | 0.22127
300 | 5 | feeder2_702 | 0.053449 | 0.2214 | 0.053549 | 0.22123
300 | 5 | feeder2_493 | 0.053422 | 0.22191 | 0.053523 | 0.22174
300 | 5 | feeder2_651 | 0.04892 | 0.17441 | 0.049038 | 0.17418
300 | 5 | feeder2_684 | 0.049246 | 0.16983 | 0.04936 | 0.16958
300 | 5 | feeder2_674 | 0.053161 | 0.22203 | 0.05326 | 0.22186
300 | 5 | feeder2_696 | 0.05367 | 0.22283 | 0.053771 | 0.22266
300 | 5 | feeder2_681 | 0.05309 | 0.22199 | 0.053188 | 0.22182
300 | 5 | feeder2_682 | 0.052189 | 0.22261 | 0.052285 | 0.22245
300 | 5 | feeder2_728 | 0.049241 | 0.16985 | 0.049357 | 0.1696
300 | 5 | feeder2_724 | 0.04975 | 0.16535 | 0.04987 | 0.16508
300 | 5 | feeder2_703 | 0.054272 | 0.22354 | 0.054375 | 0.22337
300 | 5 | feeder2_704 | 0.053799 | 0.22298 | 0.053893 | 0.22282
300 | 5 | feeder2_754 | 0.049766 | 0.16518 | 0.049893 | 0.16491
300 | 5 | feeder2_747 | 0.049973 | 0.1636 | 0.050096 | 0.16333
300 | 5 | feeder2_828 | 0.049194 | 0.16982 | 0.049311 | 0.16958
300 | 5 | feeder2_763 | 0.04925 | 0.16992 | 0.049365 | 0.16967
300 | 5 | feeder2_836 | 0.050161 | 0.16384 | 0.050285 | 0.16356
300 | 5 | feeder2_758 | 0.050143 | 0.162 | 0.050267 | 0.16172
300 | 5 | feeder2_788 | 0.051356 | 0.16035 | 0.051485 | 0.16007
300 | 5 | feeder2_812 | 0.050528 | 0.15914 | 0.05066 | 0.15884
300 | 5 | feeder2_947 | 0.049281 | 0.16954 | 0.049399 | 0.16929
300 | 5 | feeder2_868 | 0.049739 | 0.1692 | 0.049855 | 0.16895
300 | 5 | feeder2_785 | 0.049206 | 0.17053 | 0.049322 | 0.17028
300 | 5 | feeder2_1176 | 0.049892 | 0.17285 | 0.050017 | 0.17258
300 | 5 | feeder2_846 | 0.048351 | 0.17081 | 0.048473 | 0.17055
300 | 5 | feeder2_911 | 0.049196 | 0.17048 | 0.049313 | 0.17023
300 | 5 | feeder2_1107 | 0.05002 | 0.15798 | 0.050157 | 0.15769
300 | 5 | feeder2_920 | 0.050776 | 0.15867 | 0.050915 | 0.15835
300 | 5 | feeder2_926 | 0.051164 | 0.15806 | 0.051299 | 0.15774
300 | 5 | feeder2_1239 | 0.050755 | 0.15857 | 0.050891 | 0.15826
300 | 5 | feeder2_933 | 0.051304 | 0.15817 | 0.05144 | 0.15784
300 | 5 | feeder2_1146 | 0.051316 | 0.15634 | 0.051454 | 0.15601
300 | 5 | feeder2_1124 | 0.051434 | 0.15833 | 0.051573 | 0.158
300 | 5 | feeder2_942 | 0.051628 | 0.15831 | 0.051766 | 0.15796
300 | 5 | feeder2_952 | 0.052017 | 0.16007 | 0.05216 | 0.1597
300 | 5 | feeder2_965 | 0.05164 | 0.15811 | 0.051778 | 0.15776
300 | 5 | feeder2_961 | 0.052039 | 0.16051 | 0.052188 | 0.16014
300 | 5 | feeder2_963 | 0.052021 | 0.16002 | 0.05217 | 0.15964
300 | 5 | feeder2_973 | 0.052261 | 0.16274 | 0.052413 | 0.16235
300 | 5 | feeder2_1128 | 0.051864 | 0.16078 | 0.052015 | 0.1604
300 | 5 | feeder2_1113 | 0.052605 | 0.15927 | 0.052748 | 0.1589
300 | 5 | feeder2_1143 | 0.052132 | 0.15845 | 0.052279 | 0.15808
300 | 5 | feeder2_1238 | 0.053919 | 0.15524 | 0.05406 | 0.15489
300 | 5 | feeder2_979 | 0.051634 | 0.15808 | 0.051778 | 0.15774
300 | 5 | feeder2_1236 | 0.052571 | 0.16597 | 0.052725 | 0.16555
300 | 5 | feeder2_989 | 0.052262 | 0.16274 | 0.052413 | 0.16235
300 | 5 | feeder2_1196 | 0.05147 | 0.15799 | 0.051612 | 0.15765
300 | 5 | feeder2_1158 | 0.052401 | 0.1629 | 0.052553 | 0.16251
300 | 5 | feeder2_1122 | 0.049767 | 0.15728 | 0.049906 | 0.15699
300 | 5 | feeder2_1258 | 0.050285 | 0.15831 | 0.050415 | 0.15802
300 | 5 | feeder2_1303 | 0.049757 | 0.15722 | 0.04989 | 0.15693
300 | 5 | feeder2_1138 | 0.049573 | 0.15675 | 0.049704 | 0.15647
300 | 5 | feeder2_1304 | 0.047977 | 0.15723 | 0.048113 | 0.15695
300 | 5 | feeder2_1212 | 0.04944 | 0.15538 | 0.049575 | 0.1551
300 | 5 | feeder2_1311 | 0.049429 | 0.1553 | 0.049567 | 0.15502
300 | 5 | feeder2_1290 | 0.049293 | 0.15375 | 0.049425 | 0.15348
300 | 5 | feeder2_1325 | 0.052755 | 0.16908 | 0.052911 | 0.16865
300 | 5 | feeder2_1248 | 0.052573 | 0.16597 | 0.052726 | 0.16556
300 | 5 | feeder2_1249 | 0.053916 | 0.15523 | 0.054051 | 0.15488
300 | 5 | feeder2_1250 | 0.055549 | 0.15328 | 0.055685 | 0.15293
300 | 5 | feeder2_1366 | 0.052867 | 0.16732 | 0.05302 | 0.16691
300 | 5 | feeder2_1266 | 0.050345 | 0.15838 | 0.050479 | 0.15809
300 | 5 | feeder2_1372 | 0.049313 | 0.15357 | 0.04945 | 0.15329
300 | 5 | feeder2_1363 | 0.049176 | 0.15225 | 0.049313 | 0.15198
300 | 5 | feeder2_1446 | 0.053971 | 0.1675 | 0.054131 | 0.16706
300 | 5 | feeder2_1502 | 0.052819 | 0.17464 | 0.052986 | 0.17418
300 | 5 | feeder2_1428 | 0.048714 | 0.15205 | 0.048845 | 0.15179
300 | 5 | feeder2_1380 | 0.049134 | 0.15083 | 0.049271 | 0.15056
300 | 5 | feeder2_1550 | 0.049137 | 0.15079 | 0.049272 | 0.15052
300 | 5 | feeder2_1386 | 0.049116 | 0.15016 | 0.049248 | 0.1499
300 | 5 | feeder2_1551 | 0.04898 | 0.15007 | 0.049117 | 0.1498
300 | 5 | feeder2_1400 | 0.049111 | 0.14986 | 0.049244 | 0.1496
300 | 5 | feeder2_1552 | 0.048932 | 0.14974 | 0.04907 | 0.14948
300 | 5 | feeder2_1408 | 0.049111 | 0.14932 | 0.049249 | 0.14906
300 | 5 | feeder2_1553 | 0.047419 | 0.1501 | 0.047558 | 0.14985
300 | 5 | feeder2_1416 | 0.049197 | 0.1489 | 0.049337 | 0.14864
300 | 5 | feeder2_1530 | 0.050898 | 0.1467 | 0.051033 | 0.14644
300 | 5 | feeder2_1425 | 0.049267 | 0.14926 | 0.049399 | 0.149
300 | 5 | feeder2_1589 | 0.049045 | 0.14917 | 0.049183 | 0.1489
300 | 5 | feeder2_1435 | 0.049284 | 0.14934 | 0.049421 | 0.14908
300 | 5 | feeder2_1621 | 0.049597 | 0.15027 | 0.049733 | 0.15
300 | 5 | feeder2_1564 | 0.049243 | 0.14916 | 0.049374 | 0.1489
300 | 5 | feeder2_1704 | 0.053177 | 0.17564 | 0.053346 | 0.17517
300 | 5 | feeder2_1525 | 0.052763 | 0.17567 | 0.052928 | 0.17521
300 | 5 | feeder2_1716 | 0.053576 | 0.17889 | 0.053745 | 0.17842
300 | 5 | feeder2_1537 | 0.052602 | 0.17629 | 0.052768 | 0.17582
300 | 5 | feeder2_1645 | 0.051637 | 0.17663 | 0.051807 | 0.17617
300 | 5 | feeder2_1561 | 0.052542 | 0.17685 | 0.052708 | 0.17639
300 | 5 | feeder2_1657 | 0.052539 | 0.17678 | 0.052707 | 0.17631
300 | 5 | feeder2_1570 | 0.052521 | 0.17711 | 0.052687 | 0.17664
300 | 5 | feeder2_1756 | 0.052477 | 0.17699 | 0.052649 | 0.17652
300 | 5 | feeder2_1588 | 0.052503 | 0.17736 | 0.052672 | 0.17688
300 | 5 | feeder2_1628 | 0.052502 | 0.17727 | 0.052674 | 0.17679
300 | 5 | feeder2_1598 | 0.052487 | 0.1777 | 0.052663 | 0.17721
300 | 5 | feeder2_1816 | 0.052847 | 0.17809 | 0.053017 | 0.17762
300 | 5 | feeder2_1765 | 0.052943 | 0.17824 | 0.053117 | 0.17776
300 | 5 | feeder2_1641 | 0.052333 | 0.17897 | 0.052509 | 0.17848
300 | 5 | feeder2_1689 | 0.052227 | 0.18012 | 0.05241 | 0.17961
300 | 5 | feeder2_1744 | 0.05232 | 0.17893 | 0.052503 | 0.17844
300 | 5 | feeder2_1817 | 0.052219 | 0.18006 | 0.052405 | 0.17955
300 | 5 | feeder2_1779 | 0.052264 | 0.18016 | 0.052447 | 0.17965
300 | 5 | feeder2_1800 | 0.050651 | 0.1808 | 0.05083 | 0.18031
300 | 5 | feeder2_1818 | 0.051908 | 0.18134 | 0.052118 | 0.18081
300 | 5 | feeder2_1753 | 0.052293 | 0.17887 | 0.052474 | 0.17837
300 | 5 | feeder2_1754 | 0.052318 | 0.17892 | 0.052497 | 0.17842
330 | 5.5 | secondary | 0.010734 | 0.0090608 | 0.010725 | 0.0090506
330 | 5.5 | feeder2_44 | 0.020049 | 0.047431 | 0.020036 | 0.047381
330 | 5.5 | feeder2_45 | 0.02039 | 0.048871 | 0.020374 | 0.048817
330 | 5.5 | feeder2_46 | 0.020208 | 0.047991 | 0.020196 | 0.047939
330 | 5.5 | feeder2_51 | 0.020881 | 0.05186 | 0.020869 | 0.051805
330 | 5.5 | feeder2_48 | 0.023675 | 0.046005 | 0.023662 | 0.045955
330 | 5.5 | feeder2_52 | 0.020039 | 0.055126 | 0.020024 | 0.055073
330 | 5.5 | feeder2_68 | 0.022492 | 0.059179 | 0.02248 | 0.059113
330 | 5.5 | feeder2_69 | 0.022548 | 0.059324 | 0.022533 | 0.059262
330 | 5.5 | feeder2_71 | 0.022706 | 0.060145 | 0.02269 | 0.06008
330 | 5.5 | feeder2_72 | 0.022865 | 0.059902 | 0.022851 | 0.059838
330 | 5.5 | feeder2_73 | 0.023378 | 0.063205 | 0.023361 | 0.063136
330 | 5.5 | feeder2_74 | 0.022742 | 0.064951 | 0.022725 | 0.064887
330 | 5.5 | feeder2_77 | 0.024008 | 0.065582 | 0.023994 | 0.065515
330 | 5.5 | feeder2_79 | 0.024118 | 0.065885 | 0.024104 | 0.065817
330 | 5.5 | feeder2_81 | 0.024989 | 0.06923 | 0.024975 | 0.069157
330 | 5.5 | feeder2_82 | 0.02727 | 0.067035 | 0.027251 | 0.066964
330 | 5.5 | feeder2_116 | 0.029045 | 0.088289 | 0.029029 | 0.088197
330 | 5.5 | feeder2_119 | 0.028274 | 0.088444 | 0.028258 | 0.088353
330 | 5.5 | feeder2_120 | 0.030676 | 0.095404 | 0.03066 | 0.095304
330 | 5.5 | feeder2_248 | 0.030184 | 0.095464 | 0.030162 | 0.095363
330 | 5.5 | feeder2_124 | 0.031727 | 0.099801 | 0.031707 | 0.099699
330 | 5.5 | feeder2_282 | 0.031807 | 0.099661 | 0.031786 | 0.099558
330 | 5.5 | feeder2_275 | 0.030598 | 0.10164 | 0.030579 | 0.10154
330 | 5.5 | feeder2_151 | 0.033839 | 0.10648 | 0.033819 | 0.10637
330 | 5.5 | feeder2_295 | 0.033889 | 0.10658 | 0.033871 | 0.10646
330 | 5.5 | feeder2_311 | 0.033974 | 0.10674 | 0.033952 | 0.10663
330 | 5.5 | feeder2_201 | 0.037298 | 0.11731 | 0.037275 | 0.11719
330 | 5.5 | feeder2_314 | 0.038695 | 0.11596 | 0.038669 | 0.11583
330 | 5.5 | feeder2_342 | 0.041783 | 0.13593 | 0.041762 | 0.13579
330 | 5.5 | feeder2_368 | 0.04315 | 0.14234 | 0.043126 | 0.1422
330 | 5.5 | feeder2_347 | 0.041784 | 0.13326 | 0.041761 | 0.13311
330 | 5.5 | feeder2_353 | 0.041787 | 0.13207 | 0.041762 | 0.13191
330 | 5.5 | feeder2_518 | 0.041921 | 0.13301 | 0.041896 | 0.13286
330 | 5.5 | feeder2_365 | 0.041824 | 0.13076 | 0.041792 | 0.1306
330 | 5.5 | feeder2_653 | 0.041459 | 0.13207 | 0.041431 | 0.13191
330 | 5.5 | feeder2_377 | 0.041843 | 0.13005 | 0.04181 | 0.12988
330 | 5.5 | feeder2_622 | 0.041844 | 0.1308 | 0.041812 | 0.13064
330 | 5.5 | feeder2_451 | 0.04482 | 0.14061 | 0.044795 | 0.14047
330 | 5.5 | feeder2_383 | 0.045105 | 0.15423 | 0.045086 | 0.15409
330 | 5.5 | feeder2_385 | 0.041858 | 0.12919 | 0.041831 | 0.12902
330 | 5.5 | feeder2_621 | 0.041902 | 0.13015 | 0.041872 | 0.12999
330 | 5.5 | feeder2_611 | 0.04404 | 0.15531 | 0.044016 | 0.15517
330 | 5.5 | feeder2_405 | 0.04525 | 0.15492 | 0.045229 | 0.15478
330 | 5.5 | feeder2_461 | 0.042032 | 0.12577 | 0.042002 | 0.12559
330 | 5.5 | feeder2_594 | 0.041534 | 0.12919 | 0.041504 | 0.12903
330 | 5.5 | feeder2_732 | 0.043761 | 0.15639 | 0.043738 | 0.15625
330 | 5.5 | feeder2_417 | 0.046476 | 0.1599 | 0.046452 | 0.15976
330 | 5.5 | feeder2_663 | 0.046593 | 0.16006 | 0.04657 | 0.15992
330 | 5.5 | feeder2_444 | 0.047411 | 0.16366 | 0.047391 | 0.16352
330 | 5.5 | feeder2_759 | 0.049769 | 0.16121 | 0.049744 | 0.16108
330 | 5.5 | feeder2_842 | 0.062918 | 0.1847 | 0.062907 | 0.18456
330 | 5.5 | feeder2_459 | 0.047402 | 0.16388 | 0.047381 | 0.16374
330 | 5.5 | feeder2_702 | 0.047422 | 0.16383 | 0.047401 | 0.1637
330 | 5.5 | feeder2_493 | 0.04737 | 0.16473 | 0.047351 | 0.16459
330 | 5.5 | feeder2_651 | 0.042129 | 0.12595 | 0.042096 | 0.12577
330 | 5.5 | feeder2_684 | 0.042138 | 0.12279 | 0.042104 | 0.1226
330 | 5.5 | feeder2_674 | 0.047156 | 0.16491 | 0.047138 | 0.16478
330 | 5.5 | feeder2_696 | 0.047614 | 0.16653 | 0.04759 | 0.1664
330 | 5.5 | feeder2_681 | 0.047068 | 0.16489 | 0.047047 | 0.16475
330 | 5.5 | feeder2_682 | 0.046412 | 0.16569 | 0.046389 | 0.16555
330 | 5.5 | feeder2_728 | 0.042145 | 0.1225 | 0.042108 | 0.12231
330 | 5.5 | feeder2_724 | 0.042309 | 0.12043 | 0.042274 | 0.12022
330 | 5.5 | feeder2_703 | 0.047417 | 0.16778 | 0.047397 | 0.16765
330 | 5.5 | feeder2_704 | 0.047568 | 0.16678 | 0.047543 | 0.16665
330 | 5.5 | feeder2_754 | 0.043823 | 0.11891 | 0.043787 | 0.1187
330 | 5.5 | feeder2_747 | 0.042242 | 0.1203 | 0.042208 | 0.1201
330 | 5.5 | feeder2_828 | 0.042091 | 0.1225 | 0.042061 | 0.12231
330 | 5.5 | feeder2_763 | 0.042178 | 0.12209 | 0.042148 | 0.12189
330 | 5.5 | feeder2_836 | 0.042348 | 0.1205 | 0.042309 | 0.1203
330 | 5.5 | feeder2_758 | 0.042167 | 0.12011 | 0.042129 | 0.1199
330 | 5.5 | feeder2_788 | 0.042367 | 0.11977 | 0.042328 | 0.11956
330 | 5.5 | feeder2_812 | 0.041928 | 0.11991 | 0.041888 | 0.11968
330 | 5.5 | feeder2_947 | 0.042516 | 0.12151 | 0.042479 | 0.12132
330 | 5.5 | feeder2_868 | 0.042853 | 0.12137 | 0.042818 | 0.12118
330 | 5.5 | feeder2_785 | 0.042073 | 0.12247 | 0.042037 | 0.12228
330 | 5.5 | feeder2_1176 | 0.042307 | 0.12291 | 0.042277 | 0.12272
330 | 5.5 | feeder2_846 | 0.041443 | 0.12311 | 0.041409 | 0.12291
330 | 5.5 | feeder2_911 | 0.042078 | 0.12238 | 0.042043 | 0.12219
330 | 5.5 | feeder2_1107 | 0.040592 | 0.1243 | 0.040554 | 0.12407
330 | 5.5 | feeder2_920 | 0.04223 | 0.11866 | 0.042193 | 0.11843
330 | 5.5 | feeder2_926 | 0.04271 | 0.1168 | 0.042669 | 0.11657
330 | 5.5 | feeder2_1239 | 0.042196 | 0.11865 | 0.042155 | 0.11842
330 | 5.5 | feeder2_933 | 0.042874 | 0.11627 | 0.042832 | 0.11603
330 | 5.5 | feeder2_1146 | 0.042935 | 0.11547 | 0.042896 | 0.11525
330 | 5.5 | feeder2_1124 | 0.042526 | 0.11646 | 0.042491 | 0.11622
330 | 5.5 | feeder2_942 | 0.043255 | 0.11465 | 0.043212 | 0.11441
330 | 5.5 | feeder2_952 | 0.043883 | 0.11259 | 0.043838 | 0.11235
330 | 5.5 | feeder2_965 | 0.043247 | 0.11461 | 0.043204 | 0.11437
330 | 5.5 | feeder2_961 | 0.043932 | 0.11251 | 0.043888 | 0.11226
330 | 5.5 | feeder2_963 | 0.043887 | 0.11256 | 0.043846 | 0.11232
330 | 5.5 | feeder2_973 | 0.044284 | 0.1117 | 0.04424 | 0.11145
330 | 5.5 | feeder2_1128 | 0.04377 | 0.11312 | 0.043728 | 0.11288
330 | 5.5 | feeder2_1113 | 0.044447 | 0.11201 | 0.044401 | 0.11176
330 | 5.5 | feeder2_1143 | 0.043888 | 0.1123 | 0.043845 | 0.11206
330 | 5.5 | feeder2_1238 | 0.045989 | 0.11195 | 0.04595 | 0.11171
330 | 5.5 | feeder2_979 | 0.043197 | 0.11479 | 0.043158 | 0.11455
330 | 5.5 | feeder2_1236 | 0.044786 | 0.11042 | 0.044744 | 0.11016
330 | 5.5 | feeder2_989 | 0.044284 | 0.11171 | 0.044242 | 0.11145
330 | 5.5 | feeder2_1196 | 0.042541 | 0.11559 | 0.042498 | 0.11534
330 | 5.5 | feeder2_1158 | 0.044377 | 0.11186 | 0.044336 | 0.1116
330 | 5.5 | feeder2_1122 | 0.04001 | 0.12566 | 0.03997 | 0.12544
330 | 5.5 | feeder2_1258 | 0.039961 | 0.1246 | 0.039924 | 0.12437
330 | 5.5 | feeder2_1303 | 0.041589 | 0.12419 | 0.041553 | 0.12396
330 | 5.5 | feeder2_1138 | 0.039453 | 0.12733 | 0.039417 | 0.1271
330 | 5.5 | feeder2_1304 | 0.038887 | 0.12741 | 0.038844 | 0.12718
330 | 5.5 | feeder2_1212 | 0.03837 | 0.13091 | 0.038329 | 0.13069
330 | 5.5 | feeder2_1311 | 0.038444 | 0.13076 | 0.038409 | 0.13053
330 | 5.5 | feeder2_1290 | 0.037041 | 0.13558 | 0.037003 | 0.13536
330 | 5.5 | feeder2_1325 | 0.045377 | 0.10775 | 0.045335 | 0.10748
330 | 5.5 | feeder2_1248 | 0.04478 | 0.11042 | 0.044738 | 0.11016
330 | 5.5 | feeder2_1249 | 0.046006 | 0.11192 | 0.045962 | 0.11168
330 | 5.5 | feeder2_1250 | 0.04787 | 0.11019 | 0.047828 | 0.10995
330 | 5.5 | feeder2_1366 | 0.043332 | 0.11114 | 0.043288 | 0.11089
330 | 5.5 | feeder2_1266 | 0.039659 | 0.12468 | 0.03962 | 0.12446
330 | 5.5 | feeder2_1372 | 0.037209 | 0.13529 | 0.037173 | 0.13507
330 | 5.5 | feeder2_1363 | 0.035617 | 0.14114 | 0.035576 | 0.14092
330 | 5.5 | feeder2_1446 | 0.046326 | 0.10677 | 0.04628 | 0.10651
330 | 5.5 | feeder2_1502 | 0.045837 | 0.10604 | 0.045791 | 0.10576
330 | 5.5 | feeder2_1428 | 0.034493 | 0.1425 | 0.034456 | 0.14228
330 | 5.5 | feeder2_1380 | 0.034448 | 0.146 | 0.034407 | 0.14578
330 | 5.5 | feeder2_1550 | 0.034487 | 0.14594 | 0.034442 | 0.14571
330 | 5.5 | feeder2_1386 | 0.03388 | 0.14844 | 0.033841 | 0.14821
330 | 5.5 | feeder2_1551 | 0.032879 | 0.15026 | 0.032836 | 0.15004
330 | 5.5 | feeder2_1400 | 0.033697 | 0.1492 | 0.033659 | 0.14897
330 | 5.5 | feeder2_1552 | 0.033474 | 0.14922 | 0.033434 | 0.149
330 | 5.5 | feeder2_1408 | 0.03334 | 0.15078 | 0.033302 | 0.15056
330 | 5.5 | feeder2_1553 | 0.032279 | 0.15242 | 0.03224 | 0.15219
330 | 5.5 | feeder2_1416 | 0.033235 | 0.15126 | 0.033193 | 0.15104
330 | 5.5 | feeder2_1530 | 0.033381 | 0.15101 | 0.033345 | 0.15079
330 | 5.5 | feeder2_1425 | 0.033034 | 0.15231 | 0.032995 | 0.15208
330 | 5.5 | feeder2_1589 | 0.032789 | 0.15238 | 0.032749 | 0.15216
330 | 5.5 | feeder2_1435 | 0.032998 | 0.15251 | 0.032958 | 0.15229
330 | 5.5 | feeder2_1621 | 0.033121 | 0.15274 | 0.033077 | 0.15252
330 | 5.5 | feeder2_1564 | 0.032517 | 0.15468 | 0.032478 | 0.15445
330 | 5.5 | feeder2_1704 | 0.045975 | 0.10632 | 0.045927 | 0.10604
330 | 5.5 | feeder2_1525 | 0.045936 | 0.1055 | 0.045892 | 0.10522
330 | 5.5 | feeder2_1716 | 0.04605 | 0.10571 | 0.046 | 0.10543
330 | 5.5 | feeder2_1537 | 0.046039 | 0.10486 | 0.045991 | 0.10458
330 | 5.5 | feeder2_1645 | 0.045936 | 0.10482 | 0.045887 | 0.10454
330 | 5.5 | feeder2_1561 | 0.046166 | 0.10416 | 0.046117 | 0.10387
330 | 5.5 | feeder2_1657 | 0.047111 | 0.10319 | 0.047062 | 0.1029
330 | 5.5 | feeder2_1570 | 0.046182 | 0.1041 | 0.046134 | 0.10381
330 | 5.5 | feeder2_1756 | 0.046317 | 0.10384 | 0.046267 | 0.10355
330 | 5.5 | feeder2_1588 | 0.046198 | 0.10405 | 0.046149 | 0.10376
330 | 5.5 | feeder2_1628 | 0.046299 | 0.10389 | 0.046246 | 0.1036
330 | 5.5 | feeder2_1598 | 0.046217 | 0.10405 | 0.046164 | 0.10375
330 | 5.5 | feeder2_1816 | 0.046446 | 0.10443 | 0.046397 | 0.10414
330 | 5.5 | feeder2_1765 | 0.046467 | 0.10454 | 0.046422 | 0.10424
330 | 5.5 | feeder2_1641 | 0.046242 | 0.10365 | 0.046188 | 0.10335
330 | 5.5 | feeder2_1689 | 0.046065 | 0.10456 | 0.046016 | 0.10426
330 | 5.5 | feeder2_1744 | 0.046983 | 0.10289 | 0.046935 | 0.10259
330 | 5.5 | feeder2_1817 | 0.046048 | 0.10454 | 0.045993 | 0.10424
330 | 5.5 | feeder2_1779 | 0.046085 | 0.1046 | 0.046035 | 0.10429
330 | 5.5 | feeder2_1800 | 0.045373 | 0.10553 | 0.045319 | 0.10522
330 | 5.5 | feeder2_1818 | 0.044531 | 0.10487 | 0.04447 | 0.10454
330 | 5.5 | feeder2_1753 | 0.049262 | 0.10061 | 0.049209 | 0.1003
330 | 5.5 | feeder2_1754 | 0.047001 | 0.10286 | 0.04695 | 0.10256
360 | 6 | secondary | 0.013337 | 0.028162 | 0.013325 | 0.02816
360 | 6 | feeder2_44 | 0.024892 | 0.1473 | 0.024873 | 0.14729
360 | 6 | feeder2_45 | 0.025335 | 0.15199 | 0.025314 | 0.15198
360 | 6 | feeder2_46 | 0.024919 | 0.14657 | 0.0249 | 0.14656
360 | 6 | feeder2_51 | 0.026116 | 0.16015 | 0.026098 | 0.16014
360 | 6 | feeder2_48 | 0.024814 | 0.15199 | 0.024792 | 0.15198
360 | 6 | feeder2_52 | 0.026312 | 0.16036 | 0.02629 | 0.16035
360 | 6 | feeder2_68 | 0.028311 | 0.18308 | 0.028289 | 0.18307
360 | 6 | feeder2_69 | 0.028296 | 0.18293 | 0.028274 | 0.18291
360 | 6 | feeder2_71 | 0.028605 | 0.18613 | 0.028582 | 0.18612
360 | 6 | feeder2_72 | 0.028413 | 0.18611 | 0.028388 | 0.1861
360 | 6 | feeder2_73 | 0.029527 | 0.19569 | 0.029501 | 0.19567
360 | 6 | feeder2_74 | 0.029649 | 0.19582 | 0.029622 | 0.19581
360 | 6 | feeder2_77 | 0.030315 | 0.20387 | 0.030291 | 0.20385
360 | 6 | feeder2_79 | 0.031934 | 0.20154 | 0.031912 | 0.20152
360 | 6 | feeder2_81 | 0.031525 | 0.21771 | 0.031499 | 0.21769
360 | 6 | feeder2_82 | 0.031053 | 0.21769 | 0.031028 | 0.21767
360 | 6 | feeder2_116 | 0.037098 | 0.28011 | 0.037068 | 0.28009
360 | 6 | feeder2_119 | 0.037814 | 0.28086 | 0.037784 | 0.28084
360 | 6 | feeder2_120 | 0.039097 | 0.30285 | 0.039063 | 0.30282
360 | 6 | feeder2_248 | 0.040063 | 0.30369 | 0.04003 | 0.30367
360 | 6 | feeder2_124 | 0.040173 | 0.31643 | 0.04014 | 0.31641
360 | 6 | feeder2_282 | 0.040064 | 0.3164 | 0.040033 | 0.31638
360 | 6 | feeder2_275 | 0.040672 | 0.31686 | 0.04064 | 0.31683
360 | 6 | feeder2_151 | 0.041916 | 0.33976 | 0.041882 | 0.33974
360 | 6 | feeder2_295 | 0.041892 | 0.33968 | 0.04186 | 0.33966
360 | 6 | feeder2_311 | 0.041859 | 0.33952 | 0.041823 | 0.33949
360 | 6 | feeder2_201 | 0.044903 | 0.37904 | 0.044866 | 0.37901
360 | 6 | feeder2_314 | 0.044825 | 0.379 | 0.044784 | 0.37898
360 | 6 | feeder2_342 | 0.049174 | 0.43496 | 0.049131 | 0.43493
360 | 6 | feeder2_368 | 0.051903 | 0.4455 | 0.051862 | 0.44546
360 | 6 | feeder2_347 | 0.04752 | 0.44286 | 0.047477 | 0.44282
360 | 6 | feeder2_353 | 0.046719 | 0.44686 | 0.046674 | 0.44681
360 | 6 | feeder2_518 | 0.047325 | 0.44283 | 0.047283 | 0.44278
360 | 6 | feeder2_365 | 0.045804 | 0.45115 | 0.045761 | 0.4511
360 | 6 | feeder2_653 | 0.047035 | 0.44717 | 0.046987 | 0.44713
360 | 6 | feeder2_377 | 0.0453 | 0.45392 | 0.045259 | 0.45387
360 | 6 | feeder2_622 | 0.046835 | 0.44956 | 0.04679 | 0.44952
360 | 6 | feeder2_451 | 0.051839 | 0.44548 | 0.051798 | 0.44544
360 | 6 | feeder2_383 | 0.056329 | 0.46262 | 0.056287 | 0.46259
360 | 6 | feeder2_385 | 0.044733 | 0.45714 | 0.044687 | 0.45708
360 | 6 | feeder2_621 | 0.045264 | 0.45383 | 0.045218 | 0.45378
360 | 6 | feeder2_611 | 0.056543 | 0.46284 | 0.056502 | 0.46281
360 | 6 | feeder2_405 | 0.056603 | 0.46368 | 0.056561 | 0.46365
360 | 6 | feeder2_461 | 0.042013 | 0.46927 | 0.041964 | 0.46921
360 | 6 | feeder2_594 | 0.045525 | 0.45765 | 0.045481 | 0.4576
360 | 6 | feeder2_732 | 0.056934 | 0.46402 | 0.056891 | 0.464
360 | 6 | feeder2_417 | 0.058641 | 0.47161 | 0.058599 | 0.47158
360 | 6 | feeder2_663 | 0.058579 | 0.4715 | 0.058535 | 0.47147
360 | 6 | feeder2_444 | 0.060199 | 0.47768 | 0.060157 | 0.47765
360 | 6 | feeder2_759 | 0.060084 | 0.47764 | 0.060046 | 0.47761
360 | 6 | feeder2_842 | 0.060122 | 0.47755 | 0.060083 | 0.47751
360 | 6 | feeder2_459 | 0.060748 | 0.47981 | 0.060708 | 0.47978
360 | 6 | feeder2_702 | 0.059394 | 0.48084 | 0.059357 | 0.48081
360 | 6 | feeder2_493 | 0.062984 | 0.48754 | 0.06294 | 0.48751
360 | 6 | feeder2_651 | 0.042668 | 0.46791 | 0.042616 | 0.46785
360 | 6 | feeder2_684 | 0.039924 | 0.48088 | 0.039873 | 0.4808
360 | 6 | feeder2_674 | 0.067976 | 0.49265 | 0.067935 | 0.49262
360 | 6 | feeder2_696 | 0.062856 | 0.48686 | 0.06281 | 0.48683
360 | 6 | feeder2_681 | 0.081754 | 0.50662 | 0.081714 | 0.50659
360 | 6 | feeder2_682 | 0.068054 | 0.49273 | 0.068011 | 0.4927
360 | 6 | feeder2_728 | 0.039724 | 0.48164 | 0.039673 | 0.48157
360 | 6 | feeder2_724 | 0.038201 | 0.49113 | 0.038151 | 0.49105
360 | 6 | feeder2_703 | 0.062721 | 0.4863 | 0.062682 | 0.48626
360 | 6 | feeder2_704 | 0.062828 | 0.48674 | 0.062789 | 0.48671
360 | 6 | feeder2_754 | 0.038052 | 0.49112 | 0.037997 | 0.49105
360 | 6 | feeder2_747 | 0.037531 | 0.49536 | 0.03748 | 0.49528
360 | 6 | feeder2_828 | 0.039778 | 0.4817 | 0.039729 | 0.48162
360 | 6 | feeder2_763 | 0.039408 | 0.48269 | 0.039357 | 0.48262
360 | 6 | feeder2_836 | 0.037424 | 0.49516 | 0.03737 | 0.49508
360 | 6 | feeder2_758 | 0.03699 | 0.4991 | 0.036936 | 0.49901
360 | 6 | feeder2_788 | 0.035451 | 0.50025 | 0.0354 | 0.50017
360 | 6 | feeder2_812 | 0.035719 | 0.50929 | 0.035663 | 0.5092
360 | 6 | feeder2_947 | 0.039057 | 0.48267 | 0.039005 | 0.48259
360 | 6 | feeder2_868 | 0.039289 | 0.48268 | 0.039241 | 0.48261
360 | 6 | feeder2_785 | 0.03924 | 0.48336 | 0.039189 | 0.48329
360 | 6 | feeder2_1176 | 0.039139 | 0.48318 | 0.039086 | 0.48311
360 | 6 | feeder2_846 | 0.039502 | 0.48361 | 0.039454 | 0.48353
360 | 6 | feeder2_911 | 0.038799 | 0.48461 | 0.038748 | 0.48454
360 | 6 | feeder2_1107 | 0.036073 | 0.51766 | 0.036017 | 0.51757
360 | 6 | feeder2_920 | 0.035289 | 0.50985 | 0.035232 | 0.50975
360 | 6 | feeder2_926 | 0.034625 | 0.51055 | 0.034565 | 0.51045
360 | 6 | feeder2_1239 | 0.035321 | 0.51002 | 0.035266 | 0.50993
360 | 6 | feeder2_933 | 0.034375 | 0.51066 | 0.034316 | 0.51056
360 | 6 | feeder2_1146 | 0.034423 | 0.51151 | 0.034364 | 0.51141
360 | 6 | feeder2_1124 | 0.034339 | 0.51061 | 0.034279 | 0.51051
360 | 6 | feeder2_942 | 0.033754 | 0.51099 | 0.033699 | 0.51088
360 | 6 | feeder2_952 | 0.032968 | 0.51041 | 0.032909 | 0.51029
360 | 6 | feeder2_965 | 0.033738 | 0.51113 | 0.033676 | 0.51103
360 | 6 | feeder2_961 | 0.032899 | 0.51026 | 0.032839 | 0.51015
360 | 6 | feeder2_963 | 0.032964 | 0.51042 | 0.032901 | 0.51032
360 | 6 | feeder2_973 | 0.032529 | 0.50947 | 0.032473 | 0.50935
360 | 6 | feeder2_1128 | 0.03291 | 0.51032 | 0.032849 | 0.51021
360 | 6 | feeder2_1113 | 0.032424 | 0.51088 | 0.032366 | 0.51077
360 | 6 | feeder2_1143 | 0.032973 | 0.51039 | 0.032915 | 0.51028
360 | 6 | feeder2_1238 | 0.03151 | 0.513 | 0.031453 | 0.51289
360 | 6 | feeder2_979 | 0.033745 | 0.51117 | 0.033688 | 0.51107
360 | 6 | feeder2_1236 | 0.032005 | 0.50839 | 0.031942 | 0.50827
360 | 6 | feeder2_989 | 0.032529 | 0.50947 | 0.032473 | 0.50935
360 | 6 | feeder2_1196 | 0.033928 | 0.51134 | 0.033872 | 0.51123
360 | 6 | feeder2_1158 | 0.032423 | 0.50935 | 0.032364 | 0.50923
360 | 6 | feeder2_1122 | 0.036244 | 0.52099 | 0.03619 | 0.5209
360 | 6 | feeder2_1258 | 0.035992 | 0.51755 | 0.035935 | 0.51747
360 | 6 | feeder2_1303 | 0.036211 | 0.52097 | 0.036162 | 0.52087
360 | 6 | feeder2_1138 | 0.036381 | 0.52363 | 0.036325 | 0.52354
360 | 6 | feeder2_1304 | 0.036945 | 0.52415 | 0.036895 | 0.52405
360 | 6 | feeder2_1212 | 0.036603 | 0.52878 | 0.036551 | 0.52869
360 | 6 | feeder2_1311 | 0.033624 | 0.53133 | 0.033569 | 0.53124
360 | 6 | feeder2_1290 | 0.037285 | 0.5332 | 0.037234 | 0.5331
360 | 6 | feeder2_1325 | 0.031412 | 0.5086 | 0.031348 | 0.50847
360 | 6 | feeder2_1248 | 0.032007 | 0.50838 | 0.031944 | 0.50826
360 | 6 | feeder2_1249 | 0.0315 | 0.51299 | 0.03144 | 0.51289
360 | 6 | feeder2_1250 | 0.02998 | 0.51433 | 0.029919 | 0.51423
360 | 6 | feeder2_1366 | 0.032548 | 0.50653 | 0.032483 | 0.50641
360 | 6 | feeder2_1266 | 0.035947 | 0.5175 | 0.035887 | 0.51741
360 | 6 | feeder2_1372 | 0.036084 | 0.53415 | 0.036031 | 0.53406
360 | 6 | feeder2_1363 | 0.038261 | 0.53674 | 0.038213 | 0.53665
360 | 6 | feeder2_1446 | 0.031351 | 0.5086 | 0.031285 | 0.50847
360 | 6 | feeder2_1502 | 0.03075 | 0.50885 | 0.030685 | 0.50872
360 | 6 | feeder2_1428 | 0.038771 | 0.53721 | 0.038721 | 0.53712
360 | 6 | feeder2_1380 | 0.039313 | 0.54029 | 0.039259 | 0.54021
360 | 6 | feeder2_1550 | 0.037471 | 0.54187 | 0.037418 | 0.54179
360 | 6 | feeder2_1386 | 0.039973 | 0.5413 | 0.039919 | 0.54122
360 | 6 | feeder2_1551 | 0.040131 | 0.54147 | 0.040081 | 0.54139
360 | 6 | feeder2_1400 | 0.040281 | 0.54175 | 0.040229 | 0.54167
360 | 6 | feeder2_1552 | 0.040491 | 0.54197 | 0.040443 | 0.54189
360 | 6 | feeder2_1408 | 0.040903 | 0.54258 | 0.040847 | 0.54249
360 | 6 | feeder2_1553 | 0.042985 | 0.54326 | 0.042933 | 0.54318
360 | 6 | feeder2_1416 | 0.0411 | 0.5428 | 0.041045 | 0.54272
360 | 6 | feeder2_1530 | 0.041024 | 0.54278 | 0.040973 | 0.5427
360 | 6 | feeder2_1425 | 0.041469 | 0.54327 | 0.041418 | 0.54319
360 | 6 | feeder2_1589 | 0.044389 | 0.54405 | 0.04434 | 0.54397
360 | 6 | feeder2_1435 | 0.041464 | 0.54326 | 0.041411 | 0.54318
360 | 6 | feeder2_1621 | 0.041268 | 0.543 | 0.041218 | 0.54292
360 | 6 | feeder2_1564 | 0.041485 | 0.54339 | 0.041432 | 0.54332
360 | 6 | feeder2_1704 | 0.030932 | 0.50754 | 0.030862 | 0.50741
360 | 6 | feeder2_1525 | 0.030625 | 0.50942 | 0.030557 | 0.50929
360 | 6 | feeder2_1716 | 0.030481 | 0.50923 | 0.030419 | 0.50909
360 | 6 | feeder2_1537 | 0.030494 | 0.51007 | 0.030431 | 0.50994
360 | 6 | feeder2_1645 | 0.031087 | 0.51023 | 0.031019 | 0.5101
360 | 6 | feeder2_1561 | 0.030259 | 0.5107 | 0.030194 | 0.51055
360 | 6 | feeder2_1657 | 0.030213 | 0.51069 | 0.030145 | 0.51056
360 | 6 | feeder2_1570 | 0.030157 | 0.51097 | 0.030086 | 0.51083
360 | 6 | feeder2_1756 | 0.024581 | 0.516 | 0.024515 | 0.51586
360 | 6 | feeder2_1588 | 0.030117 | 0.51092 | 0.030051 | 0.51078
360 | 6 | feeder2_1628 | 0.030055 | 0.51093 | 0.029988 | 0.51079
360 | 6 | feeder2_1598 | 0.030064 | 0.51087 | 0.029999 | 0.51072
360 | 6 | feeder2_1816 | 0.029778 | 0.51055 | 0.029709 | 0.51041
360 | 6 | feeder2_1765 | 0.029726 | 0.5104 | 0.029656 | 0.51026
360 | 6 | feeder2_1641 | 0.02988 | 0.51092 | 0.029814 | 0.51077
360 | 6 | feeder2_1689 | 0.029909 | 0.50993 | 0.02984 | 0.50977
360 | 6 | feeder2_1744 | 0.029078 | 0.51162 | 0.02901 | 0.51147
360 | 6 | feeder2_1817 | 0.030198 | 0.51023 | 0.030131 | 0.51007
360 | 6 | feeder2_1779 | 0.030204 | 0.50878 | 0.030134 | 0.50862
360 | 6 | feeder2_1800 | 0.029965 | 0.50998 | 0.029897 | 0.50982
360 | 6 | feeder2_1818 | 0.027462 | 0.50858 | 0.027374 | 0.50842
360 | 6 | feeder2_1753 | 0.029049 | 0.5116 | 0.028982 | 0.51144
360 | 6 | feeder2_1754 | 0.028532 | 0.51211 | 0.028466 | 0.51196
390 | 6.5 | secondary | 0.025503 | 0.019556 | 0.025489 | 0.019544
390 | 6.5 | feeder2_44 | 0.047488 | 0.10205 | 0.047465 | 0.10199
390 | 6.5 | feeder2_45 | 0.048286 | 0.10502 | 0.048261 | 0.10496
390 | 6.5 | feeder2_46 | 0.047075 | 0.10451 | 0.04705 | 0.10445
390 | 6.5 | feeder2_51 | 0.049675 | 0.11023 | 0.049653 | 0.11016
390 | 6.5 | feeder2_48 | 0.048588 | 0.10456 | 0.048568 | 0.1045
390 | 6.5 | feeder2_52 | 0.04946 | 0.11016 | 0.049432 | 0.11009
390 | 6.5 | feeder2_68 | 0.053616 | 0.12493 | 0.053587 | 0.12486
390 | 6.5 | feeder2_69 | 0.053719 | 0.12512 | 0.053691 | 0.12504
390 | 6.5 | feeder2_71 | 0.054137 | 0.12687 | 0.054111 | 0.12679
390 | 6.5 | feeder2_72 | 0.054235 | 0.12671 | 0.05421 | 0.12663
390 | 6.5 | feeder2_73 | 0.055772 | 0.13295 | 0.055744 | 0.13287
390 | 6.5 | feeder2_74 | 0.05564 | 0.1329 | 0.055611 | 0.13282
390 | 6.5 | feeder2_77 | 0.05718 | 0.13818 | 0.057148 | 0.13809
390 | 6.5 | feeder2_79 | 0.056859 | 0.13911 | 0.056827 | 0.13902
390 | 6.5 | feeder2_81 | 0.059361 | 0.14602 | 0.059334 | 0.14593
390 | 6.5 | feeder2_82 | 0.059626 | 0.14559 | 0.059596 | 0.1455
390 | 6.5 | feeder2_116 | 0.069184 | 0.18158 | 0.069147 | 0.18146
390 | 6.5 | feeder2_119 | 0.067354 | 0.18256 | 0.067322 | 0.18244
390 | 6.5 | feeder2_120 | 0.073112 | 0.19437 | 0.073077 | 0.19424
390 | 6.5 | feeder2_248 | 0.072996 | 0.19432 | 0.072958 | 0.19419
390 | 6.5 | feeder2_124 | 0.075538 | 0.20225 | 0.075494 | 0.20212
390 | 6.5 | feeder2_282 | 0.07559 | 0.20216 | 0.075553 | 0.20202
390 | 6.5 | feeder2_275 | 0.074603 | 0.2029 | 0.074564 | 0.20277
390 | 6.5 | feeder2_151 | 0.079943 | 0.2157 | 0.0799 | 0.21556
390 | 6.5 | feeder2_295 | 0.080008 | 0.2158 | 0.079965 | 0.21566
390 | 6.5 | feeder2_311 | 0.080124 | 0.216 | 0.080084 | 0.21586
390 | 6.5 | feeder2_201 | 0.087181 | 0.23758 | 0.087134 | 0.23742
390 | 6.5 | feeder2_314 | 0.087977 | 0.23669 | 0.087932 | 0.23654
390 | 6.5 | feeder2_342 | 0.097233 | 0.2705 | 0.097185 | 0.27031
390 | 6.5 | feeder2_368 | 0.10006 | 0.28277 | 0.10001 | 0.28259
390 | 6.5 | feeder2_347 | 0.097739 | 0.26382 | 0.097684 | 0.26363
390 | 6.5 | feeder2_353 | 0.098 | 0.26058 | 0.097945 | 0.26038
390 | 6.5 | feeder2_518 | 0.097839 | 0.26364 | 0.097787 | 0.26344
390 | 6.5 | feeder2_365 | 0.098321 | 0.25706 | 0.098264 | 0.25686
390 | 6.5 | feeder2_653 | 0.097679 | 0.26046 | 0.097628 | 0.26026
390 | 6.5 | feeder2_377 | 0.098476 | 0.25493 | 0.098419 | 0.25472
390 | 6.5 | feeder2_622 | 0.097865 | 0.25779 | 0.097814 | 0.25758
390 | 6.5 | feeder2_451 | 0.10009 | 0.28271 | 0.10004 | 0.28253
390 | 6.5 | feeder2_383 | 0.10471 | 0.30267 | 0.10465 | 0.30249
390 | 6.5 | feeder2_385 | 0.098649 | 0.25244 | 0.098592 | 0.25223
390 | 6.5 | feeder2_621 | 0.098546 | 0.25505 | 0.098492 | 0.25484
390 | 6.5 | feeder2_611 | 0.10449 | 0.30259 | 0.10444 | 0.3024
390 | 6.5 | feeder2_405 | 0.105 | 0.30392 | 0.10495 | 0.30375
390 | 6.5 | feeder2_461 | 0.099393 | 0.24241 | 0.099335 | 0.24218
390 | 6.5 | feeder2_594 | 0.098573 | 0.25241 | 0.098516 | 0.2522
390 | 6.5 | feeder2_732 | 0.10252 | 0.30564 | 0.10247 | 0.30546
390 | 6.5 | feeder2_417 | 0.10743 | 0.31303 | 0.10738 | 0.31285
390 | 6.5 | feeder2_663 | 0.10727 | 0.31377 | 0.10721 | 0.3136
390 | 6.5 | feeder2_444 | 0.10926 | 0.3197 | 0.10921 | 0.31952
390 | 6.5 | feeder2_759 | 0.1093 | 0.3196 | 0.10925 | 0.31942
390 | 6.5 | feeder2_842 | 0.13896 | 0.36085 | 0.13891 | 0.36067
390 | 6.5 | feeder2_459 | 0.10932 | 0.3196 | 0.10927 | 0.31942
390 | 6.5 | feeder2_702 | 0.11094 | 0.31782 | 0.11089 | 0.31764
390 | 6.5 | feeder2_493 | 0.1094 | 0.31996 | 0.10934 | 0.31979
390 | 6.5 | feeder2_651 | 0.099514 | 0.24262 | 0.099451 | 0.2424
390 | 6.5 | feeder2_684 | 0.099977 | 0.23402 | 0.099918 | 0.23377
390 | 6.5 | feeder2_674 | 0.10935 | 0.31994 | 0.1093 | 0.31976
390 | 6.5 | feeder2_696 | 0.10968 | 0.32113 | 0.10963 | 0.32095
390 | 6.5 | feeder2_681 | 0.10927 | 0.31989 | 0.10922 | 0.31971
390 | 6.5 | feeder2_682 | 0.10928 | 0.31991 | 0.10923 | 0.31972
390 | 6.5 | feeder2_728 | 0.099936 | 0.23416 | 0.099875 | 0.23392
390 | 6.5 | feeder2_724 | 0.10062 | 0.22515 | 0.10055 | 0.22488
390 | 6.5 | feeder2_703 | 0.11037 | 0.32219 | 0.11032 | 0.32201
390 | 6.5 | feeder2_704 | 0.10978 | 0.32129 | 0.10973 | 0.3211
390 | 6.5 | feeder2_754 | 0.10073 | 0.22496 | 0.10067 | 0.22469
390 | 6.5 | feeder2_747 | 0.10089 | 0.22163 | 0.10082 | 0.22136
390 | 6.5 | feeder2_828 | 0.099884 | 0.23414 | 0.099822 | 0.23389
390 | 6.5 | feeder2_763 | 0.099895 | 0.23441 | 0.099834 | 0.23416
390 | 6.5 | feeder2_836 | 0.10102 | 0.22186 | 0.10095 | 0.22159
390 | 6.5 | feeder2_758 | 0.10111 | 0.21852 | 0.10105 | 0.21824
390 | 6.5 | feeder2_788 | 0.10395 | 0.21547 | 0.10389 | 0.21518
390 | 6.5 | feeder2_812 | 0.10121 | 0.21291 | 0.10114 | 0.21261
390 | 6.5 | feeder2_947 | 0.10014 | 0.234 | 0.10008 | 0.23375
390 | 6.5 | feeder2_868 | 0.099979 | 0.23427 | 0.099915 | 0.23403
390 | 6.5 | feeder2_785 | 0.099865 | 0.23473 | 0.0998 | 0.23448
390 | 6.5 | feeder2_1176 | 0.098865 | 0.23647 | 0.098799 | 0.23623
390 | 6.5 | feeder2_846 | 0.099607 | 0.23463 | 0.099547 | 0.23438
390 | 6.5 | feeder2_911 | 0.099866 | 0.23467 | 0.0998 | 0.23443
390 | 6.5 | feeder2_1107 | 0.10101 | 0.20952 | 0.10094 | 0.20922
390 | 6.5 | feeder2_920 | 0.1013 | 0.2123 | 0.10123 | 0.212
390 | 6.5 | feeder2_926 | 0.10158 | 0.2111 | 0.10151 | 0.21079
390 | 6.5 | feeder2_1239 | 0.10113 | 0.21265 | 0.10106 | 0.21234
390 | 6.5 | feeder2_933 | 0.10161 | 0.21119 | 0.10153 | 0.21087
390 | 6.5 | feeder2_1146 | 0.10205 | 0.20816 | 0.10198 | 0.20785
390 | 6.5 | feeder2_1124 | 0.10164 | 0.21125 | 0.10157 | 0.21093
390 | 6.5 | feeder2_942 | 0.10166 | 0.21137 | 0.10159 | 0.21104
390 | 6.5 | feeder2_952 | 0.10224 | 0.21047 | 0.10216 | 0.21014
390 | 6.5 | feeder2_965 | 0.1016 | 0.21152 | 0.10152 | 0.2112
390 | 6.5 | feeder2_961 | 0.10226 | 0.21064 | 0.10219 | 0.21031
390 | 6.5 | feeder2_963 | 0.10225 | 0.21041 | 0.10218 | 0.21008
390 | 6.5 | feeder2_973 | 0.10239 | 0.21156 | 0.10231 | 0.21122
390 | 6.5 | feeder2_1128 | 0.10225 | 0.21061 | 0.10218 | 0.21028
390 | 6.5 | feeder2_1113 | 0.10343 | 0.20916 | 0.10336 | 0.20884
390 | 6.5 | feeder2_1143 | 0.10224 | 0.21022 | 0.10217 | 0.20989
390 | 6.5 | feeder2_1238 | 0.10167 | 0.21138 | 0.1016 | 0.21106
390 | 6.5 | feeder2_979 | 0.10151 | 0.21173 | 0.10143 | 0.2114
390 | 6.5 | feeder2_1236 | 0.10255 | 0.21282 | 0.10248 | 0.21248
390 | 6.5 | feeder2_989 | 0.10239 | 0.21156 | 0.10231 | 0.21122
390 | 6.5 | feeder2_1196 | 0.10039 | 0.21274 | 0.10032 | 0.21242
390 | 6.5 | feeder2_1158 | 0.10249 | 0.21172 | 0.10242 | 0.21138
390 | 6.5 | feeder2_1122 | 0.10091 | 0.20812 | 0.10084 | 0.20781
390 | 6.5 | feeder2_1258 | 0.10109 | 0.20965 | 0.10102 | 0.20934
390 | 6.5 | feeder2_1303 | 0.10095 | 0.20804 | 0.10088 | 0.20773
390 | 6.5 | feeder2_1138 | 0.10083 | 0.20704 | 0.10076 | 0.20673
390 | 6.5 | feeder2_1304 | 0.099544 | 0.20776 | 0.099473 | 0.20745
390 | 6.5 | feeder2_1212 | 0.10096 | 0.20431 | 0.10089 | 0.204
390 | 6.5 | feeder2_1311 | 0.10102 | 0.2042 | 0.10095 | 0.20389
390 | 6.5 | feeder2_1290 | 0.10112 | 0.20102 | 0.10106 | 0.20071
390 | 6.5 | feeder2_1325 | 0.10272 | 0.21429 | 0.10264 | 0.21394
390 | 6.5 | feeder2_1248 | 0.10255 | 0.21282 | 0.10248 | 0.21248
390 | 6.5 | feeder2_1249 | 0.10169 | 0.21135 | 0.10162 | 0.21103
390 | 6.5 | feeder2_1250 | 0.1017 | 0.21134 | 0.10162 | 0.21101
390 | 6.5 | feeder2_1366 | 0.10267 | 0.21301 | 0.10259 | 0.21266
390 | 6.5 | feeder2_1266 | 0.10113 | 0.20972 | 0.10106 | 0.20941
390 | 6.5 | feeder2_1372 | 0.10126 | 0.2008 | 0.10119 | 0.2005
390 | 6.5 | feeder2_1363 | 0.1013 | 0.1978 | 0.10123 | 0.19749
390 | 6.5 | feeder2_1446 | 0.1042 | 0.21271 | 0.10413 | 0.21235
390 | 6.5 | feeder2_1502 | 0.1026 | 0.21806 | 0.10251 | 0.2177
390 | 6.5 | feeder2_1428 | 0.10079 | 0.19769 | 0.10073 | 0.19738
390 | 6.5 | feeder2_1380 | 0.10167 | 0.19419 | 0.10161 | 0.19387
390 | 6.5 | feeder2_1550 | 0.1017 | 0.19414 | 0.10164 | 0.19382
390 | 6.5 | feeder2_1386 | 0.10185 | 0.19245 | 0.10179 | 0.19214
390 | 6.5 | feeder2_1551 | 0.10107 | 0.19317 | 0.101 | 0.19285
390 | 6.5 | feeder2_1400 | 0.102 | 0.19149 | 0.10193 | 0.19117
390 | 6.5 | feeder2_1552 | 0.10178 | 0.1914 | 0.10172 | 0.19109
390 | 6.5 | feeder2_1408 | 0.10231 | 0.18954 | 0.10224 | 0.18922
390 | 6.5 | feeder2_1553 | 0.10218 | 0.1895 | 0.10211 | 0.18919
390 | 6.5 | feeder2_1416 | 0.10248 | 0.18854 | 0.10241 | 0.18822
390 | 6.5 | feeder2_1530 | 0.10608 | 0.1848 | 0.10601 | 0.18449
390 | 6.5 | feeder2_1425 | 0.10247 | 0.18862 | 0.10241 | 0.18831
390 | 6.5 | feeder2_1589 | 0.10223 | 0.18857 | 0.10216 | 0.18826
390 | 6.5 | feeder2_1435 | 0.10248 | 0.18865 | 0.10241 | 0.18833
390 | 6.5 | feeder2_1621 | 0.10264 | 0.18894 | 0.10257 | 0.18863
390 | 6.5 | feeder2_1564 | 0.10246 | 0.1886 | 0.10239 | 0.18828
390 | 6.5 | feeder2_1704 | 0.10196 | 0.21931 | 0.10187 | 0.21894
390 | 6.5 | feeder2_1525 | 0.10252 | 0.21852 | 0.10244 | 0.21814
390 | 6.5 | feeder2_1716 | 0.10099 | 0.22077 | 0.1009 | 0.22041
390 | 6.5 | feeder2_1537 | 0.1024 | 0.21862 | 0.10231 | 0.21825
390 | 6.5 | feeder2_1645 | 0.10128 | 0.21961 | 0.1012 | 0.21923
390 | 6.5 | feeder2_1561 | 0.10247 | 0.21827 | 0.10239 | 0.21789
390 | 6.5 | feeder2_1657 | 0.10253 | 0.21818 | 0.10245 | 0.2178
390 | 6.5 | feeder2_1570 | 0.1025 | 0.21814 | 0.10241 | 0.21776
390 | 6.5 | feeder2_1756 | 0.1026 | 0.21797 | 0.10251 | 0.21759
390 | 6.5 | feeder2_1588 | 0.10253 | 0.21803 | 0.10244 | 0.21764
390 | 6.5 | feeder2_1628 | 0.10335 | 0.21713 | 0.10327 | 0.21674
390 | 6.5 | feeder2_1598 | 0.10253 | 0.21815 | 0.10244 | 0.21776
390 | 6.5 | feeder2_1816 | 0.10278 | 0.21854 | 0.10269 | 0.21815
390 | 6.5 | feeder2_1765 | 0.10282 | 0.21867 | 0.10273 | 0.21828
390 | 6.5 | feeder2_1641 | 0.10245 | 0.21836 | 0.10236 | 0.21796
390 | 6.5 | feeder2_1689 | 0.1024 | 0.21863 | 0.1023 | 0.21822
390 | 6.5 | feeder2_1744 | 0.10249 | 0.2183 | 0.1024 | 0.2179
390 | 6.5 | feeder2_1817 | 0.10238 | 0.21858 | 0.10229 | 0.21817
390 | 6.5 | feeder2_1779 | 0.10242 | 0.21867 | 0.10233 | 0.21826
390 | 6.5 | feeder2_1800 | 0.10234 | 0.2186 | 0.10225 | 0.21819
390 | 6.5 | feeder2_1818 | 0.10173 | 0.21831 | 0.10163 | 0.21787
390 | 6.5 | feeder2_1753 | 0.10254 | 0.2182 | 0.10245 | 0.2178
390 | 6.5 | feeder2_1754 | 0.1025 | 0.21828 | 0.10241 | 0.21788
420 | 7 | secondary | 0.028694 | 0.018419 | 0.028682 | 0.018413
420 | 7 | feeder2_44 | 0.053395 | 0.096061 | 0.053375 | 0.096033
420 | 7 | feeder2_45 | 0.054282 | 0.098609 | 0.05426 | 0.098581
420 | 7 | feeder2_46 | 0.053004 | 0.10148 | 0.052982 | 0.10145
420 | 7 | feeder2_51 | 0.055824 | 0.10304 | 0.055805 | 0.10301
420 | 7 | feeder2_48 | 0.054653 | 0.098515 | 0.054634 | 0.098485
420 | 7 | feeder2_52 | 0.05561 | 0.10285 | 0.055586 | 0.10282
420 | 7 | feeder2_68 | 0.060194 | 0.11561 | 0.060174 | 0.11558
420 | 7 | feeder2_69 | 0.060275 | 0.11578 | 0.060251 | 0.11575
420 | 7 | feeder2_71 | 0.060772 | 0.11727 | 0.06075 | 0.11723
420 | 7 | feeder2_72 | 0.060898 | 0.11725 | 0.060878 | 0.11722
420 | 7 | feeder2_73 | 0.062584 | 0.12246 | 0.062559 | 0.12242
420 | 7 | feeder2_74 | 0.062452 | 0.12234 | 0.062425 | 0.12231
420 | 7 | feeder2_77 | 0.064143 | 0.12693 | 0.064123 | 0.12689
420 | 7 | feeder2_79 | 0.064304 | 0.12731 | 0.064282 | 0.12727
420 | 7 | feeder2_81 | 0.066586 | 0.13387 | 0.066558 | 0.13383
420 | 7 | feeder2_82 | 0.066917 | 0.13379 | 0.066895 | 0.13375
420 | 7 | feeder2_116 | 0.077577 | 0.16502 | 0.077547 | 0.16497
420 | 7 | feeder2_119 | 0.076758 | 0.16429 | 0.076726 | 0.16424
420 | 7 | feeder2_120 | 0.081752 | 0.177 | 0.08172 | 0.17695
420 | 7 | feeder2_248 | 0.081635 | 0.17689 | 0.081599 | 0.17684
420 | 7 | feeder2_124 | 0.084332 | 0.18442 | 0.084303 | 0.18436
420 | 7 | feeder2_282 | 0.084531 | 0.18449 | 0.084499 | 0.18443
420 | 7 | feeder2_275 | 0.08352 | 0.18421 | 0.083487 | 0.18416
420 | 7 | feeder2_151 | 0.089008 | 0.19748 | 0.08897 | 0.19742
420 | 7 | feeder2_295 | 0.089241 | 0.19779 | 0.089206 | 0.19772
420 | 7 | feeder2_311 | 0.08907 | 0.19758 | 0.089035 | 0.19753
420 | 7 | feeder2_201 | 0.096666 | 0.21872 | 0.096624 | 0.21866
420 | 7 | feeder2_314 | 0.09749 | 0.21805 | 0.097451 | 0.21798
420 | 7 | feeder2_342 | 0.10728 | 0.25018 | 0.10724 | 0.25011
420 | 7 | feeder2_368 | 0.10739 | 0.25024 | 0.10735 | 0.25017
420 | 7 | feeder2_347 | 0.11233 | 0.26552 | 0.11229 | 0.26545
420 | 7 | feeder2_353 | 0.11474 | 0.27367 | 0.11469 | 0.27359
420 | 7 | feeder2_518 | 0.11367 | 0.26447 | 0.11363 | 0.26439
420 | 7 | feeder2_365 | 0.11744 | 0.28286 | 0.11739 | 0.28278
420 | 7 | feeder2_653 | 0.11441 | 0.27338 | 0.11437 | 0.27329
420 | 7 | feeder2_377 | 0.11891 | 0.28785 | 0.11886 | 0.28777
420 | 7 | feeder2_622 | 0.11746 | 0.28289 | 0.11741 | 0.28281
420 | 7 | feeder2_451 | 0.10743 | 0.25024 | 0.10739 | 0.25017
420 | 7 | feeder2_383 | 0.10757 | 0.25032 | 0.10753 | 0.25024
420 | 7 | feeder2_385 | 0.12057 | 0.29349 | 0.12052 | 0.2934
420 | 7 | feeder2_621 | 0.11917 | 0.28816 | 0.11912 | 0.28807
420 | 7 | feeder2_611 | 0.10735 | 0.25012 | 0.10731 | 0.25005
420 | 7 | feeder2_405 | 0.10758 | 0.25033 | 0.10755 | 0.25026
420 | 7 | feeder2_461 | 0.12734 | 0.31653 | 0.12729 | 0.31643
420 | 7 | feeder2_594 | 0.12049 | 0.29342 | 0.12045 | 0.29333
420 | 7 | feeder2_732 | 0.10596 | 0.25007 | 0.10592 | 0.24999
420 | 7 | feeder2_417 | 0.10783 | 0.25057 | 0.10779 | 0.25049
420 | 7 | feeder2_663 | 0.10794 | 0.25069 | 0.10789 | 0.25062
420 | 7 | feeder2_444 | 0.108 | 0.25071 | 0.10796 | 0.25064
420 | 7 | feeder2_759 | 0.10807 | 0.25072 | 0.10803 | 0.25064
420 | 7 | feeder2_842 | 0.10805 | 0.25079 | 0.10801 | 0.25072
420 | 7 | feeder2_459 | 0.10806 | 0.25075 | 0.10802 | 0.25068
420 | 7 | feeder2_702 | 0.10997 | 0.24928 | 0.10993 | 0.2492
420 | 7 | feeder2_493 | 0.10811 | 0.25145 | 0.10807 | 0.25138
420 | 7 | feeder2_651 | 0.12746 | 0.31671 | 0.12741 | 0.31662
420 | 7 | feeder2_684 | 0.13282 | 0.33507 | 0.13276 | 0.33497
420 | 7 | feeder2_674 | 0.10794 | 0.2513 | 0.1079 | 0.25123
420 | 7 | feeder2_696 | 0.10843 | 0.25419 | 0.1084 | 0.25411
420 | 7 | feeder2_681 | 0.10753 | 0.25093 | 0.10749 | 0.25086
420 | 7 | feeder2_682 | 0.10786 | 0.25123 | 0.10782 | 0.25116
420 | 7 | feeder2_728 | 0.13296 | 0.33443 | 0.1329 | 0.33434
420 | 7 | feeder2_724 | 0.13822 | 0.35551 | 0.13816 | 0.3554
420 | 7 | feeder2_703 | 0.10936 | 0.2558 | 0.10932 | 0.25572
420 | 7 | feeder2_704 | 0.10831 | 0.25479 | 0.10827 | 0.25472
420 | 7 | feeder2_754 | 0.13834 | 0.35551 | 0.13828 | 0.35541
420 | 7 | feeder2_747 | 0.14043 | 0.36383 | 0.14037 | 0.36373
420 | 7 | feeder2_828 | 0.13277 | 0.33424 | 0.13272 | 0.33415
420 | 7 | feeder2_763 | 0.13323 | 0.33378 | 0.13318 | 0.33368
420 | 7 | feeder2_836 | 0.13957 | 0.36669 | 0.13951 | 0.36659
420 | 7 | feeder2_758 | 0.14227 | 0.36968 | 0.14221 | 0.36958
420 | 7 | feeder2_788 | 0.14229 | 0.36969 | 0.14223 | 0.36958
420 | 7 | feeder2_812 | 0.14793 | 0.38768 | 0.14787 | 0.38756
420 | 7 | feeder2_947 | 0.13619 | 0.33147 | 0.13614 | 0.33137
420 | 7 | feeder2_868 | 0.13326 | 0.33379 | 0.13321 | 0.33369
420 | 7 | feeder2_785 | 0.13325 | 0.33383 | 0.13319 | 0.33374
420 | 7 | feeder2_1176 | 0.13356 | 0.33432 | 0.13351 | 0.33422
420 | 7 | feeder2_846 | 0.13316 | 0.33375 | 0.13311 | 0.33365
420 | 7 | feeder2_911 | 0.13325 | 0.33385 | 0.13319 | 0.33375
420 | 7 | feeder2_1107 | 0.14692 | 0.38765 | 0.14686 | 0.38754
420 | 7 | feeder2_920 | 0.1498 | 0.39275 | 0.14974 | 0.39263
420 | 7 | feeder2_926 | 0.15259 | 0.40038 | 0.15253 | 0.40025
420 | 7 | feeder2_1239 | 0.14979 | 0.39271 | 0.14973 | 0.39259
420 | 7 | feeder2_933 | 0.15378 | 0.40404 | 0.15371 | 0.40391
420 | 7 | feeder2_1146 | 0.15285 | 0.3991 | 0.15279 | 0.39897
420 | 7 | feeder2_1124 | 0.15381 | 0.40409 | 0.15375 | 0.40396
420 | 7 | feeder2_942 | 0.15677 | 0.41329 | 0.15671 | 0.41315
420 | 7 | feeder2_952 | 0.16109 | 0.43054 | 0.16103 | 0.43039
420 | 7 | feeder2_965 | 0.15678 | 0.41283 | 0.15672 | 0.4127
420 | 7 | feeder2_961 | 0.16154 | 0.43252 | 0.16147 | 0.43237
420 | 7 | feeder2_963 | 0.1611 | 0.43052 | 0.16103 | 0.43036
420 | 7 | feeder2_973 | 0.16393 | 0.44312 | 0.16386 | 0.44296
420 | 7 | feeder2_1128 | 0.16153 | 0.43246 | 0.16147 | 0.43231
420 | 7 | feeder2_1113 | 0.16178 | 0.42991 | 0.16171 | 0.42977
420 | 7 | feeder2_1143 | 0.16109 | 0.43054 | 0.16102 | 0.43039
420 | 7 | feeder2_1238 | 0.16171 | 0.40853 | 0.16164 | 0.40839
420 | 7 | feeder2_979 | 0.15674 | 0.41257 | 0.15667 | 0.41243
420 | 7 | feeder2_1236 | 0.16743 | 0.45789 | 0.16736 | 0.45773
420 | 7 | feeder2_989 | 0.16393 | 0.44313 | 0.16386 | 0.44297
420 | 7 | feeder2_1196 | 0.15559 | 0.41153 | 0.15552 | 0.41139
420 | 7 | feeder2_1158 | 0.16366 | 0.44437 | 0.16359 | 0.44421
420 | 7 | feeder2_1122 | 0.14644 | 0.38632 | 0.14639 | 0.38621
420 | 7 | feeder2_1258 | 0.14664 | 0.38926 | 0.14658 | 0.38914
420 | 7 | feeder2_1303 | 0.14817 | 0.38507 | 0.14811 | 0.38496
420 | 7 | feeder2_1138 | 0.14598 | 0.38568 | 0.14592 | 0.38557
420 | 7 | feeder2_1304 | 0.14539 | 0.38514 | 0.14533 | 0.38503
420 | 7 | feeder2_1212 | 0.1451 | 0.38482 | 0.14504 | 0.38471
420 | 7 | feeder2_1311 | 0.14516 | 0.38485 | 0.1451 | 0.38474
420 | 7 | feeder2_1290 | 0.14404 | 0.38375 | 0.14398 | 0.38364
420 | 7 | feeder2_1325 | 0.1722 | 0.47811 | 0.17213 | 0.47793
420 | 7 | feeder2_1248 | 0.16743 | 0.4579 | 0.16736 | 0.45773
420 | 7 | feeder2_1249 | 0.16313 | 0.40727 | 0.16307 | 0.40714
420 | 7 | feeder2_1250 | 0.16173 | 0.40853 | 0.16167 | 0.40839
420 | 7 | feeder2_1366 | 0.16751 | 0.45802 | 0.16745 | 0.45786
420 | 7 | feeder2_1266 | 0.14652 | 0.3903 | 0.14646 | 0.39018
420 | 7 | feeder2_1372 | 0.14418 | 0.38376 | 0.14412 | 0.38365
420 | 7 | feeder2_1363 | 0.14294 | 0.38257 | 0.14288 | 0.38247
420 | 7 | feeder2_1446 | 0.1734 | 0.47701 | 0.17332 | 0.47683
420 | 7 | feeder2_1502 | 0.17734 | 0.5024 | 0.17727 | 0.50221
420 | 7 | feeder2_1428 | 0.14212 | 0.38233 | 0.14206 | 0.38223
420 | 7 | feeder2_1380 | 0.14206 | 0.38181 | 0.142 | 0.38171
420 | 7 | feeder2_1550 | 0.14209 | 0.38182 | 0.14204 | 0.38172
420 | 7 | feeder2_1386 | 0.14164 | 0.38148 | 0.14158 | 0.38138
420 | 7 | feeder2_1551 | 0.14089 | 0.38115 | 0.14083 | 0.38105
420 | 7 | feeder2_1400 | 0.1415 | 0.38143 | 0.14145 | 0.38133
420 | 7 | feeder2_1552 | 0.1403 | 0.38092 | 0.14025 | 0.38083
420 | 7 | feeder2_1408 | 0.14142 | 0.38171 | 0.14136 | 0.38163
420 | 7 | feeder2_1553 | 0.14129 | 0.38159 | 0.14124 | 0.38149
420 | 7 | feeder2_1416 | 0.14138 | 0.38191 | 0.14132 | 0.38182
420 | 7 | feeder2_1530 | 0.14621 | 0.38289 | 0.14616 | 0.38281
420 | 7 | feeder2_1425 | 0.14129 | 0.38142 | 0.14124 | 0.38133
420 | 7 | feeder2_1589 | 0.14014 | 0.38033 | 0.14009 | 0.38024
420 | 7 | feeder2_1435 | 0.1413 | 0.38143 | 0.14124 | 0.38134
420 | 7 | feeder2_1621 | 0.14145 | 0.38168 | 0.14139 | 0.38159
420 | 7 | feeder2_1564 | 0.14127 | 0.3813 | 0.14122 | 0.38121
420 | 7 | feeder2_1704 | 0.17737 | 0.50245 | 0.1773 | 0.50225
420 | 7 | feeder2_1525 | 0.17866 | 0.50867 | 0.17858 | 0.50848
420 | 7 | feeder2_1716 | 0.17828 | 0.51056 | 0.17821 | 0.51036
420 | 7 | feeder2_1537 | 0.18012 | 0.5154 | 0.18004 | 0.5152
420 | 7 | feeder2_1645 | 0.18003 | 0.5153 | 0.17995 | 0.5151
420 | 7 | feeder2_1561 | 0.18178 | 0.5231 | 0.18171 | 0.52289
420 | 7 | feeder2_1657 | 0.18183 | 0.52308 | 0.18175 | 0.52287
420 | 7 | feeder2_1570 | 0.1825 | 0.52643 | 0.18243 | 0.52621
420 | 7 | feeder2_1756 | 0.18257 | 0.52643 | 0.1825 | 0.52621
420 | 7 | feeder2_1588 | 0.18318 | 0.52954 | 0.1831 | 0.52932
420 | 7 | feeder2_1628 | 0.18319 | 0.52953 | 0.18311 | 0.52932
420 | 7 | feeder2_1598 | 0.18403 | 0.53347 | 0.18395 | 0.53326
420 | 7 | feeder2_1816 | 0.18422 | 0.53374 | 0.18414 | 0.53353
420 | 7 | feeder2_1765 | 0.18416 | 0.53366 | 0.18408 | 0.53345
420 | 7 | feeder2_1641 | 0.18818 | 0.5527 | 0.18811 | 0.55247
420 | 7 | feeder2_1689 | 0.19158 | 0.57015 | 0.1915 | 0.56991
420 | 7 | feeder2_1744 | 0.18894 | 0.55202 | 0.18886 | 0.5518
420 | 7 | feeder2_1817 | 0.19157 | 0.57007 | 0.19149 | 0.56983
420 | 7 | feeder2_1779 | 0.19161 | 0.57019 | 0.19152 | 0.56995
420 | 7 | feeder2_1800 | 0.19153 | 0.5701 | 0.19144 | 0.56987
420 | 7 | feeder2_1818 | 0.21407 | 0.60633 | 0.21397 | 0.60606
420 | 7 | feeder2_1753 | 0.1913 | 0.54988 | 0.19121 | 0.54965
420 | 7 | feeder2_1754 | 0.18895 | 0.55202 | 0.18887 | 0.55179
450 | 7.5 | secondary | 0.028355 | 0.041702 | 0.028338 | 0.041694
450 | 7.5 | feeder2_44 | 0.052771 | 0.21751 | 0.052738 | 0.21749
450 | 7.5 | feeder2_45 | 0.053704 | 0.22449 | 0.053675 | 0.22446
450 | 7.5 | feeder2_46 | 0.053678 | 0.21524 | 0.05365 | 0.21522
450 | 7.5 | feeder2_51 | 0.055444 | 0.23638 | 0.055413 | 0.23635
450 | 7.5 | feeder2_48 | 0.051016 | 0.22648 | 0.050989 | 0.22645
450 | 7.5 | feeder2_52 | 0.055054 | 0.23767 | 0.055021 | 0.23764
450 | 7.5 | feeder2_68 | 0.060267 | 0.26927 | 0.060233 | 0.26923
450 | 7.5 | feeder2_69 | 0.0603 | 0.26914 | 0.060266 | 0.26911
450 | 7.5 | feeder2_71 | 0.060909 | 0.27363 | 0.060874 | 0.27359
450 | 7.5 | feeder2_72 | 0.060689 | 0.27355 | 0.060654 | 0.27351
450 | 7.5 | feeder2_73 | 0.062924 | 0.2873 | 0.06289 | 0.28726
450 | 7.5 | feeder2_74 | 0.06326 | 0.28771 | 0.063221 | 0.28768
450 | 7.5 | feeder2_77 | 0.064644 | 0.29897 | 0.064608 | 0.29893
450 | 7.5 | feeder2_79 | 0.067059 | 0.2952 | 0.067024 | 0.29516
450 | 7.5 | feeder2_81 | 0.067332 | 0.31877 | 0.067295 | 0.31873
450 | 7.5 | feeder2_82 | 0.066793 | 0.31861 | 0.066755 | 0.31857
450 | 7.5 | feeder2_116 | 0.079633 | 0.40782 | 0.079588 | 0.40776
450 | 7.5 | feeder2_119 | 0.080232 | 0.40863 | 0.080184 | 0.40857
450 | 7.5 | feeder2_120 | 0.084146 | 0.44036 | 0.084099 | 0.4403
450 | 7.5 | feeder2_248 | 0.084179 | 0.44125 | 0.084127 | 0.44119
450 | 7.5 | feeder2_124 | 0.086845 | 0.45995 | 0.086795 | 0.45988
450 | 7.5 | feeder2_282 | 0.084111 | 0.45918 | 0.084058 | 0.45911
450 | 7.5 | feeder2_275 | 0.11036 | 0.48877 | 0.1103 | 0.48871
450 | 7.5 | feeder2_151 | 0.087833 | 0.47564 | 0.087779 | 0.47557
450 | 7.5 | feeder2_295 | 0.088211 | 0.47418 | 0.088157 | 0.4741
450 | 7.5 | feeder2_311 | 0.087839 | 0.47557 | 0.087784 | 0.47549
450 | 7.5 | feeder2_201 | 0.089723 | 0.50384 | 0.089664 | 0.50375
450 | 7.5 | feeder2_314 | 0.088481 | 0.50464 | 0.088424 | 0.50455
450 | 7.5 | feeder2_342 | 0.093057 | 0.54245 | 0.092994 | 0.54234
450 | 7.5 | feeder2_368 | 0.093046 | 0.54365 | 0.092984 | 0.54355
450 | 7.5 | feeder2_347 | 0.094627 | 0.55915 | 0.094562 | 0.55903
450 | 7.5 | feeder2_353 | 0.095426 | 0.56752 | 0.095361 | 0.5674
450 | 7.5 | feeder2_518 | 0.094382 | 0.55906 | 0.094316 | 0.55894
450 | 7.5 | feeder2_365 | 0.0963 | 0.57676 | 0.09623 | 0.57663
450 | 7.5 | feeder2_653 | 0.095511 | 0.56763 | 0.095446 | 0.5675
450 | 7.5 | feeder2_377 | 0.096776 | 0.58179 | 0.096706 | 0.58166
450 | 7.5 | feeder2_622 | 0.096301 | 0.57674 | 0.096231 | 0.57661
450 | 7.5 | feeder2_451 | 0.092966 | 0.54361 | 0.092902 | 0.54351
450 | 7.5 | feeder2_383 | 0.093043 | 0.54564 | 0.092979 | 0.54554
450 | 7.5 | feeder2_385 | 0.097384 | 0.58807 | 0.097313 | 0.58793
450 | 7.5 | feeder2_621 | 0.097091 | 0.58021 | 0.097023 | 0.58008
450 | 7.5 | feeder2_611 | 0.093246 | 0.54642 | 0.093178 | 0.54632
450 | 7.5 | feeder2_405 | 0.093034 | 0.54572 | 0.09297 | 0.54561
450 | 7.5 | feeder2_461 | 0.099586 | 0.61246 | 0.099509 | 0.6123
450 | 7.5 | feeder2_594 | 0.097468 | 0.58862 | 0.097396 | 0.58849
450 | 7.5 | feeder2_732 | 0.093212 | 0.54694 | 0.093145 | 0.54684
450 | 7.5 | feeder2_417 | 0.092898 | 0.546 | 0.092832 | 0.5459
450 | 7.5 | feeder2_663 | 0.09288 | 0.54592 | 0.092818 | 0.54582
450 | 7.5 | feeder2_444 | 0.092802 | 0.54624 | 0.092737 | 0.54613
450 | 7.5 | feeder2_759 | 0.090647 | 0.54765 | 0.090584 | 0.54755
450 | 7.5 | feeder2_842 | 0.092807 | 0.54618 | 0.092743 | 0.54607
450 | 7.5 | feeder2_459 | 0.092812 | 0.54625 | 0.092748 | 0.54614
450 | 7.5 | feeder2_702 | 0.092313 | 0.54607 | 0.09225 | 0.54596
450 | 7.5 | feeder2_493 | 0.092894 | 0.54637 | 0.092828 | 0.54627
450 | 7.5 | feeder2_651 | 0.099587 | 0.61242 | 0.09951 | 0.61226
450 | 7.5 | feeder2_684 | 0.10138 | 0.6324 | 0.1013 | 0.63222
450 | 7.5 | feeder2_674 | 0.093095 | 0.5467 | 0.093034 | 0.5466
450 | 7.5 | feeder2_696 | 0.092763 | 0.54522 | 0.092697 | 0.54512
450 | 7.5 | feeder2_681 | 0.09351 | 0.54745 | 0.093446 | 0.54734
450 | 7.5 | feeder2_682 | 0.093308 | 0.54694 | 0.093243 | 0.54684
450 | 7.5 | feeder2_728 | 0.10155 | 0.63386 | 0.10147 | 0.63369
450 | 7.5 | feeder2_724 | 0.10286 | 0.64948 | 0.10277 | 0.64929
450 | 7.5 | feeder2_703 | 0.092952 | 0.54381 | 0.09289 | 0.54372
450 | 7.5 | feeder2_704 | 0.092777 | 0.54512 | 0.092712 | 0.54502
450 | 7.5 | feeder2_754 | 0.10143 | 0.65032 | 0.10135 | 0.65013
450 | 7.5 | feeder2_747 | 0.10363 | 0.6561 | 0.10355 | 0.6559
450 | 7.5 | feeder2_828 | 0.10238 | 0.6349 | 0.1023 | 0.63473
450 | 7.5 | feeder2_763 | 0.10138 | 0.63444 | 0.1013 | 0.63426
450 | 7.5 | feeder2_836 | 0.10492 | 0.65443 | 0.10483 | 0.65423
450 | 7.5 | feeder2_758 | 0.10424 | 0.66254 | 0.10415 | 0.66234
450 | 7.5 | feeder2_788 | 0.10419 | 0.66252 | 0.1041 | 0.66233
450 | 7.5 | feeder2_812 | 0.10612 | 0.68242 | 0.10603 | 0.6822
450 | 7.5 | feeder2_947 | 0.10084 | 0.63425 | 0.10076 | 0.63408
450 | 7.5 | feeder2_868 | 0.10083 | 0.63478 | 0.10075 | 0.6346
450 | 7.5 | feeder2_785 | 0.10142 | 0.63462 | 0.10134 | 0.63444
450 | 7.5 | feeder2_1176 | 0.10142 | 0.63448 | 0.10134 | 0.63431
450 | 7.5 | feeder2_846 | 0.10152 | 0.63497 | 0.10144 | 0.63481
450 | 7.5 | feeder2_911 | 0.1014 | 0.63458 | 0.10132 | 0.6344
450 | 7.5 | feeder2_1107 | 0.10982 | 0.69993 | 0.10973 | 0.69971
450 | 7.5 | feeder2_920 | 0.10563 | 0.68317 | 0.10554 | 0.68294
450 | 7.5 | feeder2_926 | 0.10488 | 0.68425 | 0.10479 | 0.68402
450 | 7.5 | feeder2_1239 | 0.10564 | 0.68322 | 0.10555 | 0.683
450 | 7.5 | feeder2_933 | 0.10455 | 0.68475 | 0.10446 | 0.68451
450 | 7.5 | feeder2_1146 | 0.10487 | 0.68421 | 0.10478 | 0.68397
450 | 7.5 | feeder2_1124 | 0.10455 | 0.68471 | 0.10446 | 0.68447
450 | 7.5 | feeder2_942 | 0.10373 | 0.68605 | 0.10364 | 0.6858
450 | 7.5 | feeder2_952 | 0.10285 | 0.68587 | 0.10275 | 0.68561
450 | 7.5 | feeder2_965 | 0.10369 | 0.68632 | 0.10359 | 0.68607
450 | 7.5 | feeder2_961 | 0.10277 | 0.68588 | 0.10267 | 0.68561
450 | 7.5 | feeder2_963 | 0.10285 | 0.68586 | 0.10275 | 0.68559
450 | 7.5 | feeder2_973 | 0.10229 | 0.68582 | 0.10219 | 0.68555
450 | 7.5 | feeder2_1128 | 0.1028 | 0.68606 | 0.1027 | 0.68579
450 | 7.5 | feeder2_1113 | 0.10281 | 0.68585 | 0.10272 | 0.68558
450 | 7.5 | feeder2_1143 | 0.10273 | 0.68551 | 0.10263 | 0.68524
450 | 7.5 | feeder2_1238 | 0.099451 | 0.68948 | 0.099358 | 0.68923
450 | 7.5 | feeder2_979 | 0.10371 | 0.68645 | 0.10362 | 0.68621
450 | 7.5 | feeder2_1236 | 0.10158 | 0.6858 | 0.10148 | 0.68552
450 | 7.5 | feeder2_989 | 0.10229 | 0.68582 | 0.10219 | 0.68555
450 | 7.5 | feeder2_1196 | 0.10418 | 0.687 | 0.10408 | 0.68675
450 | 7.5 | feeder2_1158 | 0.10229 | 0.68575 | 0.10219 | 0.68548
450 | 7.5 | feeder2_1122 | 0.1112 | 0.70841 | 0.11111 | 0.70819
450 | 7.5 | feeder2_1258 | 0.11111 | 0.69787 | 0.11103 | 0.69765
450 | 7.5 | feeder2_1303 | 0.11006 | 0.70804 | 0.10997 | 0.70782
450 | 7.5 | feeder2_1138 | 0.11234 | 0.71527 | 0.11225 | 0.71506
450 | 7.5 | feeder2_1304 | 0.11281 | 0.71583 | 0.11272 | 0.71561
450 | 7.5 | feeder2_1212 | 0.11466 | 0.72934 | 0.11457 | 0.72913
450 | 7.5 | feeder2_1311 | 0.11342 | 0.73018 | 0.11332 | 0.72997
450 | 7.5 | feeder2_1290 | 0.11777 | 0.74613 | 0.11768 | 0.74592
450 | 7.5 | feeder2_1325 | 0.10064 | 0.68593 | 0.10053 | 0.68563
450 | 7.5 | feeder2_1248 | 0.10158 | 0.6858 | 0.10148 | 0.68552
450 | 7.5 | feeder2_1249 | 0.098905 | 0.68988 | 0.098814 | 0.68963
450 | 7.5 | feeder2_1250 | 0.097817 | 0.69076 | 0.097726 | 0.6905
450 | 7.5 | feeder2_1366 | 0.10158 | 0.6857 | 0.10148 | 0.68542
450 | 7.5 | feeder2_1266 | 0.11115 | 0.69736 | 0.11107 | 0.69714
450 | 7.5 | feeder2_1372 | 0.11752 | 0.74605 | 0.11743 | 0.74584
450 | 7.5 | feeder2_1363 | 0.12116 | 0.76433 | 0.12107 | 0.76412
450 | 7.5 | feeder2_1446 | 0.099517 | 0.68677 | 0.099416 | 0.68646
450 | 7.5 | feeder2_1502 | 0.099926 | 0.68512 | 0.099819 | 0.6848
450 | 7.5 | feeder2_1428 | 0.1216 | 0.76485 | 0.1215 | 0.76464
450 | 7.5 | feeder2_1380 | 0.1251 | 0.7856 | 0.12501 | 0.78539
450 | 7.5 | feeder2_1550 | 0.12338 | 0.78682 | 0.12329 | 0.78662
450 | 7.5 | feeder2_1386 | 0.12724 | 0.79545 | 0.12714 | 0.79526
450 | 7.5 | feeder2_1551 | 0.12752 | 0.79633 | 0.12743 | 0.79613
450 | 7.5 | feeder2_1400 | 0.12819 | 0.7999 | 0.1281 | 0.7997
450 | 7.5 | feeder2_1552 | 0.12832 | 0.80005 | 0.12822 | 0.79986
450 | 7.5 | feeder2_1408 | 0.13015 | 0.80905 | 0.13006 | 0.80885
450 | 7.5 | feeder2_1553 | 0.13045 | 0.81011 | 0.13035 | 0.80992
450 | 7.5 | feeder2_1416 | 0.1311 | 0.81353 | 0.131 | 0.81333
450 | 7.5 | feeder2_1530 | 0.1306 | 0.81331 | 0.1305 | 0.81312
450 | 7.5 | feeder2_1425 | 0.13294 | 0.82221 | 0.13284 | 0.82202
450 | 7.5 | feeder2_1589 | 0.14868 | 0.84079 | 0.14857 | 0.8406
450 | 7.5 | feeder2_1435 | 0.13293 | 0.82216 | 0.13283 | 0.82197
450 | 7.5 | feeder2_1621 | 0.13295 | 0.82147 | 0.13286 | 0.82128
450 | 7.5 | feeder2_1564 | 0.13296 | 0.8223 | 0.13286 | 0.82211
450 | 7.5 | feeder2_1704 | 0.099927 | 0.68508 | 0.099819 | 0.68477
450 | 7.5 | feeder2_1525 | 0.099746 | 0.68492 | 0.09964 | 0.6846
450 | 7.5 | feeder2_1716 | 0.10139 | 0.68284 | 0.10128 | 0.68252
450 | 7.5 | feeder2_1537 | 0.099517 | 0.68503 | 0.099407 | 0.68471
450 | 7.5 | feeder2_1645 | 0.10011 | 0.68572 | 0.1 | 0.6854
450 | 7.5 | feeder2_1561 | 0.099175 | 0.68476 | 0.099067 | 0.68442
450 | 7.5 | feeder2_1657 | 0.098299 | 0.68533 | 0.098188 | 0.685
450 | 7.5 | feeder2_1570 | 0.099077 | 0.68452 | 0.098968 | 0.68418
450 | 7.5 | feeder2_1756 | 0.096717 | 0.68623 | 0.096611 | 0.68589
450 | 7.5 | feeder2_1588 | 0.099021 | 0.6842 | 0.098911 | 0.68386
450 | 7.5 | feeder2_1628 | 0.098977 | 0.68418 | 0.098867 | 0.68384
450 | 7.5 | feeder2_1598 | 0.098952 | 0.6838 | 0.098842 | 0.68347
450 | 7.5 | feeder2_1816 | 0.098949 | 0.6836 | 0.098841 | 0.68326
450 | 7.5 | feeder2_1765 | 0.09895 | 0.68366 | 0.098838 | 0.68333
450 | 7.5 | feeder2_1641 | 0.098633 | 0.68197 | 0.098521 | 0.68162
450 | 7.5 | feeder2_1689 | 0.098475 | 0.68076 | 0.098359 | 0.6804
450 | 7.5 | feeder2_1744 | 0.098074 | 0.68181 | 0.097961 | 0.68146
450 | 7.5 | feeder2_1817 | 0.098494 | 0.68085 | 0.098382 | 0.68049
450 | 7.5 | feeder2_1779 | 0.099492 | 0.67954 | 0.099378 | 0.67918
450 | 7.5 | feeder2_1800 | 0.098577 | 0.68133 | 0.09846 | 0.68097
450 | 7.5 | feeder2_1818 | 0.095313 | 0.67661 | 0.095203 | 0.67624
450 | 7.5 | feeder2_1753 | 0.096437 | 0.68135 | 0.09632 | 0.681
450 | 7.5 | feeder2_1754 | 0.098045 | 0.6818 | 0.097934 | 0.68145
480 | 8 | secondary | 0.040398 | 0.053717 | 0.040392 | 0.053713
480 | 8 | feeder2_44 | 0.075214 | 0.28029 | 0.075197 | 0.28024
480 | 8 | feeder2_45 | 0.07654 | 0.28918 | 0.076525 | 0.28913
480 | 8 | feeder2_46 | 0.076015 | 0.27869 | 0.075999 | 0.27864
480 | 8 | feeder2_51 | 0.078854 | 0.30465 | 0.078838 | 0.3046
480 | 8 | feeder2_48 | 0.076357 | 0.28907 | 0.076341 | 0.28902
480 | 8 | feeder2_52 | 0.078669 | 0.30619 | 0.078651 | 0.30614
480 | 8 | feeder2_68 | 0.085324 | 0.34758 | 0.085306 | 0.34752
480 | 8 | feeder2_69 | 0.085353 | 0.3475 | 0.085334 | 0.34744
480 | 8 | feeder2_71 | 0.086186 | 0.35327 | 0.086165 | 0.35322
480 | 8 | feeder2_72 | 0.085969 | 0.35313 | 0.08595 | 0.35307
480 | 8 | feeder2_73 | 0.088891 | 0.3711 | 0.088872 | 0.37105
480 | 8 | feeder2_74 | 0.093198 | 0.37993 | 0.09318 | 0.37987
480 | 8 | feeder2_77 | 0.090955 | 0.38498 | 0.090936 | 0.38492
480 | 8 | feeder2_79 | 0.091643 | 0.38356 | 0.091624 | 0.38349
480 | 8 | feeder2_81 | 0.094283 | 0.40736 | 0.094263 | 0.40729
480 | 8 | feeder2_82 | 0.09242 | 0.40627 | 0.092397 | 0.40621
480 | 8 | feeder2_116 | 0.10961 | 0.50907 | 0.10958 | 0.50898
480 | 8 | feeder2_119 | 0.10954 | 0.51022 | 0.10951 | 0.51014
480 | 8 | feeder2_120 | 0.11521 | 0.54602 | 0.11519 | 0.54592
480 | 8 | feeder2_248 | 0.12652 | 0.56072 | 0.12649 | 0.56063
480 | 8 | feeder2_124 | 0.11745 | 0.56289 | 0.11742 | 0.56278
480 | 8 | feeder2_282 | 0.1009 | 0.55327 | 0.10088 | 0.55316
480 | 8 | feeder2_275 | 0.11834 | 0.56542 | 0.11831 | 0.56532
480 | 8 | feeder2_151 | 0.12251 | 0.59755 | 0.12248 | 0.59744
480 | 8 | feeder2_295 | 0.12509 | 0.59173 | 0.12506 | 0.59162
480 | 8 | feeder2_311 | 0.12252 | 0.59751 | 0.12249 | 0.5974
480 | 8 | feeder2_201 | 0.13243 | 0.66282 | 0.1324 | 0.6627
480 | 8 | feeder2_314 | 0.13233 | 0.66274 | 0.1323 | 0.66262
480 | 8 | feeder2_342 | 0.14656 | 0.75563 | 0.14653 | 0.75549
480 | 8 | feeder2_368 | 0.14678 | 0.75873 | 0.14675 | 0.75859
480 | 8 | feeder2_347 | 0.15303 | 0.79541 | 0.153 | 0.79526
480 | 8 | feeder2_353 | 0.15626 | 0.81523 | 0.15622 | 0.81508
480 | 8 | feeder2_518 | 0.15296 | 0.79536 | 0.15293 | 0.79521
480 | 8 | feeder2_365 | 0.15983 | 0.83717 | 0.15979 | 0.83701
480 | 8 | feeder2_653 | 0.15635 | 0.81534 | 0.15631 | 0.81519
480 | 8 | feeder2_377 | 0.16177 | 0.84908 | 0.16173 | 0.84892
480 | 8 | feeder2_622 | 0.15979 | 0.83714 | 0.15975 | 0.83699
480 | 8 | feeder2_451 | 0.14538 | 0.75929 | 0.14535 | 0.75915
480 | 8 | feeder2_383 | 0.14751 | 0.76342 | 0.14748 | 0.76328
480 | 8 | feeder2_385 | 0.16439 | 0.8646 | 0.16436 | 0.86444
480 | 8 | feeder2_621 | 0.16397 | 0.84287 | 0.16393 | 0.84272
480 | 8 | feeder2_611 | 0.14759 | 0.76351 | 0.14756 | 0.76337
480 | 8 | feeder2_405 | 0.14756 | 0.7637 | 0.14753 | 0.76356
480 | 8 | feeder2_461 | 0.17163 | 0.91118 | 0.17159 | 0.911
480 | 8 | feeder2_594 | 0.17185 | 0.8742 | 0.17181 | 0.87403
480 | 8 | feeder2_732 | 0.14769 | 0.76386 | 0.14765 | 0.76373
480 | 8 | feeder2_417 | 0.14788 | 0.76584 | 0.14785 | 0.7657
480 | 8 | feeder2_663 | 0.14789 | 0.7658 | 0.14785 | 0.76566
480 | 8 | feeder2_444 | 0.14814 | 0.76747 | 0.1481 | 0.76733
480 | 8 | feeder2_759 | 0.14658 | 0.76801 | 0.14655 | 0.76787
480 | 8 | feeder2_842 | 0.14814 | 0.76743 | 0.14811 | 0.76729
480 | 8 | feeder2_459 | 0.14826 | 0.76802 | 0.14822 | 0.76788
480 | 8 | feeder2_702 | 0.14675 | 0.76694 | 0.14672 | 0.7668
480 | 8 | feeder2_493 | 0.14884 | 0.77057 | 0.14881 | 0.77044
480 | 8 | feeder2_651 | 0.17163 | 0.91116 | 0.17159 | 0.91098
480 | 8 | feeder2_684 | 0.17757 | 0.94922 | 0.17752 | 0.94903
480 | 8 | feeder2_674 | 0.14986 | 0.77234 | 0.14982 | 0.7722
480 | 8 | feeder2_696 | 0.14876 | 0.77008 | 0.14872 | 0.76995
480 | 8 | feeder2_681 | 0.15069 | 0.77376 | 0.15066 | 0.77362
480 | 8 | feeder2_682 | 0.1529 | 0.7775 | 0.15286 | 0.77736
480 | 8 | feeder2_728 | 0.17889 | 0.95625 | 0.17885 | 0.95606
480 | 8 | feeder2_724 | 0.18112 | 0.97204 | 0.18108 | 0.97184
480 | 8 | feeder2_703 | 0.14877 | 0.77001 | 0.14873 | 0.76987
480 | 8 | feeder2_704 | 0.1488 | 0.76989 | 0.14877 | 0.76975
480 | 8 | feeder2_754 | 0.18105 | 0.97199 | 0.181 | 0.97178
480 | 8 | feeder2_747 | 0.18258 | 0.9814 | 0.18254 | 0.98119
480 | 8 | feeder2_828 | 0.1842 | 0.96299 | 0.18416 | 0.9628
480 | 8 | feeder2_763 | 0.17824 | 0.9567 | 0.17819 | 0.9565
480 | 8 | feeder2_836 | 0.18258 | 0.98135 | 0.18254 | 0.98114
480 | 8 | feeder2_758 | 0.18385 | 0.98947 | 0.1838 | 0.98926
480 | 8 | feeder2_788 | 0.1826 | 0.99002 | 0.18256 | 0.98981
480 | 8 | feeder2_812 | 0.18814 | 1.0138 | 0.18809 | 1.0135
480 | 8 | feeder2_947 | 0.17808 | 0.95658 | 0.17804 | 0.95639
480 | 8 | feeder2_868 | 0.17753 | 0.95678 | 0.17749 | 0.95659
480 | 8 | feeder2_785 | 0.17799 | 0.95698 | 0.17795 | 0.95679
480 | 8 | feeder2_1176 | 0.17799 | 0.95689 | 0.17795 | 0.9567
480 | 8 | feeder2_846 | 0.17829 | 0.95775 | 0.17825 | 0.95755
480 | 8 | feeder2_911 | 0.17726 | 0.95663 | 0.17722 | 0.95644
480 | 8 | feeder2_1107 | 0.19007 | 1.0317 | 0.19002 | 1.0315
480 | 8 | feeder2_920 | 0.18881 | 1.0156 | 0.18876 | 1.0154
480 | 8 | feeder2_926 | 0.18981 | 1.0184 | 0.18976 | 1.0181
480 | 8 | feeder2_1239 | 0.18882 | 1.0157 | 0.18877 | 1.0155
480 | 8 | feeder2_933 | 0.19025 | 1.0196 | 0.1902 | 1.0193
480 | 8 | feeder2_1146 | 0.1898 | 1.0183 | 0.18975 | 1.018
480 | 8 | feeder2_1124 | 0.19103 | 1.0186 | 0.19098 | 1.0184
480 | 8 | feeder2_942 | 0.19129 | 1.0236 | 0.19124 | 1.0233
480 | 8 | feeder2_952 | 0.19174 | 1.0211 | 0.19169 | 1.0209
480 | 8 | feeder2_965 | 0.19143 | 1.0247 | 0.19138 | 1.0244
480 | 8 | feeder2_961 | 0.1918 | 1.0209 | 0.19174 | 1.0207
480 | 8 | feeder2_963 | 0.19174 | 1.0211 | 0.19169 | 1.0208
480 | 8 | feeder2_973 | 0.19164 | 1.0175 | 0.19159 | 1.0172
480 | 8 | feeder2_1128 | 0.1926 | 1.0249 | 0.19255 | 1.0247
480 | 8 | feeder2_1113 | 0.1917 | 1.0211 | 0.19165 | 1.0208
480 | 8 | feeder2_1143 | 0.19161 | 1.0202 | 0.19156 | 1.02
480 | 8 | feeder2_1238 | 0.18606 | 1.026 | 0.18601 | 1.0258
480 | 8 | feeder2_979 | 0.19171 | 1.026 | 0.19166 | 1.0258
480 | 8 | feeder2_1236 | 0.19142 | 1.0124 | 0.19137 | 1.0122
480 | 8 | feeder2_989 | 0.19164 | 1.0175 | 0.19159 | 1.0172
480 | 8 | feeder2_1196 | 0.19607 | 1.0317 | 0.19602 | 1.0315
480 | 8 | feeder2_1158 | 0.19164 | 1.0174 | 0.19159 | 1.0172
480 | 8 | feeder2_1122 | 0.19086 | 1.0388 | 0.19081 | 1.0386
480 | 8 | feeder2_1258 | 0.19004 | 1.0316 | 0.18999 | 1.0314
480 | 8 | feeder2_1303 | 0.19045 | 1.0384 | 0.19041 | 1.0382
480 | 8 | feeder2_1138 | 0.19151 | 1.0445 | 0.19146 | 1.0443
480 | 8 | feeder2_1304 | 0.19165 | 1.0453 | 0.1916 | 1.0451
480 | 8 | feeder2_1212 | 0.19274 | 1.0558 | 0.19269 | 1.0556
480 | 8 | feeder2_1311 | 0.1912 | 1.0564 | 0.19115 | 1.0562
480 | 8 | feeder2_1290 | 0.19457 | 1.0694 | 0.19452 | 1.0692
480 | 8 | feeder2_1325 | 0.19086 | 1.0085 | 0.1908 | 1.0082
480 | 8 | feeder2_1248 | 0.19143 | 1.0124 | 0.19137 | 1.0122
480 | 8 | feeder2_1249 | 0.18576 | 1.0258 | 0.18571 | 1.0256
480 | 8 | feeder2_1250 | 0.18304 | 1.0275 | 0.18299 | 1.0273
480 | 8 | feeder2_1366 | 0.19305 | 1.0104 | 0.193 | 1.0101
480 | 8 | feeder2_1266 | 0.19002 | 1.0315 | 0.18997 | 1.0313
480 | 8 | feeder2_1372 | 0.19351 | 1.0699 | 0.19347 | 1.0697
480 | 8 | feeder2_1363 | 0.1969 | 1.0835 | 0.19685 | 1.0833
480 | 8 | feeder2_1446 | 0.1908 | 1.0084 | 0.19074 | 1.0082
480 | 8 | feeder2_1502 | 0.19024 | 1.0041 | 0.19018 | 1.0038
480 | 8 | feeder2_1428 | 0.19819 | 1.0851 | 0.19814 | 1.0849
480 | 8 | feeder2_1380 | 0.19922 | 1.0982 | 0.19918 | 1.098
480 | 8 | feeder2_1550 | 0.19917 | 1.0982 | 0.19912 | 1.098
480 | 8 | feeder2_1386 | 0.20036 | 1.1054 | 0.20031 | 1.1052
480 | 8 | feeder2_1551 | 0.20052 | 1.1056 | 0.20047 | 1.1054
480 | 8 | feeder2_1400 | 0.2009 | 1.1088 | 0.20085 | 1.1086
480 | 8 | feeder2_1552 | 0.20103 | 1.109 | 0.20098 | 1.1087
480 | 8 | feeder2_1408 | 0.202 | 1.1157 | 0.20195 | 1.1155
480 | 8 | feeder2_1553 | 0.20231 | 1.1169 | 0.20226 | 1.1166
480 | 8 | feeder2_1416 | 0.20252 | 1.1191 | 0.20247 | 1.1189
480 | 8 | feeder2_1530 | 0.19942 | 1.119 | 0.19938 | 1.1188
480 | 8 | feeder2_1425 | 0.20381 | 1.1256 | 0.20376 | 1.1254
480 | 8 | feeder2_1589 | 0.21206 | 1.1382 | 0.21202 | 1.1379
480 | 8 | feeder2_1435 | 0.20382 | 1.1257 | 0.20377 | 1.1255
480 | 8 | feeder2_1621 | 0.20372 | 1.1252 | 0.20368 | 1.125
480 | 8 | feeder2_1564 | 0.20414 | 1.1274 | 0.20409 | 1.1272
480 | 8 | feeder2_1704 | 0.19117 | 1.0029 | 0.19112 | 1.0027
480 | 8 | feeder2_1525 | 0.19004 | 1.0034 | 0.18998 | 1.0031
480 | 8 | feeder2_1716 | 0.1924 | 1.0004 | 0.19235 | 1.0001
480 | 8 | feeder2_1537 | 0.18978 | 1.0031 | 0.18972 | 1.0028
480 | 8 | feeder2_1645 | 0.19059 | 1.0046 | 0.19053 | 1.0043
480 | 8 | feeder2_1561 | 0.1893 | 1.0018 | 0.18925 | 1.0015
480 | 8 | feeder2_1657 | 0.18926 | 1.0018 | 0.1892 | 1.0015
480 | 8 | feeder2_1570 | 0.1891 | 1.0013 | 0.18904 | 1.001
480 | 8 | feeder2_1756 | 0.18621 | 1.0025 | 0.18615 | 1.0022
480 | 8 | feeder2_1588 | 0.18896 | 1.0007 | 0.1889 | 1.0004
480 | 8 | feeder2_1628 | 0.18891 | 1.0007 | 0.18885 | 1.0004
480 | 8 | feeder2_1598 | 0.18878 | 1 | 0.18871 | 0.99974
480 | 8 | feeder2_1816 | 0.19192 | 0.99607 | 0.19186 | 0.99577
480 | 8 | feeder2_1765 | 0.18877 | 0.99994 | 0.18871 | 0.99964
480 | 8 | feeder2_1641 | 0.18779 | 0.99785 | 0.18773 | 0.99754
480 | 8 | feeder2_1689 | 0.1874 | 0.99651 | 0.18733 | 0.99619
480 | 8 | feeder2_1744 | 0.18626 | 0.99768 | 0.18619 | 0.99738
480 | 8 | feeder2_1817 | 0.18757 | 0.99747 | 0.18751 | 0.99716
480 | 8 | feeder2_1779 | 0.1874 | 0.99649 | 0.18733 | 0.99617
480 | 8 | feeder2_1800 | 0.18745 | 0.99657 | 0.18738 | 0.99625
480 | 8 | feeder2_1818 | 0.18382 | 0.98749 | 0.18374 | 0.98716
480 | 8 | feeder2_1753 | 0.18566 | 0.99723 | 0.1856 | 0.99691
480 | 8 | feeder2_1754 | 0.18532 | 0.99767 | 0.18526 | 0.99736
510 | 8.5 | secondary | 0.021211 | 0.02223 | 0.021216 | 0.022232
510 | 8.5 | feeder2_44 | 0.039468 | 0.11593 | 0.039477 | 0.11594
510 | 8.5 | feeder2_45 | 0.04006 | 0.11988 | 0.040066 | 0.11989
510 | 8.5 | feeder2_46 | 0.046993 | 0.11152 | 0.047005 | 0.11153
510 | 8.5 | feeder2_51 | 0.041101 | 0.12676 | 0.041108 | 0.12677
510 | 8.5 | feeder2_48 | 0.039878 | 0.11972 | 0.039888 | 0.11974
510 | 8.5 | feeder2_52 | 0.039559 | 0.12875 | 0.039567 | 0.12876
510 | 8.5 | feeder2_68 | 0.044107 | 0.14533 | 0.044118 | 0.14534
510 | 8.5 | feeder2_69 | 0.044236 | 0.14529 | 0.044249 | 0.14531
510 | 8.5 | feeder2_71 | 0.044508 | 0.14779 | 0.044521 | 0.1478
510 | 8.5 | feeder2_72 | 0.044285 | 0.1476 | 0.044297 | 0.14762
510 | 8.5 | feeder2_73 | 0.045774 | 0.1555 | 0.045785 | 0.15552
510 | 8.5 | feeder2_74 | 0.043877 | 0.16068 | 0.043891 | 0.1607
510 | 8.5 | feeder2_77 | 0.046842 | 0.16128 | 0.046855 | 0.1613
510 | 8.5 | feeder2_79 | 0.048347 | 0.16056 | 0.048355 | 0.16058
510 | 8.5 | feeder2_81 | 0.048473 | 0.17061 | 0.048486 | 0.17064
510 | 8.5 | feeder2_82 | 0.046322 | 0.16879 | 0.046336 | 0.16881
510 | 8.5 | feeder2_116 | 0.056352 | 0.21462 | 0.056364 | 0.21465
510 | 8.5 | feeder2_119 | 0.056369 | 0.21468 | 0.056383 | 0.21473
510 | 8.5 | feeder2_120 | 0.059286 | 0.23088 | 0.059302 | 0.23093
510 | 8.5 | feeder2_248 | 0.059327 | 0.231 | 0.059341 | 0.23105
510 | 8.5 | feeder2_124 | 0.061087 | 0.24084 | 0.061101 | 0.24089
510 | 8.5 | feeder2_282 | 0.046811 | 0.23058 | 0.046823 | 0.23063
510 | 8.5 | feeder2_275 | 0.06041 | 0.24417 | 0.060428 | 0.24422
510 | 8.5 | feeder2_151 | 0.065992 | 0.26307 | 0.066011 | 0.26312
510 | 8.5 | feeder2_295 | 0.073481 | 0.26029 | 0.073494 | 0.26033
510 | 8.5 | feeder2_311 | 0.066065 | 0.26305 | 0.066078 | 0.26309
510 | 8.5 | feeder2_201 | 0.073391 | 0.30336 | 0.07341 | 0.30342
510 | 8.5 | feeder2_314 | 0.073307 | 0.3033 | 0.073326 | 0.30336
510 | 8.5 | feeder2_342 | 0.084073 | 0.36093 | 0.084094 | 0.36101
510 | 8.5 | feeder2_368 | 0.086365 | 0.37159 | 0.086385 | 0.37167
510 | 8.5 | feeder2_347 | 0.085443 | 0.3694 | 0.085462 | 0.36948
510 | 8.5 | feeder2_353 | 0.086144 | 0.37365 | 0.086162 | 0.37374
510 | 8.5 | feeder2_518 | 0.085362 | 0.36934 | 0.085382 | 0.36942
510 | 8.5 | feeder2_365 | 0.086923 | 0.37831 | 0.086945 | 0.37841
510 | 8.5 | feeder2_653 | 0.086181 | 0.37375 | 0.0862 | 0.37384
510 | 8.5 | feeder2_377 | 0.087272 | 0.38123 | 0.087291 | 0.38132
510 | 8.5 | feeder2_622 | 0.088734 | 0.37672 | 0.088755 | 0.37681
510 | 8.5 | feeder2_451 | 0.086273 | 0.37152 | 0.086298 | 0.3716
510 | 8.5 | feeder2_383 | 0.09027 | 0.38892 | 0.090291 | 0.389
510 | 8.5 | feeder2_385 | 0.08751 | 0.38561 | 0.08753 | 0.38571
510 | 8.5 | feeder2_621 | 0.094878 | 0.37754 | 0.094895 | 0.37763
510 | 8.5 | feeder2_611 | 0.090315 | 0.38901 | 0.090339 | 0.3891
510 | 8.5 | feeder2_405 | 0.09052 | 0.39 | 0.090541 | 0.39008
510 | 8.5 | feeder2_461 | 0.088463 | 0.40377 | 0.088484 | 0.40389
510 | 8.5 | feeder2_594 | 0.08754 | 0.38569 | 0.087564 | 0.38579
510 | 8.5 | feeder2_732 | 0.089136 | 0.3924 | 0.089162 | 0.39248
510 | 8.5 | feeder2_417 | 0.09245 | 0.39757 | 0.092476 | 0.39766
510 | 8.5 | feeder2_663 | 0.095012 | 0.395 | 0.095037 | 0.39508
510 | 8.5 | feeder2_444 | 0.093732 | 0.4041 | 0.093756 | 0.40418
510 | 8.5 | feeder2_759 | 0.092711 | 0.40444 | 0.092737 | 0.40452
510 | 8.5 | feeder2_842 | 0.09378 | 0.40407 | 0.093805 | 0.40415
510 | 8.5 | feeder2_459 | 0.09421 | 0.40638 | 0.094238 | 0.40646
510 | 8.5 | feeder2_702 | 0.092317 | 0.40501 | 0.092341 | 0.40509
510 | 8.5 | feeder2_493 | 0.09625 | 0.4156 | 0.096276 | 0.41568
510 | 8.5 | feeder2_651 | 0.088495 | 0.40375 | 0.088517 | 0.40387
510 | 8.5 | feeder2_684 | 0.089248 | 0.4191 | 0.089274 | 0.41924
510 | 8.5 | feeder2_674 | 0.098922 | 0.42227 | 0.098954 | 0.42235
510 | 8.5 | feeder2_696 | 0.096848 | 0.41329 | 0.096873 | 0.41337
510 | 8.5 | feeder2_681 | 0.10764 | 0.43864 | 0.10767 | 0.43873
510 | 8.5 | feeder2_682 | 0.098846 | 0.42516 | 0.098877 | 0.42524
510 | 8.5 | feeder2_728 | 0.090262 | 0.42423 | 0.090287 | 0.42437
510 | 8.5 | feeder2_724 | 0.087881 | 0.42339 | 0.087902 | 0.42354
510 | 8.5 | feeder2_703 | 0.099497 | 0.41064 | 0.099525 | 0.41073
510 | 8.5 | feeder2_704 | 0.097219 | 0.41305 | 0.097245 | 0.41313
510 | 8.5 | feeder2_754 | 0.087793 | 0.42333 | 0.087814 | 0.42349
510 | 8.5 | feeder2_747 | 0.087335 | 0.42525 | 0.087357 | 0.42541
510 | 8.5 | feeder2_828 | 0.092214 | 0.42977 | 0.092239 | 0.4299
510 | 8.5 | feeder2_763 | 0.090355 | 0.42365 | 0.090379 | 0.42378
510 | 8.5 | feeder2_836 | 0.087398 | 0.42521 | 0.087421 | 0.42537
510 | 8.5 | feeder2_758 | 0.086864 | 0.42691 | 0.086888 | 0.42708
510 | 8.5 | feeder2_788 | 0.086807 | 0.42688 | 0.086832 | 0.42704
510 | 8.5 | feeder2_812 | 0.085439 | 0.43228 | 0.085465 | 0.43247
510 | 8.5 | feeder2_947 | 0.090174 | 0.42353 | 0.090197 | 0.42367
510 | 8.5 | feeder2_868 | 0.089726 | 0.42356 | 0.08975 | 0.42371
510 | 8.5 | feeder2_785 | 0.090575 | 0.42344 | 0.090599 | 0.42358
510 | 8.5 | feeder2_1176 | 0.094186 | 0.41975 | 0.094211 | 0.41989
510 | 8.5 | feeder2_846 | 0.090434 | 0.42442 | 0.090457 | 0.42456
510 | 8.5 | feeder2_911 | 0.090548 | 0.42337 | 0.090572 | 0.42351
510 | 8.5 | feeder2_1107 | 0.085493 | 0.43702 | 0.085516 | 0.4372
510 | 8.5 | feeder2_920 | 0.085027 | 0.43254 | 0.085052 | 0.43273
510 | 8.5 | feeder2_926 | 0.084408 | 0.43293 | 0.084431 | 0.43312
510 | 8.5 | feeder2_1239 | 0.085036 | 0.43259 | 0.08506 | 0.43278
510 | 8.5 | feeder2_933 | 0.08424 | 0.43292 | 0.08426 | 0.43311
510 | 8.5 | feeder2_1146 | 0.083912 | 0.43386 | 0.083935 | 0.43406
510 | 8.5 | feeder2_1124 | 0.084273 | 0.43289 | 0.084294 | 0.43309
510 | 8.5 | feeder2_942 | 0.083813 | 0.43293 | 0.083832 | 0.43314
510 | 8.5 | feeder2_952 | 0.083139 | 0.43255 | 0.083161 | 0.43277
510 | 8.5 | feeder2_965 | 0.08382 | 0.43299 | 0.083841 | 0.4332
510 | 8.5 | feeder2_961 | 0.083156 | 0.43248 | 0.083176 | 0.4327
510 | 8.5 | feeder2_963 | 0.08312 | 0.43255 | 0.083145 | 0.43278
510 | 8.5 | feeder2_973 | 0.083181 | 0.43091 | 0.0832 | 0.43114
510 | 8.5 | feeder2_1128 | 0.083272 | 0.43457 | 0.083293 | 0.43479
510 | 8.5 | feeder2_1113 | 0.08265 | 0.43309 | 0.082675 | 0.43331
510 | 8.5 | feeder2_1143 | 0.082411 | 0.43172 | 0.082435 | 0.43195
510 | 8.5 | feeder2_1238 | 0.082573 | 0.43228 | 0.082594 | 0.43249
510 | 8.5 | feeder2_979 | 0.083849 | 0.43314 | 0.083872 | 0.43335
510 | 8.5 | feeder2_1236 | 0.083219 | 0.42862 | 0.083242 | 0.42885
510 | 8.5 | feeder2_989 | 0.083181 | 0.43091 | 0.0832 | 0.43114
510 | 8.5 | feeder2_1196 | 0.084186 | 0.43377 | 0.084207 | 0.43398
510 | 8.5 | feeder2_1158 | 0.083242 | 0.43087 | 0.083264 | 0.43109
510 | 8.5 | feeder2_1122 | 0.085509 | 0.43894 | 0.085531 | 0.43913
510 | 8.5 | feeder2_1258 | 0.085689 | 0.43688 | 0.085712 | 0.43707
510 | 8.5 | feeder2_1303 | 0.085001 | 0.43862 | 0.085025 | 0.4388
510 | 8.5 | feeder2_1138 | 0.085557 | 0.44059 | 0.08558 | 0.44078
510 | 8.5 | feeder2_1304 | 0.085572 | 0.44064 | 0.085599 | 0.44083
510 | 8.5 | feeder2_1212 | 0.085652 | 0.44404 | 0.085677 | 0.44423
510 | 8.5 | feeder2_1311 | 0.085002 | 0.44458 | 0.085024 | 0.44477
510 | 8.5 | feeder2_1290 | 0.085991 | 0.44797 | 0.086014 | 0.44815
510 | 8.5 | feeder2_1325 | 0.082647 | 0.42874 | 0.082667 | 0.42898
510 | 8.5 | feeder2_1248 | 0.083233 | 0.4286 | 0.083257 | 0.42884
510 | 8.5 | feeder2_1249 | 0.082233 | 0.43208 | 0.082255 | 0.4323
510 | 8.5 | feeder2_1250 | 0.082516 | 0.43225 | 0.082538 | 0.43246
510 | 8.5 | feeder2_1366 | 0.086973 | 0.42467 | 0.086996 | 0.42491
510 | 8.5 | feeder2_1266 | 0.085849 | 0.43677 | 0.085871 | 0.43696
510 | 8.5 | feeder2_1372 | 0.085939 | 0.44794 | 0.085962 | 0.44812
510 | 8.5 | feeder2_1363 | 0.086371 | 0.45224 | 0.086394 | 0.45242
510 | 8.5 | feeder2_1446 | 0.082093 | 0.4294 | 0.082115 | 0.42965
510 | 8.5 | feeder2_1502 | 0.08234 | 0.42821 | 0.082363 | 0.42847
510 | 8.5 | feeder2_1428 | 0.086818 | 0.4536 | 0.086842 | 0.45379
510 | 8.5 | feeder2_1380 | 0.086483 | 0.45526 | 0.086508 | 0.45543
510 | 8.5 | feeder2_1550 | 0.086016 | 0.45567 | 0.086039 | 0.45585
510 | 8.5 | feeder2_1386 | 0.086637 | 0.45658 | 0.086658 | 0.45675
510 | 8.5 | feeder2_1551 | 0.086681 | 0.4567 | 0.086706 | 0.45688
510 | 8.5 | feeder2_1400 | 0.086705 | 0.45718 | 0.08673 | 0.45736
510 | 8.5 | feeder2_1552 | 0.086758 | 0.45732 | 0.086782 | 0.45751
510 | 8.5 | feeder2_1408 | 0.086835 | 0.45835 | 0.086856 | 0.45853
510 | 8.5 | feeder2_1553 | 0.085984 | 0.45945 | 0.086009 | 0.45963
510 | 8.5 | feeder2_1416 | 0.086904 | 0.45869 | 0.086926 | 0.45887
510 | 8.5 | feeder2_1530 | 0.08618 | 0.45927 | 0.086202 | 0.45945
510 | 8.5 | feeder2_1425 | 0.087193 | 0.45911 | 0.087217 | 0.45929
510 | 8.5 | feeder2_1589 | 0.086796 | 0.46198 | 0.086824 | 0.46216
510 | 8.5 | feeder2_1435 | 0.087228 | 0.45891 | 0.087252 | 0.45909
510 | 8.5 | feeder2_1621 | 0.089966 | 0.45652 | 0.089991 | 0.4567
510 | 8.5 | feeder2_1564 | 0.087251 | 0.45905 | 0.087275 | 0.45923
510 | 8.5 | feeder2_1704 | 0.082371 | 0.42818 | 0.082393 | 0.42844
510 | 8.5 | feeder2_1525 | 0.082261 | 0.42808 | 0.082286 | 0.42834
510 | 8.5 | feeder2_1716 | 0.082394 | 0.42798 | 0.082416 | 0.42823
510 | 8.5 | feeder2_1537 | 0.082171 | 0.42795 | 0.082196 | 0.42822
510 | 8.5 | feeder2_1645 | 0.082314 | 0.4285 | 0.082337 | 0.42876
510 | 8.5 | feeder2_1561 | 0.082024 | 0.42749 | 0.082047 | 0.42776
510 | 8.5 | feeder2_1657 | 0.081968 | 0.42746 | 0.08199 | 0.42773
510 | 8.5 | feeder2_1570 | 0.081963 | 0.42731 | 0.081987 | 0.42758
510 | 8.5 | feeder2_1756 | 0.080877 | 0.42852 | 0.080895 | 0.42879
510 | 8.5 | feeder2_1588 | 0.081938 | 0.42707 | 0.081959 | 0.42734
510 | 8.5 | feeder2_1628 | 0.081888 | 0.42704 | 0.081912 | 0.42731
510 | 8.5 | feeder2_1598 | 0.081909 | 0.42678 | 0.081931 | 0.42706
510 | 8.5 | feeder2_1816 | 0.082089 | 0.42664 | 0.082107 | 0.42692
510 | 8.5 | feeder2_1765 | 0.082035 | 0.42668 | 0.082058 | 0.42696
510 | 8.5 | feeder2_1641 | 0.081762 | 0.42544 | 0.081784 | 0.42572
510 | 8.5 | feeder2_1689 | 0.081727 | 0.42459 | 0.081752 | 0.42488
510 | 8.5 | feeder2_1744 | 0.081486 | 0.42527 | 0.081509 | 0.42556
510 | 8.5 | feeder2_1817 | 0.081741 | 0.42468 | 0.081761 | 0.42496
510 | 8.5 | feeder2_1779 | 0.082395 | 0.42388 | 0.082418 | 0.42418
510 | 8.5 | feeder2_1800 | 0.081744 | 0.42464 | 0.081766 | 0.42494
510 | 8.5 | feeder2_1818 | 0.081087 | 0.4221 | 0.0811 | 0.42241
510 | 8.5 | feeder2_1753 | 0.080764 | 0.42485 | 0.080787 | 0.42513
510 | 8.5 | feeder2_1754 | 0.081452 | 0.42526 | 0.081474 | 0.42554
540 | 9 | secondary | 0.015001 | 0.0074031 | 0.014991 | 0.0073935
540 | 9 | feeder2_44 | 0.02793 | 0.038629 | 0.027916 | 0.038601
540 | 9 | feeder2_45 | 0.028472 | 0.039727 | 0.028459 | 0.039696
540 | 9 | feeder2_46 | 0.0257 | 0.040418 | 0.025687 | 0.040387
540 | 9 | feeder2_51 | 0.02941 | 0.041612 | 0.029394 | 0.041584
540 | 9 | feeder2_48 | 0.028615 | 0.039937 | 0.0286 | 0.039908
540 | 9 | feeder2_52 | 0.032385 | 0.03817 | 0.032366 | 0.038143
540 | 9 | feeder2_68 | 0.031914 | 0.048239 | 0.031897 | 0.048205
540 | 9 | feeder2_69 | 0.017682 | 0.053016 | 0.017684 | 0.05294
540 | 9 | feeder2_71 | 0.032611 | 0.050512 | 0.03259 | 0.050479
540 | 9 | feeder2_72 | 0.087251 | 0.11675 | 0.087229 | 0.11672
540 | 9 | feeder2_73 | 0.0332 | 0.050426 | 0.033187 | 0.050404
540 | 9 | feeder2_74 | 0.033573 | 0.049911 | 0.033554 | 0.049895
540 | 9 | feeder2_77 | 0.033752 | 0.051325 | 0.033736 | 0.051316
540 | 9 | feeder2_79 | 0.020196 | 0.042232 | 0.020178 | 0.0422
540 | 9 | feeder2_81 | 0.035589 | 0.059383 | 0.035572 | 0.059394
540 | 9 | feeder2_82 | 0.035632 | 0.059442 | 0.035617 | 0.059453
540 | 9 | feeder2_116 | 0.045167 | 0.11444 | 0.04515 | 0.1145
540 | 9 | feeder2_119 | 0.045201 | 0.11447 | 0.045186 | 0.11454
540 | 9 | feeder2_120 | 0.0491 | 0.13765 | 0.04908 | 0.13773
540 | 9 | feeder2_248 | 0.051028 | 0.13691 | 0.051013 | 0.13699
540 | 9 | feeder2_124 | 0.051442 | 0.1524 | 0.051428 | 0.15249
540 | 9 | feeder2_282 | 0.052485 | 0.15458 | 0.052468 | 0.15466
540 | 9 | feeder2_275 | 0.06197 | 0.1614 | 0.061958 | 0.16149
540 | 9 | feeder2_151 | 0.054929 | 0.17077 | 0.054915 | 0.17086
540 | 9 | feeder2_295 | 0.052591 | 0.16823 | 0.052578 | 0.16832
540 | 9 | feeder2_311 | 0.054816 | 0.17065 | 0.0548 | 0.17074
540 | 9 | feeder2_201 | 0.061546 | 0.2053 | 0.061531 | 0.2054
540 | 9 | feeder2_314 | 0.060379 | 0.20755 | 0.060364 | 0.20765
540 | 9 | feeder2_342 | 0.071048 | 0.24972 | 0.071032 | 0.24984
540 | 9 | feeder2_368 | 0.070957 | 0.25136 | 0.070941 | 0.25147
540 | 9 | feeder2_347 | 0.076024 | 0.2685 | 0.076007 | 0.26862
540 | 9 | feeder2_353 | 0.078493 | 0.27785 | 0.078478 | 0.27797
540 | 9 | feeder2_518 | 0.076055 | 0.26853 | 0.076042 | 0.26865
540 | 9 | feeder2_365 | 0.081215 | 0.28791 | 0.081198 | 0.28803
540 | 9 | feeder2_653 | 0.079079 | 0.27841 | 0.079059 | 0.27853
540 | 9 | feeder2_377 | 0.082695 | 0.29339 | 0.082678 | 0.29351
540 | 9 | feeder2_622 | 0.081179 | 0.28787 | 0.081162 | 0.28799
540 | 9 | feeder2_451 | 0.070993 | 0.2514 | 0.070976 | 0.25151
540 | 9 | feeder2_383 | 0.070806 | 0.25405 | 0.070789 | 0.25416
540 | 9 | feeder2_385 | 0.084587 | 0.30062 | 0.08457 | 0.30075
540 | 9 | feeder2_621 | 0.080271 | 0.29071 | 0.080254 | 0.29083
540 | 9 | feeder2_611 | 0.071373 | 0.25462 | 0.071361 | 0.25474
540 | 9 | feeder2_405 | 0.070792 | 0.25418 | 0.070774 | 0.2543
540 | 9 | feeder2_461 | 0.091832 | 0.33073 | 0.091815 | 0.33086
540 | 9 | feeder2_594 | 0.085841 | 0.30015 | 0.085825 | 0.30027
540 | 9 | feeder2_732 | 0.072675 | 0.25363 | 0.072663 | 0.25374
540 | 9 | feeder2_417 | 0.070576 | 0.25531 | 0.070562 | 0.25543
540 | 9 | feeder2_663 | 0.070485 | 0.25522 | 0.070472 | 0.25533
540 | 9 | feeder2_444 | 0.07042 | 0.2562 | 0.070408 | 0.25632
540 | 9 | feeder2_759 | 0.069043 | 0.25867 | 0.069022 | 0.25879
540 | 9 | feeder2_842 | 0.07033 | 0.25611 | 0.070314 | 0.25622
540 | 9 | feeder2_459 | 0.07038 | 0.25637 | 0.070368 | 0.25649
540 | 9 | feeder2_702 | 0.069002 | 0.26009 | 0.068985 | 0.26021
540 | 9 | feeder2_493 | 0.070257 | 0.25561 | 0.070246 | 0.25572
540 | 9 | feeder2_651 | 0.091337 | 0.32997 | 0.09132 | 0.3301
540 | 9 | feeder2_684 | 0.097971 | 0.35627 | 0.097954 | 0.35641
540 | 9 | feeder2_674 | 0.071998 | 0.25659 | 0.071987 | 0.25671
540 | 9 | feeder2_696 | 0.068366 | 0.24846 | 0.068354 | 0.24857
540 | 9 | feeder2_681 | 0.076445 | 0.25894 | 0.076435 | 0.25906
540 | 9 | feeder2_682 | 0.072596 | 0.25719 | 0.072579 | 0.25732
540 | 9 | feeder2_728 | 0.09991 | 0.36324 | 0.099893 | 0.36337
540 | 9 | feeder2_724 | 0.10105 | 0.36642 | 0.10103 | 0.36655
540 | 9 | feeder2_703 | 0.067605 | 0.24765 | 0.067594 | 0.24776
540 | 9 | feeder2_704 | 0.066507 | 0.24607 | 0.066493 | 0.24619
540 | 9 | feeder2_754 | 0.10109 | 0.36646 | 0.10107 | 0.3666
540 | 9 | feeder2_747 | 0.10231 | 0.37057 | 0.10228 | 0.37071
540 | 9 | feeder2_828 | 0.10089 | 0.36375 | 0.10087 | 0.36388
540 | 9 | feeder2_763 | 0.1025 | 0.37263 | 0.10248 | 0.37277
540 | 9 | feeder2_836 | 0.1022 | 0.37047 | 0.10218 | 0.37061
540 | 9 | feeder2_758 | 0.1034 | 0.37421 | 0.10337 | 0.37435
540 | 9 | feeder2_788 | 0.10263 | 0.37566 | 0.10261 | 0.37579
540 | 9 | feeder2_812 | 0.10679 | 0.38366 | 0.10676 | 0.3838
540 | 9 | feeder2_947 | 0.10257 | 0.37272 | 0.10255 | 0.37285
540 | 9 | feeder2_868 | 0.10461 | 0.37721 | 0.1046 | 0.37734
540 | 9 | feeder2_785 | 0.10321 | 0.3755 | 0.1032 | 0.37564
540 | 9 | feeder2_1176 | 0.103 | 0.37529 | 0.10299 | 0.37542
540 | 9 | feeder2_846 | 0.11042 | 0.38009 | 0.1104 | 0.38023
540 | 9 | feeder2_911 | 0.10323 | 0.37554 | 0.10321 | 0.37568
540 | 9 | feeder2_1107 | 0.11155 | 0.39868 | 0.11153 | 0.39881
540 | 9 | feeder2_920 | 0.10643 | 0.38218 | 0.1064 | 0.38232
540 | 9 | feeder2_926 | 0.10577 | 0.38021 | 0.10575 | 0.38035
540 | 9 | feeder2_1239 | 0.10657 | 0.38191 | 0.10654 | 0.38205
540 | 9 | feeder2_933 | 0.10547 | 0.37933 | 0.10545 | 0.37948
540 | 9 | feeder2_1146 | 0.10579 | 0.38026 | 0.10577 | 0.3804
540 | 9 | feeder2_1124 | 0.10542 | 0.37928 | 0.1054 | 0.37942
540 | 9 | feeder2_942 | 0.10474 | 0.37717 | 0.10472 | 0.37731
540 | 9 | feeder2_952 | 0.10313 | 0.37475 | 0.10311 | 0.3749
540 | 9 | feeder2_965 | 0.10481 | 0.37707 | 0.10478 | 0.37722
540 | 9 | feeder2_961 | 0.10296 | 0.37439 | 0.10294 | 0.37454
540 | 9 | feeder2_963 | 0.10313 | 0.37478 | 0.10311 | 0.37492
540 | 9 | feeder2_973 | 0.10202 | 0.37226 | 0.102 | 0.37241
540 | 9 | feeder2_1128 | 0.10297 | 0.37479 | 0.10295 | 0.37494
540 | 9 | feeder2_1113 | 0.10315 | 0.3748 | 0.10313 | 0.37495
540 | 9 | feeder2_1143 | 0.10313 | 0.37625 | 0.10311 | 0.37639
540 | 9 | feeder2_1238 | 0.10512 | 0.37757 | 0.10511 | 0.37771
540 | 9 | feeder2_979 | 0.10488 | 0.37691 | 0.10486 | 0.37706
540 | 9 | feeder2_1236 | 0.10082 | 0.36983 | 0.10081 | 0.36997
540 | 9 | feeder2_989 | 0.10202 | 0.37226 | 0.10199 | 0.37241
540 | 9 | feeder2_1196 | 0.10649 | 0.37612 | 0.10647 | 0.37626
540 | 9 | feeder2_1158 | 0.10144 | 0.37155 | 0.10142 | 0.37169
540 | 9 | feeder2_1122 | 0.11346 | 0.40478 | 0.11344 | 0.40491
540 | 9 | feeder2_1258 | 0.11127 | 0.39838 | 0.11125 | 0.39852
540 | 9 | feeder2_1303 | 0.11361 | 0.40503 | 0.11359 | 0.40516
540 | 9 | feeder2_1138 | 0.11494 | 0.40951 | 0.11492 | 0.40965
540 | 9 | feeder2_1304 | 0.11497 | 0.40954 | 0.11495 | 0.40967
540 | 9 | feeder2_1212 | 0.11807 | 0.41952 | 0.11804 | 0.41966
540 | 9 | feeder2_1311 | 0.11734 | 0.42105 | 0.11732 | 0.42118
540 | 9 | feeder2_1290 | 0.12194 | 0.43064 | 0.12191 | 0.43078
540 | 9 | feeder2_1325 | 0.09963 | 0.36836 | 0.099604 | 0.3685
540 | 9 | feeder2_1248 | 0.10082 | 0.36982 | 0.1008 | 0.36996
540 | 9 | feeder2_1249 | 0.10514 | 0.37758 | 0.10511 | 0.37773
540 | 9 | feeder2_1250 | 0.10533 | 0.37788 | 0.10531 | 0.37802
540 | 9 | feeder2_1366 | 0.09951 | 0.36832 | 0.099486 | 0.36847
540 | 9 | feeder2_1266 | 0.11104 | 0.39814 | 0.11102 | 0.39827
540 | 9 | feeder2_1372 | 0.12569 | 0.43656 | 0.12566 | 0.43669
540 | 9 | feeder2_1363 | 0.12378 | 0.4355 | 0.12375 | 0.43564
540 | 9 | feeder2_1446 | 0.099167 | 0.36929 | 0.099145 | 0.36943
540 | 9 | feeder2_1502 | 0.098295 | 0.36553 | 0.098274 | 0.36568
540 | 9 | feeder2_1428 | 0.12955 | 0.43641 | 0.12952 | 0.43655
540 | 9 | feeder2_1380 | 0.12493 | 0.4392 | 0.1249 | 0.43934
540 | 9 | feeder2_1550 | 0.12368 | 0.44276 | 0.12365 | 0.4429
540 | 9 | feeder2_1386 | 0.12543 | 0.43926 | 0.12541 | 0.4394
540 | 9 | feeder2_1551 | 0.12839 | 0.43785 | 0.12836 | 0.43799
540 | 9 | feeder2_1400 | 0.12554 | 0.43956 | 0.12552 | 0.4397
540 | 9 | feeder2_1552 | 0.12741 | 0.43872 | 0.12738 | 0.43886
540 | 9 | feeder2_1408 | 0.12557 | 0.44054 | 0.12555 | 0.44068
540 | 9 | feeder2_1553 | 0.12565 | 0.44061 | 0.12562 | 0.44075
540 | 9 | feeder2_1416 | 0.12559 | 0.44103 | 0.12557 | 0.44117
540 | 9 | feeder2_1530 | 0.12547 | 0.44371 | 0.12545 | 0.44385
540 | 9 | feeder2_1425 | 0.12547 | 0.44065 | 0.12545 | 0.44079
540 | 9 | feeder2_1589 | 0.12552 | 0.44069 | 0.1255 | 0.44083
540 | 9 | feeder2_1435 | 0.12545 | 0.44057 | 0.12543 | 0.44071
540 | 9 | feeder2_1621 | 0.12477 | 0.43977 | 0.12475 | 0.43991
540 | 9 | feeder2_1564 | 0.12545 | 0.44065 | 0.12543 | 0.44079
540 | 9 | feeder2_1704 | 0.097807 | 0.36497 | 0.097787 | 0.36511
540 | 9 | feeder2_1525 | 0.098027 | 0.36505 | 0.098001 | 0.3652
540 | 9 | feeder2_1716 | 0.094611 | 0.36138 | 0.094586 | 0.36153
540 | 9 | feeder2_1537 | 0.097857 | 0.36511 | 0.09783 | 0.36526
540 | 9 | feeder2_1645 | 0.098377 | 0.36542 | 0.098354 | 0.36558
540 | 9 | feeder2_1561 | 0.097648 | 0.36496 | 0.097622 | 0.36511
540 | 9 | feeder2_1657 | 0.097879 | 0.36529 | 0.097857 | 0.36544
540 | 9 | feeder2_1570 | 0.097534 | 0.36483 | 0.097516 | 0.36497
540 | 9 | feeder2_1756 | 0.096114 | 0.36775 | 0.096086 | 0.3679
540 | 9 | feeder2_1588 | 0.097428 | 0.36452 | 0.0974 | 0.36467
540 | 9 | feeder2_1628 | 0.097019 | 0.36533 | 0.096991 | 0.36548
540 | 9 | feeder2_1598 | 0.097295 | 0.36389 | 0.097265 | 0.36405
540 | 9 | feeder2_1816 | 0.095973 | 0.36251 | 0.095947 | 0.36266
540 | 9 | feeder2_1765 | 0.097103 | 0.36369 | 0.097083 | 0.36384
540 | 9 | feeder2_1641 | 0.09674 | 0.36135 | 0.096713 | 0.36151
540 | 9 | feeder2_1689 | 0.096202 | 0.35898 | 0.096177 | 0.35914
540 | 9 | feeder2_1744 | 0.096827 | 0.3615 | 0.096802 | 0.36166
540 | 9 | feeder2_1817 | 0.096204 | 0.35903 | 0.096184 | 0.35919
540 | 9 | feeder2_1779 | 0.094929 | 0.35757 | 0.094905 | 0.35773
540 | 9 | feeder2_1800 | 0.097395 | 0.35833 | 0.097374 | 0.35849
540 | 9 | feeder2_1818 | 0.093688 | 0.35634 | 0.093669 | 0.3565
540 | 9 | feeder2_1753 | 0.097041 | 0.36189 | 0.097018 | 0.36205
540 | 9 | feeder2_1754 | 0.096841 | 0.36152 | 0.096819 | 0.36167
570 | 9.5 | secondary | 0.016883 | 0.044882 | 0.016873 | 0.044878
570 | 9.5 | feeder2_44 | 0.031458 | 0.23437 | 0.031439 | 0.23435
570 | 9.5 | feeder2_45 | 0.03206 | 0.24188 | 0.032042 | 0.24186
570 | 9.5 | feeder2_46 | 0.029964 | 0.2329 | 0.029942 | 0.23287
570 | 9.5 | feeder2_51 | 0.0331 | 0.25444 | 0.033079 | 0.25441
570 | 9.5 | feeder2_48 | 0.030762 | 0.24515 | 0.030743 | 0.24513
570 | 9.5 | feeder2_52 | 0.033214 | 0.25453 | 0.03319 | 0.25451
570 | 9.5 | feeder2_68 | 0.03604 | 0.28982 | 0.036017 | 0.28979
570 | 9.5 | feeder2_69 | 0.011723 | 0.23957 | 0.011747 | 0.23954
570 | 9.5 | feeder2_71 | 0.036912 | 0.29712 | 0.03689 | 0.29709
570 | 9.5 | feeder2_72 | 0.084642 | 0.34363 | 0.08462 | 0.34359
570 | 9.5 | feeder2_73 | 0.038255 | 0.31575 | 0.038226 | 0.31572
570 | 9.5 | feeder2_74 | 0.054069 | 0.32556 | 0.054046 | 0.32554
570 | 9.5 | feeder2_77 | 0.039361 | 0.33009 | 0.039333 | 0.33006
570 | 9.5 | feeder2_79 | 0.03716 | 0.3277 | 0.037137 | 0.32767
570 | 9.5 | feeder2_81 | 0.041299 | 0.3538 | 0.041272 | 0.35377
570 | 9.5 | feeder2_82 | 0.040323 | 0.3559 | 0.040298 | 0.35587
570 | 9.5 | feeder2_116 | 0.050114 | 0.45915 | 0.050082 | 0.45912
570 | 9.5 | feeder2_119 | 0.05339 | 0.45934 | 0.05336 | 0.45931
570 | 9.5 | feeder2_120 | 0.053155 | 0.49817 | 0.053122 | 0.49814
570 | 9.5 | feeder2_248 | 0.057986 | 0.50203 | 0.05795 | 0.50201
570 | 9.5 | feeder2_124 | 0.054917 | 0.52044 | 0.054886 | 0.5204
570 | 9.5 | feeder2_282 | 0.055801 | 0.52165 | 0.055767 | 0.52162
570 | 9.5 | feeder2_275 | 0.062848 | 0.52649 | 0.062809 | 0.52647
570 | 9.5 | feeder2_151 | 0.057457 | 0.55416 | 0.057417 | 0.55412
570 | 9.5 | feeder2_295 | 0.055826 | 0.55244 | 0.055789 | 0.5524
570 | 9.5 | feeder2_311 | 0.057344 | 0.55404 | 0.057301 | 0.55401
570 | 9.5 | feeder2_201 | 0.062303 | 0.61302 | 0.06226 | 0.61297
570 | 9.5 | feeder2_314 | 0.061254 | 0.61529 | 0.061216 | 0.61524
570 | 9.5 | feeder2_342 | 0.069275 | 0.69198 | 0.069229 | 0.69193
570 | 9.5 | feeder2_368 | 0.069564 | 0.69577 | 0.069517 | 0.69572
570 | 9.5 | feeder2_347 | 0.072708 | 0.72376 | 0.072655 | 0.7237
570 | 9.5 | feeder2_353 | 0.074445 | 0.73963 | 0.074395 | 0.73956
570 | 9.5 | feeder2_518 | 0.072753 | 0.7238 | 0.072705 | 0.72374
570 | 9.5 | feeder2_365 | 0.076397 | 0.75705 | 0.076342 | 0.75699
570 | 9.5 | feeder2_653 | 0.074817 | 0.74 | 0.07477 | 0.73993
570 | 9.5 | feeder2_377 | 0.07747 | 0.76655 | 0.077421 | 0.76648
570 | 9.5 | feeder2_622 | 0.07636 | 0.75702 | 0.076307 | 0.75695
570 | 9.5 | feeder2_451 | 0.069611 | 0.69581 | 0.069565 | 0.69576
570 | 9.5 | feeder2_383 | 0.070058 | 0.70196 | 0.070014 | 0.70191
570 | 9.5 | feeder2_385 | 0.078826 | 0.77812 | 0.078773 | 0.77805
570 | 9.5 | feeder2_621 | 0.075725 | 0.76473 | 0.075679 | 0.76466
570 | 9.5 | feeder2_611 | 0.072004 | 0.70206 | 0.071962 | 0.70201
570 | 9.5 | feeder2_405 | 0.070067 | 0.70234 | 0.070022 | 0.70229
570 | 9.5 | feeder2_461 | 0.084536 | 0.82087 | 0.084486 | 0.82078
570 | 9.5 | feeder2_594 | 0.081153 | 0.78041 | 0.081102 | 0.78033
570 | 9.5 | feeder2_732 | 0.070154 | 0.70243 | 0.070113 | 0.70238
570 | 9.5 | feeder2_417 | 0.070137 | 0.70516 | 0.070095 | 0.70511
570 | 9.5 | feeder2_663 | 0.06974 | 0.70474 | 0.069691 | 0.7047
570 | 9.5 | feeder2_444 | 0.07023 | 0.70744 | 0.070189 | 0.70739
570 | 9.5 | feeder2_759 | 0.070303 | 0.70751 | 0.070259 | 0.70747
570 | 9.5 | feeder2_842 | 0.068559 | 0.70569 | 0.06851 | 0.70565
570 | 9.5 | feeder2_459 | 0.070289 | 0.70834 | 0.070242 | 0.70829
570 | 9.5 | feeder2_702 | 0.069397 | 0.71238 | 0.069354 | 0.71233
570 | 9.5 | feeder2_493 | 0.070481 | 0.71025 | 0.070439 | 0.7102
570 | 9.5 | feeder2_651 | 0.084485 | 0.82082 | 0.084434 | 0.82072
570 | 9.5 | feeder2_684 | 0.089385 | 0.85611 | 0.08933 | 0.85601
570 | 9.5 | feeder2_674 | 0.072518 | 0.71199 | 0.072476 | 0.71194
570 | 9.5 | feeder2_696 | 0.069665 | 0.70725 | 0.069623 | 0.7072
570 | 9.5 | feeder2_681 | 0.07256 | 0.71203 | 0.07252 | 0.71198
570 | 9.5 | feeder2_682 | 0.081592 | 0.71922 | 0.081551 | 0.71917
570 | 9.5 | feeder2_728 | 0.089725 | 0.8584 | 0.089668 | 0.8583
570 | 9.5 | feeder2_724 | 0.093915 | 0.88727 | 0.093859 | 0.88715
570 | 9.5 | feeder2_703 | 0.068888 | 0.70644 | 0.068842 | 0.70639
570 | 9.5 | feeder2_704 | 0.06884 | 0.70636 | 0.068793 | 0.70631
570 | 9.5 | feeder2_754 | 0.093626 | 0.88874 | 0.093563 | 0.88863
570 | 9.5 | feeder2_747 | 0.095753 | 0.89933 | 0.095695 | 0.89921
570 | 9.5 | feeder2_828 | 0.090067 | 0.8588 | 0.09001 | 0.8587
570 | 9.5 | feeder2_763 | 0.090202 | 0.8611 | 0.090146 | 0.861
570 | 9.5 | feeder2_836 | 0.09371 | 0.89787 | 0.093651 | 0.89774
570 | 9.5 | feeder2_758 | 0.09762 | 0.91051 | 0.097563 | 0.91038
570 | 9.5 | feeder2_788 | 0.097037 | 0.91339 | 0.096982 | 0.91326
570 | 9.5 | feeder2_812 | 0.1032 | 0.94145 | 0.10314 | 0.94131
570 | 9.5 | feeder2_947 | 0.090326 | 0.8612 | 0.090268 | 0.8611
570 | 9.5 | feeder2_868 | 0.090655 | 0.86249 | 0.090602 | 0.86238
570 | 9.5 | feeder2_785 | 0.090294 | 0.86179 | 0.090238 | 0.86169
570 | 9.5 | feeder2_1176 | 0.089093 | 0.86053 | 0.08904 | 0.86043
570 | 9.5 | feeder2_846 | 0.09171 | 0.86194 | 0.091658 | 0.86184
570 | 9.5 | feeder2_911 | 0.09033 | 0.8635 | 0.090277 | 0.8634
570 | 9.5 | feeder2_1107 | 0.11025 | 0.9704 | 0.11018 | 0.97025
570 | 9.5 | feeder2_920 | 0.10285 | 0.94227 | 0.10278 | 0.94213
570 | 9.5 | feeder2_926 | 0.10232 | 0.94348 | 0.10226 | 0.94334
570 | 9.5 | feeder2_1239 | 0.10284 | 0.94229 | 0.10278 | 0.94215
570 | 9.5 | feeder2_933 | 0.10209 | 0.94401 | 0.10202 | 0.94387
570 | 9.5 | feeder2_1146 | 0.10235 | 0.94353 | 0.10229 | 0.94339
570 | 9.5 | feeder2_1124 | 0.10204 | 0.94396 | 0.10197 | 0.94382
570 | 9.5 | feeder2_942 | 0.1015 | 0.94543 | 0.10143 | 0.94529
570 | 9.5 | feeder2_952 | 0.10001 | 0.94722 | 0.099945 | 0.94707
570 | 9.5 | feeder2_965 | 0.10158 | 0.94548 | 0.10151 | 0.94533
570 | 9.5 | feeder2_961 | 0.099845 | 0.94731 | 0.099779 | 0.94716
570 | 9.5 | feeder2_963 | 0.10002 | 0.94724 | 0.099947 | 0.94709
570 | 9.5 | feeder2_973 | 0.099183 | 0.94498 | 0.099114 | 0.94482
570 | 9.5 | feeder2_1128 | 0.099454 | 0.95225 | 0.099387 | 0.9521
570 | 9.5 | feeder2_1113 | 0.10005 | 0.94727 | 0.099983 | 0.94712
570 | 9.5 | feeder2_1143 | 0.10013 | 0.94872 | 0.10007 | 0.94857
570 | 9.5 | feeder2_1238 | 0.10236 | 0.94877 | 0.1023 | 0.94862
570 | 9.5 | feeder2_979 | 0.10164 | 0.94528 | 0.10157 | 0.94514
570 | 9.5 | feeder2_1236 | 0.098285 | 0.94201 | 0.098213 | 0.94186
570 | 9.5 | feeder2_989 | 0.099182 | 0.94497 | 0.099111 | 0.94482
570 | 9.5 | feeder2_1196 | 0.10338 | 0.94431 | 0.10331 | 0.94417
570 | 9.5 | feeder2_1158 | 0.098638 | 0.9444 | 0.098571 | 0.94425
570 | 9.5 | feeder2_1122 | 0.11346 | 0.98352 | 0.1134 | 0.98337
570 | 9.5 | feeder2_1258 | 0.1079 | 0.96852 | 0.10784 | 0.96837
570 | 9.5 | feeder2_1303 | 0.11458 | 0.9863 | 0.11452 | 0.98615
570 | 9.5 | feeder2_1138 | 0.11582 | 0.99297 | 0.11575 | 0.99282
570 | 9.5 | feeder2_1304 | 0.11752 | 0.99267 | 0.11746 | 0.99252
570 | 9.5 | feeder2_1212 | 0.12075 | 1.0132 | 0.12069 | 1.013
570 | 9.5 | feeder2_1311 | 0.12084 | 1.0133 | 0.12078 | 1.0131
570 | 9.5 | feeder2_1290 | 0.12687 | 1.0384 | 0.12681 | 1.0382
570 | 9.5 | feeder2_1325 | 0.097446 | 0.94043 | 0.09737 | 0.94027
570 | 9.5 | feeder2_1248 | 0.098274 | 0.942 | 0.098201 | 0.94185
570 | 9.5 | feeder2_1249 | 0.10238 | 0.94878 | 0.10231 | 0.94864
570 | 9.5 | feeder2_1250 | 0.10293 | 0.95104 | 0.10287 | 0.95089
570 | 9.5 | feeder2_1366 | 0.09699 | 0.94066 | 0.096916 | 0.94051
570 | 9.5 | feeder2_1266 | 0.10632 | 0.96712 | 0.10625 | 0.96698
570 | 9.5 | feeder2_1372 | 0.12743 | 1.0388 | 0.12736 | 1.0386
570 | 9.5 | feeder2_1363 | 0.13328 | 1.0653 | 0.13322 | 1.0651
570 | 9.5 | feeder2_1446 | 0.097498 | 0.94047 | 0.097427 | 0.9403
570 | 9.5 | feeder2_1502 | 0.096502 | 0.93862 | 0.096427 | 0.93845
570 | 9.5 | feeder2_1428 | 0.13353 | 1.0654 | 0.13347 | 1.0652
570 | 9.5 | feeder2_1380 | 0.14116 | 1.0981 | 0.1411 | 1.0979
570 | 9.5 | feeder2_1550 | 0.14262 | 1.099 | 0.14256 | 1.0988
570 | 9.5 | feeder2_1386 | 0.14485 | 1.1138 | 0.14479 | 1.1137
570 | 9.5 | feeder2_1551 | 0.14752 | 1.1119 | 0.14746 | 1.1118
570 | 9.5 | feeder2_1400 | 0.14653 | 1.1218 | 0.14647 | 1.1216
570 | 9.5 | feeder2_1552 | 0.14667 | 1.122 | 0.14662 | 1.1218
570 | 9.5 | feeder2_1408 | 0.15005 | 1.1381 | 0.14999 | 1.1379
570 | 9.5 | feeder2_1553 | 0.15006 | 1.1381 | 0.15001 | 1.1379
570 | 9.5 | feeder2_1416 | 0.1519 | 1.1466 | 0.15184 | 1.1464
570 | 9.5 | feeder2_1530 | 0.17426 | 1.1801 | 0.17421 | 1.1799
570 | 9.5 | feeder2_1425 | 0.15175 | 1.1463 | 0.15169 | 1.1461
570 | 9.5 | feeder2_1589 | 0.15176 | 1.1463 | 0.1517 | 1.1461
570 | 9.5 | feeder2_1435 | 0.15172 | 1.1462 | 0.15166 | 1.1461
570 | 9.5 | feeder2_1621 | 0.15053 | 1.1457 | 0.15047 | 1.1455
570 | 9.5 | feeder2_1564 | 0.15171 | 1.1463 | 0.15165 | 1.1461
570 | 9.5 | feeder2_1704 | 0.094823 | 0.93754 | 0.094744 | 0.93737
570 | 9.5 | feeder2_1525 | 0.09644 | 0.93863 | 0.096361 | 0.93845
570 | 9.5 | feeder2_1716 | 0.091738 | 0.93512 | 0.091658 | 0.93494
570 | 9.5 | feeder2_1537 | 0.096556 | 0.93925 | 0.096476 | 0.93907
570 | 9.5 | feeder2_1645 | 0.097393 | 0.93914 | 0.097311 | 0.93896
570 | 9.5 | feeder2_1561 | 0.096656 | 0.93995 | 0.096572 | 0.93977
570 | 9.5 | feeder2_1657 | 0.097047 | 0.94127 | 0.096968 | 0.94108
570 | 9.5 | feeder2_1570 | 0.096648 | 0.93995 | 0.096572 | 0.93976
570 | 9.5 | feeder2_1756 | 0.096818 | 0.94009 | 0.096736 | 0.93991
570 | 9.5 | feeder2_1588 | 0.096638 | 0.93994 | 0.096561 | 0.93976
570 | 9.5 | feeder2_1628 | 0.096677 | 0.93997 | 0.096601 | 0.93979
570 | 9.5 | feeder2_1598 | 0.096622 | 0.93993 | 0.096544 | 0.93974
570 | 9.5 | feeder2_1816 | 0.09299 | 0.93598 | 0.09291 | 0.93579
570 | 9.5 | feeder2_1765 | 0.096439 | 0.93972 | 0.096359 | 0.93954
570 | 9.5 | feeder2_1641 | 0.096737 | 0.94116 | 0.096655 | 0.94097
570 | 9.5 | feeder2_1689 | 0.096347 | 0.93899 | 0.096264 | 0.93879
570 | 9.5 | feeder2_1744 | 0.097193 | 0.94326 | 0.097116 | 0.94307
570 | 9.5 | feeder2_1817 | 0.096341 | 0.93903 | 0.096256 | 0.93884
570 | 9.5 | feeder2_1779 | 0.095428 | 0.93791 | 0.095344 | 0.93771
570 | 9.5 | feeder2_1800 | 0.097914 | 0.93808 | 0.097827 | 0.93788
570 | 9.5 | feeder2_1818 | 0.09069 | 0.93336 | 0.090593 | 0.93315
570 | 9.5 | feeder2_1753 | 0.098998 | 0.94717 | 0.098918 | 0.94698
570 | 9.5 | feeder2_1754 | 0.097148 | 0.94387 | 0.097065 | 0.94368
600 | 10 | secondary | 0.045772 | 0.061029 | 0.045776 | 0.061036
600 | 10 | feeder2_44 | 0.085297 | 0.31874 | 0.08531 | 0.31877
600 | 10 | feeder2_45 | 0.086785 | 0.32874 | 0.086797 | 0.32878
600 | 10 | feeder2_46 | 0.085326 | 0.31862 | 0.085337 | 0.31866
600 | 10 | feeder2_51 | 0.089381 | 0.34615 | 0.089394 | 0.34619
600 | 10 | feeder2_48 | 0.086602 | 0.32868 | 0.086614 | 0.32872
600 | 10 | feeder2_52 | 0.089546 | 0.34638 | 0.089559 | 0.34642
600 | 10 | feeder2_68 | 0.096713 | 0.39516 | 0.096727 | 0.3952
600 | 10 | feeder2_69 | 0.11708 | 0.36102 | 0.1171 | 0.36106
600 | 10 | feeder2_71 | 0.097855 | 0.40327 | 0.097868 | 0.40331
600 | 10 | feeder2_72 | 0.042942 | 0.39205 | 0.042952 | 0.3921
600 | 10 | feeder2_73 | 0.10255 | 0.43158 | 0.10256 | 0.43163
600 | 10 | feeder2_74 | 0.1228 | 0.45868 | 0.12281 | 0.45873
600 | 10 | feeder2_77 | 0.10569 | 0.45158 | 0.10571 | 0.45162
600 | 10 | feeder2_79 | 0.11137 | 0.44312 | 0.11138 | 0.44317
600 | 10 | feeder2_81 | 0.11056 | 0.48629 | 0.11057 | 0.48634
600 | 10 | feeder2_82 | 0.1105 | 0.48627 | 0.11052 | 0.48632
600 | 10 | feeder2_116 | 0.13274 | 0.64211 | 0.13276 | 0.64218
600 | 10 | feeder2_119 | 0.13279 | 0.64218 | 0.13281 | 0.64224
600 | 10 | feeder2_120 | 0.14106 | 0.69982 | 0.14107 | 0.69989
600 | 10 | feeder2_248 | 0.14119 | 0.70075 | 0.14121 | 0.70083
600 | 10 | feeder2_124 | 0.1461 | 0.73489 | 0.14612 | 0.73497
600 | 10 | feeder2_282 | 0.14356 | 0.7339 | 0.14358 | 0.73397
600 | 10 | feeder2_275 | 0.15156 | 0.74166 | 0.15157 | 0.74174
600 | 10 | feeder2_151 | 0.15417 | 0.79225 | 0.15419 | 0.79233
600 | 10 | feeder2_295 | 0.15428 | 0.79095 | 0.1543 | 0.79103
600 | 10 | feeder2_311 | 0.15417 | 0.79218 | 0.15419 | 0.79226
600 | 10 | feeder2_201 | 0.16798 | 0.88958 | 0.168 | 0.88966
600 | 10 | feeder2_314 | 0.16791 | 0.88954 | 0.16793 | 0.88963
600 | 10 | feeder2_342 | 0.18772 | 1.0278 | 0.18775 | 1.0279
600 | 10 | feeder2_368 | 0.18956 | 1.0357 | 0.18959 | 1.0358
600 | 10 | feeder2_347 | 0.19475 | 1.081 | 0.19477 | 1.0811
600 | 10 | feeder2_353 | 0.19826 | 1.1075 | 0.19828 | 1.1076
600 | 10 | feeder2_518 | 0.19468 | 1.081 | 0.1947 | 1.0811
600 | 10 | feeder2_365 | 0.20197 | 1.136 | 0.202 | 1.1361
600 | 10 | feeder2_653 | 0.19963 | 1.1091 | 0.19966 | 1.1092
600 | 10 | feeder2_377 | 0.20396 | 1.1519 | 0.20398 | 1.152
600 | 10 | feeder2_622 | 0.20328 | 1.1343 | 0.20331 | 1.1345
600 | 10 | feeder2_451 | 0.18786 | 1.0365 | 0.18789 | 1.0366
600 | 10 | feeder2_383 | 0.19295 | 1.048 | 0.19297 | 1.0481
600 | 10 | feeder2_385 | 0.20632 | 1.1707 | 0.20635 | 1.1708
600 | 10 | feeder2_621 | 0.20392 | 1.1506 | 0.20395 | 1.1507
600 | 10 | feeder2_611 | 0.1938 | 1.0495 | 0.19383 | 1.0496
600 | 10 | feeder2_405 | 0.19314 | 1.0487 | 0.19317 | 1.0488
600 | 10 | feeder2_461 | 0.21566 | 1.2456 | 0.21569 | 1.2458
600 | 10 | feeder2_594 | 0.20654 | 1.1713 | 0.20657 | 1.1714
600 | 10 | feeder2_732 | 0.19358 | 1.0503 | 0.1936 | 1.0504
600 | 10 | feeder2_417 | 0.1945 | 1.0535 | 0.19452 | 1.0536
600 | 10 | feeder2_663 | 0.1945 | 1.0527 | 0.19452 | 1.0528
600 | 10 | feeder2_444 | 0.19556 | 1.0574 | 0.19559 | 1.0575
600 | 10 | feeder2_759 | 0.19543 | 1.0573 | 0.19545 | 1.0574
600 | 10 | feeder2_842 | 0.19553 | 1.0559 | 0.19555 | 1.056
600 | 10 | feeder2_459 | 0.19595 | 1.0589 | 0.19598 | 1.059
600 | 10 | feeder2_702 | 0.19529 | 1.0586 | 0.19532 | 1.0587
600 | 10 | feeder2_493 | 0.19748 | 1.0645 | 0.19751 | 1.0646
600 | 10 | feeder2_651 | 0.21565 | 1.2456 | 0.21568 | 1.2457
600 | 10 | feeder2_684 | 0.22329 | 1.3067 | 0.22332 | 1.3068
600 | 10 | feeder2_674 | 0.20069 | 1.0683 | 0.20071 | 1.0684
600 | 10 | feeder2_696 | 0.19737 | 1.0638 | 0.19739 | 1.0639
600 | 10 | feeder2_681 | 0.20075 | 1.0684 | 0.20077 | 1.0685
600 | 10 | feeder2_682 | 0.21399 | 1.0841 | 0.21402 | 1.0842
600 | 10 | feeder2_728 | 0.22362 | 1.3082 | 0.22365 | 1.3083
600 | 10 | feeder2_724 | 0.23037 | 1.3658 | 0.2304 | 1.366
600 | 10 | feeder2_703 | 0.19736 | 1.0637 | 0.19739 | 1.0638
600 | 10 | feeder2_704 | 0.19736 | 1.0636 | 0.19739 | 1.0637
600 | 10 | feeder2_754 | 0.2303 | 1.3658 | 0.23033 | 1.366
600 | 10 | feeder2_747 | 0.23327 | 1.39 | 0.2333 | 1.3902
600 | 10 | feeder2_828 | 0.22454 | 1.3092 | 0.22457 | 1.3094
600 | 10 | feeder2_763 | 0.22369 | 1.3087 | 0.22372 | 1.3089
600 | 10 | feeder2_836 | 0.23326 | 1.3899 | 0.23329 | 1.3901
600 | 10 | feeder2_758 | 0.23577 | 1.4108 | 0.23581 | 1.411
600 | 10 | feeder2_788 | 0.23572 | 1.4108 | 0.23576 | 1.411
600 | 10 | feeder2_812 | 0.24348 | 1.475 | 0.24352 | 1.4751
600 | 10 | feeder2_947 | 0.22354 | 1.3087 | 0.22357 | 1.3088
600 | 10 | feeder2_868 | 0.22133 | 1.3088 | 0.22136 | 1.309
600 | 10 | feeder2_785 | 0.22415 | 1.3092 | 0.22418 | 1.3093
600 | 10 | feeder2_1176 | 0.22689 | 1.3047 | 0.22692 | 1.3049
600 | 10 | feeder2_846 | 0.22625 | 1.312 | 0.22628 | 1.3121
600 | 10 | feeder2_911 | 0.224 | 1.3087 | 0.22403 | 1.3088
600 | 10 | feeder2_1107 | 0.24767 | 1.4938 | 0.24771 | 1.494
600 | 10 | feeder2_920 | 0.24449 | 1.4877 | 0.24453 | 1.4879
600 | 10 | feeder2_926 | 0.24599 | 1.5067 | 0.24602 | 1.5069
600 | 10 | feeder2_1239 | 0.2445 | 1.4878 | 0.24454 | 1.488
600 | 10 | feeder2_933 | 0.24683 | 1.5147 | 0.24687 | 1.5148
600 | 10 | feeder2_1146 | 0.24512 | 1.5089 | 0.24516 | 1.509
600 | 10 | feeder2_1124 | 0.24751 | 1.5136 | 0.24755 | 1.5138
600 | 10 | feeder2_942 | 0.24893 | 1.5358 | 0.24897 | 1.536
600 | 10 | feeder2_952 | 0.2526 | 1.5655 | 0.25264 | 1.5656
600 | 10 | feeder2_965 | 0.24886 | 1.536 | 0.2489 | 1.5362
600 | 10 | feeder2_961 | 0.25308 | 1.5685 | 0.25312 | 1.5687
600 | 10 | feeder2_963 | 0.25258 | 1.5655 | 0.25262 | 1.5657
600 | 10 | feeder2_973 | 0.25418 | 1.5779 | 0.25422 | 1.5781
600 | 10 | feeder2_1128 | 0.25563 | 1.5807 | 0.25566 | 1.5809
600 | 10 | feeder2_1113 | 0.25095 | 1.5665 | 0.25098 | 1.5667
600 | 10 | feeder2_1143 | 0.2524 | 1.5645 | 0.25244 | 1.5647
600 | 10 | feeder2_1238 | 0.24356 | 1.5395 | 0.2436 | 1.5396
600 | 10 | feeder2_979 | 0.24886 | 1.536 | 0.2489 | 1.5362
600 | 10 | feeder2_1236 | 0.2559 | 1.5924 | 0.25594 | 1.5926
600 | 10 | feeder2_989 | 0.25418 | 1.5779 | 0.25422 | 1.5781
600 | 10 | feeder2_1196 | 0.24892 | 1.5361 | 0.24895 | 1.5362
600 | 10 | feeder2_1158 | 0.25413 | 1.5774 | 0.25417 | 1.5776
600 | 10 | feeder2_1122 | 0.24942 | 1.5018 | 0.24945 | 1.5019
600 | 10 | feeder2_1258 | 0.24757 | 1.4931 | 0.2476 | 1.4933
600 | 10 | feeder2_1303 | 0.24784 | 1.5011 | 0.24788 | 1.5012
600 | 10 | feeder2_1138 | 0.25086 | 1.5083 | 0.2509 | 1.5085
600 | 10 | feeder2_1304 | 0.2509 | 1.5084 | 0.25094 | 1.5085
600 | 10 | feeder2_1212 | 0.2539 | 1.5221 | 0.25394 | 1.5223
600 | 10 | feeder2_1311 | 0.25381 | 1.5221 | 0.25385 | 1.5223
600 | 10 | feeder2_1290 | 0.25767 | 1.5393 | 0.2577 | 1.5395
600 | 10 | feeder2_1325 | 0.25849 | 1.6133 | 0.25853 | 1.6135
600 | 10 | feeder2_1248 | 0.2559 | 1.5924 | 0.25594 | 1.5926
600 | 10 | feeder2_1249 | 0.24275 | 1.54 | 0.24279 | 1.5402
600 | 10 | feeder2_1250 | 0.24181 | 1.5406 | 0.24185 | 1.5408
600 | 10 | feeder2_1366 | 0.25589 | 1.5923 | 0.25593 | 1.5925
600 | 10 | feeder2_1266 | 0.24747 | 1.4924 | 0.24751 | 1.4925
600 | 10 | feeder2_1372 | 0.25706 | 1.5387 | 0.25709 | 1.5389
600 | 10 | feeder2_1363 | 0.26176 | 1.5586 | 0.26179 | 1.5587
600 | 10 | feeder2_1446 | 0.2571 | 1.6142 | 0.25714 | 1.6144
600 | 10 | feeder2_1502 | 0.26181 | 1.6358 | 0.26186 | 1.636
600 | 10 | feeder2_1428 | 0.26337 | 1.5604 | 0.26341 | 1.5606
600 | 10 | feeder2_1380 | 0.2661 | 1.579 | 0.26613 | 1.5792
600 | 10 | feeder2_1550 | 0.26605 | 1.579 | 0.26608 | 1.5791
600 | 10 | feeder2_1386 | 0.26822 | 1.589 | 0.26826 | 1.5891
600 | 10 | feeder2_1551 | 0.26833 | 1.5891 | 0.26837 | 1.5893
600 | 10 | feeder2_1400 | 0.26922 | 1.5937 | 0.26926 | 1.5939
600 | 10 | feeder2_1552 | 0.27027 | 1.5949 | 0.2703 | 1.595
600 | 10 | feeder2_1408 | 0.27117 | 1.6028 | 0.2712 | 1.603
600 | 10 | feeder2_1553 | 0.27176 | 1.604 | 0.27179 | 1.6042
600 | 10 | feeder2_1416 | 0.2721 | 1.6073 | 0.27214 | 1.6075
600 | 10 | feeder2_1530 | 0.26897 | 1.6063 | 0.269 | 1.6065
600 | 10 | feeder2_1425 | 0.27407 | 1.6165 | 0.2741 | 1.6167
600 | 10 | feeder2_1589 | 0.29034 | 1.6355 | 0.29037 | 1.6356
600 | 10 | feeder2_1435 | 0.27408 | 1.6165 | 0.27412 | 1.6167
600 | 10 | feeder2_1621 | 0.27385 | 1.6152 | 0.27389 | 1.6153
600 | 10 | feeder2_1564 | 0.27451 | 1.6183 | 0.27455 | 1.6184
600 | 10 | feeder2_1704 | 0.2618 | 1.6358 | 0.26185 | 1.636
600 | 10 | feeder2_1525 | 0.26267 | 1.6416 | 0.26271 | 1.6418
600 | 10 | feeder2_1716 | 0.26248 | 1.64 | 0.26252 | 1.6402
600 | 10 | feeder2_1537 | 0.26367 | 1.6484 | 0.26371 | 1.6486
600 | 10 | feeder2_1645 | 0.27717 | 1.664 | 0.27721 | 1.6642
600 | 10 | feeder2_1561 | 0.26296 | 1.6472 | 0.26301 | 1.6474
600 | 10 | feeder2_1657 | 0.26172 | 1.6476 | 0.26176 | 1.6478
600 | 10 | feeder2_1570 | 0.26272 | 1.6467 | 0.26276 | 1.6469
600 | 10 | feeder2_1756 | 0.26254 | 1.6466 | 0.26258 | 1.6468
600 | 10 | feeder2_1588 | 0.26248 | 1.6461 | 0.26253 | 1.6464
600 | 10 | feeder2_1628 | 0.26244 | 1.6461 | 0.26249 | 1.6463
600 | 10 | feeder2_1598 | 0.26219 | 1.6455 | 0.26224 | 1.6457
600 | 10 | feeder2_1816 | 0.2618 | 1.6421 | 0.26185 | 1.6423
600 | 10 | feeder2_1765 | 0.26217 | 1.6454 | 0.26221 | 1.6456
600 | 10 | feeder2_1641 | 0.26098 | 1.6434 | 0.26102 | 1.6436
600 | 10 | feeder2_1689 | 0.26011 | 1.6427 | 0.26016 | 1.6429
600 | 10 | feeder2_1744 | 0.25991 | 1.6428 | 0.25995 | 1.6431
600 | 10 | feeder2_1817 | 0.26031 | 1.6434 | 0.26036 | 1.6436
600 | 10 | feeder2_1779 | 0.26011 | 1.6426 | 0.26016 | 1.6429
600 | 10 | feeder2_1800 | 0.26016 | 1.6427 | 0.26021 | 1.643
600 | 10 | feeder2_1818 | 0.25053 | 1.6327 | 0.25059 | 1.6329
600 | 10 | feeder2_1753 | 0.25766 | 1.6418 | 0.25771 | 1.642
600 | 10 | feeder2_1754 | 0.25965 | 1.6427 | 0.2597 | 1.6429
630 | 10.5 | secondary | 0.015416 | 0.011613 | 0.015423 | 0.011618
630 | 10.5 | feeder2_44 | 0.028708 | 0.060608 | 0.028725 | 0.060635
630 | 10.5 | feeder2_45 | 0.029216 | 0.062276 | 0.029228 | 0.06231
630 | 10.5 | feeder2_46 | 0.026926 | 0.063202 | 0.026937 | 0.063232
630 | 10.5 | feeder2_51 | 0.030098 | 0.065172 | 0.030113 | 0.0652
630 | 10.5 | feeder2_48 | 0.029351 | 0.062254 | 0.029366 | 0.062286
630 | 10.5 | feeder2_52 | 0.029889 | 0.064984 | 0.029902 | 0.065017
630 | 10.5 | feeder2_68 | 0.032605 | 0.073403 | 0.032618 | 0.073447
630 | 10.5 | feeder2_69 | 0.06236 | 0.12197 | 0.062382 | 0.12202
630 | 10.5 | feeder2_71 | 0.032566 | 0.07221 | 0.032581 | 0.072251
630 | 10.5 | feeder2_72 | 0.088321 | 0.090132 | 0.088328 | 0.090096
630 | 10.5 | feeder2_73 | 0.031991 | 0.068985 | 0.032004 | 0.06903
630 | 10.5 | feeder2_74 | 0.015231 | 0.056401 | 0.015237 | 0.056469
630 | 10.5 | feeder2_77 | 0.032184 | 0.068898 | 0.0322 | 0.068946
630 | 10.5 | feeder2_79 | 0.031499 | 0.07159 | 0.031516 | 0.071639
630 | 10.5 | feeder2_81 | 0.032444 | 0.067792 | 0.03246 | 0.067851
630 | 10.5 | feeder2_82 | 0.032486 | 0.067779 | 0.032501 | 0.067835
630 | 10.5 | feeder2_116 | 0.033686 | 0.064094 | 0.033705 | 0.06419
630 | 10.5 | feeder2_119 | 0.033273 | 0.063839 | 0.033291 | 0.063936
630 | 10.5 | feeder2_120 | 0.034225 | 0.063445 | 0.034244 | 0.063553
630 | 10.5 | feeder2_248 | 0.034107 | 0.063371 | 0.034126 | 0.063482
630 | 10.5 | feeder2_124 | 0.034573 | 0.063226 | 0.034597 | 0.06334
630 | 10.5 | feeder2_282 | 0.035887 | 0.062152 | 0.035911 | 0.062265
630 | 10.5 | feeder2_275 | 0.033943 | 0.063695 | 0.033964 | 0.063813
630 | 10.5 | feeder2_151 | 0.035321 | 0.063483 | 0.035346 | 0.063615
630 | 10.5 | feeder2_295 | 0.03593 | 0.064971 | 0.035957 | 0.065101
630 | 10.5 | feeder2_311 | 0.035375 | 0.063602 | 0.035402 | 0.063733
630 | 10.5 | feeder2_201 | 0.036221 | 0.062419 | 0.036246 | 0.06258
630 | 10.5 | feeder2_314 | 0.036264 | 0.062362 | 0.036294 | 0.062522
630 | 10.5 | feeder2_342 | 0.037603 | 0.062994 | 0.037636 | 0.063193
630 | 10.5 | feeder2_368 | 0.036575 | 0.06042 | 0.036605 | 0.060619
630 | 10.5 | feeder2_347 | 0.039965 | 0.068832 | 0.039996 | 0.069046
630 | 10.5 | feeder2_353 | 0.041165 | 0.071954 | 0.041196 | 0.072177
630 | 10.5 | feeder2_518 | 0.040067 | 0.068635 | 0.040098 | 0.068849
630 | 10.5 | feeder2_365 | 0.042609 | 0.075539 | 0.042642 | 0.075771
630 | 10.5 | feeder2_653 | 0.040132 | 0.071948 | 0.040166 | 0.072169
630 | 10.5 | feeder2_377 | 0.043396 | 0.077497 | 0.04343 | 0.077732
630 | 10.5 | feeder2_622 | 0.042631 | 0.075573 | 0.042665 | 0.075803
630 | 10.5 | feeder2_451 | 0.036741 | 0.060119 | 0.036768 | 0.06032
630 | 10.5 | feeder2_383 | 0.034924 | 0.056494 | 0.03495 | 0.056696
630 | 10.5 | feeder2_385 | 0.044206 | 0.079288 | 0.044241 | 0.079529
630 | 10.5 | feeder2_621 | 0.044279 | 0.078848 | 0.044316 | 0.079083
630 | 10.5 | feeder2_611 | 0.034169 | 0.056434 | 0.034199 | 0.056633
630 | 10.5 | feeder2_405 | 0.034832 | 0.056256 | 0.034862 | 0.056457
630 | 10.5 | feeder2_461 | 0.047548 | 0.086781 | 0.047587 | 0.087039
630 | 10.5 | feeder2_594 | 0.04413 | 0.079285 | 0.044164 | 0.079525
630 | 10.5 | feeder2_732 | 0.033411 | 0.058346 | 0.03344 | 0.058545
630 | 10.5 | feeder2_417 | 0.034278 | 0.054052 | 0.034309 | 0.054253
630 | 10.5 | feeder2_663 | 0.034697 | 0.056282 | 0.034731 | 0.056479
630 | 10.5 | feeder2_444 | 0.033755 | 0.051651 | 0.033783 | 0.051852
630 | 10.5 | feeder2_759 | 0.033838 | 0.051517 | 0.033868 | 0.051717
630 | 10.5 | feeder2_842 | 0.03526 | 0.054685 | 0.035289 | 0.054885
630 | 10.5 | feeder2_459 | 0.033536 | 0.050637 | 0.033565 | 0.050835
630 | 10.5 | feeder2_702 | 0.041389 | 0.041038 | 0.041411 | 0.041228
630 | 10.5 | feeder2_493 | 0.032337 | 0.050732 | 0.032362 | 0.050936
630 | 10.5 | feeder2_651 | 0.047581 | 0.086825 | 0.047618 | 0.087083
630 | 10.5 | feeder2_684 | 0.05029 | 0.09302 | 0.050327 | 0.093293
630 | 10.5 | feeder2_674 | 0.029536 | 0.051068 | 0.029567 | 0.051274
630 | 10.5 | feeder2_696 | 0.032381 | 0.051485 | 0.03241 | 0.051686
630 | 10.5 | feeder2_681 | 0.029469 | 0.051068 | 0.029499 | 0.051273
630 | 10.5 | feeder2_682 | 0.018174 | 0.054174 | 0.018199 | 0.05438
630 | 10.5 | feeder2_728 | 0.049915 | 0.092106 | 0.049955 | 0.092379
630 | 10.5 | feeder2_724 | 0.053854 | 0.10164 | 0.053897 | 0.10193
630 | 10.5 | feeder2_703 | 0.032464 | 0.051644 | 0.032494 | 0.051847
630 | 10.5 | feeder2_704 | 0.032222 | 0.051686 | 0.032251 | 0.051888
630 | 10.5 | feeder2_754 | 0.053878 | 0.10156 | 0.053921 | 0.10185
630 | 10.5 | feeder2_747 | 0.055322 | 0.10521 | 0.05537 | 0.1055
630 | 10.5 | feeder2_828 | 0.049181 | 0.092236 | 0.04922 | 0.092508
630 | 10.5 | feeder2_763 | 0.049645 | 0.090689 | 0.049689 | 0.090961
630 | 10.5 | feeder2_836 | 0.055395 | 0.1053 | 0.055442 | 0.10559
630 | 10.5 | feeder2_758 | 0.05658 | 0.10823 | 0.056623 | 0.10853
630 | 10.5 | feeder2_788 | 0.056596 | 0.10818 | 0.05664 | 0.10848
630 | 10.5 | feeder2_812 | 0.060474 | 0.11761 | 0.060522 | 0.11792
630 | 10.5 | feeder2_947 | 0.049826 | 0.090196 | 0.04987 | 0.090466
630 | 10.5 | feeder2_868 | 0.050609 | 0.089014 | 0.050653 | 0.089283
630 | 10.5 | feeder2_785 | 0.049387 | 0.091121 | 0.049427 | 0.091394
630 | 10.5 | feeder2_1176 | 0.050126 | 0.092051 | 0.050164 | 0.092323
630 | 10.5 | feeder2_846 | 0.047379 | 0.092029 | 0.047423 | 0.0923
630 | 10.5 | feeder2_911 | 0.049392 | 0.090738 | 0.049431 | 0.091012
630 | 10.5 | feeder2_1107 | 0.062213 | 0.11262 | 0.062258 | 0.11294
630 | 10.5 | feeder2_920 | 0.06112 | 0.12169 | 0.061167 | 0.12201
630 | 10.5 | feeder2_926 | 0.062129 | 0.12784 | 0.062182 | 0.12817
630 | 10.5 | feeder2_1239 | 0.061113 | 0.12169 | 0.061166 | 0.12201
630 | 10.5 | feeder2_933 | 0.062559 | 0.13083 | 0.062609 | 0.13115
630 | 10.5 | feeder2_1146 | 0.06228 | 0.12673 | 0.062328 | 0.12705
630 | 10.5 | feeder2_1124 | 0.062738 | 0.13102 | 0.062791 | 0.13135
630 | 10.5 | feeder2_942 | 0.063646 | 0.13823 | 0.063695 | 0.13856
630 | 10.5 | feeder2_952 | 0.065255 | 0.15017 | 0.065309 | 0.15051
630 | 10.5 | feeder2_965 | 0.06366 | 0.13811 | 0.063715 | 0.13845
630 | 10.5 | feeder2_961 | 0.065437 | 0.15166 | 0.065489 | 0.15201
630 | 10.5 | feeder2_963 | 0.065255 | 0.15013 | 0.065307 | 0.15047
630 | 10.5 | feeder2_973 | 0.067191 | 0.15834 | 0.067249 | 0.15869
630 | 10.5 | feeder2_1128 | 0.064117 | 0.15421 | 0.064175 | 0.15455
630 | 10.5 | feeder2_1113 | 0.065703 | 0.14969 | 0.065757 | 0.15004
630 | 10.5 | feeder2_1143 | 0.065094 | 0.14853 | 0.065147 | 0.14887
630 | 10.5 | feeder2_1238 | 0.065574 | 0.13629 | 0.065627 | 0.13663
630 | 10.5 | feeder2_979 | 0.063658 | 0.13811 | 0.063711 | 0.13845
630 | 10.5 | feeder2_1236 | 0.069604 | 0.1675 | 0.06966 | 0.16787
630 | 10.5 | feeder2_989 | 0.067193 | 0.15834 | 0.067253 | 0.1587
630 | 10.5 | feeder2_1196 | 0.063606 | 0.13812 | 0.063658 | 0.13845
630 | 10.5 | feeder2_1158 | 0.068175 | 0.15929 | 0.068234 | 0.15965
630 | 10.5 | feeder2_1122 | 0.061767 | 0.1057 | 0.061816 | 0.10602
630 | 10.5 | feeder2_1258 | 0.066667 | 0.1185 | 0.066716 | 0.11882
630 | 10.5 | feeder2_1303 | 0.067323 | 0.094082 | 0.067366 | 0.094395
630 | 10.5 | feeder2_1138 | 0.061577 | 0.10428 | 0.061623 | 0.1046
630 | 10.5 | feeder2_1304 | 0.061276 | 0.10432 | 0.061318 | 0.10464
630 | 10.5 | feeder2_1212 | 0.061224 | 0.10148 | 0.061271 | 0.10179
630 | 10.5 | feeder2_1311 | 0.062826 | 0.10001 | 0.062873 | 0.10033
630 | 10.5 | feeder2_1290 | 0.06059 | 0.099663 | 0.060637 | 0.099979
630 | 10.5 | feeder2_1325 | 0.069792 | 0.16799 | 0.069851 | 0.16836
630 | 10.5 | feeder2_1248 | 0.069659 | 0.16756 | 0.069717 | 0.16792
630 | 10.5 | feeder2_1249 | 0.06613 | 0.13579 | 0.06618 | 0.13613
630 | 10.5 | feeder2_1250 | 0.065583 | 0.13624 | 0.065637 | 0.13657
630 | 10.5 | feeder2_1366 | 0.069769 | 0.16766 | 0.069829 | 0.16803
630 | 10.5 | feeder2_1266 | 0.071515 | 0.12441 | 0.071562 | 0.12472
630 | 10.5 | feeder2_1372 | 0.061805 | 0.098192 | 0.061847 | 0.098506
630 | 10.5 | feeder2_1363 | 0.059722 | 0.10026 | 0.059765 | 0.10057
630 | 10.5 | feeder2_1446 | 0.070855 | 0.16694 | 0.070916 | 0.16732
630 | 10.5 | feeder2_1502 | 0.069897 | 0.17007 | 0.069959 | 0.17046
630 | 10.5 | feeder2_1428 | 0.057453 | 0.10205 | 0.057499 | 0.10236
630 | 10.5 | feeder2_1380 | 0.059508 | 0.098759 | 0.059556 | 0.099069
630 | 10.5 | feeder2_1550 | 0.061374 | 0.097333 | 0.06142 | 0.097644
630 | 10.5 | feeder2_1386 | 0.05925 | 0.098874 | 0.059295 | 0.099184
630 | 10.5 | feeder2_1551 | 0.059136 | 0.09891 | 0.05918 | 0.09922
630 | 10.5 | feeder2_1400 | 0.059132 | 0.098931 | 0.059176 | 0.099237
630 | 10.5 | feeder2_1552 | 0.057316 | 0.09963 | 0.057363 | 0.099937
630 | 10.5 | feeder2_1408 | 0.059053 | 0.098789 | 0.059099 | 0.099098
630 | 10.5 | feeder2_1553 | 0.058927 | 0.098828 | 0.058972 | 0.099134
630 | 10.5 | feeder2_1416 | 0.059017 | 0.09871 | 0.059066 | 0.099017
630 | 10.5 | feeder2_1530 | 0.061147 | 0.095373 | 0.061187 | 0.095682
630 | 10.5 | feeder2_1425 | 0.058887 | 0.10034 | 0.058932 | 0.10064
630 | 10.5 | feeder2_1589 | 0.056873 | 0.10254 | 0.05692 | 0.10284
630 | 10.5 | feeder2_1435 | 0.058911 | 0.10046 | 0.058953 | 0.10077
630 | 10.5 | feeder2_1621 | 0.059968 | 0.10163 | 0.060013 | 0.10194
630 | 10.5 | feeder2_1564 | 0.058823 | 0.10057 | 0.05887 | 0.10088
630 | 10.5 | feeder2_1704 | 0.069938 | 0.17011 | 0.070001 | 0.1705
630 | 10.5 | feeder2_1525 | 0.069932 | 0.1706 | 0.069998 | 0.17099
630 | 10.5 | feeder2_1716 | 0.071165 | 0.17171 | 0.071224 | 0.17211
630 | 10.5 | feeder2_1537 | 0.069928 | 0.17102 | 0.069994 | 0.17142
630 | 10.5 | feeder2_1645 | 0.05818 | 0.17535 | 0.058245 | 0.17574
630 | 10.5 | feeder2_1561 | 0.070813 | 0.17022 | 0.070881 | 0.17062
630 | 10.5 | feeder2_1657 | 0.070841 | 0.16973 | 0.070902 | 0.17014
630 | 10.5 | feeder2_1570 | 0.071209 | 0.17007 | 0.07127 | 0.17047
630 | 10.5 | feeder2_1756 | 0.073845 | 0.16734 | 0.073908 | 0.16774
630 | 10.5 | feeder2_1588 | 0.07156 | 0.17016 | 0.071622 | 0.17056
630 | 10.5 | feeder2_1628 | 0.07156 | 0.17011 | 0.071621 | 0.17051
630 | 10.5 | feeder2_1598 | 0.072007 | 0.17034 | 0.072076 | 0.17075
630 | 10.5 | feeder2_1816 | 0.11059 | 0.20714 | 0.11066 | 0.20755
630 | 10.5 | feeder2_1765 | 0.072176 | 0.17051 | 0.072239 | 0.17092
630 | 10.5 | feeder2_1641 | 0.071303 | 0.16019 | 0.07137 | 0.16061
630 | 10.5 | feeder2_1689 | 0.071588 | 0.16033 | 0.07166 | 0.16076
630 | 10.5 | feeder2_1744 | 0.072039 | 0.15464 | 0.072105 | 0.15506
630 | 10.5 | feeder2_1817 | 0.071578 | 0.16033 | 0.071645 | 0.16076
630 | 10.5 | feeder2_1779 | 0.071629 | 0.16035 | 0.0717 | 0.16078
630 | 10.5 | feeder2_1800 | 0.071539 | 0.16034 | 0.071608 | 0.16077
630 | 10.5 | feeder2_1818 | 0.071163 | 0.15939 | 0.071243 | 0.15984
630 | 10.5 | feeder2_1753 | 0.077025 | 0.13788 | 0.077086 | 0.13831
630 | 10.5 | feeder2_1754 | 0.072061 | 0.15451 | 0.072126 | 0.15494
660 | 11 | secondary | 0.0436 | 0.049966 | 0.043579 | 0.049925
660 | 11 | feeder2_44 | 0.081224 | 0.26087 | 0.081185 | 0.26066
660 | 11 | feeder2_45 | 0.082637 | 0.26904 | 0.082596 | 0.26883
660 | 11 | feeder2_46 | 0.081285 | 0.26103 | 0.081244 | 0.26083
660 | 11 | feeder2_51 | 0.085089 | 0.28328 | 0.085045 | 0.28306
660 | 11 | feeder2_48 | 0.083416 | 0.26867 | 0.083374 | 0.26846
660 | 11 | feeder2_52 | 0.083661 | 0.28365 | 0.083618 | 0.28342
660 | 11 | feeder2_68 | 0.092266 | 0.32345 | 0.092217 | 0.3232
660 | 11 | feeder2_69 | 0.092339 | 0.32363 | 0.092294 | 0.32338
660 | 11 | feeder2_71 | 0.09322 | 0.32877 | 0.09317 | 0.32852
660 | 11 | feeder2_72 | 0.093356 | 0.32873 | 0.093307 | 0.32847
660 | 11 | feeder2_73 | 0.09621 | 0.34543 | 0.096162 | 0.34516
660 | 11 | feeder2_74 | 0.093701 | 0.34427 | 0.093655 | 0.344
660 | 11 | feeder2_77 | 0.098891 | 0.35997 | 0.098846 | 0.35969
660 | 11 | feeder2_79 | 0.098455 | 0.37008 | 0.098405 | 0.3698
660 | 11 | feeder2_81 | 0.10278 | 0.37913 | 0.10273 | 0.37883
660 | 11 | feeder2_82 | 0.10281 | 0.37912 | 0.10276 | 0.37882
660 | 11 | feeder2_116 | 0.12024 | 0.46538 | 0.12018 | 0.465
660 | 11 | feeder2_119 | 0.11896 | 0.46513 | 0.1189 | 0.46475
660 | 11 | feeder2_120 | 0.12695 | 0.49773 | 0.12689 | 0.49732
660 | 11 | feeder2_248 | 0.12653 | 0.49737 | 0.12646 | 0.49696
660 | 11 | feeder2_124 | 0.13112 | 0.51781 | 0.13106 | 0.51738
660 | 11 | feeder2_282 | 0.13259 | 0.51759 | 0.13252 | 0.51717
660 | 11 | feeder2_275 | 0.12948 | 0.51791 | 0.12942 | 0.51747
660 | 11 | feeder2_151 | 0.13877 | 0.55296 | 0.13871 | 0.5525
660 | 11 | feeder2_295 | 0.13966 | 0.5547 | 0.13959 | 0.55425
660 | 11 | feeder2_311 | 0.13883 | 0.55306 | 0.13876 | 0.5526
660 | 11 | feeder2_201 | 0.151 | 0.60904 | 0.15092 | 0.60854
660 | 11 | feeder2_314 | 0.15238 | 0.60781 | 0.15231 | 0.6073
660 | 11 | feeder2_342 | 0.16787 | 0.69135 | 0.16779 | 0.69076
660 | 11 | feeder2_368 | 0.17361 | 0.7157 | 0.17353 | 0.71511
660 | 11 | feeder2_347 | 0.1668 | 0.68774 | 0.16671 | 0.68713
660 | 11 | feeder2_353 | 0.16619 | 0.687 | 0.16609 | 0.68638
660 | 11 | feeder2_518 | 0.16857 | 0.68665 | 0.16849 | 0.68603
660 | 11 | feeder2_365 | 0.16563 | 0.68704 | 0.16554 | 0.6864
660 | 11 | feeder2_653 | 0.16532 | 0.68622 | 0.16523 | 0.6856
660 | 11 | feeder2_377 | 0.16535 | 0.68682 | 0.16526 | 0.68617
660 | 11 | feeder2_622 | 0.16483 | 0.68859 | 0.16474 | 0.68795
660 | 11 | feeder2_451 | 0.1739 | 0.71568 | 0.17382 | 0.71509
660 | 11 | feeder2_383 | 0.18322 | 0.75567 | 0.18314 | 0.75508
660 | 11 | feeder2_385 | 0.16492 | 0.68621 | 0.16482 | 0.68555
660 | 11 | feeder2_621 | 0.16623 | 0.68852 | 0.16614 | 0.68787
660 | 11 | feeder2_611 | 0.1827 | 0.7552 | 0.18261 | 0.75461
660 | 11 | feeder2_405 | 0.18384 | 0.75822 | 0.18377 | 0.75762
660 | 11 | feeder2_461 | 0.16345 | 0.68607 | 0.16335 | 0.68538
660 | 11 | feeder2_594 | 0.16464 | 0.68595 | 0.16454 | 0.6853
660 | 11 | feeder2_732 | 0.18369 | 0.75809 | 0.18361 | 0.7575
660 | 11 | feeder2_417 | 0.18857 | 0.77751 | 0.18849 | 0.77692
660 | 11 | feeder2_663 | 0.22017 | 0.82819 | 0.2201 | 0.82759
660 | 11 | feeder2_444 | 0.1887 | 0.77736 | 0.18862 | 0.77676
660 | 11 | feeder2_759 | 0.19108 | 0.77517 | 0.191 | 0.77458
660 | 11 | feeder2_842 | 0.19051 | 0.78062 | 0.19043 | 0.78004
660 | 11 | feeder2_459 | 0.18866 | 0.77725 | 0.18858 | 0.77666
660 | 11 | feeder2_702 | 0.18913 | 0.77692 | 0.18905 | 0.77632
660 | 11 | feeder2_493 | 0.18848 | 0.77697 | 0.1884 | 0.77638
660 | 11 | feeder2_651 | 0.16347 | 0.68612 | 0.16337 | 0.68543
660 | 11 | feeder2_684 | 0.16247 | 0.68816 | 0.16236 | 0.68745
660 | 11 | feeder2_674 | 0.18801 | 0.77672 | 0.18793 | 0.77613
660 | 11 | feeder2_696 | 0.18858 | 0.77739 | 0.1885 | 0.7768
660 | 11 | feeder2_681 | 0.18785 | 0.77659 | 0.18777 | 0.776
660 | 11 | feeder2_682 | 0.18633 | 0.77592 | 0.18625 | 0.77532
660 | 11 | feeder2_728 | 0.16264 | 0.6916 | 0.16253 | 0.69088
660 | 11 | feeder2_724 | 0.16107 | 0.68449 | 0.16096 | 0.68377
660 | 11 | feeder2_703 | 0.18868 | 0.77756 | 0.1886 | 0.77697
660 | 11 | feeder2_704 | 0.18865 | 0.77752 | 0.18857 | 0.77693
660 | 11 | feeder2_754 | 0.16145 | 0.68458 | 0.16134 | 0.68385
660 | 11 | feeder2_747 | 0.1606 | 0.68356 | 0.16048 | 0.68283
660 | 11 | feeder2_828 | 0.1617 | 0.69065 | 0.16159 | 0.68993
660 | 11 | feeder2_763 | 0.16331 | 0.69813 | 0.1632 | 0.69742
660 | 11 | feeder2_836 | 0.15967 | 0.68516 | 0.15956 | 0.68442
660 | 11 | feeder2_758 | 0.16027 | 0.68233 | 0.16015 | 0.68159
660 | 11 | feeder2_788 | 0.16031 | 0.68235 | 0.16019 | 0.68161
660 | 11 | feeder2_812 | 0.15957 | 0.6802 | 0.15945 | 0.67945
660 | 11 | feeder2_947 | 0.16744 | 0.6965 | 0.16733 | 0.69579
660 | 11 | feeder2_868 | 0.1641 | 0.69836 | 0.16399 | 0.69765
660 | 11 | feeder2_785 | 0.16342 | 0.70211 | 0.16331 | 0.7014
660 | 11 | feeder2_1176 | 0.16339 | 0.72644 | 0.16328 | 0.72573
660 | 11 | feeder2_846 | 0.16193 | 0.70062 | 0.16182 | 0.69991
660 | 11 | feeder2_911 | 0.16343 | 0.70214 | 0.16332 | 0.70143
660 | 11 | feeder2_1107 | 0.16294 | 0.69276 | 0.16282 | 0.69201
660 | 11 | feeder2_920 | 0.15854 | 0.67658 | 0.15841 | 0.67583
660 | 11 | feeder2_926 | 0.15846 | 0.67829 | 0.15834 | 0.67754
660 | 11 | feeder2_1239 | 0.15687 | 0.66864 | 0.15674 | 0.66789
660 | 11 | feeder2_933 | 0.15845 | 0.67918 | 0.15832 | 0.67844
660 | 11 | feeder2_1146 | 0.15847 | 0.67835 | 0.15834 | 0.6776
660 | 11 | feeder2_1124 | 0.15852 | 0.6794 | 0.15839 | 0.67865
660 | 11 | feeder2_942 | 0.15842 | 0.68169 | 0.15829 | 0.68094
660 | 11 | feeder2_952 | 0.1585 | 0.68633 | 0.15837 | 0.68558
660 | 11 | feeder2_965 | 0.15842 | 0.6817 | 0.15829 | 0.68095
660 | 11 | feeder2_961 | 0.15842 | 0.68635 | 0.15829 | 0.6856
660 | 11 | feeder2_963 | 0.15852 | 0.68645 | 0.15839 | 0.68571
660 | 11 | feeder2_973 | 0.15817 | 0.68734 | 0.15804 | 0.6866
660 | 11 | feeder2_1128 | 0.15813 | 0.685 | 0.158 | 0.68425
660 | 11 | feeder2_1113 | 0.15856 | 0.68648 | 0.15843 | 0.68573
660 | 11 | feeder2_1143 | 0.16002 | 0.69482 | 0.15989 | 0.69409
660 | 11 | feeder2_1238 | 0.15908 | 0.68205 | 0.15895 | 0.6813
660 | 11 | feeder2_979 | 0.15841 | 0.68169 | 0.15828 | 0.68094
660 | 11 | feeder2_1236 | 0.15782 | 0.68771 | 0.15769 | 0.68696
660 | 11 | feeder2_989 | 0.15817 | 0.68736 | 0.15804 | 0.68661
660 | 11 | feeder2_1196 | 0.15836 | 0.68163 | 0.15823 | 0.68089
660 | 11 | feeder2_1158 | 0.15731 | 0.68919 | 0.15718 | 0.68844
660 | 11 | feeder2_1122 | 0.16323 | 0.69215 | 0.16311 | 0.69139
660 | 11 | feeder2_1258 | 0.1641 | 0.70031 | 0.16399 | 0.69955
660 | 11 | feeder2_1303 | 0.17858 | 0.69725 | 0.17846 | 0.69652
660 | 11 | feeder2_1138 | 0.16286 | 0.68942 | 0.16274 | 0.68867
660 | 11 | feeder2_1304 | 0.16225 | 0.68853 | 0.16213 | 0.68778
660 | 11 | feeder2_1212 | 0.1623 | 0.68446 | 0.16218 | 0.68372
660 | 11 | feeder2_1311 | 0.16363 | 0.68371 | 0.1635 | 0.68297
660 | 11 | feeder2_1290 | 0.16137 | 0.67888 | 0.16126 | 0.67813
660 | 11 | feeder2_1325 | 0.15746 | 0.68702 | 0.15732 | 0.68629
660 | 11 | feeder2_1248 | 0.15782 | 0.68772 | 0.15768 | 0.68697
660 | 11 | feeder2_1249 | 0.1591 | 0.68206 | 0.15897 | 0.68131
660 | 11 | feeder2_1250 | 0.15949 | 0.68226 | 0.15936 | 0.68151
660 | 11 | feeder2_1366 | 0.15632 | 0.68978 | 0.15619 | 0.68903
660 | 11 | feeder2_1266 | 0.16582 | 0.70781 | 0.1657 | 0.70705
660 | 11 | feeder2_1372 | 0.16826 | 0.68194 | 0.16814 | 0.68119
660 | 11 | feeder2_1363 | 0.1594 | 0.66775 | 0.15928 | 0.66699
660 | 11 | feeder2_1446 | 0.15752 | 0.68707 | 0.15738 | 0.68632
660 | 11 | feeder2_1502 | 0.15721 | 0.68748 | 0.15707 | 0.68675
660 | 11 | feeder2_1428 | 0.15043 | 0.6578 | 0.15031 | 0.65704
660 | 11 | feeder2_1380 | 0.16041 | 0.67085 | 0.16029 | 0.67008
660 | 11 | feeder2_1550 | 0.16046 | 0.67087 | 0.16034 | 0.6701
660 | 11 | feeder2_1386 | 0.16091 | 0.67246 | 0.16078 | 0.67168
660 | 11 | feeder2_1551 | 0.16039 | 0.67168 | 0.16027 | 0.67089
660 | 11 | feeder2_1400 | 0.16121 | 0.67347 | 0.16109 | 0.67269
660 | 11 | feeder2_1552 | 0.15945 | 0.67135 | 0.15933 | 0.67057
660 | 11 | feeder2_1408 | 0.16215 | 0.67678 | 0.16203 | 0.67599
660 | 11 | feeder2_1553 | 0.16166 | 0.67609 | 0.16154 | 0.67531
660 | 11 | feeder2_1416 | 0.1627 | 0.6787 | 0.16258 | 0.67791
660 | 11 | feeder2_1530 | 0.16542 | 0.6781 | 0.1653 | 0.67731
660 | 11 | feeder2_1425 | 0.16351 | 0.68258 | 0.16339 | 0.6818
660 | 11 | feeder2_1589 | 0.16269 | 0.6817 | 0.16257 | 0.68091
660 | 11 | feeder2_1435 | 0.1637 | 0.68345 | 0.16357 | 0.68267
660 | 11 | feeder2_1621 | 0.16688 | 0.69464 | 0.16676 | 0.69385
660 | 11 | feeder2_1564 | 0.16352 | 0.68257 | 0.1634 | 0.68178
660 | 11 | feeder2_1704 | 0.15721 | 0.6875 | 0.15708 | 0.68677
660 | 11 | feeder2_1525 | 0.15717 | 0.68781 | 0.15703 | 0.68708
660 | 11 | feeder2_1716 | 0.15502 | 0.69124 | 0.15488 | 0.69051
660 | 11 | feeder2_1537 | 0.15716 | 0.6878 | 0.15702 | 0.68707
660 | 11 | feeder2_1645 | 0.14806 | 0.6764 | 0.14792 | 0.67568
660 | 11 | feeder2_1561 | 0.1585 | 0.69423 | 0.15836 | 0.69351
660 | 11 | feeder2_1657 | 0.15879 | 0.69448 | 0.15865 | 0.69375
660 | 11 | feeder2_1570 | 0.15908 | 0.69699 | 0.15893 | 0.69626
660 | 11 | feeder2_1756 | 0.16144 | 0.69628 | 0.1613 | 0.69557
660 | 11 | feeder2_1588 | 0.15958 | 0.6996 | 0.15944 | 0.69889
660 | 11 | feeder2_1628 | 0.16721 | 0.70412 | 0.16707 | 0.70341
660 | 11 | feeder2_1598 | 0.15991 | 0.70146 | 0.15976 | 0.70074
660 | 11 | feeder2_1816 | 0.15984 | 0.70258 | 0.1597 | 0.70186
660 | 11 | feeder2_1765 | 0.15991 | 0.70153 | 0.15976 | 0.70081
660 | 11 | feeder2_1641 | 0.16142 | 0.71043 | 0.16127 | 0.70971
660 | 11 | feeder2_1689 | 0.16093 | 0.70964 | 0.16077 | 0.70891
660 | 11 | feeder2_1744 | 0.16914 | 0.71519 | 0.169 | 0.71447
660 | 11 | feeder2_1817 | 0.16091 | 0.70956 | 0.16076 | 0.70882
660 | 11 | feeder2_1779 | 0.16092 | 0.70966 | 0.16077 | 0.70892
660 | 11 | feeder2_1800 | 0.16088 | 0.70959 | 0.16073 | 0.70884
660 | 11 | feeder2_1818 | 0.15676 | 0.70499 | 0.15659 | 0.70422
660 | 11 | feeder2_1753 | 0.19384 | 0.73069 | 0.1937 | 0.73
660 | 11 | feeder2_1754 | 0.16917 | 0.71521 | 0.16903 | 0.7145
690 | 11.5 | secondary | 0.024997 | 0.0081086 | 0.025001 | 0.008105
690 | 11.5 | feeder2_44 | 0.04653 | 0.0423 | 0.046534 | 0.042265
690 | 11.5 | feeder2_45 | 0.047388 | 0.043358 | 0.047394 | 0.043322
690 | 11.5 | feeder2_46 | 0.043376 | 0.045619 | 0.04338 | 0.045584
690 | 11.5 | feeder2_51 | 0.048755 | 0.045164 | 0.04876 | 0.045129
690 | 11.5 | feeder2_48 | 0.050074 | 0.04329 | 0.050079 | 0.043244
690 | 11.5 | feeder2_52 | 0.049681 | 0.040472 | 0.04968 | 0.04044
690 | 11.5 | feeder2_68 | 0.052794 | 0.052109 | 0.052796 | 0.052065
690 | 11.5 | feeder2_69 | 0.052717 | 0.052164 | 0.05272 | 0.052125
690 | 11.5 | feeder2_71 | 0.053331 | 0.053027 | 0.053336 | 0.052984
690 | 11.5 | feeder2_72 | 0.053564 | 0.053202 | 0.053571 | 0.053165
690 | 11.5 | feeder2_73 | 0.055011 | 0.055877 | 0.055017 | 0.055837
690 | 11.5 | feeder2_74 | 0.053991 | 0.053646 | 0.053995 | 0.053603
690 | 11.5 | feeder2_77 | 0.056521 | 0.05866 | 0.056525 | 0.058617
690 | 11.5 | feeder2_79 | 0.055878 | 0.059194 | 0.055884 | 0.05915
690 | 11.5 | feeder2_81 | 0.05891 | 0.062925 | 0.058916 | 0.06288
690 | 11.5 | feeder2_82 | 0.060244 | 0.063857 | 0.060249 | 0.063806
690 | 11.5 | feeder2_116 | 0.069436 | 0.080962 | 0.06944 | 0.080902
690 | 11.5 | feeder2_119 | 0.068772 | 0.079848 | 0.068778 | 0.079788
690 | 11.5 | feeder2_120 | 0.073486 | 0.088235 | 0.073492 | 0.08817
690 | 11.5 | feeder2_248 | 0.074044 | 0.086686 | 0.074048 | 0.086626
690 | 11.5 | feeder2_124 | 0.076026 | 0.093382 | 0.076033 | 0.093313
690 | 11.5 | feeder2_282 | 0.084252 | 0.097164 | 0.084259 | 0.097082
690 | 11.5 | feeder2_275 | 0.077023 | 0.090833 | 0.077025 | 0.090774
690 | 11.5 | feeder2_151 | 0.079513 | 0.10164 | 0.079519 | 0.10157
690 | 11.5 | feeder2_295 | 0.075808 | 0.10549 | 0.075816 | 0.10543
690 | 11.5 | feeder2_311 | 0.079393 | 0.10174 | 0.0794 | 0.10168
690 | 11.5 | feeder2_201 | 0.085719 | 0.11047 | 0.085727 | 0.11039
690 | 11.5 | feeder2_314 | 0.08635 | 0.11038 | 0.086357 | 0.1103
690 | 11.5 | feeder2_342 | 0.094183 | 0.1232 | 0.09419 | 0.1231
690 | 11.5 | feeder2_368 | 0.093941 | 0.1218 | 0.093949 | 0.12173
690 | 11.5 | feeder2_347 | 0.097944 | 0.13434 | 0.097948 | 0.13419
690 | 11.5 | feeder2_353 | 0.099777 | 0.14037 | 0.099783 | 0.1402
690 | 11.5 | feeder2_518 | 0.098871 | 0.13513 | 0.098875 | 0.13498
690 | 11.5 | feeder2_365 | 0.10185 | 0.14767 | 0.10185 | 0.14748
690 | 11.5 | feeder2_653 | 0.099713 | 0.14027 | 0.099717 | 0.1401
690 | 11.5 | feeder2_377 | 0.10299 | 0.15186 | 0.10299 | 0.15166
690 | 11.5 | feeder2_622 | 0.10184 | 0.14767 | 0.10184 | 0.14748
690 | 11.5 | feeder2_451 | 0.094243 | 0.12202 | 0.09425 | 0.12195
690 | 11.5 | feeder2_383 | 0.093702 | 0.12106 | 0.093714 | 0.12103
690 | 11.5 | feeder2_385 | 0.10443 | 0.15649 | 0.10443 | 0.15627
690 | 11.5 | feeder2_621 | 0.098832 | 0.15388 | 0.098836 | 0.15369
690 | 11.5 | feeder2_611 | 0.089064 | 0.11404 | 0.089072 | 0.11401
690 | 11.5 | feeder2_405 | 0.093786 | 0.12145 | 0.093798 | 0.12143
690 | 11.5 | feeder2_461 | 0.11055 | 0.18071 | 0.11055 | 0.18043
690 | 11.5 | feeder2_594 | 0.10481 | 0.15523 | 0.10482 | 0.15501
690 | 11.5 | feeder2_732 | 0.094254 | 0.11941 | 0.094265 | 0.11938
690 | 11.5 | feeder2_417 | 0.094508 | 0.12516 | 0.094523 | 0.12514
690 | 11.5 | feeder2_663 | 0.092498 | 0.13206 | 0.092519 | 0.13207
690 | 11.5 | feeder2_444 | 0.094993 | 0.12645 | 0.09501 | 0.12644
690 | 11.5 | feeder2_759 | 0.098583 | 0.12601 | 0.098599 | 0.12599
690 | 11.5 | feeder2_842 | 0.092761 | 0.14114 | 0.092791 | 0.14118
690 | 11.5 | feeder2_459 | 0.095053 | 0.12626 | 0.095066 | 0.12625
690 | 11.5 | feeder2_702 | 0.098046 | 0.12559 | 0.098063 | 0.12558
690 | 11.5 | feeder2_493 | 0.094913 | 0.12571 | 0.094927 | 0.1257
690 | 11.5 | feeder2_651 | 0.11053 | 0.18069 | 0.11052 | 0.18041
690 | 11.5 | feeder2_684 | 0.11572 | 0.20325 | 0.11571 | 0.20293
690 | 11.5 | feeder2_674 | 0.094641 | 0.12532 | 0.094655 | 0.1253
690 | 11.5 | feeder2_696 | 0.094936 | 0.12583 | 0.094949 | 0.12583
690 | 11.5 | feeder2_681 | 0.094499 | 0.1251 | 0.094513 | 0.12509
690 | 11.5 | feeder2_682 | 0.093735 | 0.12402 | 0.093748 | 0.12401
690 | 11.5 | feeder2_728 | 0.11565 | 0.20169 | 0.11564 | 0.20137
690 | 11.5 | feeder2_724 | 0.12148 | 0.23126 | 0.12147 | 0.23091
690 | 11.5 | feeder2_703 | 0.09491 | 0.12592 | 0.094925 | 0.12591
690 | 11.5 | feeder2_704 | 0.09493 | 0.12587 | 0.094946 | 0.12586
690 | 11.5 | feeder2_754 | 0.12272 | 0.23246 | 0.12271 | 0.23211
690 | 11.5 | feeder2_747 | 0.12367 | 0.24215 | 0.12366 | 0.24179
690 | 11.5 | feeder2_828 | 0.11521 | 0.19903 | 0.1152 | 0.19871
690 | 11.5 | feeder2_763 | 0.11614 | 0.20319 | 0.11614 | 0.20286
690 | 11.5 | feeder2_836 | 0.12362 | 0.2421 | 0.12361 | 0.24174
690 | 11.5 | feeder2_758 | 0.12555 | 0.2516 | 0.12554 | 0.25123
690 | 11.5 | feeder2_788 | 0.12561 | 0.25166 | 0.1256 | 0.25129
690 | 11.5 | feeder2_812 | 0.1314 | 0.28083 | 0.13138 | 0.28042
690 | 11.5 | feeder2_947 | 0.11823 | 0.20536 | 0.11823 | 0.20503
690 | 11.5 | feeder2_868 | 0.11701 | 0.20409 | 0.117 | 0.20376
690 | 11.5 | feeder2_785 | 0.11616 | 0.20298 | 0.11615 | 0.20265
690 | 11.5 | feeder2_1176 | 0.1147 | 0.20178 | 0.11469 | 0.20146
690 | 11.5 | feeder2_846 | 0.11562 | 0.20229 | 0.11562 | 0.20196
690 | 11.5 | feeder2_911 | 0.11655 | 0.20397 | 0.11654 | 0.20364
690 | 11.5 | feeder2_1107 | 0.13546 | 0.2965 | 0.13545 | 0.2961
690 | 11.5 | feeder2_920 | 0.13193 | 0.28478 | 0.13191 | 0.28437
690 | 11.5 | feeder2_926 | 0.13284 | 0.29107 | 0.13282 | 0.29064
690 | 11.5 | feeder2_1239 | 0.13179 | 0.28443 | 0.13177 | 0.28402
690 | 11.5 | feeder2_933 | 0.13324 | 0.29386 | 0.13322 | 0.29343
690 | 11.5 | feeder2_1146 | 0.13286 | 0.29119 | 0.13284 | 0.29076
690 | 11.5 | feeder2_1124 | 0.13313 | 0.29376 | 0.13312 | 0.29334
690 | 11.5 | feeder2_942 | 0.13426 | 0.30112 | 0.13424 | 0.30068
690 | 11.5 | feeder2_952 | 0.13549 | 0.31181 | 0.13548 | 0.31135
690 | 11.5 | feeder2_965 | 0.13429 | 0.30115 | 0.13428 | 0.30071
690 | 11.5 | feeder2_961 | 0.1356 | 0.31282 | 0.13558 | 0.31235
690 | 11.5 | feeder2_963 | 0.1355 | 0.31185 | 0.13549 | 0.31138
690 | 11.5 | feeder2_973 | 0.13624 | 0.31839 | 0.13622 | 0.31791
690 | 11.5 | feeder2_1128 | 0.13543 | 0.31245 | 0.13541 | 0.31198
690 | 11.5 | feeder2_1113 | 0.13555 | 0.3119 | 0.13553 | 0.31143
690 | 11.5 | feeder2_1143 | 0.13596 | 0.31414 | 0.13594 | 0.31367
690 | 11.5 | feeder2_1238 | 0.1364 | 0.30358 | 0.13639 | 0.30313
690 | 11.5 | feeder2_979 | 0.13429 | 0.30098 | 0.13427 | 0.30053
690 | 11.5 | feeder2_1236 | 0.13722 | 0.32739 | 0.1372 | 0.32689
690 | 11.5 | feeder2_989 | 0.13624 | 0.31838 | 0.13622 | 0.31791
690 | 11.5 | feeder2_1196 | 0.13462 | 0.30023 | 0.1346 | 0.29979
690 | 11.5 | feeder2_1158 | 0.13568 | 0.31781 | 0.13566 | 0.31733
690 | 11.5 | feeder2_1122 | 0.13725 | 0.30434 | 0.13723 | 0.30394
690 | 11.5 | feeder2_1258 | 0.13204 | 0.29491 | 0.13203 | 0.29451
690 | 11.5 | feeder2_1303 | 0.14523 | 0.31274 | 0.14521 | 0.31234
690 | 11.5 | feeder2_1138 | 0.1381 | 0.30755 | 0.13809 | 0.30715
690 | 11.5 | feeder2_1304 | 0.13773 | 0.30718 | 0.13771 | 0.30678
690 | 11.5 | feeder2_1212 | 0.14003 | 0.31462 | 0.14002 | 0.31422
690 | 11.5 | feeder2_1311 | 0.14083 | 0.31554 | 0.14081 | 0.31514
690 | 11.5 | feeder2_1290 | 0.14221 | 0.32253 | 0.14219 | 0.32212
690 | 11.5 | feeder2_1325 | 0.1386 | 0.34083 | 0.13858 | 0.34031
690 | 11.5 | feeder2_1248 | 0.13721 | 0.32738 | 0.1372 | 0.32689
690 | 11.5 | feeder2_1249 | 0.13643 | 0.30361 | 0.13642 | 0.30316
690 | 11.5 | feeder2_1250 | 0.13784 | 0.30522 | 0.13782 | 0.30478
690 | 11.5 | feeder2_1366 | 0.13714 | 0.3273 | 0.13712 | 0.32681
690 | 11.5 | feeder2_1266 | 0.12971 | 0.29296 | 0.12971 | 0.29257
690 | 11.5 | feeder2_1372 | 0.15042 | 0.33119 | 0.1504 | 0.33079
690 | 11.5 | feeder2_1363 | 0.14223 | 0.31878 | 0.14221 | 0.31838
690 | 11.5 | feeder2_1446 | 0.13933 | 0.34188 | 0.1393 | 0.34137
690 | 11.5 | feeder2_1502 | 0.13982 | 0.35468 | 0.13979 | 0.35414
690 | 11.5 | feeder2_1428 | 0.14222 | 0.31836 | 0.1422 | 0.31795
690 | 11.5 | feeder2_1380 | 0.14235 | 0.3149 | 0.14233 | 0.31449
690 | 11.5 | feeder2_1550 | 0.14241 | 0.31497 | 0.1424 | 0.31456
690 | 11.5 | feeder2_1386 | 0.14241 | 0.31298 | 0.14239 | 0.31257
690 | 11.5 | feeder2_1551 | 0.14294 | 0.31181 | 0.14293 | 0.3114
690 | 11.5 | feeder2_1400 | 0.14244 | 0.31234 | 0.14242 | 0.31193
690 | 11.5 | feeder2_1552 | 0.14188 | 0.3116 | 0.14186 | 0.31119
690 | 11.5 | feeder2_1408 | 0.14263 | 0.31133 | 0.14261 | 0.31092
690 | 11.5 | feeder2_1553 | 0.14478 | 0.30716 | 0.14476 | 0.30675
690 | 11.5 | feeder2_1416 | 0.14272 | 0.31174 | 0.14271 | 0.31132
690 | 11.5 | feeder2_1530 | 0.14508 | 0.31444 | 0.14506 | 0.31403
690 | 11.5 | feeder2_1425 | 0.14256 | 0.31101 | 0.14255 | 0.3106
690 | 11.5 | feeder2_1589 | 0.14222 | 0.31057 | 0.1422 | 0.31016
690 | 11.5 | feeder2_1435 | 0.14255 | 0.3109 | 0.14253 | 0.31048
690 | 11.5 | feeder2_1621 | 0.14107 | 0.31008 | 0.14105 | 0.30967
690 | 11.5 | feeder2_1564 | 0.14247 | 0.31072 | 0.14245 | 0.3103
690 | 11.5 | feeder2_1704 | 0.13979 | 0.35464 | 0.13976 | 0.3541
690 | 11.5 | feeder2_1525 | 0.14014 | 0.35828 | 0.14011 | 0.35774
690 | 11.5 | feeder2_1716 | 0.13787 | 0.35823 | 0.13784 | 0.35768
690 | 11.5 | feeder2_1537 | 0.14055 | 0.36238 | 0.14052 | 0.36183
690 | 11.5 | feeder2_1645 | 0.13799 | 0.3596 | 0.13796 | 0.35905
690 | 11.5 | feeder2_1561 | 0.14174 | 0.36827 | 0.14172 | 0.36771
690 | 11.5 | feeder2_1657 | 0.14602 | 0.37275 | 0.14599 | 0.37219
690 | 11.5 | feeder2_1570 | 0.14205 | 0.36974 | 0.14202 | 0.36918
690 | 11.5 | feeder2_1756 | 0.14346 | 0.37189 | 0.14344 | 0.37132
690 | 11.5 | feeder2_1588 | 0.1423 | 0.37096 | 0.14227 | 0.3704
690 | 11.5 | feeder2_1628 | 0.14312 | 0.37183 | 0.14309 | 0.37126
690 | 11.5 | feeder2_1598 | 0.14256 | 0.37227 | 0.14254 | 0.3717
690 | 11.5 | feeder2_1816 | 0.14046 | 0.3699 | 0.14043 | 0.36933
690 | 11.5 | feeder2_1765 | 0.1422 | 0.37184 | 0.14217 | 0.37127
690 | 11.5 | feeder2_1641 | 0.1439 | 0.3797 | 0.14387 | 0.37911
690 | 11.5 | feeder2_1689 | 0.14361 | 0.37902 | 0.14359 | 0.37842
690 | 11.5 | feeder2_1744 | 0.14789 | 0.3841 | 0.14786 | 0.38351
690 | 11.5 | feeder2_1817 | 0.1436 | 0.379 | 0.14357 | 0.3784
690 | 11.5 | feeder2_1779 | 0.14359 | 0.37899 | 0.14356 | 0.37839
690 | 11.5 | feeder2_1800 | 0.14359 | 0.379 | 0.14356 | 0.3784
690 | 11.5 | feeder2_1818 | 0.14065 | 0.37598 | 0.1406 | 0.37536
690 | 11.5 | feeder2_1753 | 0.15932 | 0.3961 | 0.15929 | 0.39551
690 | 11.5 | feeder2_1754 | 0.14817 | 0.38453 | 0.14815 | 0.38394
720 | 12 | secondary | 0.013548 | 0.0089561 | 0.013553 | 0.0089637
720 | 12 | feeder2_44 | 0.025208 | 0.046703 | 0.025219 | 0.046749
720 | 12 | feeder2_45 | 0.025644 | 0.048158 | 0.025657 | 0.048206
720 | 12 | feeder2_46 | 0.025233 | 0.046805 | 0.025243 | 0.046856
720 | 12 | feeder2_51 | 0.026386 | 0.05062 | 0.026398 | 0.050674
720 | 12 | feeder2_48 | 0.026573 | 0.048475 | 0.026586 | 0.048522
720 | 12 | feeder2_52 | 0.023892 | 0.047013 | 0.023907 | 0.047065
720 | 12 | feeder2_68 | 0.028828 | 0.059038 | 0.028839 | 0.0591
720 | 12 | feeder2_69 | 0.038693 | 0.077358 | 0.038694 | 0.077422
720 | 12 | feeder2_71 | 0.028992 | 0.059469 | 0.029004 | 0.059528
720 | 12 | feeder2_72 | 0.056258 | 0.077442 | 0.056272 | 0.077496
720 | 12 | feeder2_73 | 0.029199 | 0.059038 | 0.029213 | 0.059101
720 | 12 | feeder2_74 | 0.027375 | 0.056941 | 0.027388 | 0.057008
720 | 12 | feeder2_77 | 0.029449 | 0.058998 | 0.029462 | 0.059063
720 | 12 | feeder2_79 | 0.033802 | 0.068695 | 0.033806 | 0.068767
720 | 12 | feeder2_81 | 0.02914 | 0.056335 | 0.029151 | 0.056406
720 | 12 | feeder2_82 | 0.030412 | 0.05713 | 0.030428 | 0.0572
720 | 12 | feeder2_116 | 0.027635 | 0.049523 | 0.027653 | 0.049593
720 | 12 | feeder2_119 | 0.026406 | 0.04826 | 0.026426 | 0.048328
720 | 12 | feeder2_120 | 0.027244 | 0.050564 | 0.027259 | 0.050632
720 | 12 | feeder2_248 | 0.027132 | 0.050469 | 0.027151 | 0.050534
720 | 12 | feeder2_124 | 0.027016 | 0.051966 | 0.027034 | 0.05203
720 | 12 | feeder2_282 | 0.027847 | 0.052648 | 0.027865 | 0.052713
720 | 12 | feeder2_275 | 0.026903 | 0.051877 | 0.026921 | 0.051938
720 | 12 | feeder2_151 | 0.026559 | 0.055122 | 0.026579 | 0.055176
720 | 12 | feeder2_295 | 0.026406 | 0.055149 | 0.026423 | 0.055204
720 | 12 | feeder2_311 | 0.026578 | 0.055075 | 0.026597 | 0.055129
720 | 12 | feeder2_201 | 0.025743 | 0.063179 | 0.025765 | 0.063212
720 | 12 | feeder2_314 | 0.026544 | 0.06377 | 0.026564 | 0.063803
720 | 12 | feeder2_342 | 0.024253 | 0.077124 | 0.024274 | 0.077133
720 | 12 | feeder2_368 | 0.024133 | 0.076093 | 0.02416 | 0.076103
720 | 12 | feeder2_347 | 0.023672 | 0.086817 | 0.023696 | 0.086817
720 | 12 | feeder2_353 | 0.023312 | 0.09108 | 0.023339 | 0.091073
720 | 12 | feeder2_518 | 0.024898 | 0.088218 | 0.024924 | 0.088221
720 | 12 | feeder2_365 | 0.022927 | 0.095916 | 0.022952 | 0.095907
720 | 12 | feeder2_653 | 0.023224 | 0.091068 | 0.023254 | 0.091062
720 | 12 | feeder2_377 | 0.022718 | 0.09859 | 0.022747 | 0.098575
720 | 12 | feeder2_622 | 0.022928 | 0.095884 | 0.022956 | 0.095876
720 | 12 | feeder2_451 | 0.024207 | 0.076184 | 0.02423 | 0.076195
720 | 12 | feeder2_383 | 0.023928 | 0.074357 | 0.023951 | 0.074365
720 | 12 | feeder2_385 | 0.022473 | 0.10184 | 0.022503 | 0.10183
720 | 12 | feeder2_621 | 0.022486 | 0.098247 | 0.022514 | 0.098235
720 | 12 | feeder2_611 | 0.023216 | 0.07296 | 0.023241 | 0.072966
720 | 12 | feeder2_405 | 0.023934 | 0.074317 | 0.023958 | 0.074325
720 | 12 | feeder2_461 | 0.021527 | 0.11534 | 0.021555 | 0.11532
720 | 12 | feeder2_594 | 0.022404 | 0.10184 | 0.022434 | 0.10182
720 | 12 | feeder2_732 | 0.023632 | 0.072516 | 0.023658 | 0.072525
720 | 12 | feeder2_417 | 0.024039 | 0.074394 | 0.024063 | 0.074406
720 | 12 | feeder2_663 | 0.023091 | 0.073835 | 0.023112 | 0.073851
720 | 12 | feeder2_444 | 0.024148 | 0.074698 | 0.024172 | 0.074707
720 | 12 | feeder2_759 | 0.027293 | 0.077994 | 0.027319 | 0.078002
720 | 12 | feeder2_842 | 0.024438 | 0.073164 | 0.024463 | 0.073175
720 | 12 | feeder2_459 | 0.024122 | 0.074691 | 0.024142 | 0.074701
720 | 12 | feeder2_702 | 0.025731 | 0.076102 | 0.025755 | 0.076106
720 | 12 | feeder2_493 | 0.023828 | 0.074074 | 0.023851 | 0.074083
720 | 12 | feeder2_651 | 0.020491 | 0.11523 | 0.020521 | 0.1152
720 | 12 | feeder2_684 | 0.020935 | 0.12697 | 0.020968 | 0.12693
720 | 12 | feeder2_674 | 0.023344 | 0.073749 | 0.023367 | 0.073756
720 | 12 | feeder2_696 | 0.023736 | 0.073535 | 0.02376 | 0.073547
720 | 12 | feeder2_681 | 0.022741 | 0.073021 | 0.022763 | 0.073029
720 | 12 | feeder2_682 | 0.0223 | 0.073533 | 0.022323 | 0.073538
720 | 12 | feeder2_728 | 0.020876 | 0.12739 | 0.020907 | 0.12735
720 | 12 | feeder2_724 | 0.020494 | 0.13838 | 0.020526 | 0.13833
720 | 12 | feeder2_703 | 0.023762 | 0.073406 | 0.023784 | 0.073419
720 | 12 | feeder2_704 | 0.023408 | 0.07344 | 0.02343 | 0.073451
720 | 12 | feeder2_754 | 0.020968 | 0.13882 | 0.021003 | 0.13876
720 | 12 | feeder2_747 | 0.020289 | 0.14296 | 0.020324 | 0.14291
720 | 12 | feeder2_828 | 0.020719 | 0.12728 | 0.020753 | 0.12725
720 | 12 | feeder2_763 | 0.02089 | 0.12816 | 0.020922 | 0.12813
720 | 12 | feeder2_836 | 0.017741 | 0.14201 | 0.017776 | 0.14195
720 | 12 | feeder2_758 | 0.020267 | 0.14757 | 0.020304 | 0.1475
720 | 12 | feeder2_788 | 0.021402 | 0.14896 | 0.021437 | 0.1489
720 | 12 | feeder2_812 | 0.019924 | 0.16056 | 0.019964 | 0.16048
720 | 12 | feeder2_947 | 0.023818 | 0.13101 | 0.023853 | 0.13098
720 | 12 | feeder2_868 | 0.021597 | 0.12886 | 0.021628 | 0.12882
720 | 12 | feeder2_785 | 0.020645 | 0.12761 | 0.02068 | 0.12757
720 | 12 | feeder2_1176 | 0.017814 | 0.12498 | 0.017845 | 0.12495
720 | 12 | feeder2_846 | 0.019876 | 0.12762 | 0.019909 | 0.12758
720 | 12 | feeder2_911 | 0.020665 | 0.12769 | 0.020698 | 0.12766
720 | 12 | feeder2_1107 | 0.020793 | 0.16655 | 0.020832 | 0.16646
720 | 12 | feeder2_920 | 0.019629 | 0.1627 | 0.01967 | 0.16261
720 | 12 | feeder2_926 | 0.019303 | 0.16579 | 0.019342 | 0.16569
720 | 12 | feeder2_1239 | 0.019493 | 0.16293 | 0.019531 | 0.16283
720 | 12 | feeder2_933 | 0.019033 | 0.16657 | 0.019073 | 0.16647
720 | 12 | feeder2_1146 | 0.019901 | 0.16871 | 0.019941 | 0.16861
720 | 12 | feeder2_1124 | 0.019021 | 0.16651 | 0.019061 | 0.16641
720 | 12 | feeder2_942 | 0.018347 | 0.16868 | 0.018388 | 0.16857
720 | 12 | feeder2_952 | 0.017456 | 0.17314 | 0.017498 | 0.17302
720 | 12 | feeder2_965 | 0.018332 | 0.16853 | 0.018374 | 0.16842
720 | 12 | feeder2_961 | 0.017262 | 0.17318 | 0.017306 | 0.17306
720 | 12 | feeder2_963 | 0.017477 | 0.17323 | 0.017518 | 0.17311
720 | 12 | feeder2_973 | 0.016344 | 0.17319 | 0.016388 | 0.17307
720 | 12 | feeder2_1128 | 0.017075 | 0.17361 | 0.017115 | 0.1735
720 | 12 | feeder2_1113 | 0.018391 | 0.17448 | 0.018432 | 0.17436
720 | 12 | feeder2_1143 | 0.018179 | 0.17618 | 0.018218 | 0.17607
720 | 12 | feeder2_1238 | 0.019054 | 0.16898 | 0.019096 | 0.16887
720 | 12 | feeder2_979 | 0.018303 | 0.16829 | 0.018344 | 0.16818
720 | 12 | feeder2_1236 | 0.014918 | 0.17429 | 0.014963 | 0.17416
720 | 12 | feeder2_989 | 0.016345 | 0.17318 | 0.016388 | 0.17305
720 | 12 | feeder2_1196 | 0.018801 | 0.16719 | 0.018844 | 0.16708
720 | 12 | feeder2_1158 | 0.016128 | 0.17206 | 0.01617 | 0.17194
720 | 12 | feeder2_1122 | 0.021154 | 0.16899 | 0.021191 | 0.16891
720 | 12 | feeder2_1258 | 0.020764 | 0.1664 | 0.020803 | 0.16632
720 | 12 | feeder2_1303 | 0.021299 | 0.16909 | 0.021337 | 0.169
720 | 12 | feeder2_1138 | 0.021442 | 0.1709 | 0.021479 | 0.17081
720 | 12 | feeder2_1304 | 0.02086 | 0.17118 | 0.020899 | 0.1711
720 | 12 | feeder2_1212 | 0.022237 | 0.17462 | 0.022274 | 0.17454
720 | 12 | feeder2_1311 | 0.023232 | 0.17613 | 0.023272 | 0.17604
720 | 12 | feeder2_1290 | 0.023019 | 0.17796 | 0.023057 | 0.17788
720 | 12 | feeder2_1325 | 0.013087 | 0.17847 | 0.013132 | 0.17832
720 | 12 | feeder2_1248 | 0.01491 | 0.17428 | 0.014955 | 0.17415
720 | 12 | feeder2_1249 | 0.01908 | 0.169 | 0.019123 | 0.16889
720 | 12 | feeder2_1250 | 0.0195 | 0.16925 | 0.01954 | 0.16915
720 | 12 | feeder2_1366 | 0.013201 | 0.17331 | 0.013245 | 0.17318
720 | 12 | feeder2_1266 | 0.020751 | 0.16631 | 0.020787 | 0.16623
720 | 12 | feeder2_1372 | 0.028352 | 0.18214 | 0.028389 | 0.18206
720 | 12 | feeder2_1363 | 0.022469 | 0.17626 | 0.022508 | 0.17617
720 | 12 | feeder2_1446 | 0.0138 | 0.17939 | 0.013846 | 0.17925
720 | 12 | feeder2_1502 | 0.010784 | 0.18231 | 0.010833 | 0.18215
720 | 12 | feeder2_1428 | 0.02241 | 0.176 | 0.022449 | 0.17591
720 | 12 | feeder2_1380 | 0.022076 | 0.17456 | 0.022112 | 0.17447
720 | 12 | feeder2_1550 | 0.02323 | 0.17653 | 0.023269 | 0.17644
720 | 12 | feeder2_1386 | 0.021694 | 0.17275 | 0.021731 | 0.17266
720 | 12 | feeder2_1551 | 0.022132 | 0.17208 | 0.022171 | 0.17199
720 | 12 | feeder2_1400 | 0.021522 | 0.17203 | 0.021559 | 0.17194
720 | 12 | feeder2_1552 | 0.020724 | 0.17259 | 0.020762 | 0.17249
720 | 12 | feeder2_1408 | 0.021324 | 0.17019 | 0.02136 | 0.17009
720 | 12 | feeder2_1553 | 0.021252 | 0.17024 | 0.021291 | 0.17014
720 | 12 | feeder2_1416 | 0.021226 | 0.16922 | 0.021266 | 0.16913
720 | 12 | feeder2_1530 | 0.021346 | 0.1693 | 0.021382 | 0.1692
720 | 12 | feeder2_1425 | 0.02103 | 0.16733 | 0.021066 | 0.16723
720 | 12 | feeder2_1589 | 0.021515 | 0.16643 | 0.021553 | 0.16633
720 | 12 | feeder2_1435 | 0.02101 | 0.16702 | 0.021049 | 0.16693
720 | 12 | feeder2_1621 | 0.018711 | 0.16384 | 0.018751 | 0.16375
720 | 12 | feeder2_1564 | 0.020984 | 0.16708 | 0.021019 | 0.16699
720 | 12 | feeder2_1704 | 0.0097288 | 0.18167 | 0.0097748 | 0.18151
720 | 12 | feeder2_1525 | 0.010252 | 0.18363 | 0.010302 | 0.18347
720 | 12 | feeder2_1716 | 0.0084255 | 0.18143 | 0.0084706 | 0.18127
720 | 12 | feeder2_1537 | 0.0096916 | 0.18551 | 0.0097387 | 0.18535
720 | 12 | feeder2_1645 | 0.0074884 | 0.18918 | 0.0075187 | 0.18901
720 | 12 | feeder2_1561 | 0.0098774 | 0.18536 | 0.0099252 | 0.18519
720 | 12 | feeder2_1657 | 0.010882 | 0.18644 | 0.01093 | 0.18627
720 | 12 | feeder2_1570 | 0.0098989 | 0.18504 | 0.0099493 | 0.18487
720 | 12 | feeder2_1756 | 0.012125 | 0.18794 | 0.012174 | 0.18777
720 | 12 | feeder2_1588 | 0.0098809 | 0.18457 | 0.009928 | 0.18439
720 | 12 | feeder2_1628 | 0.010564 | 0.18495 | 0.010614 | 0.18478
720 | 12 | feeder2_1598 | 0.0098251 | 0.18387 | 0.0098758 | 0.1837
720 | 12 | feeder2_1816 | 0.0093456 | 0.17938 | 0.0093905 | 0.1792
720 | 12 | feeder2_1765 | 0.0097751 | 0.18367 | 0.0098227 | 0.18349
720 | 12 | feeder2_1641 | 0.0094923 | 0.18194 | 0.0095426 | 0.18176
720 | 12 | feeder2_1689 | 0.0091854 | 0.18024 | 0.0092369 | 0.18005
720 | 12 | feeder2_1744 | 0.0096051 | 0.18198 | 0.009656 | 0.1818
720 | 12 | feeder2_1817 | 0.0091097 | 0.17982 | 0.0091615 | 0.17963
720 | 12 | feeder2_1779 | 0.0080285 | 0.17952 | 0.0080789 | 0.17934
720 | 12 | feeder2_1800 | 0.0097861 | 0.17952 | 0.0098345 | 0.17933
720 | 12 | feeder2_1818 | 0.0086712 | 0.17907 | 0.0087318 | 0.17888
720 | 12 | feeder2_1753 | 0.0098102 | 0.18206 | 0.0098585 | 0.18188
720 | 12 | feeder2_1754 | 0.0096386 | 0.182 | 0.0096903 | 0.18182
750 | 12.5 | secondary | 0.031473 | 0.043113 | 0.031458 | 0.043094
750 | 12.5 | feeder2_44 | 0.058577 | 0.22489 | 0.058551 | 0.22479
750 | 12.5 | feeder2_45 | 0.059601 | 0.23181 | 0.059573 | 0.23172
750 | 12.5 | feeder2_46 | 0.056883 | 0.22596 | 0.056855 | 0.22587
750 | 12.5 | feeder2_51 | 0.061371 | 0.24402 | 0.061343 | 0.24391
750 | 12.5 | feeder2_48 | 0.060697 | 0.2306 | 0.060668 | 0.2305
750 | 12.5 | feeder2_52 | 0.057898 | 0.24481 | 0.05787 | 0.24471
750 | 12.5 | feeder2_68 | 0.066744 | 0.27833 | 0.06671 | 0.27822
750 | 12.5 | feeder2_69 | 0.066634 | 0.27943 | 0.066606 | 0.27931
750 | 12.5 | feeder2_71 | 0.067451 | 0.28282 | 0.067418 | 0.2827
750 | 12.5 | feeder2_72 | 0.068991 | 0.28113 | 0.068962 | 0.28101
750 | 12.5 | feeder2_73 | 0.069642 | 0.29707 | 0.069607 | 0.29694
750 | 12.5 | feeder2_74 | 0.06878 | 0.29842 | 0.068748 | 0.29829
750 | 12.5 | feeder2_77 | 0.071586 | 0.30912 | 0.071553 | 0.30898
750 | 12.5 | feeder2_79 | 0.070389 | 0.31041 | 0.070358 | 0.31028
750 | 12.5 | feeder2_81 | 0.074654 | 0.32759 | 0.07462 | 0.32744
750 | 12.5 | feeder2_82 | 0.076024 | 0.32604 | 0.075991 | 0.3259
750 | 12.5 | feeder2_116 | 0.088404 | 0.41186 | 0.088365 | 0.41168
750 | 12.5 | feeder2_119 | 0.087217 | 0.41288 | 0.08718 | 0.4127
750 | 12.5 | feeder2_120 | 0.093751 | 0.44265 | 0.093709 | 0.44245
750 | 12.5 | feeder2_248 | 0.093633 | 0.4426 | 0.09359 | 0.4424
750 | 12.5 | feeder2_124 | 0.097054 | 0.46161 | 0.097011 | 0.46141
750 | 12.5 | feeder2_282 | 0.097299 | 0.46133 | 0.097256 | 0.46112
750 | 12.5 | feeder2_275 | 0.096934 | 0.46156 | 0.096889 | 0.46136
750 | 12.5 | feeder2_151 | 0.10283 | 0.49482 | 0.10278 | 0.4946
750 | 12.5 | feeder2_295 | 0.10298 | 0.49516 | 0.10293 | 0.49494
750 | 12.5 | feeder2_311 | 0.10288 | 0.49494 | 0.10283 | 0.49472
750 | 12.5 | feeder2_201 | 0.11234 | 0.54947 | 0.11229 | 0.54923
750 | 12.5 | feeder2_314 | 0.11238 | 0.54942 | 0.11233 | 0.54917
750 | 12.5 | feeder2_342 | 0.12587 | 0.62715 | 0.12582 | 0.62687
750 | 12.5 | feeder2_368 | 0.12625 | 0.63405 | 0.12619 | 0.63377
750 | 12.5 | feeder2_347 | 0.13162 | 0.65255 | 0.13156 | 0.65226
750 | 12.5 | feeder2_353 | 0.13448 | 0.66563 | 0.13442 | 0.66533
750 | 12.5 | feeder2_518 | 0.13235 | 0.65171 | 0.13229 | 0.65142
750 | 12.5 | feeder2_365 | 0.13765 | 0.68018 | 0.13759 | 0.67987
750 | 12.5 | feeder2_653 | 0.13438 | 0.66559 | 0.13432 | 0.66529
750 | 12.5 | feeder2_377 | 0.13938 | 0.68808 | 0.13932 | 0.68776
750 | 12.5 | feeder2_622 | 0.13767 | 0.68021 | 0.13761 | 0.6799
750 | 12.5 | feeder2_451 | 0.12785 | 0.63239 | 0.12779 | 0.6321
750 | 12.5 | feeder2_383 | 0.12656 | 0.64661 | 0.1265 | 0.64632
750 | 12.5 | feeder2_385 | 0.14134 | 0.69706 | 0.14128 | 0.69674
750 | 12.5 | feeder2_621 | 0.13955 | 0.68843 | 0.13949 | 0.68812
750 | 12.5 | feeder2_611 | 0.12511 | 0.64609 | 0.12506 | 0.6458
750 | 12.5 | feeder2_405 | 0.1266 | 0.64743 | 0.12654 | 0.64715
750 | 12.5 | feeder2_461 | 0.14933 | 0.73368 | 0.14927 | 0.73334
750 | 12.5 | feeder2_594 | 0.14126 | 0.69703 | 0.1412 | 0.6967
750 | 12.5 | feeder2_732 | 0.12645 | 0.64737 | 0.12639 | 0.64708
750 | 12.5 | feeder2_417 | 0.12692 | 0.65363 | 0.12686 | 0.65335
750 | 12.5 | feeder2_663 | 0.12614 | 0.65651 | 0.12608 | 0.65622
750 | 12.5 | feeder2_444 | 0.12712 | 0.65739 | 0.12706 | 0.6571
750 | 12.5 | feeder2_759 | 0.12985 | 0.65427 | 0.1298 | 0.65398
750 | 12.5 | feeder2_842 | 0.13992 | 0.68216 | 0.13986 | 0.68187
750 | 12.5 | feeder2_459 | 0.12687 | 0.65743 | 0.12681 | 0.65714
750 | 12.5 | feeder2_702 | 0.12861 | 0.65559 | 0.12855 | 0.6553
750 | 12.5 | feeder2_493 | 0.12572 | 0.65835 | 0.12566 | 0.65806
750 | 12.5 | feeder2_651 | 0.1495 | 0.73409 | 0.14944 | 0.73374
750 | 12.5 | feeder2_684 | 0.15575 | 0.76309 | 0.15568 | 0.76273
750 | 12.5 | feeder2_674 | 0.12329 | 0.65901 | 0.12323 | 0.65871
750 | 12.5 | feeder2_696 | 0.12592 | 0.65931 | 0.12586 | 0.65901
750 | 12.5 | feeder2_681 | 0.11718 | 0.66041 | 0.11712 | 0.66011
750 | 12.5 | feeder2_682 | 0.12259 | 0.65973 | 0.12253 | 0.65944
750 | 12.5 | feeder2_728 | 0.15697 | 0.76867 | 0.1569 | 0.76832
750 | 12.5 | feeder2_724 | 0.15988 | 0.78036 | 0.15982 | 0.77998
750 | 12.5 | feeder2_703 | 0.126 | 0.65948 | 0.12595 | 0.65919
750 | 12.5 | feeder2_704 | 0.12607 | 0.65961 | 0.12601 | 0.65932
750 | 12.5 | feeder2_754 | 0.1603 | 0.77992 | 0.16024 | 0.77954
750 | 12.5 | feeder2_747 | 0.16157 | 0.78763 | 0.1615 | 0.78725
750 | 12.5 | feeder2_828 | 0.15681 | 0.76859 | 0.15674 | 0.76824
750 | 12.5 | feeder2_763 | 0.15885 | 0.77706 | 0.15879 | 0.77671
750 | 12.5 | feeder2_836 | 0.16192 | 0.78835 | 0.16186 | 0.78797
750 | 12.5 | feeder2_758 | 0.16296 | 0.79357 | 0.1629 | 0.79319
750 | 12.5 | feeder2_788 | 0.16438 | 0.7921 | 0.16431 | 0.79172
750 | 12.5 | feeder2_812 | 0.16692 | 0.81377 | 0.16685 | 0.81337
750 | 12.5 | feeder2_947 | 0.16048 | 0.7753 | 0.16041 | 0.77495
750 | 12.5 | feeder2_868 | 0.15969 | 0.77618 | 0.15962 | 0.77582
750 | 12.5 | feeder2_785 | 0.15981 | 0.78303 | 0.15975 | 0.78268
750 | 12.5 | feeder2_1176 | 0.17367 | 0.81218 | 0.17358 | 0.81183
750 | 12.5 | feeder2_846 | 0.15883 | 0.78317 | 0.15877 | 0.78281
750 | 12.5 | feeder2_911 | 0.15982 | 0.78299 | 0.15975 | 0.78262
750 | 12.5 | feeder2_1107 | 0.16819 | 0.82656 | 0.16812 | 0.82615
750 | 12.5 | feeder2_920 | 0.16769 | 0.81593 | 0.16762 | 0.81552
750 | 12.5 | feeder2_926 | 0.16894 | 0.81946 | 0.16887 | 0.81905
750 | 12.5 | feeder2_1239 | 0.16756 | 0.81558 | 0.16749 | 0.81517
750 | 12.5 | feeder2_933 | 0.16945 | 0.82131 | 0.16938 | 0.82089
750 | 12.5 | feeder2_1146 | 0.16916 | 0.81822 | 0.1691 | 0.8178
750 | 12.5 | feeder2_1124 | 0.16898 | 0.82185 | 0.16891 | 0.82144
750 | 12.5 | feeder2_942 | 0.17074 | 0.82545 | 0.17067 | 0.82503
750 | 12.5 | feeder2_952 | 0.17242 | 0.83338 | 0.17235 | 0.83295
750 | 12.5 | feeder2_965 | 0.17077 | 0.82522 | 0.17071 | 0.8248
750 | 12.5 | feeder2_961 | 0.17255 | 0.83489 | 0.17248 | 0.83446
750 | 12.5 | feeder2_963 | 0.17243 | 0.83324 | 0.17236 | 0.83281
750 | 12.5 | feeder2_973 | 0.17333 | 0.84271 | 0.17326 | 0.84228
750 | 12.5 | feeder2_1128 | 0.17237 | 0.83524 | 0.1723 | 0.83481
750 | 12.5 | feeder2_1113 | 0.17295 | 0.83271 | 0.17288 | 0.83228
750 | 12.5 | feeder2_1143 | 0.17297 | 0.82526 | 0.17291 | 0.82484
750 | 12.5 | feeder2_1238 | 0.17437 | 0.82158 | 0.1743 | 0.82117
750 | 12.5 | feeder2_979 | 0.17077 | 0.82522 | 0.1707 | 0.8248
750 | 12.5 | feeder2_1236 | 0.17434 | 0.85339 | 0.17427 | 0.85293
750 | 12.5 | feeder2_989 | 0.17334 | 0.84272 | 0.17326 | 0.84228
750 | 12.5 | feeder2_1196 | 0.17072 | 0.82519 | 0.17064 | 0.82477
750 | 12.5 | feeder2_1158 | 0.17379 | 0.84387 | 0.17372 | 0.84344
750 | 12.5 | feeder2_1122 | 0.16865 | 0.83142 | 0.16858 | 0.83101
750 | 12.5 | feeder2_1258 | 0.16828 | 0.82673 | 0.16821 | 0.82632
750 | 12.5 | feeder2_1303 | 0.16873 | 0.83135 | 0.16866 | 0.83094
750 | 12.5 | feeder2_1138 | 0.16902 | 0.83528 | 0.16896 | 0.83487
750 | 12.5 | feeder2_1304 | 0.1681 | 0.83583 | 0.16804 | 0.83542
750 | 12.5 | feeder2_1212 | 0.17005 | 0.84313 | 0.16998 | 0.84272
750 | 12.5 | feeder2_1311 | 0.17171 | 0.8414 | 0.17164 | 0.84098
750 | 12.5 | feeder2_1290 | 0.17107 | 0.85429 | 0.17099 | 0.85387
750 | 12.5 | feeder2_1325 | 0.17546 | 0.8665 | 0.17539 | 0.86603
750 | 12.5 | feeder2_1248 | 0.17434 | 0.85339 | 0.17427 | 0.85294
750 | 12.5 | feeder2_1249 | 0.17438 | 0.82157 | 0.17431 | 0.82115
750 | 12.5 | feeder2_1250 | 0.17685 | 0.81907 | 0.17679 | 0.81865
750 | 12.5 | feeder2_1366 | 0.1744 | 0.85354 | 0.17432 | 0.85309
750 | 12.5 | feeder2_1266 | 0.16834 | 0.82684 | 0.16827 | 0.82643
750 | 12.5 | feeder2_1372 | 0.17227 | 0.85304 | 0.1722 | 0.85262
750 | 12.5 | feeder2_1363 | 0.17187 | 0.86806 | 0.1718 | 0.86763
750 | 12.5 | feeder2_1446 | 0.1755 | 0.86646 | 0.17543 | 0.86599
750 | 12.5 | feeder2_1502 | 0.17672 | 0.88127 | 0.17664 | 0.88078
750 | 12.5 | feeder2_1428 | 0.17116 | 0.86875 | 0.17109 | 0.86832
750 | 12.5 | feeder2_1380 | 0.17326 | 0.88388 | 0.17319 | 0.88345
750 | 12.5 | feeder2_1550 | 0.17331 | 0.88383 | 0.17323 | 0.8834
750 | 12.5 | feeder2_1386 | 0.17395 | 0.89163 | 0.17388 | 0.8912
750 | 12.5 | feeder2_1551 | 0.17384 | 0.89158 | 0.17376 | 0.89115
750 | 12.5 | feeder2_1400 | 0.17429 | 0.89533 | 0.17421 | 0.8949
750 | 12.5 | feeder2_1552 | 0.17269 | 0.89464 | 0.17262 | 0.8942
750 | 12.5 | feeder2_1408 | 0.17513 | 0.90343 | 0.17506 | 0.903
750 | 12.5 | feeder2_1553 | 0.17501 | 0.90337 | 0.17493 | 0.90294
750 | 12.5 | feeder2_1416 | 0.17558 | 0.90766 | 0.1755 | 0.90723
750 | 12.5 | feeder2_1530 | 0.17564 | 0.90759 | 0.17557 | 0.90716
750 | 12.5 | feeder2_1425 | 0.17644 | 0.91576 | 0.17636 | 0.91533
750 | 12.5 | feeder2_1589 | 0.17469 | 0.91653 | 0.17461 | 0.9161
750 | 12.5 | feeder2_1435 | 0.17666 | 0.91734 | 0.17658 | 0.91691
750 | 12.5 | feeder2_1621 | 0.18372 | 0.933 | 0.18364 | 0.93257
750 | 12.5 | feeder2_1564 | 0.17622 | 0.91837 | 0.17614 | 0.91793
750 | 12.5 | feeder2_1704 | 0.17618 | 0.88196 | 0.17609 | 0.88148
750 | 12.5 | feeder2_1525 | 0.17705 | 0.88478 | 0.17697 | 0.88429
750 | 12.5 | feeder2_1716 | 0.18592 | 0.91068 | 0.18582 | 0.91019
750 | 12.5 | feeder2_1537 | 0.17679 | 0.88472 | 0.17672 | 0.88422
750 | 12.5 | feeder2_1645 | 0.17609 | 0.88522 | 0.17601 | 0.88472
750 | 12.5 | feeder2_1561 | 0.17665 | 0.88445 | 0.17657 | 0.88394
750 | 12.5 | feeder2_1657 | 0.17721 | 0.88392 | 0.17713 | 0.88342
750 | 12.5 | feeder2_1570 | 0.17658 | 0.88444 | 0.17649 | 0.88393
750 | 12.5 | feeder2_1756 | 0.17975 | 0.88115 | 0.17967 | 0.88064
750 | 12.5 | feeder2_1588 | 0.17647 | 0.88464 | 0.17639 | 0.88413
750 | 12.5 | feeder2_1628 | 0.1769 | 0.88424 | 0.17683 | 0.88373
750 | 12.5 | feeder2_1598 | 0.17634 | 0.885 | 0.17626 | 0.88449
750 | 12.5 | feeder2_1816 | 0.17796 | 0.88918 | 0.17787 | 0.88867
750 | 12.5 | feeder2_1765 | 0.17643 | 0.88521 | 0.17635 | 0.88469
750 | 12.5 | feeder2_1641 | 0.17545 | 0.88539 | 0.17536 | 0.88486
750 | 12.5 | feeder2_1689 | 0.17469 | 0.8858 | 0.17461 | 0.88525
750 | 12.5 | feeder2_1744 | 0.17551 | 0.88533 | 0.17543 | 0.8848
750 | 12.5 | feeder2_1817 | 0.17444 | 0.8863 | 0.17436 | 0.88575
750 | 12.5 | feeder2_1779 | 0.17472 | 0.88586 | 0.17464 | 0.88531
750 | 12.5 | feeder2_1800 | 0.17412 | 0.88638 | 0.17404 | 0.88583
750 | 12.5 | feeder2_1818 | 0.1725 | 0.88104 | 0.17244 | 0.88046
750 | 12.5 | feeder2_1753 | 0.17562 | 0.88524 | 0.17554 | 0.8847
750 | 12.5 | feeder2_1754 | 0.17553 | 0.88531 | 0.17545 | 0.88478
780 | 13 | secondary | 0.03627 | 0.02886 | 0.036245 | 0.028832
780 | 13 | feeder2_44 | 0.067658 | 0.15088 | 0.067609 | 0.15072
780 | 13 | feeder2_45 | 0.068841 | 0.15563 | 0.068792 | 0.15547
780 | 13 | feeder2_46 | 0.067545 | 0.15079 | 0.067499 | 0.15064
780 | 13 | feeder2_51 | 0.070133 | 0.16012 | 0.070083 | 0.15995
780 | 13 | feeder2_48 | 0.09011 | 0.17984 | 0.090065 | 0.17969
780 | 13 | feeder2_52 | 0.073761 | 0.15348 | 0.073706 | 0.15332
780 | 13 | feeder2_68 | 0.073834 | 0.17521 | 0.073783 | 0.17502
780 | 13 | feeder2_69 | 0.070446 | 0.1751 | 0.070399 | 0.17491
780 | 13 | feeder2_71 | 0.074359 | 0.17724 | 0.074307 | 0.17705
780 | 13 | feeder2_72 | 0.07789 | 0.18178 | 0.077842 | 0.18159
780 | 13 | feeder2_73 | 0.075886 | 0.18304 | 0.075833 | 0.18284
780 | 13 | feeder2_74 | 0.075846 | 0.18297 | 0.075792 | 0.18277
780 | 13 | feeder2_77 | 0.07721 | 0.18803 | 0.077158 | 0.18782
780 | 13 | feeder2_79 | 0.07528 | 0.1879 | 0.075226 | 0.18769
780 | 13 | feeder2_81 | 0.07943 | 0.19609 | 0.079371 | 0.19587
780 | 13 | feeder2_82 | 0.080309 | 0.19705 | 0.080254 | 0.19683
780 | 13 | feeder2_116 | 0.089395 | 0.23171 | 0.08933 | 0.23145
780 | 13 | feeder2_119 | 0.086105 | 0.22519 | 0.086027 | 0.22495
780 | 13 | feeder2_120 | 0.094499 | 0.24801 | 0.094428 | 0.24772
780 | 13 | feeder2_248 | 0.095499 | 0.24602 | 0.095428 | 0.24573
780 | 13 | feeder2_124 | 0.097682 | 0.25885 | 0.097611 | 0.25854
780 | 13 | feeder2_282 | 0.099198 | 0.26044 | 0.099131 | 0.26013
780 | 13 | feeder2_275 | 0.097626 | 0.25881 | 0.09756 | 0.25849
780 | 13 | feeder2_151 | 0.10314 | 0.27685 | 0.10307 | 0.2765
780 | 13 | feeder2_295 | 0.10259 | 0.27623 | 0.10252 | 0.27588
780 | 13 | feeder2_311 | 0.10308 | 0.27678 | 0.103 | 0.27643
780 | 13 | feeder2_201 | 0.11241 | 0.30805 | 0.11233 | 0.30765
780 | 13 | feeder2_314 | 0.11322 | 0.30898 | 0.11314 | 0.30858
780 | 13 | feeder2_342 | 0.12528 | 0.3504 | 0.1252 | 0.34992
780 | 13 | feeder2_368 | 0.12313 | 0.34582 | 0.12305 | 0.34537
780 | 13 | feeder2_347 | 0.13538 | 0.38096 | 0.13529 | 0.3804
780 | 13 | feeder2_353 | 0.13986 | 0.39405 | 0.13977 | 0.39346
780 | 13 | feeder2_518 | 0.14047 | 0.38607 | 0.14039 | 0.38552
780 | 13 | feeder2_365 | 0.14488 | 0.40908 | 0.1448 | 0.40845
780 | 13 | feeder2_653 | 0.1398 | 0.39399 | 0.13972 | 0.39339
780 | 13 | feeder2_377 | 0.14777 | 0.41703 | 0.14769 | 0.41638
780 | 13 | feeder2_622 | 0.14171 | 0.41091 | 0.14163 | 0.41027
780 | 13 | feeder2_451 | 0.12323 | 0.34592 | 0.12314 | 0.34546
780 | 13 | feeder2_383 | 0.11972 | 0.33931 | 0.11963 | 0.3389
780 | 13 | feeder2_385 | 0.15109 | 0.42651 | 0.15101 | 0.42583
780 | 13 | feeder2_621 | 0.14736 | 0.41656 | 0.14728 | 0.41591
780 | 13 | feeder2_611 | 0.11449 | 0.33386 | 0.11439 | 0.33347
780 | 13 | feeder2_405 | 0.11965 | 0.33919 | 0.11956 | 0.33877
780 | 13 | feeder2_461 | 0.16482 | 0.46844 | 0.16474 | 0.46767
780 | 13 | feeder2_594 | 0.15148 | 0.42518 | 0.15139 | 0.4245
780 | 13 | feeder2_732 | 0.11939 | 0.33895 | 0.11931 | 0.33854
780 | 13 | feeder2_417 | 0.11913 | 0.33834 | 0.11905 | 0.33793
780 | 13 | feeder2_663 | 0.11909 | 0.33827 | 0.119 | 0.33786
780 | 13 | feeder2_444 | 0.11875 | 0.33775 | 0.11866 | 0.33735
780 | 13 | feeder2_759 | 0.12213 | 0.34186 | 0.12205 | 0.34147
780 | 13 | feeder2_842 | 0.11791 | 0.33677 | 0.11782 | 0.33637
780 | 13 | feeder2_459 | 0.11854 | 0.33734 | 0.11846 | 0.33695
780 | 13 | feeder2_702 | 0.11963 | 0.33851 | 0.11954 | 0.33812
780 | 13 | feeder2_493 | 0.11764 | 0.33537 | 0.11755 | 0.33498
780 | 13 | feeder2_651 | 0.1648 | 0.46842 | 0.16472 | 0.46765
780 | 13 | feeder2_684 | 0.17611 | 0.5037 | 0.17603 | 0.50285
780 | 13 | feeder2_674 | 0.1165 | 0.33401 | 0.11641 | 0.33362
780 | 13 | feeder2_696 | 0.1176 | 0.33476 | 0.11751 | 0.33437
780 | 13 | feeder2_681 | 0.11378 | 0.33041 | 0.11368 | 0.33005
780 | 13 | feeder2_682 | 0.11647 | 0.33398 | 0.11638 | 0.3336
780 | 13 | feeder2_728 | 0.1771 | 0.50673 | 0.17702 | 0.50588
780 | 13 | feeder2_724 | 0.18614 | 0.53394 | 0.18605 | 0.53301
780 | 13 | feeder2_703 | 0.11751 | 0.33464 | 0.11742 | 0.33425
780 | 13 | feeder2_704 | 0.11747 | 0.33458 | 0.11738 | 0.33419
780 | 13 | feeder2_754 | 0.19639 | 0.54426 | 0.1963 | 0.54333
780 | 13 | feeder2_747 | 0.18934 | 0.54103 | 0.18925 | 0.54007
780 | 13 | feeder2_828 | 0.17675 | 0.50635 | 0.17666 | 0.50551
780 | 13 | feeder2_763 | 0.17877 | 0.51174 | 0.17868 | 0.5109
780 | 13 | feeder2_836 | 0.1859 | 0.53916 | 0.18582 | 0.53818
780 | 13 | feeder2_758 | 0.1919 | 0.54865 | 0.19181 | 0.54767
780 | 13 | feeder2_788 | 0.19299 | 0.54914 | 0.19291 | 0.54815
780 | 13 | feeder2_812 | 0.19942 | 0.57168 | 0.19933 | 0.57062
780 | 13 | feeder2_947 | 0.19056 | 0.52198 | 0.19047 | 0.52115
780 | 13 | feeder2_868 | 0.17947 | 0.51247 | 0.17939 | 0.51163
780 | 13 | feeder2_785 | 0.17891 | 0.51196 | 0.17882 | 0.51112
780 | 13 | feeder2_1176 | 0.17851 | 0.5116 | 0.17843 | 0.51076
780 | 13 | feeder2_846 | 0.17836 | 0.51131 | 0.17827 | 0.51047
780 | 13 | feeder2_911 | 0.17948 | 0.51342 | 0.1794 | 0.51259
780 | 13 | feeder2_1107 | 0.19731 | 0.55704 | 0.19722 | 0.55598
780 | 13 | feeder2_920 | 0.20213 | 0.58226 | 0.20204 | 0.58118
780 | 13 | feeder2_926 | 0.20631 | 0.59912 | 0.20622 | 0.59802
780 | 13 | feeder2_1239 | 0.20194 | 0.58102 | 0.20185 | 0.57995
780 | 13 | feeder2_933 | 0.20817 | 0.60658 | 0.20807 | 0.60547
780 | 13 | feeder2_1146 | 0.20633 | 0.59924 | 0.20624 | 0.59813
780 | 13 | feeder2_1124 | 0.20815 | 0.60657 | 0.20806 | 0.60545
780 | 13 | feeder2_942 | 0.21286 | 0.62555 | 0.21276 | 0.6244
780 | 13 | feeder2_952 | 0.21663 | 0.63943 | 0.21653 | 0.63822
780 | 13 | feeder2_965 | 0.21327 | 0.62742 | 0.21317 | 0.62628
780 | 13 | feeder2_961 | 0.21686 | 0.63996 | 0.21677 | 0.63875
780 | 13 | feeder2_963 | 0.21667 | 0.63964 | 0.21657 | 0.63844
780 | 13 | feeder2_973 | 0.21813 | 0.64296 | 0.21803 | 0.64172
780 | 13 | feeder2_1128 | 0.21685 | 0.63991 | 0.21676 | 0.6387
780 | 13 | feeder2_1113 | 0.21672 | 0.63969 | 0.21662 | 0.63849
780 | 13 | feeder2_1143 | 0.21932 | 0.65457 | 0.21923 | 0.65337
780 | 13 | feeder2_1238 | 0.24767 | 0.65608 | 0.24758 | 0.65496
780 | 13 | feeder2_979 | 0.21327 | 0.62741 | 0.21317 | 0.62627
780 | 13 | feeder2_1236 | 0.22015 | 0.6473 | 0.22006 | 0.64601
780 | 13 | feeder2_989 | 0.21813 | 0.64297 | 0.21804 | 0.64172
780 | 13 | feeder2_1196 | 0.21322 | 0.62737 | 0.21313 | 0.62622
780 | 13 | feeder2_1158 | 0.21677 | 0.64384 | 0.21667 | 0.64259
780 | 13 | feeder2_1122 | 0.19646 | 0.55144 | 0.19638 | 0.55038
780 | 13 | feeder2_1258 | 0.19716 | 0.55697 | 0.19708 | 0.55591
780 | 13 | feeder2_1303 | 0.19724 | 0.55222 | 0.19715 | 0.55116
780 | 13 | feeder2_1138 | 0.19575 | 0.54675 | 0.19567 | 0.54569
780 | 13 | feeder2_1304 | 0.1892 | 0.53845 | 0.1891 | 0.5374
780 | 13 | feeder2_1212 | 0.19596 | 0.54322 | 0.19587 | 0.54215
780 | 13 | feeder2_1311 | 0.19731 | 0.54455 | 0.19722 | 0.54349
780 | 13 | feeder2_1290 | 0.19604 | 0.53784 | 0.19596 | 0.53676
780 | 13 | feeder2_1325 | 0.22221 | 0.65518 | 0.22211 | 0.65383
780 | 13 | feeder2_1248 | 0.22014 | 0.6473 | 0.22004 | 0.64601
780 | 13 | feeder2_1249 | 0.25676 | 0.66392 | 0.25666 | 0.6628
780 | 13 | feeder2_1250 | 0.24995 | 0.65764 | 0.24986 | 0.65652
780 | 13 | feeder2_1366 | 0.22011 | 0.64729 | 0.22001 | 0.646
780 | 13 | feeder2_1266 | 0.19704 | 0.55691 | 0.19695 | 0.55585
780 | 13 | feeder2_1372 | 0.1963 | 0.53811 | 0.19622 | 0.53703
780 | 13 | feeder2_1363 | 0.19609 | 0.53185 | 0.19601 | 0.53076
780 | 13 | feeder2_1446 | 0.22246 | 0.65542 | 0.22236 | 0.65408
780 | 13 | feeder2_1502 | 0.22449 | 0.66393 | 0.22439 | 0.66253
780 | 13 | feeder2_1428 | 0.19603 | 0.53178 | 0.19595 | 0.53069
780 | 13 | feeder2_1380 | 0.19621 | 0.52494 | 0.19613 | 0.52384
780 | 13 | feeder2_1550 | 0.1963 | 0.52504 | 0.19623 | 0.52394
780 | 13 | feeder2_1386 | 0.19627 | 0.52161 | 0.19619 | 0.52051
780 | 13 | feeder2_1551 | 0.19653 | 0.51974 | 0.19644 | 0.51863
780 | 13 | feeder2_1400 | 0.19634 | 0.5205 | 0.19625 | 0.51939
780 | 13 | feeder2_1552 | 0.19542 | 0.51737 | 0.19535 | 0.51626
780 | 13 | feeder2_1408 | 0.19674 | 0.51985 | 0.19666 | 0.51874
780 | 13 | feeder2_1553 | 0.19664 | 0.51975 | 0.19656 | 0.51863
780 | 13 | feeder2_1416 | 0.19696 | 0.51957 | 0.19689 | 0.51845
780 | 13 | feeder2_1530 | 0.19859 | 0.51993 | 0.19851 | 0.51882
780 | 13 | feeder2_1425 | 0.19716 | 0.5188 | 0.19708 | 0.51768
780 | 13 | feeder2_1589 | 0.19631 | 0.51776 | 0.19623 | 0.51664
780 | 13 | feeder2_1435 | 0.19722 | 0.51876 | 0.19715 | 0.51763
780 | 13 | feeder2_1621 | 0.19311 | 0.5201 | 0.19305 | 0.51897
780 | 13 | feeder2_1564 | 0.1972 | 0.51865 | 0.19712 | 0.51752
780 | 13 | feeder2_1704 | 0.22345 | 0.66489 | 0.22335 | 0.66349
780 | 13 | feeder2_1525 | 0.22514 | 0.66589 | 0.22504 | 0.66447
780 | 13 | feeder2_1716 | 0.22167 | 0.66659 | 0.22159 | 0.66515
780 | 13 | feeder2_1537 | 0.22567 | 0.66832 | 0.22557 | 0.66689
780 | 13 | feeder2_1645 | 0.22519 | 0.66708 | 0.22509 | 0.66564
780 | 13 | feeder2_1561 | 0.22639 | 0.67176 | 0.22629 | 0.67031
780 | 13 | feeder2_1657 | 0.2344 | 0.67929 | 0.23429 | 0.67784
780 | 13 | feeder2_1570 | 0.2264 | 0.67134 | 0.2263 | 0.66988
780 | 13 | feeder2_1756 | 0.22893 | 0.67372 | 0.22883 | 0.67226
780 | 13 | feeder2_1588 | 0.22638 | 0.67078 | 0.22628 | 0.66932
780 | 13 | feeder2_1628 | 0.22766 | 0.67149 | 0.22756 | 0.67003
780 | 13 | feeder2_1598 | 0.22629 | 0.66986 | 0.22618 | 0.66838
780 | 13 | feeder2_1816 | 0.22105 | 0.67215 | 0.22099 | 0.67064
780 | 13 | feeder2_1765 | 0.22626 | 0.66984 | 0.22615 | 0.66837
780 | 13 | feeder2_1641 | 0.22504 | 0.66615 | 0.22493 | 0.66463
780 | 13 | feeder2_1689 | 0.22354 | 0.66168 | 0.22343 | 0.66013
780 | 13 | feeder2_1744 | 0.22636 | 0.66688 | 0.22625 | 0.66537
780 | 13 | feeder2_1817 | 0.22348 | 0.66147 | 0.22337 | 0.65992
780 | 13 | feeder2_1779 | 0.22353 | 0.66167 | 0.22342 | 0.66012
780 | 13 | feeder2_1800 | 0.21905 | 0.65466 | 0.21893 | 0.65311
780 | 13 | feeder2_1818 | 0.21644 | 0.65956 | 0.21628 | 0.65795
780 | 13 | feeder2_1753 | 0.22745 | 0.66792 | 0.22734 | 0.66641
780 | 13 | feeder2_1754 | 0.22703 | 0.66717 | 0.22692 | 0.66566
810 | 13.5 | secondary | 0.052171 | 0.062669 | 0.052159 | 0.062655
810 | 13.5 | feeder2_44 | 0.097203 | 0.32724 | 0.097174 | 0.32715
810 | 13.5 | feeder2_45 | 0.098955 | 0.33728 | 0.098926 | 0.3372
810 | 13.5 | feeder2_46 | 0.094167 | 0.33008 | 0.09414 | 0.33
810 | 13.5 | feeder2_51 | 0.10191 | 0.35439 | 0.10188 | 0.3543
810 | 13.5 | feeder2_48 | 0.10117 | 0.33941 | 0.10114 | 0.33932
810 | 13.5 | feeder2_52 | 0.10176 | 0.35318 | 0.10172 | 0.35309
810 | 13.5 | feeder2_68 | 0.11036 | 0.40305 | 0.11033 | 0.40295
810 | 13.5 | feeder2_69 | 0.11023 | 0.40304 | 0.1102 | 0.40293
810 | 13.5 | feeder2_71 | 0.11148 | 0.4095 | 0.11145 | 0.4094
810 | 13.5 | feeder2_72 | 0.11171 | 0.40973 | 0.11168 | 0.40963
810 | 13.5 | feeder2_73 | 0.115 | 0.42968 | 0.11496 | 0.42957
810 | 13.5 | feeder2_74 | 0.11618 | 0.42793 | 0.11614 | 0.42782
810 | 13.5 | feeder2_77 | 0.11801 | 0.44728 | 0.11797 | 0.44717
810 | 13.5 | feeder2_79 | 0.11792 | 0.44727 | 0.11789 | 0.44716
810 | 13.5 | feeder2_81 | 0.12279 | 0.47513 | 0.12275 | 0.47502
810 | 13.5 | feeder2_82 | 0.12538 | 0.47743 | 0.12534 | 0.47731
810 | 13.5 | feeder2_116 | 0.14355 | 0.59745 | 0.14351 | 0.5973
810 | 13.5 | feeder2_119 | 0.14353 | 0.5974 | 0.14349 | 0.59725
810 | 13.5 | feeder2_120 | 0.1513 | 0.64285 | 0.15126 | 0.64268
810 | 13.5 | feeder2_248 | 0.15126 | 0.64275 | 0.15122 | 0.64258
810 | 13.5 | feeder2_124 | 0.15609 | 0.67081 | 0.15605 | 0.67064
810 | 13.5 | feeder2_282 | 0.16276 | 0.67661 | 0.16272 | 0.67644
810 | 13.5 | feeder2_275 | 0.15605 | 0.67072 | 0.15601 | 0.67054
810 | 13.5 | feeder2_151 | 0.16338 | 0.71573 | 0.16334 | 0.71554
810 | 13.5 | feeder2_295 | 0.15844 | 0.7175 | 0.15839 | 0.71731
810 | 13.5 | feeder2_311 | 0.16331 | 0.71571 | 0.16326 | 0.71552
810 | 13.5 | feeder2_201 | 0.17655 | 0.78875 | 0.1765 | 0.78854
810 | 13.5 | feeder2_314 | 0.17663 | 0.78884 | 0.17658 | 0.78863
810 | 13.5 | feeder2_342 | 0.19522 | 0.89239 | 0.19517 | 0.89215
810 | 13.5 | feeder2_368 | 0.19672 | 0.8962 | 0.19667 | 0.89597
810 | 13.5 | feeder2_347 | 0.20257 | 0.93616 | 0.2025 | 0.93591
810 | 13.5 | feeder2_353 | 0.2061 | 0.9573 | 0.20604 | 0.95704
810 | 13.5 | feeder2_518 | 0.20379 | 0.93737 | 0.20374 | 0.93711
810 | 13.5 | feeder2_365 | 0.21004 | 0.9808 | 0.20997 | 0.98053
810 | 13.5 | feeder2_653 | 0.20606 | 0.95722 | 0.206 | 0.95696
810 | 13.5 | feeder2_377 | 0.21234 | 0.99295 | 0.21227 | 0.99268
810 | 13.5 | feeder2_622 | 0.20685 | 0.98337 | 0.20678 | 0.9831
810 | 13.5 | feeder2_451 | 0.19682 | 0.8963 | 0.19676 | 0.89606
810 | 13.5 | feeder2_383 | 0.19914 | 0.90232 | 0.19908 | 0.90208
810 | 13.5 | feeder2_385 | 0.21522 | 1.0066 | 0.21515 | 1.0063
810 | 13.5 | feeder2_621 | 0.20723 | 0.99468 | 0.20716 | 0.99441
810 | 13.5 | feeder2_611 | 0.1992 | 0.90169 | 0.19915 | 0.90146
810 | 13.5 | feeder2_405 | 0.19929 | 0.90273 | 0.19924 | 0.9025
810 | 13.5 | feeder2_461 | 0.22693 | 1.062 | 0.22686 | 1.0617
810 | 13.5 | feeder2_594 | 0.21519 | 1.0065 | 0.21512 | 1.0062
810 | 13.5 | feeder2_732 | 0.20085 | 0.89862 | 0.20079 | 0.89838
810 | 13.5 | feeder2_417 | 0.20044 | 0.90676 | 0.20038 | 0.90653
810 | 13.5 | feeder2_663 | 0.20038 | 0.90675 | 0.20032 | 0.90651
810 | 13.5 | feeder2_444 | 0.20131 | 0.90984 | 0.20125 | 0.9096
810 | 13.5 | feeder2_759 | 0.20226 | 0.91078 | 0.2022 | 0.91054
810 | 13.5 | feeder2_842 | 0.20103 | 0.90977 | 0.20097 | 0.90954
810 | 13.5 | feeder2_459 | 0.2016 | 0.91086 | 0.20154 | 0.91062
810 | 13.5 | feeder2_702 | 0.21301 | 0.92211 | 0.21295 | 0.92187
810 | 13.5 | feeder2_493 | 0.20137 | 0.91016 | 0.20131 | 0.90992
810 | 13.5 | feeder2_651 | 0.2269 | 1.062 | 0.22683 | 1.0617
810 | 13.5 | feeder2_684 | 0.23647 | 1.1073 | 0.2364 | 1.107
810 | 13.5 | feeder2_674 | 0.2014 | 0.90946 | 0.20134 | 0.90923
810 | 13.5 | feeder2_696 | 0.20098 | 0.91111 | 0.20092 | 0.91088
810 | 13.5 | feeder2_681 | 0.20108 | 0.90825 | 0.20102 | 0.90801
810 | 13.5 | feeder2_682 | 0.20201 | 0.90843 | 0.20195 | 0.90819
810 | 13.5 | feeder2_728 | 0.23808 | 1.1121 | 0.23801 | 1.1118
810 | 13.5 | feeder2_724 | 0.24387 | 1.1424 | 0.24379 | 1.1421
810 | 13.5 | feeder2_703 | 0.20087 | 0.91109 | 0.20081 | 0.91085
810 | 13.5 | feeder2_704 | 0.20048 | 0.91151 | 0.20042 | 0.91128
810 | 13.5 | feeder2_754 | 0.24502 | 1.1435 | 0.24494 | 1.1432
810 | 13.5 | feeder2_747 | 0.24677 | 1.1562 | 0.24669 | 1.1558
810 | 13.5 | feeder2_828 | 0.2382 | 1.1092 | 0.23813 | 1.1089
810 | 13.5 | feeder2_763 | 0.24082 | 1.1235 | 0.24074 | 1.1232
810 | 13.5 | feeder2_836 | 0.23962 | 1.1549 | 0.23954 | 1.1546
810 | 13.5 | feeder2_758 | 0.24942 | 1.1691 | 0.24934 | 1.1688
810 | 13.5 | feeder2_788 | 0.25039 | 1.1701 | 0.25031 | 1.1697
810 | 13.5 | feeder2_812 | 0.25734 | 1.2079 | 0.25726 | 1.2076
810 | 13.5 | feeder2_947 | 0.24357 | 1.1262 | 0.2435 | 1.1259
810 | 13.5 | feeder2_868 | 0.24181 | 1.1245 | 0.24174 | 1.1241
810 | 13.5 | feeder2_785 | 0.24209 | 1.129 | 0.24202 | 1.1287
810 | 13.5 | feeder2_1176 | 0.23726 | 1.1312 | 0.23718 | 1.1308
810 | 13.5 | feeder2_846 | 0.24167 | 1.1279 | 0.2416 | 1.1276
810 | 13.5 | feeder2_911 | 0.24572 | 1.1417 | 0.24564 | 1.1414
810 | 13.5 | feeder2_1107 | 0.2554 | 1.2028 | 0.25532 | 1.2025
810 | 13.5 | feeder2_920 | 0.26009 | 1.2202 | 0.26001 | 1.2199
810 | 13.5 | feeder2_926 | 0.2643 | 1.2398 | 0.26422 | 1.2394
810 | 13.5 | feeder2_1239 | 0.25996 | 1.2189 | 0.25988 | 1.2185
810 | 13.5 | feeder2_933 | 0.2661 | 1.2483 | 0.26601 | 1.2479
810 | 13.5 | feeder2_1146 | 0.26461 | 1.2404 | 0.26453 | 1.24
810 | 13.5 | feeder2_1124 | 0.26607 | 1.2483 | 0.26598 | 1.2479
810 | 13.5 | feeder2_942 | 0.27065 | 1.2698 | 0.27056 | 1.2695
810 | 13.5 | feeder2_952 | 0.27462 | 1.2901 | 0.27452 | 1.2897
810 | 13.5 | feeder2_965 | 0.27101 | 1.2713 | 0.27092 | 1.271
810 | 13.5 | feeder2_961 | 0.27485 | 1.2915 | 0.27476 | 1.2911
810 | 13.5 | feeder2_963 | 0.27466 | 1.2903 | 0.27456 | 1.2899
810 | 13.5 | feeder2_973 | 0.27612 | 1.2992 | 0.27602 | 1.2988
810 | 13.5 | feeder2_1128 | 0.27485 | 1.2906 | 0.27476 | 1.2902
810 | 13.5 | feeder2_1113 | 0.27501 | 1.2905 | 0.27492 | 1.2901
810 | 13.5 | feeder2_1143 | 0.27712 | 1.3017 | 0.27702 | 1.3013
810 | 13.5 | feeder2_1238 | 0.29766 | 1.2973 | 0.29757 | 1.297
810 | 13.5 | feeder2_979 | 0.27101 | 1.2711 | 0.27092 | 1.2707
810 | 13.5 | feeder2_1236 | 0.27803 | 1.311 | 0.27793 | 1.3106
810 | 13.5 | feeder2_989 | 0.27612 | 1.2992 | 0.27602 | 1.2988
810 | 13.5 | feeder2_1196 | 0.2715 | 1.2702 | 0.27141 | 1.2698
810 | 13.5 | feeder2_1158 | 0.27564 | 1.2991 | 0.27554 | 1.2987
810 | 13.5 | feeder2_1122 | 0.25494 | 1.1999 | 0.25486 | 1.1996
810 | 13.5 | feeder2_1258 | 0.25329 | 1.2041 | 0.25321 | 1.2038
810 | 13.5 | feeder2_1303 | 0.25657 | 1.2013 | 0.25649 | 1.2009
810 | 13.5 | feeder2_1138 | 0.25441 | 1.1972 | 0.25433 | 1.1968
810 | 13.5 | feeder2_1304 | 0.25439 | 1.1971 | 0.25431 | 1.1968
810 | 13.5 | feeder2_1212 | 0.25329 | 1.1913 | 0.25321 | 1.191
810 | 13.5 | feeder2_1311 | 0.25588 | 1.1939 | 0.2558 | 1.1935
810 | 13.5 | feeder2_1290 | 0.25145 | 1.182 | 0.25137 | 1.1817
810 | 13.5 | feeder2_1325 | 0.28074 | 1.3275 | 0.28064 | 1.3271
810 | 13.5 | feeder2_1248 | 0.27802 | 1.311 | 0.27792 | 1.3106
810 | 13.5 | feeder2_1249 | 0.29853 | 1.2981 | 0.29844 | 1.2977
810 | 13.5 | feeder2_1250 | 0.3143 | 1.3138 | 0.31421 | 1.3135
810 | 13.5 | feeder2_1366 | 0.27794 | 1.311 | 0.27784 | 1.3106
810 | 13.5 | feeder2_1266 | 0.25216 | 1.2047 | 0.25207 | 1.2043
810 | 13.5 | feeder2_1372 | 0.25217 | 1.1828 | 0.25209 | 1.1824
810 | 13.5 | feeder2_1363 | 0.2493 | 1.171 | 0.24921 | 1.1706
810 | 13.5 | feeder2_1446 | 0.28204 | 1.3285 | 0.28194 | 1.3281
810 | 13.5 | feeder2_1502 | 0.28328 | 1.3446 | 0.28318 | 1.3441
810 | 13.5 | feeder2_1428 | 0.24926 | 1.1709 | 0.24918 | 1.1706
810 | 13.5 | feeder2_1380 | 0.2467 | 1.1577 | 0.24662 | 1.1573
810 | 13.5 | feeder2_1550 | 0.24848 | 1.1589 | 0.2484 | 1.1586
810 | 13.5 | feeder2_1386 | 0.24513 | 1.1505 | 0.24504 | 1.1501
810 | 13.5 | feeder2_1551 | 0.24508 | 1.1504 | 0.245 | 1.15
810 | 13.5 | feeder2_1400 | 0.24438 | 1.1471 | 0.2443 | 1.1467
810 | 13.5 | feeder2_1552 | 0.24394 | 1.1461 | 0.24385 | 1.1458
810 | 13.5 | feeder2_1408 | 0.24295 | 1.1405 | 0.24286 | 1.1401
810 | 13.5 | feeder2_1553 | 0.24289 | 1.1404 | 0.24281 | 1.14
810 | 13.5 | feeder2_1416 | 0.24221 | 1.137 | 0.24212 | 1.1367
810 | 13.5 | feeder2_1530 | 0.24303 | 1.1376 | 0.24295 | 1.1372
810 | 13.5 | feeder2_1425 | 0.24063 | 1.1302 | 0.24054 | 1.1298
810 | 13.5 | feeder2_1589 | 0.23526 | 1.117 | 0.23517 | 1.1167
810 | 13.5 | feeder2_1435 | 0.24058 | 1.13 | 0.2405 | 1.1296
810 | 13.5 | feeder2_1621 | 0.23308 | 1.1292 | 0.233 | 1.1288
810 | 13.5 | feeder2_1564 | 0.24056 | 1.1299 | 0.24047 | 1.1295
810 | 13.5 | feeder2_1704 | 0.2828 | 1.3445 | 0.2827 | 1.344
810 | 13.5 | feeder2_1525 | 0.28394 | 1.349 | 0.28384 | 1.3486
810 | 13.5 | feeder2_1716 | 0.27749 | 1.3475 | 0.27738 | 1.3471
810 | 13.5 | feeder2_1537 | 0.28472 | 1.3544 | 0.28462 | 1.354
810 | 13.5 | feeder2_1645 | 0.28504 | 1.3536 | 0.28494 | 1.3532
810 | 13.5 | feeder2_1561 | 0.28561 | 1.361 | 0.28551 | 1.3606
810 | 13.5 | feeder2_1657 | 0.28596 | 1.3613 | 0.28586 | 1.3609
810 | 13.5 | feeder2_1570 | 0.28598 | 1.3638 | 0.28587 | 1.3633
810 | 13.5 | feeder2_1756 | 0.29095 | 1.3686 | 0.29084 | 1.3681
810 | 13.5 | feeder2_1588 | 0.28625 | 1.3661 | 0.28615 | 1.3656
810 | 13.5 | feeder2_1628 | 0.28747 | 1.3671 | 0.28736 | 1.3666
810 | 13.5 | feeder2_1598 | 0.2865 | 1.3686 | 0.2864 | 1.3681
810 | 13.5 | feeder2_1816 | 0.2825 | 1.3683 | 0.28239 | 1.3678
810 | 13.5 | feeder2_1765 | 0.2864 | 1.3686 | 0.28629 | 1.3681
810 | 13.5 | feeder2_1641 | 0.28783 | 1.3814 | 0.28772 | 1.3809
810 | 13.5 | feeder2_1689 | 0.28653 | 1.3808 | 0.28642 | 1.3803
810 | 13.5 | feeder2_1744 | 0.29498 | 1.3883 | 0.29487 | 1.3879
810 | 13.5 | feeder2_1817 | 0.28644 | 1.3805 | 0.28633 | 1.38
810 | 13.5 | feeder2_1779 | 0.28458 | 1.3822 | 0.28447 | 1.3817
810 | 13.5 | feeder2_1800 | 0.28651 | 1.3808 | 0.2864 | 1.3803
810 | 13.5 | feeder2_1818 | 0.27748 | 1.3719 | 0.27735 | 1.3714
810 | 13.5 | feeder2_1753 | 0.29737 | 1.3902 | 0.29726 | 1.3898
810 | 13.5 | feeder2_1754 | 0.29941 | 1.3927 | 0.2993 | 1.3922
840 | 14 | secondary | 0.048574 | 0.046593 | 0.04857 | 0.046585
840 | 14 | feeder2_44 | 0.090507 | 0.24331 | 0.090502 | 0.24327
840 | 14 | feeder2_45 | 0.092077 | 0.25085 | 0.092073 | 0.25081
840 | 14 | feeder2_46 | 0.09029 | 0.24445 | 0.090287 | 0.24441
840 | 14 | feeder2_51 | 0.094608 | 0.26454 | 0.094602 | 0.2645
840 | 14 | feeder2_48 | 0.097599 | 0.24664 | 0.097596 | 0.2466
840 | 14 | feeder2_52 | 0.093056 | 0.26267 | 0.093051 | 0.26263
840 | 14 | feeder2_68 | 0.10195 | 0.30381 | 0.10194 | 0.30376
840 | 14 | feeder2_69 | 0.10194 | 0.30397 | 0.10193 | 0.30392
840 | 14 | feeder2_71 | 0.10292 | 0.309 | 0.10292 | 0.30895
840 | 14 | feeder2_72 | 0.10314 | 0.30902 | 0.10314 | 0.30897
840 | 14 | feeder2_73 | 0.10598 | 0.32526 | 0.10598 | 0.3252
840 | 14 | feeder2_74 | 0.10598 | 0.32501 | 0.10598 | 0.32497
840 | 14 | feeder2_77 | 0.10864 | 0.33928 | 0.10864 | 0.33922
840 | 14 | feeder2_79 | 0.10688 | 0.34133 | 0.10687 | 0.34128
840 | 14 | feeder2_81 | 0.11295 | 0.36064 | 0.11294 | 0.36058
840 | 14 | feeder2_82 | 0.11565 | 0.36064 | 0.11565 | 0.36058
840 | 14 | feeder2_116 | 0.132 | 0.45613 | 0.132 | 0.45605
840 | 14 | feeder2_119 | 0.13195 | 0.45591 | 0.13194 | 0.45584
840 | 14 | feeder2_120 | 0.13924 | 0.49176 | 0.13923 | 0.49168
840 | 14 | feeder2_248 | 0.13913 | 0.49164 | 0.13913 | 0.49156
840 | 14 | feeder2_124 | 0.14372 | 0.51373 | 0.14371 | 0.51365
840 | 14 | feeder2_282 | 0.16346 | 0.51474 | 0.16345 | 0.51466
840 | 14 | feeder2_275 | 0.14351 | 0.51336 | 0.14351 | 0.51328
840 | 14 | feeder2_151 | 0.15021 | 0.55093 | 0.1502 | 0.55084
840 | 14 | feeder2_295 | 0.15075 | 0.56445 | 0.15075 | 0.56436
840 | 14 | feeder2_311 | 0.15022 | 0.55102 | 0.15021 | 0.55094
840 | 14 | feeder2_201 | 0.15875 | 0.59395 | 0.15875 | 0.59386
840 | 14 | feeder2_314 | 0.15954 | 0.5933 | 0.15954 | 0.59321
840 | 14 | feeder2_342 | 0.17062 | 0.65631 | 0.17062 | 0.65621
840 | 14 | feeder2_368 | 0.17019 | 0.65473 | 0.17018 | 0.65463
840 | 14 | feeder2_347 | 0.17724 | 0.6899 | 0.17723 | 0.68979
840 | 14 | feeder2_353 | 0.1805 | 0.70655 | 0.18049 | 0.70643
840 | 14 | feeder2_518 | 0.17811 | 0.68994 | 0.1781 | 0.68983
840 | 14 | feeder2_365 | 0.18414 | 0.72506 | 0.18413 | 0.72494
840 | 14 | feeder2_653 | 0.18041 | 0.70645 | 0.1804 | 0.70634
840 | 14 | feeder2_377 | 0.18612 | 0.73511 | 0.18611 | 0.73499
840 | 14 | feeder2_622 | 0.18414 | 0.7251 | 0.18414 | 0.72497
840 | 14 | feeder2_451 | 0.17026 | 0.65474 | 0.17026 | 0.65464
840 | 14 | feeder2_383 | 0.16948 | 0.65218 | 0.16947 | 0.65208
840 | 14 | feeder2_385 | 0.18774 | 0.74214 | 0.18773 | 0.74202
840 | 14 | feeder2_621 | 0.18792 | 0.74948 | 0.18792 | 0.74936
840 | 14 | feeder2_611 | 0.1683 | 0.65106 | 0.1683 | 0.65095
840 | 14 | feeder2_405 | 0.16946 | 0.65209 | 0.16946 | 0.65199
840 | 14 | feeder2_461 | 0.19434 | 0.77096 | 0.19433 | 0.77083
840 | 14 | feeder2_594 | 0.18766 | 0.74206 | 0.18766 | 0.74195
840 | 14 | feeder2_732 | 0.1668 | 0.64944 | 0.1668 | 0.64933
840 | 14 | feeder2_417 | 0.16958 | 0.65209 | 0.16957 | 0.65199
840 | 14 | feeder2_663 | 0.16857 | 0.65341 | 0.16856 | 0.65331
840 | 14 | feeder2_444 | 0.16972 | 0.65167 | 0.16972 | 0.65156
840 | 14 | feeder2_759 | 0.17102 | 0.6517 | 0.17101 | 0.6516
840 | 14 | feeder2_842 | 0.16996 | 0.65404 | 0.16995 | 0.65394
840 | 14 | feeder2_459 | 0.16974 | 0.65138 | 0.16973 | 0.65127
840 | 14 | feeder2_702 | 0.17333 | 0.64957 | 0.17332 | 0.64946
840 | 14 | feeder2_493 | 0.16942 | 0.6509 | 0.16942 | 0.65079
840 | 14 | feeder2_651 | 0.19441 | 0.77166 | 0.19441 | 0.77153
840 | 14 | feeder2_684 | 0.1996 | 0.79386 | 0.19959 | 0.79371
840 | 14 | feeder2_674 | 0.1688 | 0.65028 | 0.1688 | 0.65018
840 | 14 | feeder2_696 | 0.16955 | 0.65251 | 0.16954 | 0.65241
840 | 14 | feeder2_681 | 0.16725 | 0.64871 | 0.16725 | 0.64861
840 | 14 | feeder2_682 | 0.16861 | 0.65012 | 0.1686 | 0.65002
840 | 14 | feeder2_728 | 0.19739 | 0.78565 | 0.19738 | 0.78551
840 | 14 | feeder2_724 | 0.20905 | 0.83653 | 0.20904 | 0.83638
840 | 14 | feeder2_703 | 0.16956 | 0.65266 | 0.16956 | 0.65256
840 | 14 | feeder2_704 | 0.16949 | 0.6531 | 0.16948 | 0.653
840 | 14 | feeder2_754 | 0.21176 | 0.8349 | 0.21175 | 0.83475
840 | 14 | feeder2_747 | 0.21261 | 0.85479 | 0.2126 | 0.85464
840 | 14 | feeder2_828 | 0.1904 | 0.77843 | 0.19039 | 0.77829
840 | 14 | feeder2_763 | 0.19743 | 0.78482 | 0.19742 | 0.78467
840 | 14 | feeder2_836 | 0.21463 | 0.86844 | 0.21462 | 0.86828
840 | 14 | feeder2_758 | 0.21479 | 0.86494 | 0.21478 | 0.86478
840 | 14 | feeder2_788 | 0.2158 | 0.86506 | 0.21579 | 0.8649
840 | 14 | feeder2_812 | 0.22138 | 0.89638 | 0.22137 | 0.89621
840 | 14 | feeder2_947 | 0.19935 | 0.78503 | 0.19935 | 0.78488
840 | 14 | feeder2_868 | 0.19838 | 0.7849 | 0.19837 | 0.78475
840 | 14 | feeder2_785 | 0.19723 | 0.78411 | 0.19723 | 0.78397
840 | 14 | feeder2_1176 | 0.19727 | 0.78429 | 0.19726 | 0.78414
840 | 14 | feeder2_846 | 0.19593 | 0.78276 | 0.19592 | 0.78262
840 | 14 | feeder2_911 | 0.1973 | 0.78423 | 0.19729 | 0.78409
840 | 14 | feeder2_1107 | 0.22278 | 0.90063 | 0.22276 | 0.90047
840 | 14 | feeder2_920 | 0.22286 | 0.90414 | 0.22285 | 0.90397
840 | 14 | feeder2_926 | 0.22521 | 0.91642 | 0.2252 | 0.91624
840 | 14 | feeder2_1239 | 0.22269 | 0.90333 | 0.22268 | 0.90315
840 | 14 | feeder2_933 | 0.2262 | 0.92203 | 0.22619 | 0.92185
840 | 14 | feeder2_1146 | 0.22547 | 0.91564 | 0.22546 | 0.91546
840 | 14 | feeder2_1124 | 0.22621 | 0.92207 | 0.2262 | 0.92189
840 | 14 | feeder2_942 | 0.22869 | 0.93622 | 0.22868 | 0.93604
840 | 14 | feeder2_952 | 0.23207 | 0.95759 | 0.23206 | 0.9574
840 | 14 | feeder2_965 | 0.22873 | 0.93617 | 0.22872 | 0.93598
840 | 14 | feeder2_961 | 0.23238 | 0.95997 | 0.23237 | 0.95978
840 | 14 | feeder2_963 | 0.23209 | 0.95757 | 0.23207 | 0.95738
840 | 14 | feeder2_973 | 0.23409 | 0.97281 | 0.23408 | 0.97262
840 | 14 | feeder2_1128 | 0.23226 | 0.95965 | 0.23225 | 0.95946
840 | 14 | feeder2_1113 | 0.23258 | 0.95721 | 0.23257 | 0.95702
840 | 14 | feeder2_1143 | 0.23262 | 0.95749 | 0.23261 | 0.9573
840 | 14 | feeder2_1238 | 0.23521 | 0.93559 | 0.2352 | 0.93541
840 | 14 | feeder2_979 | 0.22871 | 0.9361 | 0.2287 | 0.93591
840 | 14 | feeder2_1236 | 0.23655 | 0.99145 | 0.23654 | 0.99125
840 | 14 | feeder2_989 | 0.23409 | 0.97282 | 0.23408 | 0.97263
840 | 14 | feeder2_1196 | 0.22855 | 0.93588 | 0.22854 | 0.9357
840 | 14 | feeder2_1158 | 0.23421 | 0.97351 | 0.2342 | 0.97332
840 | 14 | feeder2_1122 | 0.22331 | 0.90152 | 0.2233 | 0.90135
840 | 14 | feeder2_1258 | 0.2224 | 0.90166 | 0.22239 | 0.90148
840 | 14 | feeder2_1303 | 0.22412 | 0.90167 | 0.22411 | 0.90149
840 | 14 | feeder2_1138 | 0.22371 | 0.90216 | 0.2237 | 0.90199
840 | 14 | feeder2_1304 | 0.22353 | 0.90183 | 0.22352 | 0.90166
840 | 14 | feeder2_1212 | 0.22471 | 0.90394 | 0.2247 | 0.90376
840 | 14 | feeder2_1311 | 0.23987 | 0.90546 | 0.23986 | 0.90528
840 | 14 | feeder2_1290 | 0.22431 | 0.90387 | 0.2243 | 0.9037
840 | 14 | feeder2_1325 | 0.23977 | 1.0108 | 0.23976 | 1.0106
840 | 14 | feeder2_1248 | 0.23654 | 0.99148 | 0.23653 | 0.99128
840 | 14 | feeder2_1249 | 0.23653 | 0.93535 | 0.23652 | 0.93516
840 | 14 | feeder2_1250 | 0.23658 | 0.93581 | 0.23657 | 0.93563
840 | 14 | feeder2_1366 | 0.23512 | 0.99351 | 0.23511 | 0.99331
840 | 14 | feeder2_1266 | 0.22243 | 0.90209 | 0.22242 | 0.90191
840 | 14 | feeder2_1372 | 0.22459 | 0.90422 | 0.22458 | 0.90405
840 | 14 | feeder2_1363 | 0.22389 | 0.90327 | 0.22388 | 0.9031
840 | 14 | feeder2_1446 | 0.2417 | 1.0103 | 0.24169 | 1.0101
840 | 14 | feeder2_1502 | 0.24297 | 1.033 | 0.24296 | 1.0328
840 | 14 | feeder2_1428 | 0.22368 | 0.90289 | 0.22367 | 0.90272
840 | 14 | feeder2_1380 | 0.22367 | 0.90338 | 0.22366 | 0.90321
840 | 14 | feeder2_1550 | 0.22552 | 0.90284 | 0.22551 | 0.90267
840 | 14 | feeder2_1386 | 0.2234 | 0.90363 | 0.22339 | 0.90346
840 | 14 | feeder2_1551 | 0.22319 | 0.90327 | 0.22318 | 0.90309
840 | 14 | feeder2_1400 | 0.22331 | 0.90386 | 0.2233 | 0.90369
840 | 14 | feeder2_1552 | 0.22219 | 0.90263 | 0.22218 | 0.90246
840 | 14 | feeder2_1408 | 0.22327 | 0.905 | 0.22326 | 0.90483
840 | 14 | feeder2_1553 | 0.22291 | 0.90434 | 0.2229 | 0.90416
840 | 14 | feeder2_1416 | 0.22332 | 0.9058 | 0.22331 | 0.90563
840 | 14 | feeder2_1530 | 0.22342 | 0.90582 | 0.22341 | 0.90565
840 | 14 | feeder2_1425 | 0.22342 | 0.90729 | 0.22341 | 0.90712
840 | 14 | feeder2_1589 | 0.22335 | 0.90722 | 0.22334 | 0.90705
840 | 14 | feeder2_1435 | 0.22344 | 0.9076 | 0.22343 | 0.90743
840 | 14 | feeder2_1621 | 0.22266 | 0.91115 | 0.22265 | 0.91098
840 | 14 | feeder2_1564 | 0.22341 | 0.90747 | 0.2234 | 0.90729
840 | 14 | feeder2_1704 | 0.24308 | 1.0338 | 0.24307 | 1.0336
840 | 14 | feeder2_1525 | 0.24375 | 1.0384 | 0.24374 | 1.0382
840 | 14 | feeder2_1716 | 0.24065 | 1.0442 | 0.24064 | 1.044
840 | 14 | feeder2_1537 | 0.24464 | 1.0436 | 0.24463 | 1.0434
840 | 14 | feeder2_1645 | 0.24389 | 1.0428 | 0.24388 | 1.0426
840 | 14 | feeder2_1561 | 0.24578 | 1.05 | 0.24576 | 1.0498
840 | 14 | feeder2_1657 | 0.24767 | 1.0491 | 0.24766 | 1.0489
840 | 14 | feeder2_1570 | 0.24618 | 1.053 | 0.24617 | 1.0528
840 | 14 | feeder2_1756 | 0.27428 | 1.0565 | 0.27427 | 1.0562
840 | 14 | feeder2_1588 | 0.24634 | 1.0554 | 0.24633 | 1.0552
840 | 14 | feeder2_1628 | 0.24706 | 1.0556 | 0.24705 | 1.0553
840 | 14 | feeder2_1598 | 0.24653 | 1.0584 | 0.24651 | 1.0582
840 | 14 | feeder2_1816 | 0.24325 | 1.0723 | 0.24324 | 1.0721
840 | 14 | feeder2_1765 | 0.24656 | 1.0586 | 0.24655 | 1.0583
840 | 14 | feeder2_1641 | 0.24719 | 1.0689 | 0.24717 | 1.0687
840 | 14 | feeder2_1689 | 0.24768 | 1.0777 | 0.24767 | 1.0774
840 | 14 | feeder2_1744 | 0.24769 | 1.0691 | 0.24768 | 1.0688
840 | 14 | feeder2_1817 | 0.24739 | 1.0767 | 0.24737 | 1.0765
840 | 14 | feeder2_1779 | 0.24735 | 1.0789 | 0.24734 | 1.0786
840 | 14 | feeder2_1800 | 0.2474 | 1.0774 | 0.24739 | 1.0771
840 | 14 | feeder2_1818 | 0.24398 | 1.0928 | 0.24396 | 1.0925
840 | 14 | feeder2_1753 | 0.2488 | 1.0693 | 0.24878 | 1.0691
840 | 14 | feeder2_1754 | 0.2478 | 1.0691 | 0.24779 | 1.0689
870 | 14.5 | secondary | 0.056478 | 0.056493 | 0.056469 | 0.056486
870 | 14.5 | feeder2_44 | 0.10525 | 0.29506 | 0.10524 | 0.29504
870 | 14.5 | feeder2_45 | 0.10709 | 0.30352 | 0.10707 | 0.3035
870 | 14.5 | feeder2_46 | 0.10081 | 0.30453 | 0.10079 | 0.30451
870 | 14.5 | feeder2_51 | 0.11028 | 0.31823 | 0.11026 | 0.31821
870 | 14.5 | feeder2_48 | 0.10726 | 0.30353 | 0.10724 | 0.30352
870 | 14.5 | feeder2_52 | 0.10752 | 0.31525 | 0.10751 | 0.31523
870 | 14.5 | feeder2_68 | 0.11956 | 0.3609 | 0.11954 | 0.36087
870 | 14.5 | feeder2_69 | 0.11958 | 0.36106 | 0.11956 | 0.36104
870 | 14.5 | feeder2_71 | 0.12079 | 0.36655 | 0.12077 | 0.36653
870 | 14.5 | feeder2_72 | 0.12099 | 0.36657 | 0.12097 | 0.36654
870 | 14.5 | feeder2_73 | 0.12465 | 0.38425 | 0.12463 | 0.38423
870 | 14.5 | feeder2_74 | 0.12453 | 0.38412 | 0.12451 | 0.38409
870 | 14.5 | feeder2_77 | 0.12796 | 0.39946 | 0.12794 | 0.39943
870 | 14.5 | feeder2_79 | 0.12797 | 0.39957 | 0.12795 | 0.39955
870 | 14.5 | feeder2_81 | 0.1332 | 0.4235 | 0.13318 | 0.42347
870 | 14.5 | feeder2_82 | 0.13645 | 0.42363 | 0.13643 | 0.4236
870 | 14.5 | feeder2_116 | 0.15641 | 0.53085 | 0.15639 | 0.53082
870 | 14.5 | feeder2_119 | 0.15635 | 0.53079 | 0.15633 | 0.53076
870 | 14.5 | feeder2_120 | 0.16506 | 0.57071 | 0.16503 | 0.57067
870 | 14.5 | feeder2_248 | 0.16495 | 0.57059 | 0.16492 | 0.57055
870 | 14.5 | feeder2_124 | 0.1704 | 0.59528 | 0.17037 | 0.59524
870 | 14.5 | feeder2_282 | 0.17286 | 0.5956 | 0.17283 | 0.59556
870 | 14.5 | feeder2_275 | 0.16974 | 0.59466 | 0.16971 | 0.59462
870 | 14.5 | feeder2_151 | 0.17987 | 0.63833 | 0.17985 | 0.63828
870 | 14.5 | feeder2_295 | 0.18018 | 0.64011 | 0.18015 | 0.64006
870 | 14.5 | feeder2_311 | 0.1799 | 0.63842 | 0.17987 | 0.63838
870 | 14.5 | feeder2_201 | 0.19526 | 0.7075 | 0.19523 | 0.70745
870 | 14.5 | feeder2_314 | 0.19737 | 0.70581 | 0.19734 | 0.70576
870 | 14.5 | feeder2_342 | 0.21626 | 0.80903 | 0.21622 | 0.80898
870 | 14.5 | feeder2_368 | 0.21633 | 0.80904 | 0.21629 | 0.80899
870 | 14.5 | feeder2_347 | 0.22643 | 0.85887 | 0.22639 | 0.85881
870 | 14.5 | feeder2_353 | 0.23142 | 0.88349 | 0.23138 | 0.88342
870 | 14.5 | feeder2_518 | 0.22788 | 0.85908 | 0.22784 | 0.85902
870 | 14.5 | feeder2_365 | 0.23698 | 0.91085 | 0.23694 | 0.91078
870 | 14.5 | feeder2_653 | 0.23132 | 0.88339 | 0.23129 | 0.88332
870 | 14.5 | feeder2_377 | 0.24 | 0.9257 | 0.23996 | 0.92563
870 | 14.5 | feeder2_622 | 0.23699 | 0.91088 | 0.23695 | 0.91081
870 | 14.5 | feeder2_451 | 0.21788 | 0.80783 | 0.21785 | 0.80777
870 | 14.5 | feeder2_383 | 0.21607 | 0.80995 | 0.21604 | 0.8099
870 | 14.5 | feeder2_385 | 0.24336 | 0.94223 | 0.24332 | 0.94216
870 | 14.5 | feeder2_621 | 0.24045 | 0.92757 | 0.24041 | 0.92749
870 | 14.5 | feeder2_611 | 0.21599 | 0.80987 | 0.21595 | 0.80981
870 | 14.5 | feeder2_405 | 0.21606 | 0.81002 | 0.21602 | 0.80996
870 | 14.5 | feeder2_461 | 0.25708 | 1.0095 | 0.25704 | 1.0094
870 | 14.5 | feeder2_594 | 0.24329 | 0.94216 | 0.24325 | 0.94209
870 | 14.5 | feeder2_732 | 0.21212 | 0.80597 | 0.21208 | 0.80591
870 | 14.5 | feeder2_417 | 0.2162 | 0.81139 | 0.21617 | 0.81133
870 | 14.5 | feeder2_663 | 0.2153 | 0.81276 | 0.21526 | 0.8127
870 | 14.5 | feeder2_444 | 0.21635 | 0.812 | 0.21632 | 0.81195
870 | 14.5 | feeder2_759 | 0.21827 | 0.8123 | 0.21823 | 0.81224
870 | 14.5 | feeder2_842 | 0.21688 | 0.81402 | 0.21684 | 0.81397
870 | 14.5 | feeder2_459 | 0.21636 | 0.81208 | 0.21633 | 0.81203
870 | 14.5 | feeder2_702 | 0.21769 | 0.81232 | 0.21765 | 0.81226
870 | 14.5 | feeder2_493 | 0.2163 | 0.81222 | 0.21626 | 0.81216
870 | 14.5 | feeder2_651 | 0.2576 | 1.011 | 0.25756 | 1.011
870 | 14.5 | feeder2_684 | 0.26792 | 1.0626 | 0.26787 | 1.0625
870 | 14.5 | feeder2_674 | 0.21596 | 0.81188 | 0.21593 | 0.81181
870 | 14.5 | feeder2_696 | 0.21656 | 0.81417 | 0.21653 | 0.81412
870 | 14.5 | feeder2_681 | 0.2151 | 0.81099 | 0.21506 | 0.81093
870 | 14.5 | feeder2_682 | 0.21589 | 0.8118 | 0.21585 | 0.81174
870 | 14.5 | feeder2_728 | 0.26769 | 1.0607 | 0.26765 | 1.0606
870 | 14.5 | feeder2_724 | 0.2796 | 1.1214 | 0.27956 | 1.1213
870 | 14.5 | feeder2_703 | 0.2166 | 0.81431 | 0.21656 | 0.81426
870 | 14.5 | feeder2_704 | 0.21662 | 0.81491 | 0.21659 | 0.81486
870 | 14.5 | feeder2_754 | 0.27966 | 1.1214 | 0.27961 | 1.1213
870 | 14.5 | feeder2_747 | 0.28437 | 1.1454 | 0.28433 | 1.1453
870 | 14.5 | feeder2_828 | 0.26667 | 1.0596 | 0.26662 | 1.0596
870 | 14.5 | feeder2_763 | 0.26782 | 1.0594 | 0.26778 | 1.0594
870 | 14.5 | feeder2_836 | 0.28481 | 1.1618 | 0.28476 | 1.1617
870 | 14.5 | feeder2_758 | 0.28766 | 1.1592 | 0.28761 | 1.1591
870 | 14.5 | feeder2_788 | 0.28991 | 1.1583 | 0.28986 | 1.1582
870 | 14.5 | feeder2_812 | 0.2973 | 1.2024 | 0.29725 | 1.2023
870 | 14.5 | feeder2_947 | 0.27103 | 1.06 | 0.27098 | 1.0599
870 | 14.5 | feeder2_868 | 0.26913 | 1.0592 | 0.26908 | 1.0591
870 | 14.5 | feeder2_785 | 0.26756 | 1.0586 | 0.26752 | 1.0586
870 | 14.5 | feeder2_1176 | 0.26762 | 1.0588 | 0.26758 | 1.0587
870 | 14.5 | feeder2_846 | 0.26612 | 1.0572 | 0.26608 | 1.0571
870 | 14.5 | feeder2_911 | 0.26758 | 1.0587 | 0.26753 | 1.0586
870 | 14.5 | feeder2_1107 | 0.29944 | 1.2009 | 0.29938 | 1.2008
870 | 14.5 | feeder2_920 | 0.29943 | 1.215 | 0.29938 | 1.2149
870 | 14.5 | feeder2_926 | 0.30273 | 1.2343 | 0.30267 | 1.2342
870 | 14.5 | feeder2_1239 | 0.29928 | 1.2143 | 0.29923 | 1.2142
870 | 14.5 | feeder2_933 | 0.30414 | 1.243 | 0.30408 | 1.2429
870 | 14.5 | feeder2_1146 | 0.30299 | 1.2334 | 0.30294 | 1.2333
870 | 14.5 | feeder2_1124 | 0.30353 | 1.244 | 0.30348 | 1.2439
870 | 14.5 | feeder2_942 | 0.30774 | 1.2643 | 0.30768 | 1.2641
870 | 14.5 | feeder2_952 | 0.31301 | 1.2972 | 0.31295 | 1.2971
870 | 14.5 | feeder2_965 | 0.30775 | 1.264 | 0.3077 | 1.2639
870 | 14.5 | feeder2_961 | 0.31355 | 1.3008 | 0.31349 | 1.3007
870 | 14.5 | feeder2_963 | 0.31301 | 1.2972 | 0.31296 | 1.2971
870 | 14.5 | feeder2_973 | 0.31643 | 1.32 | 0.31638 | 1.3199
870 | 14.5 | feeder2_1128 | 0.31354 | 1.3007 | 0.31348 | 1.3006
870 | 14.5 | feeder2_1113 | 0.31356 | 1.2968 | 0.31351 | 1.2967
870 | 14.5 | feeder2_1143 | 0.31314 | 1.2978 | 0.31309 | 1.2977
870 | 14.5 | feeder2_1238 | 0.31451 | 1.2627 | 0.31445 | 1.2626
870 | 14.5 | feeder2_979 | 0.30768 | 1.2638 | 0.30763 | 1.2637
870 | 14.5 | feeder2_1236 | 0.32061 | 1.348 | 0.32055 | 1.3478
870 | 14.5 | feeder2_989 | 0.31643 | 1.32 | 0.31637 | 1.3199
870 | 14.5 | feeder2_1196 | 0.30686 | 1.2631 | 0.30681 | 1.263
870 | 14.5 | feeder2_1158 | 0.31673 | 1.3209 | 0.31667 | 1.3208
870 | 14.5 | feeder2_1122 | 0.30017 | 1.1997 | 0.30012 | 1.1996
870 | 14.5 | feeder2_1258 | 0.29959 | 1.2019 | 0.29954 | 1.2018
870 | 14.5 | feeder2_1303 | 0.30178 | 1.1998 | 0.30173 | 1.1997
870 | 14.5 | feeder2_1138 | 0.30069 | 1.1986 | 0.30064 | 1.1985
870 | 14.5 | feeder2_1304 | 0.30065 | 1.1985 | 0.3006 | 1.1984
870 | 14.5 | feeder2_1212 | 0.30184 | 1.1964 | 0.30179 | 1.1963
870 | 14.5 | feeder2_1311 | 0.31798 | 1.1965 | 0.31793 | 1.1965
870 | 14.5 | feeder2_1290 | 0.30163 | 1.1924 | 0.30158 | 1.1923
870 | 14.5 | feeder2_1325 | 0.32403 | 1.3727 | 0.32397 | 1.3726
870 | 14.5 | feeder2_1248 | 0.32062 | 1.348 | 0.32056 | 1.3479
870 | 14.5 | feeder2_1249 | 0.31515 | 1.2628 | 0.3151 | 1.2627
870 | 14.5 | feeder2_1250 | 0.3177 | 1.2614 | 0.31764 | 1.2613
870 | 14.5 | feeder2_1366 | 0.32066 | 1.3481 | 0.3206 | 1.348
870 | 14.5 | feeder2_1266 | 0.29972 | 1.2029 | 0.29967 | 1.2028
870 | 14.5 | feeder2_1372 | 0.30322 | 1.1918 | 0.30317 | 1.1917
870 | 14.5 | feeder2_1363 | 0.30102 | 1.1889 | 0.30097 | 1.1888
870 | 14.5 | feeder2_1446 | 0.32527 | 1.3732 | 0.3252 | 1.3731
870 | 14.5 | feeder2_1502 | 0.32778 | 1.3999 | 0.32772 | 1.3997
870 | 14.5 | feeder2_1428 | 0.30094 | 1.1888 | 0.30088 | 1.1887
870 | 14.5 | feeder2_1380 | 0.30031 | 1.1848 | 0.30027 | 1.1847
870 | 14.5 | feeder2_1550 | 0.30168 | 1.185 | 0.30163 | 1.1849
870 | 14.5 | feeder2_1386 | 0.2999 | 1.1826 | 0.29985 | 1.1825
870 | 14.5 | feeder2_1551 | 0.29916 | 1.1818 | 0.29911 | 1.1818
870 | 14.5 | feeder2_1400 | 0.29981 | 1.1818 | 0.29976 | 1.1817
870 | 14.5 | feeder2_1552 | 0.29835 | 1.1803 | 0.29831 | 1.1802
870 | 14.5 | feeder2_1408 | 0.2998 | 1.181 | 0.29975 | 1.1809
870 | 14.5 | feeder2_1553 | 0.29933 | 1.1805 | 0.29928 | 1.1804
870 | 14.5 | feeder2_1416 | 0.29985 | 1.1807 | 0.2998 | 1.1806
870 | 14.5 | feeder2_1530 | 0.3018 | 1.1792 | 0.30175 | 1.1791
870 | 14.5 | feeder2_1425 | 0.29972 | 1.1808 | 0.29967 | 1.1807
870 | 14.5 | feeder2_1589 | 0.29926 | 1.1804 | 0.29921 | 1.1803
870 | 14.5 | feeder2_1435 | 0.29972 | 1.1809 | 0.29968 | 1.1808
870 | 14.5 | feeder2_1621 | 0.30021 | 1.1828 | 0.30016 | 1.1827
870 | 14.5 | feeder2_1564 | 0.29937 | 1.1801 | 0.29932 | 1.18
870 | 14.5 | feeder2_1704 | 0.32739 | 1.4018 | 0.32733 | 1.4017
870 | 14.5 | feeder2_1525 | 0.3287 | 1.4061 | 0.32864 | 1.406
870 | 14.5 | feeder2_1716 | 0.32609 | 1.4199 | 0.32603 | 1.4197
870 | 14.5 | feeder2_1537 | 0.32959 | 1.4111 | 0.32952 | 1.411
870 | 14.5 | feeder2_1645 | 0.32851 | 1.4102 | 0.32844 | 1.41
870 | 14.5 | feeder2_1561 | 0.33079 | 1.4173 | 0.33072 | 1.4172
870 | 14.5 | feeder2_1657 | 0.33083 | 1.4173 | 0.33076 | 1.4172
870 | 14.5 | feeder2_1570 | 0.3313 | 1.42 | 0.33124 | 1.4198
870 | 14.5 | feeder2_1756 | 0.36077 | 1.4183 | 0.36071 | 1.4181
870 | 14.5 | feeder2_1588 | 0.33158 | 1.4224 | 0.33151 | 1.4223
870 | 14.5 | feeder2_1628 | 0.33211 | 1.4225 | 0.33204 | 1.4224
870 | 14.5 | feeder2_1598 | 0.33192 | 1.4255 | 0.33185 | 1.4253
870 | 14.5 | feeder2_1816 | 0.34467 | 1.4693 | 0.34459 | 1.4691
870 | 14.5 | feeder2_1765 | 0.33199 | 1.4256 | 0.33192 | 1.4255
870 | 14.5 | feeder2_1641 | 0.33143 | 1.428 | 0.33136 | 1.4279
870 | 14.5 | feeder2_1689 | 0.3309 | 1.43 | 0.33083 | 1.4299
870 | 14.5 | feeder2_1744 | 0.33215 | 1.428 | 0.33208 | 1.4279
870 | 14.5 | feeder2_1817 | 0.33058 | 1.4291 | 0.33051 | 1.429
870 | 14.5 | feeder2_1779 | 0.33118 | 1.431 | 0.33111 | 1.4308
870 | 14.5 | feeder2_1800 | 0.3303 | 1.4297 | 0.33024 | 1.4295
870 | 14.5 | feeder2_1818 | 0.32448 | 1.4291 | 0.3244 | 1.4289
870 | 14.5 | feeder2_1753 | 0.33433 | 1.4281 | 0.33427 | 1.428
870 | 14.5 | feeder2_1754 | 0.33217 | 1.428 | 0.3321 | 1.4279
900 | 15 | secondary | 0.04095 | 0.020852 | 0.040968 | 0.02088
900 | 15 | feeder2_44 | 0.076248 | 0.10881 | 0.076281 | 0.10895
900 | 15 | feeder2_45 | 0.077547 | 0.11196 | 0.077583 | 0.11211
900 | 15 | feeder2_46 | 0.076165 | 0.112 | 0.076199 | 0.11214
900 | 15 | feeder2_51 | 0.079805 | 0.11745 | 0.079841 | 0.11759
900 | 15 | feeder2_48 | 0.077711 | 0.11192 | 0.077745 | 0.11207
900 | 15 | feeder2_52 | 0.073592 | 0.11352 | 0.073623 | 0.11368
900 | 15 | feeder2_68 | 0.087165 | 0.13538 | 0.087206 | 0.13554
900 | 15 | feeder2_69 | 0.08718 | 0.13556 | 0.087219 | 0.13572
900 | 15 | feeder2_71 | 0.088143 | 0.13777 | 0.088184 | 0.13794
900 | 15 | feeder2_72 | 0.088336 | 0.13774 | 0.088378 | 0.1379
900 | 15 | feeder2_73 | 0.091207 | 0.14529 | 0.091247 | 0.14547
900 | 15 | feeder2_74 | 0.091088 | 0.14517 | 0.091129 | 0.14535
900 | 15 | feeder2_77 | 0.093846 | 0.15179 | 0.093884 | 0.15198
900 | 15 | feeder2_79 | 0.091148 | 0.15493 | 0.091193 | 0.1551
900 | 15 | feeder2_81 | 0.098128 | 0.16086 | 0.09817 | 0.16105
900 | 15 | feeder2_82 | 0.099647 | 0.16059 | 0.099691 | 0.16078
900 | 15 | feeder2_116 | 0.11723 | 0.20185 | 0.11728 | 0.20208
900 | 15 | feeder2_119 | 0.11717 | 0.20179 | 0.11723 | 0.20202
900 | 15 | feeder2_120 | 0.12434 | 0.21714 | 0.1244 | 0.21739
900 | 15 | feeder2_248 | 0.12419 | 0.21699 | 0.12425 | 0.21724
900 | 15 | feeder2_124 | 0.12874 | 0.22662 | 0.12879 | 0.22689
900 | 15 | feeder2_282 | 0.13626 | 0.22619 | 0.13632 | 0.22644
900 | 15 | feeder2_275 | 0.12841 | 0.22649 | 0.12846 | 0.22676
900 | 15 | feeder2_151 | 0.13605 | 0.24318 | 0.13611 | 0.24347
900 | 15 | feeder2_295 | 0.13694 | 0.24908 | 0.137 | 0.24937
900 | 15 | feeder2_311 | 0.13607 | 0.24329 | 0.13613 | 0.24357
900 | 15 | feeder2_201 | 0.14702 | 0.26228 | 0.14708 | 0.2626
900 | 15 | feeder2_314 | 0.14709 | 0.26228 | 0.14715 | 0.2626
900 | 15 | feeder2_342 | 0.16264 | 0.28938 | 0.16271 | 0.28975
900 | 15 | feeder2_368 | 0.16296 | 0.28838 | 0.16303 | 0.28874
900 | 15 | feeder2_347 | 0.16996 | 0.30453 | 0.17003 | 0.30492
900 | 15 | feeder2_353 | 0.17347 | 0.31261 | 0.17355 | 0.31302
900 | 15 | feeder2_518 | 0.17119 | 0.30344 | 0.17127 | 0.30383
900 | 15 | feeder2_365 | 0.17739 | 0.32163 | 0.17746 | 0.32206
900 | 15 | feeder2_653 | 0.17338 | 0.31252 | 0.17345 | 0.31293
900 | 15 | feeder2_377 | 0.17951 | 0.32652 | 0.17959 | 0.32696
900 | 15 | feeder2_622 | 0.1774 | 0.32166 | 0.17747 | 0.32209
900 | 15 | feeder2_451 | 0.16303 | 0.28838 | 0.1631 | 0.28875
900 | 15 | feeder2_383 | 0.16347 | 0.28677 | 0.16354 | 0.28714
900 | 15 | feeder2_385 | 0.18164 | 0.33014 | 0.18173 | 0.33058
900 | 15 | feeder2_621 | 0.18084 | 0.3328 | 0.18092 | 0.33324
900 | 15 | feeder2_611 | 0.16339 | 0.28669 | 0.16346 | 0.28705
900 | 15 | feeder2_405 | 0.16351 | 0.28668 | 0.16357 | 0.28704
900 | 15 | feeder2_461 | 0.19033 | 0.34498 | 0.19042 | 0.34546
900 | 15 | feeder2_594 | 0.18154 | 0.33004 | 0.18162 | 0.33048
900 | 15 | feeder2_732 | 0.15892 | 0.28279 | 0.15898 | 0.28316
900 | 15 | feeder2_417 | 0.16411 | 0.28691 | 0.16418 | 0.28728
900 | 15 | feeder2_663 | 0.16413 | 0.28699 | 0.1642 | 0.28736
900 | 15 | feeder2_444 | 0.16456 | 0.28708 | 0.16463 | 0.28744
900 | 15 | feeder2_759 | 0.17399 | 0.28265 | 0.17406 | 0.283
900 | 15 | feeder2_842 | 0.16496 | 0.28892 | 0.16503 | 0.28928
900 | 15 | feeder2_459 | 0.16456 | 0.28728 | 0.16463 | 0.28763
900 | 15 | feeder2_702 | 0.16553 | 0.28729 | 0.1656 | 0.28765
900 | 15 | feeder2_493 | 0.16446 | 0.28799 | 0.16453 | 0.28835
900 | 15 | feeder2_651 | 0.18998 | 0.34763 | 0.19007 | 0.34811
900 | 15 | feeder2_684 | 0.19716 | 0.35412 | 0.19725 | 0.35462
900 | 15 | feeder2_674 | 0.16421 | 0.28776 | 0.16429 | 0.28811
900 | 15 | feeder2_696 | 0.16452 | 0.29113 | 0.16459 | 0.29149
900 | 15 | feeder2_681 | 0.16359 | 0.28717 | 0.16366 | 0.28752
900 | 15 | feeder2_682 | 0.16414 | 0.28768 | 0.16421 | 0.28804
900 | 15 | feeder2_728 | 0.19667 | 0.34867 | 0.19676 | 0.34917
900 | 15 | feeder2_724 | 0.20512 | 0.37607 | 0.20522 | 0.37659
900 | 15 | feeder2_703 | 0.16456 | 0.29128 | 0.16463 | 0.29165
900 | 15 | feeder2_704 | 0.16422 | 0.29227 | 0.16429 | 0.29263
900 | 15 | feeder2_754 | 0.20518 | 0.37607 | 0.20528 | 0.3766
900 | 15 | feeder2_747 | 0.20837 | 0.38504 | 0.20847 | 0.38557
900 | 15 | feeder2_828 | 0.19359 | 0.34585 | 0.19368 | 0.34636
900 | 15 | feeder2_763 | 0.19734 | 0.34508 | 0.19744 | 0.34558
900 | 15 | feeder2_836 | 0.20882 | 0.38677 | 0.20892 | 0.38731
900 | 15 | feeder2_758 | 0.21104 | 0.39202 | 0.21114 | 0.39257
900 | 15 | feeder2_788 | 0.22384 | 0.3904 | 0.22393 | 0.39093
900 | 15 | feeder2_812 | 0.21763 | 0.41453 | 0.21774 | 0.41513
900 | 15 | feeder2_947 | 0.20011 | 0.34265 | 0.2002 | 0.34315
900 | 15 | feeder2_868 | 0.19881 | 0.34416 | 0.1989 | 0.34466
900 | 15 | feeder2_785 | 0.19731 | 0.344 | 0.1974 | 0.3445
900 | 15 | feeder2_1176 | 0.19737 | 0.34419 | 0.19746 | 0.3447
900 | 15 | feeder2_846 | 0.19618 | 0.34324 | 0.19626 | 0.34375
900 | 15 | feeder2_911 | 0.19778 | 0.34265 | 0.19787 | 0.34315
900 | 15 | feeder2_1107 | 0.21897 | 0.41704 | 0.21907 | 0.41763
900 | 15 | feeder2_920 | 0.21913 | 0.4203 | 0.21923 | 0.42091
900 | 15 | feeder2_926 | 0.2215 | 0.4296 | 0.22161 | 0.43024
900 | 15 | feeder2_1239 | 0.21898 | 0.41966 | 0.21909 | 0.42027
900 | 15 | feeder2_933 | 0.22248 | 0.43408 | 0.22259 | 0.43473
900 | 15 | feeder2_1146 | 0.22183 | 0.4282 | 0.22194 | 0.42885
900 | 15 | feeder2_1124 | 0.2225 | 0.43413 | 0.22261 | 0.43478
900 | 15 | feeder2_942 | 0.22498 | 0.44553 | 0.2251 | 0.44621
900 | 15 | feeder2_952 | 0.23048 | 0.47387 | 0.2306 | 0.47458
900 | 15 | feeder2_965 | 0.22475 | 0.44409 | 0.22486 | 0.44478
900 | 15 | feeder2_961 | 0.23104 | 0.47709 | 0.23116 | 0.47781
900 | 15 | feeder2_963 | 0.23049 | 0.47383 | 0.23061 | 0.47455
900 | 15 | feeder2_973 | 0.23403 | 0.49435 | 0.23415 | 0.49509
900 | 15 | feeder2_1128 | 0.23103 | 0.47704 | 0.23115 | 0.47776
900 | 15 | feeder2_1113 | 0.23119 | 0.47318 | 0.23131 | 0.4739
900 | 15 | feeder2_1143 | 0.23068 | 0.47352 | 0.23079 | 0.47423
900 | 15 | feeder2_1238 | 0.23374 | 0.43912 | 0.23385 | 0.43978
900 | 15 | feeder2_979 | 0.22435 | 0.44256 | 0.22446 | 0.44325
900 | 15 | feeder2_1236 | 0.2384 | 0.51949 | 0.23853 | 0.52026
900 | 15 | feeder2_989 | 0.23403 | 0.49436 | 0.23415 | 0.4951
900 | 15 | feeder2_1196 | 0.21708 | 0.43677 | 0.21719 | 0.43746
900 | 15 | feeder2_1158 | 0.23432 | 0.49537 | 0.23444 | 0.49611
900 | 15 | feeder2_1122 | 0.21941 | 0.41576 | 0.21951 | 0.41635
900 | 15 | feeder2_1258 | 0.21805 | 0.41981 | 0.21815 | 0.4204
900 | 15 | feeder2_1303 | 0.22249 | 0.41423 | 0.2226 | 0.41481
900 | 15 | feeder2_1138 | 0.2196 | 0.41521 | 0.2197 | 0.4158
900 | 15 | feeder2_1304 | 0.21955 | 0.41517 | 0.21965 | 0.41576
900 | 15 | feeder2_1212 | 0.22 | 0.4141 | 0.2201 | 0.41467
900 | 15 | feeder2_1311 | 0.22507 | 0.4121 | 0.22518 | 0.41268
900 | 15 | feeder2_1290 | 0.21993 | 0.41401 | 0.22003 | 0.4146
900 | 15 | feeder2_1325 | 0.24239 | 0.54027 | 0.24251 | 0.54109
900 | 15 | feeder2_1248 | 0.23841 | 0.51956 | 0.23854 | 0.52034
900 | 15 | feeder2_1249 | 0.23446 | 0.43911 | 0.23457 | 0.43977
900 | 15 | feeder2_1250 | 0.23832 | 0.43573 | 0.23843 | 0.4364
900 | 15 | feeder2_1366 | 0.23736 | 0.52118 | 0.23748 | 0.52195
900 | 15 | feeder2_1266 | 0.21775 | 0.42166 | 0.21786 | 0.42226
900 | 15 | feeder2_1372 | 0.21999 | 0.41416 | 0.22009 | 0.41475
900 | 15 | feeder2_1363 | 0.21988 | 0.41369 | 0.21998 | 0.41428
900 | 15 | feeder2_1446 | 0.24491 | 0.53864 | 0.24504 | 0.53945
900 | 15 | feeder2_1502 | 0.24649 | 0.56579 | 0.24662 | 0.56665
900 | 15 | feeder2_1428 | 0.21979 | 0.41361 | 0.21989 | 0.4142
900 | 15 | feeder2_1380 | 0.21984 | 0.41345 | 0.21995 | 0.41403
900 | 15 | feeder2_1550 | 0.22267 | 0.41221 | 0.22278 | 0.4128
900 | 15 | feeder2_1386 | 0.21963 | 0.41384 | 0.21973 | 0.41443
900 | 15 | feeder2_1551 | 0.21952 | 0.41374 | 0.21962 | 0.41433
900 | 15 | feeder2_1400 | 0.21953 | 0.41406 | 0.21963 | 0.41465
900 | 15 | feeder2_1552 | 0.21812 | 0.41279 | 0.21822 | 0.41339
900 | 15 | feeder2_1408 | 0.21949 | 0.41522 | 0.21959 | 0.41582
900 | 15 | feeder2_1553 | 0.21894 | 0.41513 | 0.21903 | 0.41573
900 | 15 | feeder2_1416 | 0.21953 | 0.41589 | 0.21963 | 0.41649
900 | 15 | feeder2_1530 | 0.21962 | 0.41589 | 0.21971 | 0.41649
900 | 15 | feeder2_1425 | 0.2196 | 0.41716 | 0.2197 | 0.41777
900 | 15 | feeder2_1589 | 0.21903 | 0.41715 | 0.21914 | 0.41775
900 | 15 | feeder2_1435 | 0.21965 | 0.41744 | 0.21975 | 0.41804
900 | 15 | feeder2_1621 | 0.22037 | 0.42062 | 0.22047 | 0.42122
900 | 15 | feeder2_1564 | 0.21962 | 0.41732 | 0.21972 | 0.41792
900 | 15 | feeder2_1704 | 0.25007 | 0.57914 | 0.25021 | 0.58
900 | 15 | feeder2_1525 | 0.24681 | 0.56761 | 0.24695 | 0.56848
900 | 15 | feeder2_1716 | 0.2477 | 0.5715 | 0.24783 | 0.57237
900 | 15 | feeder2_1537 | 0.24709 | 0.56907 | 0.24723 | 0.56994
900 | 15 | feeder2_1645 | 0.24638 | 0.56853 | 0.24652 | 0.56941
900 | 15 | feeder2_1561 | 0.24748 | 0.57105 | 0.24762 | 0.57194
900 | 15 | feeder2_1657 | 0.24751 | 0.57104 | 0.24765 | 0.57194
900 | 15 | feeder2_1570 | 0.24765 | 0.57192 | 0.24779 | 0.57282
900 | 15 | feeder2_1756 | 0.25678 | 0.56588 | 0.25691 | 0.56677
900 | 15 | feeder2_1588 | 0.24774 | 0.57307 | 0.24788 | 0.57397
900 | 15 | feeder2_1628 | 0.24821 | 0.57288 | 0.24835 | 0.57378
900 | 15 | feeder2_1598 | 0.24784 | 0.57456 | 0.24799 | 0.57547
900 | 15 | feeder2_1816 | 0.26268 | 0.6141 | 0.26284 | 0.61502
900 | 15 | feeder2_1765 | 0.24792 | 0.57476 | 0.24807 | 0.57567
900 | 15 | feeder2_1641 | 0.2464 | 0.57013 | 0.24654 | 0.57107
900 | 15 | feeder2_1689 | 0.24462 | 0.56916 | 0.24477 | 0.57013
900 | 15 | feeder2_1744 | 0.24855 | 0.56831 | 0.2487 | 0.56926
900 | 15 | feeder2_1817 | 0.24239 | 0.56512 | 0.24254 | 0.5661
900 | 15 | feeder2_1779 | 0.24464 | 0.57117 | 0.24479 | 0.57215
900 | 15 | feeder2_1800 | 0.24457 | 0.56912 | 0.24472 | 0.57009
900 | 15 | feeder2_1818 | 0.24288 | 0.56769 | 0.24304 | 0.56871
900 | 15 | feeder2_1753 | 0.25279 | 0.56516 | 0.25293 | 0.5661
900 | 15 | feeder2_1754 | 0.24913 | 0.56775 | 0.24927 | 0.5687
930 | 15.5 | secondary | 0.018172 | 0.019983 | 0.018176 | 0.019987
930 | 15.5 | feeder2_44 | 0.033814 | 0.10421 | 0.033823 | 0.10424
930 | 15.5 | feeder2_45 | 0.034335 | 0.10699 | 0.034344 | 0.10701
930 | 15.5 | feeder2_46 | 0.034978 | 0.10977 | 0.034987 | 0.10979
930 | 15.5 | feeder2_51 | 0.03524 | 0.11182 | 0.035252 | 0.11185
930 | 15.5 | feeder2_48 | 0.034424 | 0.10689 | 0.034433 | 0.10691
930 | 15.5 | feeder2_52 | 0.032054 | 0.10995 | 0.032066 | 0.10997
930 | 15.5 | feeder2_68 | 0.038006 | 0.12629 | 0.038015 | 0.12632
930 | 15.5 | feeder2_69 | 0.038105 | 0.12648 | 0.038117 | 0.12651
930 | 15.5 | feeder2_71 | 0.038371 | 0.1282 | 0.038383 | 0.12823
930 | 15.5 | feeder2_72 | 0.038473 | 0.12809 | 0.038487 | 0.12812
930 | 15.5 | feeder2_73 | 0.039513 | 0.13419 | 0.039523 | 0.13423
930 | 15.5 | feeder2_74 | 0.039382 | 0.13411 | 0.039397 | 0.13414
930 | 15.5 | feeder2_77 | 0.040497 | 0.13934 | 0.040512 | 0.13938
930 | 15.5 | feeder2_79 | 0.040564 | 0.13947 | 0.040573 | 0.13951
930 | 15.5 | feeder2_81 | 0.042043 | 0.14745 | 0.042059 | 0.14749
930 | 15.5 | feeder2_82 | 0.043657 | 0.14583 | 0.043667 | 0.14587
930 | 15.5 | feeder2_116 | 0.049034 | 0.1852 | 0.049048 | 0.18525
930 | 15.5 | feeder2_119 | 0.047964 | 0.18593 | 0.047982 | 0.18597
930 | 15.5 | feeder2_120 | 0.051839 | 0.1989 | 0.051853 | 0.19895
930 | 15.5 | feeder2_248 | 0.049936 | 0.19919 | 0.049951 | 0.19925
930 | 15.5 | feeder2_124 | 0.053773 | 0.20732 | 0.05379 | 0.20737
930 | 15.5 | feeder2_282 | 0.05502 | 0.20603 | 0.055035 | 0.20609
930 | 15.5 | feeder2_275 | 0.052922 | 0.20769 | 0.052935 | 0.20775
930 | 15.5 | feeder2_151 | 0.057351 | 0.22247 | 0.057366 | 0.22253
930 | 15.5 | feeder2_295 | 0.058474 | 0.22445 | 0.058489 | 0.22451
930 | 15.5 | feeder2_311 | 0.057424 | 0.22259 | 0.057439 | 0.22265
930 | 15.5 | feeder2_201 | 0.062743 | 0.24468 | 0.062766 | 0.24475
930 | 15.5 | feeder2_314 | 0.062771 | 0.24465 | 0.062788 | 0.24472
930 | 15.5 | feeder2_342 | 0.070445 | 0.27634 | 0.070463 | 0.27642
930 | 15.5 | feeder2_368 | 0.072948 | 0.28708 | 0.072968 | 0.28716
930 | 15.5 | feeder2_347 | 0.070302 | 0.27202 | 0.070327 | 0.27209
930 | 15.5 | feeder2_353 | 0.070237 | 0.26993 | 0.070255 | 0.27001
930 | 15.5 | feeder2_518 | 0.070327 | 0.27199 | 0.070348 | 0.27207
930 | 15.5 | feeder2_365 | 0.070176 | 0.2677 | 0.070195 | 0.26778
930 | 15.5 | feeder2_653 | 0.070139 | 0.26986 | 0.070164 | 0.26993
930 | 15.5 | feeder2_377 | 0.070124 | 0.26617 | 0.070144 | 0.26624
930 | 15.5 | feeder2_622 | 0.069729 | 0.26888 | 0.069752 | 0.26896
930 | 15.5 | feeder2_451 | 0.072972 | 0.28705 | 0.07299 | 0.28713
930 | 15.5 | feeder2_383 | 0.077075 | 0.30451 | 0.077096 | 0.30459
930 | 15.5 | feeder2_385 | 0.069928 | 0.26373 | 0.069948 | 0.26381
930 | 15.5 | feeder2_621 | 0.071346 | 0.26824 | 0.071368 | 0.26832
930 | 15.5 | feeder2_611 | 0.07699 | 0.30445 | 0.077008 | 0.30453
930 | 15.5 | feeder2_405 | 0.077337 | 0.3056 | 0.07736 | 0.30568
930 | 15.5 | feeder2_461 | 0.069746 | 0.25439 | 0.069769 | 0.25447
930 | 15.5 | feeder2_594 | 0.068647 | 0.26373 | 0.068665 | 0.26381
930 | 15.5 | feeder2_732 | 0.071244 | 0.30329 | 0.071266 | 0.30336
930 | 15.5 | feeder2_417 | 0.079679 | 0.31448 | 0.079702 | 0.31455
930 | 15.5 | feeder2_663 | 0.079499 | 0.31539 | 0.079523 | 0.31546
930 | 15.5 | feeder2_444 | 0.081448 | 0.32091 | 0.081468 | 0.32099
930 | 15.5 | feeder2_759 | 0.081941 | 0.3201 | 0.081961 | 0.32018
930 | 15.5 | feeder2_842 | 0.083562 | 0.32405 | 0.083586 | 0.32412
930 | 15.5 | feeder2_459 | 0.082029 | 0.32303 | 0.082055 | 0.3231
930 | 15.5 | feeder2_702 | 0.083961 | 0.32065 | 0.083982 | 0.32072
930 | 15.5 | feeder2_493 | 0.084154 | 0.33189 | 0.084177 | 0.33197
930 | 15.5 | feeder2_651 | 0.070529 | 0.2557 | 0.070553 | 0.25578
930 | 15.5 | feeder2_684 | 0.069341 | 0.24577 | 0.069366 | 0.24585
930 | 15.5 | feeder2_674 | 0.083706 | 0.33161 | 0.083731 | 0.33168
930 | 15.5 | feeder2_696 | 0.090875 | 0.35901 | 0.090899 | 0.35909
930 | 15.5 | feeder2_681 | 0.082529 | 0.33086 | 0.082554 | 0.33093
930 | 15.5 | feeder2_682 | 0.083633 | 0.33156 | 0.083657 | 0.33163
930 | 15.5 | feeder2_728 | 0.068959 | 0.24484 | 0.068979 | 0.24492
930 | 15.5 | feeder2_724 | 0.069589 | 0.23955 | 0.069616 | 0.23962
930 | 15.5 | feeder2_703 | 0.091004 | 0.35919 | 0.091022 | 0.35927
930 | 15.5 | feeder2_704 | 0.098107 | 0.36919 | 0.098134 | 0.36926
930 | 15.5 | feeder2_754 | 0.069624 | 0.23954 | 0.06965 | 0.23961
930 | 15.5 | feeder2_747 | 0.069707 | 0.23716 | 0.069733 | 0.23723
930 | 15.5 | feeder2_828 | 0.067977 | 0.24412 | 0.068002 | 0.2442
930 | 15.5 | feeder2_763 | 0.06878 | 0.24465 | 0.068806 | 0.24472
930 | 15.5 | feeder2_836 | 0.070695 | 0.23898 | 0.070722 | 0.23905
930 | 15.5 | feeder2_758 | 0.069658 | 0.23439 | 0.069683 | 0.23446
930 | 15.5 | feeder2_788 | 0.071024 | 0.2331 | 0.07105 | 0.23316
930 | 15.5 | feeder2_812 | 0.069252 | 0.22791 | 0.069274 | 0.22797
930 | 15.5 | feeder2_947 | 0.068846 | 0.24461 | 0.068867 | 0.24469
930 | 15.5 | feeder2_868 | 0.069524 | 0.24403 | 0.069545 | 0.2441
930 | 15.5 | feeder2_785 | 0.068577 | 0.24492 | 0.0686 | 0.245
930 | 15.5 | feeder2_1176 | 0.067548 | 0.24793 | 0.067571 | 0.24801
930 | 15.5 | feeder2_846 | 0.067343 | 0.24437 | 0.067368 | 0.24444
930 | 15.5 | feeder2_911 | 0.068578 | 0.24491 | 0.068601 | 0.24499
930 | 15.5 | feeder2_1107 | 0.068617 | 0.22814 | 0.068641 | 0.22821
930 | 15.5 | feeder2_920 | 0.069327 | 0.22615 | 0.06935 | 0.22621
930 | 15.5 | feeder2_926 | 0.069686 | 0.22433 | 0.069712 | 0.22439
930 | 15.5 | feeder2_1239 | 0.069037 | 0.22537 | 0.069064 | 0.22542
930 | 15.5 | feeder2_933 | 0.069785 | 0.22388 | 0.06981 | 0.22393
930 | 15.5 | feeder2_1146 | 0.069971 | 0.22298 | 0.069997 | 0.22304
930 | 15.5 | feeder2_1124 | 0.069816 | 0.22393 | 0.069843 | 0.22398
930 | 15.5 | feeder2_942 | 0.070025 | 0.22282 | 0.070054 | 0.22287
930 | 15.5 | feeder2_952 | 0.07172 | 0.23222 | 0.07175 | 0.23226
930 | 15.5 | feeder2_965 | 0.069851 | 0.22144 | 0.069876 | 0.22149
930 | 15.5 | feeder2_961 | 0.07188 | 0.23333 | 0.071909 | 0.23337
930 | 15.5 | feeder2_963 | 0.071726 | 0.2322 | 0.071753 | 0.23224
930 | 15.5 | feeder2_973 | 0.072734 | 0.23932 | 0.072764 | 0.23936
930 | 15.5 | feeder2_1128 | 0.071869 | 0.23327 | 0.071892 | 0.23332
930 | 15.5 | feeder2_1113 | 0.072423 | 0.23161 | 0.072447 | 0.23167
930 | 15.5 | feeder2_1143 | 0.071719 | 0.23254 | 0.071744 | 0.23259
930 | 15.5 | feeder2_1238 | 0.080869 | 0.21697 | 0.080891 | 0.21701
930 | 15.5 | feeder2_979 | 0.069546 | 0.21993 | 0.069574 | 0.21998
930 | 15.5 | feeder2_1236 | 0.073734 | 0.24619 | 0.073761 | 0.24624
930 | 15.5 | feeder2_989 | 0.072737 | 0.23934 | 0.072763 | 0.23938
930 | 15.5 | feeder2_1196 | 0.062846 | 0.21402 | 0.062868 | 0.21408
930 | 15.5 | feeder2_1158 | 0.073075 | 0.24177 | 0.073105 | 0.24181
930 | 15.5 | feeder2_1122 | 0.068256 | 0.22766 | 0.068278 | 0.22772
930 | 15.5 | feeder2_1258 | 0.069029 | 0.22889 | 0.069055 | 0.22895
930 | 15.5 | feeder2_1303 | 0.06892 | 0.22755 | 0.068942 | 0.22761
930 | 15.5 | feeder2_1138 | 0.067978 | 0.22727 | 0.068004 | 0.22733
930 | 15.5 | feeder2_1304 | 0.067296 | 0.22731 | 0.067319 | 0.22737
930 | 15.5 | feeder2_1212 | 0.067596 | 0.22652 | 0.067617 | 0.22658
930 | 15.5 | feeder2_1311 | 0.069622 | 0.2261 | 0.069645 | 0.22616
930 | 15.5 | feeder2_1290 | 0.067108 | 0.2257 | 0.067132 | 0.22576
930 | 15.5 | feeder2_1325 | 0.07466 | 0.25227 | 0.074688 | 0.2523
930 | 15.5 | feeder2_1248 | 0.073735 | 0.24621 | 0.073763 | 0.24625
930 | 15.5 | feeder2_1249 | 0.083931 | 0.21581 | 0.083951 | 0.21585
930 | 15.5 | feeder2_1250 | 0.081618 | 0.21703 | 0.081644 | 0.21706
930 | 15.5 | feeder2_1366 | 0.073046 | 0.24805 | 0.073075 | 0.24809
930 | 15.5 | feeder2_1266 | 0.069413 | 0.22957 | 0.069441 | 0.22964
930 | 15.5 | feeder2_1372 | 0.067093 | 0.22582 | 0.067118 | 0.22589
930 | 15.5 | feeder2_1363 | 0.066627 | 0.22467 | 0.066653 | 0.22473
930 | 15.5 | feeder2_1446 | 0.076682 | 0.25174 | 0.076709 | 0.25177
930 | 15.5 | feeder2_1502 | 0.07551 | 0.25958 | 0.075537 | 0.25962
930 | 15.5 | feeder2_1428 | 0.066541 | 0.22459 | 0.066567 | 0.22466
930 | 15.5 | feeder2_1380 | 0.066073 | 0.22361 | 0.066097 | 0.22368
930 | 15.5 | feeder2_1550 | 0.066628 | 0.22383 | 0.066649 | 0.22391
930 | 15.5 | feeder2_1386 | 0.065848 | 0.22293 | 0.065869 | 0.22301
930 | 15.5 | feeder2_1551 | 0.065733 | 0.22284 | 0.065752 | 0.22291
930 | 15.5 | feeder2_1400 | 0.065746 | 0.22265 | 0.065767 | 0.22272
930 | 15.5 | feeder2_1552 | 0.062671 | 0.22106 | 0.062695 | 0.22114
930 | 15.5 | feeder2_1408 | 0.065922 | 0.22306 | 0.065946 | 0.22313
930 | 15.5 | feeder2_1553 | 0.064629 | 0.22328 | 0.064649 | 0.22336
930 | 15.5 | feeder2_1416 | 0.066121 | 0.22328 | 0.066146 | 0.22335
930 | 15.5 | feeder2_1530 | 0.067727 | 0.22177 | 0.067749 | 0.22185
930 | 15.5 | feeder2_1425 | 0.066347 | 0.22445 | 0.06637 | 0.22453
930 | 15.5 | feeder2_1589 | 0.066273 | 0.2244 | 0.066298 | 0.22447
930 | 15.5 | feeder2_1435 | 0.066393 | 0.2247 | 0.066414 | 0.22478
930 | 15.5 | feeder2_1621 | 0.067719 | 0.22747 | 0.067744 | 0.22755
930 | 15.5 | feeder2_1564 | 0.066369 | 0.22458 | 0.066393 | 0.22466
930 | 15.5 | feeder2_1704 | 0.075066 | 0.26069 | 0.075092 | 0.26073
930 | 15.5 | feeder2_1525 | 0.075719 | 0.26105 | 0.075751 | 0.26108
930 | 15.5 | feeder2_1716 | 0.077583 | 0.26389 | 0.077616 | 0.26393
930 | 15.5 | feeder2_1537 | 0.075851 | 0.26229 | 0.075884 | 0.26232
930 | 15.5 | feeder2_1645 | 0.075655 | 0.2621 | 0.075685 | 0.26214
930 | 15.5 | feeder2_1561 | 0.076022 | 0.26381 | 0.076053 | 0.26385
930 | 15.5 | feeder2_1657 | 0.076047 | 0.26382 | 0.076079 | 0.26385
930 | 15.5 | feeder2_1570 | 0.076096 | 0.26447 | 0.076129 | 0.2645
930 | 15.5 | feeder2_1756 | 0.079746 | 0.26525 | 0.079774 | 0.26527
930 | 15.5 | feeder2_1588 | 0.076166 | 0.265 | 0.076193 | 0.26504
930 | 15.5 | feeder2_1628 | 0.077341 | 0.26449 | 0.077367 | 0.26453
930 | 15.5 | feeder2_1598 | 0.076218 | 0.26578 | 0.076245 | 0.26582
930 | 15.5 | feeder2_1816 | 0.079298 | 0.27168 | 0.07933 | 0.27172
930 | 15.5 | feeder2_1765 | 0.076327 | 0.26594 | 0.076354 | 0.26597
930 | 15.5 | feeder2_1641 | 0.076094 | 0.26784 | 0.076128 | 0.26788
930 | 15.5 | feeder2_1689 | 0.076011 | 0.26936 | 0.076044 | 0.2694
930 | 15.5 | feeder2_1744 | 0.076389 | 0.26794 | 0.076424 | 0.26797
930 | 15.5 | feeder2_1817 | 0.075669 | 0.26752 | 0.075698 | 0.26756
930 | 15.5 | feeder2_1779 | 0.076848 | 0.2701 | 0.076878 | 0.27015
930 | 15.5 | feeder2_1800 | 0.075956 | 0.26931 | 0.075991 | 0.26935
930 | 15.5 | feeder2_1818 | 0.073051 | 0.27314 | 0.073085 | 0.27319
930 | 15.5 | feeder2_1753 | 0.077283 | 0.26821 | 0.077314 | 0.26824
930 | 15.5 | feeder2_1754 | 0.076404 | 0.26794 | 0.076435 | 0.26798
960 | 16 | secondary | 0.067223 | 0.049455 | 0.067196 | 0.04942
960 | 16 | feeder2_44 | 0.12528 | 0.25831 | 0.12523 | 0.25812
960 | 16 | feeder2_45 | 0.12746 | 0.2663 | 0.12741 | 0.26611
960 | 16 | feeder2_46 | 0.12408 | 0.26004 | 0.12403 | 0.25985
960 | 16 | feeder2_51 | 0.13115 | 0.28035 | 0.1311 | 0.28015
960 | 16 | feeder2_48 | 0.12951 | 0.2649 | 0.12946 | 0.26471
960 | 16 | feeder2_52 | 0.13101 | 0.28012 | 0.13096 | 0.27992
960 | 16 | feeder2_68 | 0.14161 | 0.32005 | 0.14155 | 0.31982
960 | 16 | feeder2_69 | 0.14098 | 0.32099 | 0.14093 | 0.32077
960 | 16 | feeder2_71 | 0.14299 | 0.32528 | 0.14294 | 0.32504
960 | 16 | feeder2_72 | 0.14529 | 0.32657 | 0.14523 | 0.32634
960 | 16 | feeder2_73 | 0.14729 | 0.34146 | 0.14723 | 0.34121
960 | 16 | feeder2_74 | 0.14774 | 0.34033 | 0.14769 | 0.34008
960 | 16 | feeder2_77 | 0.151 | 0.35555 | 0.15094 | 0.35529
960 | 16 | feeder2_79 | 0.15096 | 0.35561 | 0.1509 | 0.35536
960 | 16 | feeder2_81 | 0.15688 | 0.37782 | 0.15682 | 0.37756
960 | 16 | feeder2_82 | 0.15694 | 0.37786 | 0.15688 | 0.37759
960 | 16 | feeder2_116 | 0.18343 | 0.47791 | 0.18336 | 0.47758
960 | 16 | feeder2_119 | 0.18338 | 0.47785 | 0.18331 | 0.47751
960 | 16 | feeder2_120 | 0.19333 | 0.5151 | 0.19326 | 0.51473
960 | 16 | feeder2_248 | 0.19174 | 0.51266 | 0.19166 | 0.5123
960 | 16 | feeder2_124 | 0.19964 | 0.53897 | 0.19956 | 0.53858
960 | 16 | feeder2_282 | 0.21863 | 0.55016 | 0.21855 | 0.54979
960 | 16 | feeder2_275 | 0.19955 | 0.53884 | 0.19947 | 0.53846
960 | 16 | feeder2_151 | 0.20877 | 0.57309 | 0.20869 | 0.57267
960 | 16 | feeder2_295 | 0.20547 | 0.57977 | 0.20539 | 0.57934
960 | 16 | feeder2_311 | 0.20875 | 0.57313 | 0.20867 | 0.57272
960 | 16 | feeder2_201 | 0.223 | 0.62195 | 0.22291 | 0.62149
960 | 16 | feeder2_314 | 0.22368 | 0.62169 | 0.22359 | 0.62123
960 | 16 | feeder2_342 | 0.24286 | 0.69185 | 0.24276 | 0.69133
960 | 16 | feeder2_368 | 0.24257 | 0.69411 | 0.24247 | 0.69358
960 | 16 | feeder2_347 | 0.25253 | 0.72235 | 0.25243 | 0.7218
960 | 16 | feeder2_353 | 0.25734 | 0.73765 | 0.25723 | 0.73709
960 | 16 | feeder2_518 | 0.2526 | 0.72241 | 0.2525 | 0.72186
960 | 16 | feeder2_365 | 0.26268 | 0.75476 | 0.26257 | 0.75419
960 | 16 | feeder2_653 | 0.25726 | 0.73754 | 0.25715 | 0.73698
960 | 16 | feeder2_377 | 0.26559 | 0.7641 | 0.26547 | 0.76352
960 | 16 | feeder2_622 | 0.26267 | 0.75478 | 0.26256 | 0.7542
960 | 16 | feeder2_451 | 0.24266 | 0.69417 | 0.24256 | 0.69364
960 | 16 | feeder2_383 | 0.24211 | 0.69785 | 0.24201 | 0.69731
960 | 16 | feeder2_385 | 0.26866 | 0.7734 | 0.26855 | 0.77282
960 | 16 | feeder2_621 | 0.26226 | 0.77007 | 0.26215 | 0.76948
960 | 16 | feeder2_611 | 0.24225 | 0.69692 | 0.24215 | 0.69638
960 | 16 | feeder2_405 | 0.24209 | 0.69814 | 0.24199 | 0.6976
960 | 16 | feeder2_461 | 0.28177 | 0.81512 | 0.28165 | 0.81452
960 | 16 | feeder2_594 | 0.26757 | 0.77182 | 0.26746 | 0.77124
960 | 16 | feeder2_732 | 0.23854 | 0.69332 | 0.23844 | 0.69278
960 | 16 | feeder2_417 | 0.24219 | 0.70141 | 0.24209 | 0.70088
960 | 16 | feeder2_663 | 0.23966 | 0.70453 | 0.23956 | 0.70399
960 | 16 | feeder2_444 | 0.24243 | 0.703 | 0.24233 | 0.70247
960 | 16 | feeder2_759 | 0.24259 | 0.70311 | 0.24248 | 0.70256
960 | 16 | feeder2_842 | 0.24201 | 0.70406 | 0.24192 | 0.70352
960 | 16 | feeder2_459 | 0.24251 | 0.70351 | 0.24241 | 0.70297
960 | 16 | feeder2_702 | 0.24586 | 0.70443 | 0.24576 | 0.70389
960 | 16 | feeder2_493 | 0.24245 | 0.70496 | 0.24235 | 0.70442
960 | 16 | feeder2_651 | 0.27863 | 0.81945 | 0.27851 | 0.81885
960 | 16 | feeder2_684 | 0.29185 | 0.84748 | 0.29172 | 0.84688
960 | 16 | feeder2_674 | 0.24219 | 0.70439 | 0.24209 | 0.70385
960 | 16 | feeder2_696 | 0.24285 | 0.71194 | 0.24275 | 0.71139
960 | 16 | feeder2_681 | 0.24141 | 0.7033 | 0.24132 | 0.70275
960 | 16 | feeder2_682 | 0.24227 | 0.70371 | 0.24217 | 0.70316
960 | 16 | feeder2_728 | 0.29012 | 0.84051 | 0.28999 | 0.83991
960 | 16 | feeder2_724 | 0.30566 | 0.89862 | 0.30553 | 0.89802
960 | 16 | feeder2_703 | 0.24283 | 0.71203 | 0.24273 | 0.71147
960 | 16 | feeder2_704 | 0.24165 | 0.71506 | 0.24155 | 0.7145
960 | 16 | feeder2_754 | 0.30672 | 0.89848 | 0.30659 | 0.89788
960 | 16 | feeder2_747 | 0.31117 | 0.91991 | 0.31104 | 0.91931
960 | 16 | feeder2_828 | 0.28555 | 0.83345 | 0.28542 | 0.83286
960 | 16 | feeder2_763 | 0.29014 | 0.84056 | 0.29002 | 0.83997
960 | 16 | feeder2_836 | 0.31065 | 0.92028 | 0.31052 | 0.91968
960 | 16 | feeder2_758 | 0.31588 | 0.93831 | 0.31574 | 0.93771
960 | 16 | feeder2_788 | 0.31907 | 0.93989 | 0.31893 | 0.9393
960 | 16 | feeder2_812 | 0.32961 | 0.99342 | 0.32947 | 0.99282
960 | 16 | feeder2_947 | 0.29032 | 0.8407 | 0.2902 | 0.84011
960 | 16 | feeder2_868 | 0.29052 | 0.84084 | 0.29039 | 0.84025
960 | 16 | feeder2_785 | 0.29009 | 0.84033 | 0.28996 | 0.83974
960 | 16 | feeder2_1176 | 0.29004 | 0.84038 | 0.28992 | 0.83978
960 | 16 | feeder2_846 | 0.28976 | 0.83985 | 0.28963 | 0.83926
960 | 16 | feeder2_911 | 0.29011 | 0.84042 | 0.28998 | 0.83983
960 | 16 | feeder2_1107 | 0.33733 | 1.0214 | 0.33719 | 1.0208
960 | 16 | feeder2_920 | 0.33135 | 1.0014 | 0.33121 | 1.0008
960 | 16 | feeder2_926 | 0.33401 | 1.0137 | 0.33387 | 1.013
960 | 16 | feeder2_1239 | 0.33127 | 1.0011 | 0.33113 | 1.0005
960 | 16 | feeder2_933 | 0.33514 | 1.0191 | 0.33499 | 1.0184
960 | 16 | feeder2_1146 | 0.33427 | 1.0138 | 0.33413 | 1.0131
960 | 16 | feeder2_1124 | 0.33512 | 1.0191 | 0.33498 | 1.0184
960 | 16 | feeder2_942 | 0.33798 | 1.0327 | 0.33783 | 1.0321
960 | 16 | feeder2_952 | 0.34063 | 1.047 | 0.34048 | 1.0464
960 | 16 | feeder2_965 | 0.33818 | 1.0335 | 0.33803 | 1.0328
960 | 16 | feeder2_961 | 0.34086 | 1.0484 | 0.34071 | 1.0477
960 | 16 | feeder2_963 | 0.34064 | 1.0471 | 0.34049 | 1.0464
960 | 16 | feeder2_973 | 0.34213 | 1.0561 | 0.34197 | 1.0554
960 | 16 | feeder2_1128 | 0.34081 | 1.0477 | 0.34065 | 1.047
960 | 16 | feeder2_1113 | 0.34104 | 1.0471 | 0.34088 | 1.0464
960 | 16 | feeder2_1143 | 0.34115 | 1.0498 | 0.34099 | 1.0491
960 | 16 | feeder2_1238 | 0.36713 | 1.0553 | 0.36698 | 1.0547
960 | 16 | feeder2_979 | 0.33802 | 1.0326 | 0.33787 | 1.0319
960 | 16 | feeder2_1236 | 0.34393 | 1.0676 | 0.34377 | 1.0669
960 | 16 | feeder2_989 | 0.34213 | 1.0561 | 0.34197 | 1.0554
960 | 16 | feeder2_1196 | 0.33633 | 1.0287 | 0.33618 | 1.0281
960 | 16 | feeder2_1158 | 0.34144 | 1.0566 | 0.34128 | 1.0559
960 | 16 | feeder2_1122 | 0.34032 | 1.0325 | 0.34018 | 1.0319
960 | 16 | feeder2_1258 | 0.337 | 1.0215 | 0.33686 | 1.0209
960 | 16 | feeder2_1303 | 0.34191 | 1.0338 | 0.34177 | 1.0332
960 | 16 | feeder2_1138 | 0.3426 | 1.0408 | 0.34246 | 1.0402
960 | 16 | feeder2_1304 | 0.34257 | 1.0408 | 0.34243 | 1.0402
960 | 16 | feeder2_1212 | 0.34744 | 1.0587 | 0.3473 | 1.0582
960 | 16 | feeder2_1311 | 0.36353 | 1.0723 | 0.36339 | 1.0718
960 | 16 | feeder2_1290 | 0.3511 | 1.0694 | 0.35096 | 1.0689
960 | 16 | feeder2_1325 | 0.34642 | 1.0824 | 0.34625 | 1.0816
960 | 16 | feeder2_1248 | 0.34393 | 1.0676 | 0.34376 | 1.0669
960 | 16 | feeder2_1249 | 0.36838 | 1.0558 | 0.36823 | 1.0552
960 | 16 | feeder2_1250 | 0.38444 | 1.0696 | 0.38429 | 1.069
960 | 16 | feeder2_1366 | 0.34388 | 1.0676 | 0.34372 | 1.0669
960 | 16 | feeder2_1266 | 0.3367 | 1.0216 | 0.33656 | 1.0211
960 | 16 | feeder2_1372 | 0.3667 | 1.0806 | 0.36656 | 1.08
960 | 16 | feeder2_1363 | 0.35062 | 1.064 | 0.35048 | 1.0634
960 | 16 | feeder2_1446 | 0.34857 | 1.0842 | 0.34841 | 1.0834
960 | 16 | feeder2_1502 | 0.34878 | 1.0965 | 0.3486 | 1.0957
960 | 16 | feeder2_1428 | 0.35099 | 1.0628 | 0.35085 | 1.0622
960 | 16 | feeder2_1380 | 0.35016 | 1.0594 | 0.35002 | 1.0589
960 | 16 | feeder2_1550 | 0.35159 | 1.0609 | 0.35145 | 1.0604
960 | 16 | feeder2_1386 | 0.34983 | 1.0564 | 0.34969 | 1.0559
960 | 16 | feeder2_1551 | 0.3501 | 1.0554 | 0.34996 | 1.0548
960 | 16 | feeder2_1400 | 0.34968 | 1.0553 | 0.34955 | 1.0547
960 | 16 | feeder2_1552 | 0.34768 | 1.0522 | 0.34754 | 1.0517
960 | 16 | feeder2_1408 | 0.34973 | 1.0544 | 0.34959 | 1.0539
960 | 16 | feeder2_1553 | 0.34965 | 1.0543 | 0.34951 | 1.0537
960 | 16 | feeder2_1416 | 0.34976 | 1.0539 | 0.34963 | 1.0534
960 | 16 | feeder2_1530 | 0.35118 | 1.0541 | 0.35104 | 1.0535
960 | 16 | feeder2_1425 | 0.3496 | 1.053 | 0.34946 | 1.0524
960 | 16 | feeder2_1589 | 0.34827 | 1.051 | 0.34813 | 1.0505
960 | 16 | feeder2_1435 | 0.34961 | 1.0529 | 0.34947 | 1.0524
960 | 16 | feeder2_1621 | 0.34859 | 1.0531 | 0.34845 | 1.0526
960 | 16 | feeder2_1564 | 0.34958 | 1.0528 | 0.34945 | 1.0523
960 | 16 | feeder2_1704 | 0.34714 | 1.098 | 0.34697 | 1.0972
960 | 16 | feeder2_1525 | 0.34942 | 1.0997 | 0.34924 | 1.0989
960 | 16 | feeder2_1716 | 0.34855 | 1.1003 | 0.34837 | 1.0995
960 | 16 | feeder2_1537 | 0.35011 | 1.1032 | 0.34993 | 1.1024
960 | 16 | feeder2_1645 | 0.34976 | 1.1016 | 0.34958 | 1.1008
960 | 16 | feeder2_1561 | 0.35103 | 1.1082 | 0.35085 | 1.1073
960 | 16 | feeder2_1657 | 0.3517 | 1.1081 | 0.35152 | 1.1073
960 | 16 | feeder2_1570 | 0.35138 | 1.1103 | 0.3512 | 1.1095
960 | 16 | feeder2_1756 | 0.38191 | 1.134 | 0.38173 | 1.1332
960 | 16 | feeder2_1588 | 0.35137 | 1.1107 | 0.35119 | 1.1098
960 | 16 | feeder2_1628 | 0.35177 | 1.111 | 0.35158 | 1.1102
960 | 16 | feeder2_1598 | 0.35135 | 1.1111 | 0.35117 | 1.1102
960 | 16 | feeder2_1816 | 0.34691 | 1.1152 | 0.34673 | 1.1143
960 | 16 | feeder2_1765 | 0.35131 | 1.1111 | 0.35112 | 1.1103
960 | 16 | feeder2_1641 | 0.35126 | 1.1121 | 0.35107 | 1.1112
960 | 16 | feeder2_1689 | 0.35099 | 1.112 | 0.3508 | 1.1111
960 | 16 | feeder2_1744 | 0.35202 | 1.1126 | 0.35183 | 1.1118
960 | 16 | feeder2_1817 | 0.35097 | 1.1119 | 0.35078 | 1.111
960 | 16 | feeder2_1779 | 0.35094 | 1.112 | 0.35075 | 1.1111
960 | 16 | feeder2_1800 | 0.35095 | 1.1119 | 0.35076 | 1.111
960 | 16 | feeder2_1818 | 0.33814 | 1.1095 | 0.33792 | 1.1085
960 | 16 | feeder2_1753 | 0.35429 | 1.1144 | 0.3541 | 1.1135
960 | 16 | feeder2_1754 | 0.35206 | 1.1127 | 0.35187 | 1.1118
990 | 16.5 | secondary | 0.042755 | 0.052693 | 0.042752 | 0.052688
990 | 16.5 | feeder2_44 | 0.079649 | 0.27511 | 0.07965 | 0.27508
990 | 16.5 | feeder2_45 | 0.080983 | 0.28344 | 0.080983 | 0.28341
990 | 16.5 | feeder2_46 | 0.080157 | 0.27815 | 0.080157 | 0.27812
990 | 16.5 | feeder2_51 | 0.083306 | 0.29795 | 0.083304 | 0.29792
990 | 16.5 | feeder2_48 | 0.081057 | 0.28328 | 0.081053 | 0.28325
990 | 16.5 | feeder2_52 | 0.078104 | 0.30198 | 0.078098 | 0.30196
990 | 16.5 | feeder2_68 | 0.090414 | 0.33763 | 0.090414 | 0.33759
990 | 16.5 | feeder2_69 | 0.092351 | 0.34083 | 0.092348 | 0.34079
990 | 16.5 | feeder2_71 | 0.091325 | 0.34273 | 0.09132 | 0.34269
990 | 16.5 | feeder2_72 | 0.093041 | 0.33919 | 0.093035 | 0.33916
990 | 16.5 | feeder2_73 | 0.094195 | 0.35907 | 0.094195 | 0.35903
990 | 16.5 | feeder2_74 | 0.091063 | 0.36182 | 0.091059 | 0.36179
990 | 16.5 | feeder2_77 | 0.096805 | 0.37274 | 0.096805 | 0.3727
990 | 16.5 | feeder2_79 | 0.096262 | 0.37332 | 0.096263 | 0.37328
990 | 16.5 | feeder2_81 | 0.10089 | 0.39406 | 0.10089 | 0.39401
990 | 16.5 | feeder2_82 | 0.10202 | 0.3917 | 0.10202 | 0.39165
990 | 16.5 | feeder2_116 | 0.11942 | 0.49207 | 0.11941 | 0.49202
990 | 16.5 | feeder2_119 | 0.11918 | 0.49202 | 0.11917 | 0.49197
990 | 16.5 | feeder2_120 | 0.12634 | 0.52845 | 0.12634 | 0.52839
990 | 16.5 | feeder2_248 | 0.12429 | 0.52803 | 0.12429 | 0.52797
990 | 16.5 | feeder2_124 | 0.13074 | 0.55109 | 0.13074 | 0.55103
990 | 16.5 | feeder2_282 | 0.13192 | 0.54813 | 0.13192 | 0.54807
990 | 16.5 | feeder2_275 | 0.13063 | 0.55105 | 0.13062 | 0.55099
990 | 16.5 | feeder2_151 | 0.13855 | 0.59221 | 0.13855 | 0.59214
990 | 16.5 | feeder2_295 | 0.14038 | 0.59485 | 0.14038 | 0.59478
990 | 16.5 | feeder2_311 | 0.13863 | 0.59233 | 0.13863 | 0.59226
990 | 16.5 | feeder2_201 | 0.15073 | 0.65652 | 0.15072 | 0.65645
990 | 16.5 | feeder2_314 | 0.15279 | 0.65429 | 0.15278 | 0.65422
990 | 16.5 | feeder2_342 | 0.16746 | 0.75253 | 0.16746 | 0.75245
990 | 16.5 | feeder2_368 | 0.1694 | 0.75512 | 0.16939 | 0.75504
990 | 16.5 | feeder2_347 | 0.173 | 0.79487 | 0.173 | 0.79478
990 | 16.5 | feeder2_353 | 0.17577 | 0.81597 | 0.17576 | 0.81588
990 | 16.5 | feeder2_518 | 0.17302 | 0.79481 | 0.17301 | 0.79472
990 | 16.5 | feeder2_365 | 0.17886 | 0.83939 | 0.17886 | 0.8393
990 | 16.5 | feeder2_653 | 0.17568 | 0.81594 | 0.17568 | 0.81585
990 | 16.5 | feeder2_377 | 0.18051 | 0.85195 | 0.1805 | 0.85186
990 | 16.5 | feeder2_622 | 0.17865 | 0.83992 | 0.17864 | 0.83984
990 | 16.5 | feeder2_451 | 0.16942 | 0.75505 | 0.16941 | 0.75498
990 | 16.5 | feeder2_383 | 0.17255 | 0.75935 | 0.17254 | 0.75927
990 | 16.5 | feeder2_385 | 0.18221 | 0.86543 | 0.1822 | 0.86534
990 | 16.5 | feeder2_621 | 0.18259 | 0.85477 | 0.18258 | 0.85468
990 | 16.5 | feeder2_611 | 0.17246 | 0.75932 | 0.17245 | 0.75925
990 | 16.5 | feeder2_405 | 0.17274 | 0.75962 | 0.17274 | 0.75954
990 | 16.5 | feeder2_461 | 0.18946 | 0.92094 | 0.18945 | 0.92084
990 | 16.5 | feeder2_594 | 0.1809 | 0.86511 | 0.1809 | 0.86502
990 | 16.5 | feeder2_732 | 0.16889 | 0.75876 | 0.16888 | 0.75869
990 | 16.5 | feeder2_417 | 0.17444 | 0.76189 | 0.17443 | 0.76181
990 | 16.5 | feeder2_663 | 0.17572 | 0.76364 | 0.17572 | 0.76356
990 | 16.5 | feeder2_444 | 0.17559 | 0.76308 | 0.17559 | 0.76299
990 | 16.5 | feeder2_759 | 0.17968 | 0.75794 | 0.17967 | 0.75785
990 | 16.5 | feeder2_842 | 0.17797 | 0.76664 | 0.17797 | 0.76656
990 | 16.5 | feeder2_459 | 0.17588 | 0.7636 | 0.17588 | 0.76352
990 | 16.5 | feeder2_702 | 0.18126 | 0.75588 | 0.18125 | 0.7558
990 | 16.5 | feeder2_493 | 0.17665 | 0.7686 | 0.17665 | 0.76852
990 | 16.5 | feeder2_651 | 0.19022 | 0.92213 | 0.19022 | 0.92203
990 | 16.5 | feeder2_684 | 0.19508 | 0.96472 | 0.19508 | 0.96461
990 | 16.5 | feeder2_674 | 0.17556 | 0.76877 | 0.17555 | 0.76869
990 | 16.5 | feeder2_696 | 0.1802 | 0.78277 | 0.1802 | 0.78269
990 | 16.5 | feeder2_681 | 0.17397 | 0.76832 | 0.17396 | 0.76824
990 | 16.5 | feeder2_682 | 0.17348 | 0.77016 | 0.17347 | 0.77008
990 | 16.5 | feeder2_728 | 0.19476 | 0.96262 | 0.19475 | 0.96252
990 | 16.5 | feeder2_724 | 0.20139 | 1.0144 | 0.20138 | 1.0143
990 | 16.5 | feeder2_703 | 0.18033 | 0.78294 | 0.18033 | 0.78286
990 | 16.5 | feeder2_704 | 0.18386 | 0.78791 | 0.18386 | 0.78783
990 | 16.5 | feeder2_754 | 0.2014 | 1.0143 | 0.2014 | 1.0142
990 | 16.5 | feeder2_747 | 0.20397 | 1.0347 | 0.20397 | 1.0346
990 | 16.5 | feeder2_828 | 0.19347 | 0.96228 | 0.19347 | 0.96217
990 | 16.5 | feeder2_763 | 0.19475 | 0.96023 | 0.19474 | 0.96013
990 | 16.5 | feeder2_836 | 0.20485 | 1.0359 | 0.20484 | 1.0358
990 | 16.5 | feeder2_758 | 0.20609 | 1.0517 | 0.20608 | 1.0516
990 | 16.5 | feeder2_788 | 0.20651 | 1.0502 | 0.2065 | 1.0501
990 | 16.5 | feeder2_812 | 0.21278 | 1.1057 | 0.21277 | 1.1056
990 | 16.5 | feeder2_947 | 0.19478 | 0.9601 | 0.19477 | 0.96
990 | 16.5 | feeder2_868 | 0.19494 | 0.95953 | 0.19494 | 0.95943
990 | 16.5 | feeder2_785 | 0.19477 | 0.95928 | 0.19476 | 0.95918
990 | 16.5 | feeder2_1176 | 0.19494 | 0.9595 | 0.19493 | 0.9594
990 | 16.5 | feeder2_846 | 0.19367 | 0.95901 | 0.19367 | 0.9589
990 | 16.5 | feeder2_911 | 0.19511 | 0.95756 | 0.1951 | 0.95746
990 | 16.5 | feeder2_1107 | 0.206 | 1.0813 | 0.20599 | 1.0812
990 | 16.5 | feeder2_920 | 0.21653 | 1.1276 | 0.21653 | 1.1275
990 | 16.5 | feeder2_926 | 0.2222 | 1.1605 | 0.22219 | 1.1604
990 | 16.5 | feeder2_1239 | 0.21645 | 1.1274 | 0.21645 | 1.1273
990 | 16.5 | feeder2_933 | 0.2247 | 1.1752 | 0.2247 | 1.175
990 | 16.5 | feeder2_1146 | 0.22219 | 1.1605 | 0.22218 | 1.1603
990 | 16.5 | feeder2_1124 | 0.22475 | 1.1752 | 0.22474 | 1.1751
990 | 16.5 | feeder2_942 | 0.23105 | 1.2122 | 0.23104 | 1.212
990 | 16.5 | feeder2_952 | 0.24092 | 1.2686 | 0.24091 | 1.2685
990 | 16.5 | feeder2_965 | 0.23098 | 1.212 | 0.23098 | 1.2118
990 | 16.5 | feeder2_961 | 0.24199 | 1.2747 | 0.24199 | 1.2746
990 | 16.5 | feeder2_963 | 0.24092 | 1.2686 | 0.24091 | 1.2685
990 | 16.5 | feeder2_973 | 0.24791 | 1.3068 | 0.24791 | 1.3067
990 | 16.5 | feeder2_1128 | 0.24159 | 1.2755 | 0.24158 | 1.2754
990 | 16.5 | feeder2_1113 | 0.24093 | 1.2686 | 0.24092 | 1.2684
990 | 16.5 | feeder2_1143 | 0.24091 | 1.2685 | 0.24091 | 1.2684
990 | 16.5 | feeder2_1238 | 0.23206 | 1.207 | 0.23205 | 1.2069
990 | 16.5 | feeder2_979 | 0.23094 | 1.2121 | 0.23094 | 1.2119
990 | 16.5 | feeder2_1236 | 0.25615 | 1.3519 | 0.25615 | 1.3518
990 | 16.5 | feeder2_989 | 0.24792 | 1.3069 | 0.24791 | 1.3067
990 | 16.5 | feeder2_1196 | 0.23033 | 1.2125 | 0.23032 | 1.2124
990 | 16.5 | feeder2_1158 | 0.25029 | 1.3101 | 0.25029 | 1.3099
990 | 16.5 | feeder2_1122 | 0.20311 | 1.0708 | 0.2031 | 1.0707
990 | 16.5 | feeder2_1258 | 0.20709 | 1.0827 | 0.20708 | 1.0826
990 | 16.5 | feeder2_1303 | 0.20359 | 1.0689 | 0.20358 | 1.0688
990 | 16.5 | feeder2_1138 | 0.20089 | 1.0632 | 0.20089 | 1.063
990 | 16.5 | feeder2_1304 | 0.20073 | 1.0631 | 0.20072 | 1.063
990 | 16.5 | feeder2_1212 | 0.19623 | 1.0473 | 0.19623 | 1.0472
990 | 16.5 | feeder2_1311 | 0.19729 | 1.0444 | 0.19728 | 1.0443
990 | 16.5 | feeder2_1290 | 0.19062 | 1.0303 | 0.19061 | 1.0302
990 | 16.5 | feeder2_1325 | 0.26468 | 1.4005 | 0.26467 | 1.4003
990 | 16.5 | feeder2_1248 | 0.2562 | 1.352 | 0.25619 | 1.3518
990 | 16.5 | feeder2_1249 | 0.23211 | 1.2066 | 0.2321 | 1.2064
990 | 16.5 | feeder2_1250 | 0.2328 | 1.2045 | 0.23279 | 1.2044
990 | 16.5 | feeder2_1366 | 0.25614 | 1.3529 | 0.25613 | 1.3527
990 | 16.5 | feeder2_1266 | 0.20808 | 1.0841 | 0.20808 | 1.0839
990 | 16.5 | feeder2_1372 | 0.19191 | 1.0286 | 0.1919 | 1.0285
990 | 16.5 | feeder2_1363 | 0.18445 | 1.0153 | 0.18444 | 1.0152
990 | 16.5 | feeder2_1446 | 0.26503 | 1.3992 | 0.26502 | 1.399
990 | 16.5 | feeder2_1502 | 0.27445 | 1.4568 | 0.27444 | 1.4566
990 | 16.5 | feeder2_1428 | 0.18437 | 1.0153 | 0.18437 | 1.0152
990 | 16.5 | feeder2_1380 | 0.17703 | 0.99789 | 0.17703 | 0.99781
990 | 16.5 | feeder2_1550 | 0.17972 | 0.98476 | 0.17971 | 0.98468
990 | 16.5 | feeder2_1386 | 0.17414 | 0.9961 | 0.17414 | 0.99603
990 | 16.5 | feeder2_1551 | 0.17157 | 0.99846 | 0.17156 | 0.99839
990 | 16.5 | feeder2_1400 | 0.17293 | 0.9949 | 0.17293 | 0.99483
990 | 16.5 | feeder2_1552 | 0.16865 | 0.9947 | 0.16864 | 0.99464
990 | 16.5 | feeder2_1408 | 0.17079 | 0.993 | 0.17079 | 0.99294
990 | 16.5 | feeder2_1553 | 0.16976 | 0.99271 | 0.16976 | 0.99265
990 | 16.5 | feeder2_1416 | 0.16972 | 0.99221 | 0.16972 | 0.99215
990 | 16.5 | feeder2_1530 | 0.16972 | 0.99211 | 0.16972 | 0.99205
990 | 16.5 | feeder2_1425 | 0.16772 | 0.99097 | 0.16772 | 0.99092
990 | 16.5 | feeder2_1589 | 0.13835 | 0.99251 | 0.13836 | 0.99247
990 | 16.5 | feeder2_1435 | 0.16772 | 0.99098 | 0.16772 | 0.99092
990 | 16.5 | feeder2_1621 | 0.16783 | 0.9911 | 0.16783 | 0.99105
990 | 16.5 | feeder2_1564 | 0.16771 | 0.99095 | 0.1677 | 0.9909
990 | 16.5 | feeder2_1704 | 0.27567 | 1.4584 | 0.27566 | 1.4583
990 | 16.5 | feeder2_1525 | 0.27683 | 1.4707 | 0.27682 | 1.4705
990 | 16.5 | feeder2_1716 | 0.27797 | 1.4745 | 0.27796 | 1.4743
990 | 16.5 | feeder2_1537 | 0.27937 | 1.4855 | 0.27936 | 1.4853
990 | 16.5 | feeder2_1645 | 0.27853 | 1.4862 | 0.27852 | 1.486
990 | 16.5 | feeder2_1561 | 0.28237 | 1.5021 | 0.28235 | 1.5019
990 | 16.5 | feeder2_1657 | 0.28237 | 1.5021 | 0.28236 | 1.5019
990 | 16.5 | feeder2_1570 | 0.28366 | 1.5092 | 0.28365 | 1.5091
990 | 16.5 | feeder2_1756 | 0.28567 | 1.5043 | 0.28566 | 1.5041
990 | 16.5 | feeder2_1588 | 0.28489 | 1.5162 | 0.28488 | 1.516
990 | 16.5 | feeder2_1628 | 0.28501 | 1.5158 | 0.285 | 1.5156
990 | 16.5 | feeder2_1598 | 0.28645 | 1.5252 | 0.28645 | 1.525
990 | 16.5 | feeder2_1816 | 0.31489 | 1.5625 | 0.31489 | 1.5623
990 | 16.5 | feeder2_1765 | 0.28662 | 1.5254 | 0.28661 | 1.5252
990 | 16.5 | feeder2_1641 | 0.29174 | 1.5574 | 0.29173 | 1.5572
990 | 16.5 | feeder2_1689 | 0.2962 | 1.5874 | 0.29619 | 1.5872
990 | 16.5 | feeder2_1744 | 0.29268 | 1.5558 | 0.29268 | 1.5556
990 | 16.5 | feeder2_1817 | 0.29591 | 1.588 | 0.29591 | 1.5878
990 | 16.5 | feeder2_1779 | 0.30386 | 1.5975 | 0.30386 | 1.5973
990 | 16.5 | feeder2_1800 | 0.2936 | 1.5891 | 0.29358 | 1.5889
990 | 16.5 | feeder2_1818 | 0.31884 | 1.6188 | 0.31883 | 1.6186
990 | 16.5 | feeder2_1753 | 0.29335 | 1.5534 | 0.29334 | 1.5532
990 | 16.5 | feeder2_1754 | 0.2932 | 1.5552 | 0.29319 | 1.555
1020 | 17 | secondary | 0.030077 | 0.038919 | 0.030071 | 0.038907
1020 | 17 | feeder2_44 | 0.056058 | 0.2033 | 0.056042 | 0.20323
1020 | 17 | feeder2_45 | 0.056982 | 0.20961 | 0.056965 | 0.20953
1020 | 17 | feeder2_46 | 0.059021 | 0.20378 | 0.059004 | 0.2037
1020 | 17 | feeder2_51 | 0.058597 | 0.2206 | 0.058583 | 0.22053
1020 | 17 | feeder2_48 | 0.056907 | 0.20941 | 0.056893 | 0.20934
1020 | 17 | feeder2_52 | 0.054026 | 0.2262 | 0.054009 | 0.22613
1020 | 17 | feeder2_68 | 0.063357 | 0.24964 | 0.063336 | 0.24955
1020 | 17 | feeder2_69 | 0.064974 | 0.25006 | 0.064955 | 0.24997
1020 | 17 | feeder2_71 | 0.063973 | 0.25346 | 0.063954 | 0.25337
1020 | 17 | feeder2_72 | 0.063123 | 0.25124 | 0.063107 | 0.25114
1020 | 17 | feeder2_73 | 0.06595 | 0.2657 | 0.065931 | 0.2656
1020 | 17 | feeder2_74 | 0.061763 | 0.2716 | 0.061744 | 0.2715
1020 | 17 | feeder2_77 | 0.067677 | 0.27539 | 0.067664 | 0.27529
1020 | 17 | feeder2_79 | 0.067983 | 0.27546 | 0.067967 | 0.27536
1020 | 17 | feeder2_81 | 0.070385 | 0.2907 | 0.07037 | 0.29059
1020 | 17 | feeder2_82 | 0.068689 | 0.28556 | 0.068669 | 0.28545
1020 | 17 | feeder2_116 | 0.08353 | 0.36539 | 0.083504 | 0.36525
1020 | 17 | feeder2_119 | 0.081116 | 0.36815 | 0.081092 | 0.36801
1020 | 17 | feeder2_120 | 0.088606 | 0.39171 | 0.088579 | 0.39157
1020 | 17 | feeder2_248 | 0.085256 | 0.39557 | 0.085233 | 0.39543
1020 | 17 | feeder2_124 | 0.091888 | 0.40646 | 0.091863 | 0.4063
1020 | 17 | feeder2_282 | 0.090002 | 0.40127 | 0.089976 | 0.40112
1020 | 17 | feeder2_275 | 0.076436 | 0.43082 | 0.076411 | 0.43067
1020 | 17 | feeder2_151 | 0.098869 | 0.42187 | 0.098839 | 0.42171
1020 | 17 | feeder2_295 | 0.10233 | 0.42301 | 0.10231 | 0.42285
1020 | 17 | feeder2_311 | 0.098983 | 0.42192 | 0.098957 | 0.42176
1020 | 17 | feeder2_201 | 0.10968 | 0.44735 | 0.10965 | 0.44717
1020 | 17 | feeder2_314 | 0.10964 | 0.44726 | 0.10962 | 0.44708
1020 | 17 | feeder2_342 | 0.12548 | 0.48688 | 0.12544 | 0.48668
1020 | 17 | feeder2_368 | 0.12666 | 0.49256 | 0.12663 | 0.49236
1020 | 17 | feeder2_347 | 0.13158 | 0.49672 | 0.13155 | 0.4965
1020 | 17 | feeder2_353 | 0.13466 | 0.50181 | 0.13463 | 0.50159
1020 | 17 | feeder2_518 | 0.13155 | 0.49663 | 0.13152 | 0.49642
1020 | 17 | feeder2_365 | 0.1381 | 0.50756 | 0.13807 | 0.50733
1020 | 17 | feeder2_653 | 0.13459 | 0.50186 | 0.13456 | 0.50164
1020 | 17 | feeder2_377 | 0.13964 | 0.50973 | 0.13961 | 0.5095
1020 | 17 | feeder2_622 | 0.14399 | 0.51096 | 0.14395 | 0.51073
1020 | 17 | feeder2_451 | 0.12762 | 0.49158 | 0.12759 | 0.49137
1020 | 17 | feeder2_383 | 0.12847 | 0.50266 | 0.12844 | 0.50246
1020 | 17 | feeder2_385 | 0.14116 | 0.51148 | 0.14112 | 0.51124
1020 | 17 | feeder2_621 | 0.14316 | 0.51171 | 0.14313 | 0.51148
1020 | 17 | feeder2_611 | 0.12721 | 0.50365 | 0.12718 | 0.50345
1020 | 17 | feeder2_405 | 0.1286 | 0.50325 | 0.12857 | 0.50305
1020 | 17 | feeder2_461 | 0.14801 | 0.51537 | 0.14798 | 0.51512
1020 | 17 | feeder2_594 | 0.1387 | 0.51359 | 0.13867 | 0.51336
1020 | 17 | feeder2_732 | 0.12055 | 0.51113 | 0.12052 | 0.51093
1020 | 17 | feeder2_417 | 0.12997 | 0.50608 | 0.12994 | 0.50587
1020 | 17 | feeder2_663 | 0.13228 | 0.50742 | 0.13225 | 0.50722
1020 | 17 | feeder2_444 | 0.13082 | 0.50778 | 0.13079 | 0.50758
1020 | 17 | feeder2_759 | 0.13079 | 0.5035 | 0.13076 | 0.5033
1020 | 17 | feeder2_842 | 0.13393 | 0.50946 | 0.13391 | 0.50925
1020 | 17 | feeder2_459 | 0.13108 | 0.50854 | 0.13105 | 0.50834
1020 | 17 | feeder2_702 | 0.13066 | 0.50627 | 0.13063 | 0.50607
1020 | 17 | feeder2_493 | 0.13223 | 0.51236 | 0.1322 | 0.51216
1020 | 17 | feeder2_651 | 0.15 | 0.51614 | 0.14997 | 0.51589
1020 | 17 | feeder2_684 | 0.15308 | 0.5176 | 0.15305 | 0.51734
1020 | 17 | feeder2_674 | 0.13108 | 0.5133 | 0.13105 | 0.51309
1020 | 17 | feeder2_696 | 0.13648 | 0.52005 | 0.13646 | 0.51984
1020 | 17 | feeder2_681 | 0.12982 | 0.51441 | 0.12979 | 0.51421
1020 | 17 | feeder2_682 | 0.12831 | 0.5155 | 0.12828 | 0.51529
1020 | 17 | feeder2_728 | 0.15255 | 0.51745 | 0.15252 | 0.51718
1020 | 17 | feeder2_724 | 0.15913 | 0.52048 | 0.15909 | 0.5202
1020 | 17 | feeder2_703 | 0.13762 | 0.51908 | 0.13758 | 0.51888
1020 | 17 | feeder2_704 | 0.14143 | 0.52284 | 0.1414 | 0.52264
1020 | 17 | feeder2_754 | 0.15911 | 0.52038 | 0.15908 | 0.52011
1020 | 17 | feeder2_747 | 0.16164 | 0.52178 | 0.16161 | 0.5215
1020 | 17 | feeder2_828 | 0.15111 | 0.51834 | 0.15107 | 0.51808
1020 | 17 | feeder2_763 | 0.1522 | 0.51615 | 0.15217 | 0.51588
1020 | 17 | feeder2_836 | 0.17368 | 0.52862 | 0.17365 | 0.52834
1020 | 17 | feeder2_758 | 0.16244 | 0.51945 | 0.16241 | 0.51916
1020 | 17 | feeder2_788 | 0.16226 | 0.5176 | 0.16223 | 0.51731
1020 | 17 | feeder2_812 | 0.16528 | 0.51466 | 0.16525 | 0.51436
1020 | 17 | feeder2_947 | 0.15216 | 0.51596 | 0.15212 | 0.51569
1020 | 17 | feeder2_868 | 0.15232 | 0.51417 | 0.15229 | 0.51391
1020 | 17 | feeder2_785 | 0.1521 | 0.51682 | 0.15207 | 0.51656
1020 | 17 | feeder2_1176 | 0.154 | 0.51618 | 0.15396 | 0.51591
1020 | 17 | feeder2_846 | 0.14996 | 0.51839 | 0.14993 | 0.51812
1020 | 17 | feeder2_911 | 0.15208 | 0.51672 | 0.15205 | 0.51645
1020 | 17 | feeder2_1107 | 0.16419 | 0.50856 | 0.16416 | 0.50825
1020 | 17 | feeder2_920 | 0.16641 | 0.51501 | 0.16637 | 0.5147
1020 | 17 | feeder2_926 | 0.16869 | 0.51336 | 0.16865 | 0.51304
1020 | 17 | feeder2_1239 | 0.16571 | 0.51767 | 0.16568 | 0.51736
1020 | 17 | feeder2_933 | 0.16969 | 0.51297 | 0.16965 | 0.51265
1020 | 17 | feeder2_1146 | 0.16877 | 0.51185 | 0.16872 | 0.51154
1020 | 17 | feeder2_1124 | 0.16987 | 0.5127 | 0.16983 | 0.51238
1020 | 17 | feeder2_942 | 0.17211 | 0.51219 | 0.17207 | 0.51187
1020 | 17 | feeder2_952 | 0.17575 | 0.51598 | 0.17571 | 0.51565
1020 | 17 | feeder2_965 | 0.17211 | 0.51157 | 0.17207 | 0.51125
1020 | 17 | feeder2_961 | 0.17613 | 0.51654 | 0.17609 | 0.51621
1020 | 17 | feeder2_963 | 0.17575 | 0.51595 | 0.17571 | 0.51562
1020 | 17 | feeder2_973 | 0.17839 | 0.51907 | 0.17835 | 0.51874
1020 | 17 | feeder2_1128 | 0.17581 | 0.51748 | 0.17578 | 0.51714
1020 | 17 | feeder2_1113 | 0.17627 | 0.51533 | 0.17623 | 0.515
1020 | 17 | feeder2_1143 | 0.17573 | 0.51582 | 0.17569 | 0.51549
1020 | 17 | feeder2_1238 | 0.17743 | 0.50209 | 0.17739 | 0.50177
1020 | 17 | feeder2_979 | 0.17211 | 0.51158 | 0.17208 | 0.51125
1020 | 17 | feeder2_1236 | 0.18132 | 0.52155 | 0.18128 | 0.5212
1020 | 17 | feeder2_989 | 0.17839 | 0.51908 | 0.17835 | 0.51875
1020 | 17 | feeder2_1196 | 0.17207 | 0.51159 | 0.17203 | 0.51127
1020 | 17 | feeder2_1158 | 0.18045 | 0.52062 | 0.18041 | 0.52029
1020 | 17 | feeder2_1122 | 0.16224 | 0.5023 | 0.1622 | 0.50199
1020 | 17 | feeder2_1258 | 0.17132 | 0.51276 | 0.17128 | 0.51245
1020 | 17 | feeder2_1303 | 0.16209 | 0.48939 | 0.16206 | 0.48909
1020 | 17 | feeder2_1138 | 0.16124 | 0.502 | 0.16121 | 0.50169
1020 | 17 | feeder2_1304 | 0.15937 | 0.50367 | 0.15933 | 0.50337
1020 | 17 | feeder2_1212 | 0.1594 | 0.50034 | 0.15935 | 0.50003
1020 | 17 | feeder2_1311 | 0.16376 | 0.49267 | 0.16373 | 0.49237
1020 | 17 | feeder2_1290 | 0.15715 | 0.50534 | 0.15712 | 0.50503
1020 | 17 | feeder2_1325 | 0.18249 | 0.51616 | 0.18245 | 0.51581
1020 | 17 | feeder2_1248 | 0.18137 | 0.52158 | 0.18133 | 0.52124
1020 | 17 | feeder2_1249 | 0.17788 | 0.5011 | 0.17784 | 0.50078
1020 | 17 | feeder2_1250 | 0.18024 | 0.49783 | 0.18021 | 0.49751
1020 | 17 | feeder2_1366 | 0.18167 | 0.52118 | 0.18163 | 0.52083
1020 | 17 | feeder2_1266 | 0.17739 | 0.51691 | 0.17736 | 0.5166
1020 | 17 | feeder2_1372 | 0.15853 | 0.50347 | 0.15849 | 0.50316
1020 | 17 | feeder2_1363 | 0.1547 | 0.51388 | 0.15467 | 0.51357
1020 | 17 | feeder2_1446 | 0.18473 | 0.51241 | 0.18469 | 0.51206
1020 | 17 | feeder2_1502 | 0.18378 | 0.51526 | 0.18373 | 0.51489
1020 | 17 | feeder2_1428 | 0.15463 | 0.51392 | 0.1546 | 0.51361
1020 | 17 | feeder2_1380 | 0.15177 | 0.52453 | 0.15174 | 0.52421
1020 | 17 | feeder2_1550 | 0.15137 | 0.5223 | 0.15134 | 0.52198
1020 | 17 | feeder2_1386 | 0.15052 | 0.53097 | 0.15049 | 0.53066
1020 | 17 | feeder2_1551 | 0.15043 | 0.53103 | 0.1504 | 0.53072
1020 | 17 | feeder2_1400 | 0.14993 | 0.53406 | 0.1499 | 0.53374
1020 | 17 | feeder2_1552 | 0.14709 | 0.53615 | 0.14705 | 0.53583
1020 | 17 | feeder2_1408 | 0.14889 | 0.53956 | 0.14885 | 0.53925
1020 | 17 | feeder2_1553 | 0.14775 | 0.54038 | 0.14771 | 0.54007
1020 | 17 | feeder2_1416 | 0.14837 | 0.54229 | 0.14833 | 0.54197
1020 | 17 | feeder2_1530 | 0.14835 | 0.54216 | 0.14831 | 0.54185
1020 | 17 | feeder2_1425 | 0.1474 | 0.54757 | 0.14737 | 0.54726
1020 | 17 | feeder2_1589 | 0.13635 | 0.55741 | 0.13631 | 0.5571
1020 | 17 | feeder2_1435 | 0.14736 | 0.54778 | 0.14733 | 0.54746
1020 | 17 | feeder2_1621 | 0.14748 | 0.54784 | 0.14744 | 0.54753
1020 | 17 | feeder2_1564 | 0.14689 | 0.55012 | 0.14686 | 0.5498
1020 | 17 | feeder2_1704 | 0.18502 | 0.51628 | 0.18498 | 0.51591
1020 | 17 | feeder2_1525 | 0.18399 | 0.51462 | 0.18395 | 0.51425
1020 | 17 | feeder2_1716 | 0.1946 | 0.52282 | 0.19456 | 0.52246
1020 | 17 | feeder2_1537 | 0.1838 | 0.51253 | 0.18376 | 0.51216
1020 | 17 | feeder2_1645 | 0.18315 | 0.51325 | 0.1831 | 0.51288
1020 | 17 | feeder2_1561 | 0.18368 | 0.50977 | 0.18364 | 0.5094
1020 | 17 | feeder2_1657 | 0.18369 | 0.50851 | 0.18364 | 0.50814
1020 | 17 | feeder2_1570 | 0.18366 | 0.50888 | 0.18362 | 0.5085
1020 | 17 | feeder2_1756 | 0.19346 | 0.49307 | 0.19342 | 0.49269
1020 | 17 | feeder2_1588 | 0.18362 | 0.5091 | 0.18358 | 0.50872
1020 | 17 | feeder2_1628 | 0.18417 | 0.50088 | 0.18413 | 0.50049
1020 | 17 | feeder2_1598 | 0.18381 | 0.51171 | 0.18378 | 0.51132
1020 | 17 | feeder2_1816 | 0.21557 | 0.53789 | 0.21553 | 0.53752
1020 | 17 | feeder2_1765 | 0.18399 | 0.51185 | 0.18394 | 0.51147
1020 | 17 | feeder2_1641 | 0.18229 | 0.51601 | 0.18225 | 0.51562
1020 | 17 | feeder2_1689 | 0.18198 | 0.52906 | 0.18194 | 0.52865
1020 | 17 | feeder2_1744 | 0.18258 | 0.51019 | 0.18254 | 0.5098
1020 | 17 | feeder2_1817 | 0.18197 | 0.52908 | 0.18193 | 0.52867
1020 | 17 | feeder2_1779 | 0.1832 | 0.53006 | 0.18315 | 0.52965
1020 | 17 | feeder2_1800 | 0.15767 | 0.54157 | 0.15763 | 0.54116
1020 | 17 | feeder2_1818 | 0.19647 | 0.53825 | 0.19643 | 0.53783
1020 | 17 | feeder2_1753 | 0.18463 | 0.49185 | 0.1846 | 0.49145
1020 | 17 | feeder2_1754 | 0.18258 | 0.51016 | 0.18254 | 0.50976
1050 | 17.5 | secondary | 0.059831 | 0.048002 | 0.059839 | 0.048018
1050 | 17.5 | feeder2_44 | 0.11167 | 0.25108 | 0.11168 | 0.25115
1050 | 17.5 | feeder2_45 | 0.11356 | 0.25686 | 0.11357 | 0.25693
1050 | 17.5 | feeder2_46 | 0.10278 | 0.27851 | 0.10279 | 0.27858
1050 | 17.5 | feeder2_51 | 0.11683 | 0.26697 | 0.11685 | 0.26704
1050 | 17.5 | feeder2_48 | 0.11375 | 0.2569 | 0.11376 | 0.25697
1050 | 17.5 | feeder2_52 | 0.11451 | 0.26232 | 0.11453 | 0.2624
1050 | 17.5 | feeder2_68 | 0.12646 | 0.29775 | 0.12647 | 0.29783
1050 | 17.5 | feeder2_69 | 0.12513 | 0.30146 | 0.12515 | 0.30156
1050 | 17.5 | feeder2_71 | 0.12772 | 0.3017 | 0.12774 | 0.30179
1050 | 17.5 | feeder2_72 | 0.13341 | 0.30278 | 0.13343 | 0.30287
1050 | 17.5 | feeder2_73 | 0.13156 | 0.31392 | 0.13157 | 0.31402
1050 | 17.5 | feeder2_74 | 0.12911 | 0.31017 | 0.12913 | 0.31027
1050 | 17.5 | feeder2_77 | 0.13498 | 0.32508 | 0.13499 | 0.32518
1050 | 17.5 | feeder2_79 | 0.13124 | 0.33643 | 0.13126 | 0.33653
1050 | 17.5 | feeder2_81 | 0.14012 | 0.33913 | 0.14014 | 0.33923
1050 | 17.5 | feeder2_82 | 0.14629 | 0.33899 | 0.1463 | 0.3391
1050 | 17.5 | feeder2_116 | 0.16192 | 0.40416 | 0.16194 | 0.40428
1050 | 17.5 | feeder2_119 | 0.16039 | 0.40174 | 0.16041 | 0.40187
1050 | 17.5 | feeder2_120 | 0.17028 | 0.43036 | 0.1703 | 0.4305
1050 | 17.5 | feeder2_248 | 0.16882 | 0.42812 | 0.16884 | 0.42825
1050 | 17.5 | feeder2_124 | 0.17561 | 0.44755 | 0.17563 | 0.44769
1050 | 17.5 | feeder2_282 | 0.17962 | 0.44893 | 0.17964 | 0.44906
1050 | 17.5 | feeder2_275 | 0.17452 | 0.44587 | 0.17454 | 0.44601
1050 | 17.5 | feeder2_151 | 0.18468 | 0.47775 | 0.18471 | 0.4779
1050 | 17.5 | feeder2_295 | 0.1837 | 0.47963 | 0.18372 | 0.47977
1050 | 17.5 | feeder2_311 | 0.18465 | 0.47782 | 0.18468 | 0.47796
1050 | 17.5 | feeder2_201 | 0.19965 | 0.52598 | 0.19968 | 0.52614
1050 | 17.5 | feeder2_314 | 0.19973 | 0.52602 | 0.19976 | 0.52618
1050 | 17.5 | feeder2_342 | 0.22091 | 0.59531 | 0.22093 | 0.59549
1050 | 17.5 | feeder2_368 | 0.22013 | 0.59919 | 0.22015 | 0.59937
1050 | 17.5 | feeder2_347 | 0.23144 | 0.62449 | 0.23147 | 0.62466
1050 | 17.5 | feeder2_353 | 0.23571 | 0.63619 | 0.23575 | 0.63636
1050 | 17.5 | feeder2_518 | 0.24281 | 0.63077 | 0.24284 | 0.63094
1050 | 17.5 | feeder2_365 | 0.2405 | 0.64962 | 0.24053 | 0.64981
1050 | 17.5 | feeder2_653 | 0.23565 | 0.63608 | 0.23568 | 0.63626
1050 | 17.5 | feeder2_377 | 0.24308 | 0.65696 | 0.24311 | 0.65715
1050 | 17.5 | feeder2_622 | 0.23999 | 0.65031 | 0.24003 | 0.65049
1050 | 17.5 | feeder2_451 | 0.22022 | 0.59924 | 0.22025 | 0.59942
1050 | 17.5 | feeder2_383 | 0.219 | 0.60646 | 0.21903 | 0.60665
1050 | 17.5 | feeder2_385 | 0.24605 | 0.66518 | 0.24608 | 0.66537
1050 | 17.5 | feeder2_621 | 0.24188 | 0.65843 | 0.24191 | 0.65862
1050 | 17.5 | feeder2_611 | 0.21893 | 0.60637 | 0.21896 | 0.60656
1050 | 17.5 | feeder2_405 | 0.21894 | 0.60697 | 0.21897 | 0.60715
1050 | 17.5 | feeder2_461 | 0.25871 | 0.70297 | 0.25874 | 0.70315
1050 | 17.5 | feeder2_594 | 0.24516 | 0.66372 | 0.2452 | 0.6639
1050 | 17.5 | feeder2_732 | 0.21674 | 0.60173 | 0.21676 | 0.60192
1050 | 17.5 | feeder2_417 | 0.21873 | 0.61209 | 0.21876 | 0.61228
1050 | 17.5 | feeder2_663 | 0.21826 | 0.61347 | 0.21829 | 0.61366
1050 | 17.5 | feeder2_444 | 0.21859 | 0.61577 | 0.21862 | 0.61596
1050 | 17.5 | feeder2_759 | 0.22283 | 0.61628 | 0.22285 | 0.61648
1050 | 17.5 | feeder2_842 | 0.21175 | 0.64501 | 0.21177 | 0.64521
1050 | 17.5 | feeder2_459 | 0.21842 | 0.61555 | 0.21845 | 0.61574
1050 | 17.5 | feeder2_702 | 0.22025 | 0.61639 | 0.22028 | 0.61658
1050 | 17.5 | feeder2_493 | 0.2176 | 0.61435 | 0.21763 | 0.61454
1050 | 17.5 | feeder2_651 | 0.25778 | 0.70385 | 0.25782 | 0.70404
1050 | 17.5 | feeder2_684 | 0.26911 | 0.73502 | 0.26915 | 0.7352
1050 | 17.5 | feeder2_674 | 0.21612 | 0.61176 | 0.21615 | 0.61195
1050 | 17.5 | feeder2_696 | 0.21796 | 0.62282 | 0.21798 | 0.62302
1050 | 17.5 | feeder2_681 | 0.21318 | 0.60618 | 0.21321 | 0.60637
1050 | 17.5 | feeder2_682 | 0.21455 | 0.60952 | 0.21457 | 0.60971
1050 | 17.5 | feeder2_728 | 0.27069 | 0.73659 | 0.27073 | 0.73677
1050 | 17.5 | feeder2_724 | 0.27803 | 0.76526 | 0.27807 | 0.76545
1050 | 17.5 | feeder2_703 | 0.21793 | 0.62293 | 0.21795 | 0.62313
1050 | 17.5 | feeder2_704 | 0.21683 | 0.62638 | 0.21686 | 0.62658
1050 | 17.5 | feeder2_754 | 0.27812 | 0.76533 | 0.27816 | 0.76552
1050 | 17.5 | feeder2_747 | 0.28167 | 0.77763 | 0.28171 | 0.77782
1050 | 17.5 | feeder2_828 | 0.26995 | 0.73512 | 0.26998 | 0.7353
1050 | 17.5 | feeder2_763 | 0.27353 | 0.74136 | 0.27357 | 0.74153
1050 | 17.5 | feeder2_836 | 0.28019 | 0.77867 | 0.28024 | 0.77887
1050 | 17.5 | feeder2_758 | 0.28475 | 0.788 | 0.28479 | 0.7882
1050 | 17.5 | feeder2_788 | 0.28802 | 0.78951 | 0.28806 | 0.7897
1050 | 17.5 | feeder2_812 | 0.29336 | 0.81786 | 0.2934 | 0.81806
1050 | 17.5 | feeder2_947 | 0.29917 | 0.76039 | 0.29921 | 0.76056
1050 | 17.5 | feeder2_868 | 0.28093 | 0.74648 | 0.28096 | 0.74665
1050 | 17.5 | feeder2_785 | 0.2724 | 0.73611 | 0.27244 | 0.73629
1050 | 17.5 | feeder2_1176 | 0.27196 | 0.73637 | 0.272 | 0.73654
1050 | 17.5 | feeder2_846 | 0.26782 | 0.72654 | 0.26786 | 0.72672
1050 | 17.5 | feeder2_911 | 0.27242 | 0.7362 | 0.27246 | 0.73637
1050 | 17.5 | feeder2_1107 | 0.29511 | 0.82218 | 0.29516 | 0.82238
1050 | 17.5 | feeder2_920 | 0.29529 | 0.8251 | 0.29533 | 0.8253
1050 | 17.5 | feeder2_926 | 0.29821 | 0.83652 | 0.29826 | 0.83673
1050 | 17.5 | feeder2_1239 | 0.29523 | 0.82435 | 0.29528 | 0.82455
1050 | 17.5 | feeder2_933 | 0.29945 | 0.84131 | 0.2995 | 0.84152
1050 | 17.5 | feeder2_1146 | 0.29849 | 0.83777 | 0.29853 | 0.83798
1050 | 17.5 | feeder2_1124 | 0.29943 | 0.84132 | 0.29948 | 0.84153
1050 | 17.5 | feeder2_942 | 0.30259 | 0.85344 | 0.30264 | 0.85366
1050 | 17.5 | feeder2_952 | 0.30645 | 0.87155 | 0.30649 | 0.87177
1050 | 17.5 | feeder2_965 | 0.30269 | 0.85341 | 0.30273 | 0.85362
1050 | 17.5 | feeder2_961 | 0.30682 | 0.8734 | 0.30687 | 0.87361
1050 | 17.5 | feeder2_963 | 0.30646 | 0.87157 | 0.3065 | 0.87179
1050 | 17.5 | feeder2_973 | 0.30901 | 0.88419 | 0.30905 | 0.88441
1050 | 17.5 | feeder2_1128 | 0.30648 | 0.87175 | 0.30653 | 0.87197
1050 | 17.5 | feeder2_1113 | 0.30711 | 0.87207 | 0.30716 | 0.87229
1050 | 17.5 | feeder2_1143 | 0.30676 | 0.87157 | 0.3068 | 0.87179
1050 | 17.5 | feeder2_1238 | 0.31097 | 0.85703 | 0.31102 | 0.85724
1050 | 17.5 | feeder2_979 | 0.30267 | 0.85303 | 0.30272 | 0.85325
1050 | 17.5 | feeder2_1236 | 0.3124 | 0.89901 | 0.31244 | 0.89925
1050 | 17.5 | feeder2_989 | 0.30901 | 0.8842 | 0.30905 | 0.88443
1050 | 17.5 | feeder2_1196 | 0.30328 | 0.85154 | 0.30332 | 0.85176
1050 | 17.5 | feeder2_1158 | 0.30699 | 0.88595 | 0.30704 | 0.88618
1050 | 17.5 | feeder2_1122 | 0.29581 | 0.82233 | 0.29585 | 0.82252
1050 | 17.5 | feeder2_1258 | 0.2909 | 0.8251 | 0.29094 | 0.82529
1050 | 17.5 | feeder2_1303 | 0.30924 | 0.83171 | 0.30928 | 0.83191
1050 | 17.5 | feeder2_1138 | 0.29545 | 0.81894 | 0.2955 | 0.81913
1050 | 17.5 | feeder2_1304 | 0.2945 | 0.81733 | 0.29454 | 0.81752
1050 | 17.5 | feeder2_1212 | 0.29499 | 0.8132 | 0.29503 | 0.81338
1050 | 17.5 | feeder2_1311 | 0.31149 | 0.82524 | 0.31153 | 0.82541
1050 | 17.5 | feeder2_1290 | 0.29182 | 0.79557 | 0.29186 | 0.79575
1050 | 17.5 | feeder2_1325 | 0.31681 | 0.91771 | 0.31687 | 0.91795
1050 | 17.5 | feeder2_1248 | 0.31238 | 0.89903 | 0.31243 | 0.89926
1050 | 17.5 | feeder2_1249 | 0.31212 | 0.85761 | 0.31216 | 0.85783
1050 | 17.5 | feeder2_1250 | 0.31405 | 0.8582 | 0.31409 | 0.85842
1050 | 17.5 | feeder2_1366 | 0.31233 | 0.89906 | 0.31238 | 0.89929
1050 | 17.5 | feeder2_1266 | 0.28732 | 0.82779 | 0.28736 | 0.828
1050 | 17.5 | feeder2_1372 | 0.29188 | 0.79561 | 0.29192 | 0.7958
1050 | 17.5 | feeder2_1363 | 0.28843 | 0.77665 | 0.28848 | 0.77683
1050 | 17.5 | feeder2_1446 | 0.31941 | 0.91892 | 0.31947 | 0.91915
1050 | 17.5 | feeder2_1502 | 0.32104 | 0.93694 | 0.3211 | 0.93718
1050 | 17.5 | feeder2_1428 | 0.28891 | 0.77548 | 0.28896 | 0.77566
1050 | 17.5 | feeder2_1380 | 0.28443 | 0.75578 | 0.28448 | 0.75596
1050 | 17.5 | feeder2_1550 | 0.28721 | 0.75759 | 0.28726 | 0.75776
1050 | 17.5 | feeder2_1386 | 0.2822 | 0.74463 | 0.28224 | 0.7448
1050 | 17.5 | feeder2_1551 | 0.28213 | 0.74452 | 0.28217 | 0.74469
1050 | 17.5 | feeder2_1400 | 0.28114 | 0.73936 | 0.28118 | 0.73954
1050 | 17.5 | feeder2_1552 | 0.28022 | 0.73471 | 0.28026 | 0.73488
1050 | 17.5 | feeder2_1408 | 0.2793 | 0.73087 | 0.27934 | 0.73104
1050 | 17.5 | feeder2_1553 | 0.27811 | 0.72635 | 0.27815 | 0.72652
1050 | 17.5 | feeder2_1416 | 0.2785 | 0.72746 | 0.27854 | 0.72763
1050 | 17.5 | feeder2_1530 | 0.27862 | 0.72756 | 0.27867 | 0.72774
1050 | 17.5 | feeder2_1425 | 0.27696 | 0.7209 | 0.27701 | 0.72107
1050 | 17.5 | feeder2_1589 | 0.26949 | 0.70561 | 0.26954 | 0.70578
1050 | 17.5 | feeder2_1435 | 0.27694 | 0.72101 | 0.27698 | 0.72118
1050 | 17.5 | feeder2_1621 | 0.27559 | 0.72225 | 0.27563 | 0.72241
1050 | 17.5 | feeder2_1564 | 0.27691 | 0.72089 | 0.27695 | 0.72106
1050 | 17.5 | feeder2_1704 | 0.31918 | 0.93855 | 0.31923 | 0.9388
1050 | 17.5 | feeder2_1525 | 0.32218 | 0.94138 | 0.32224 | 0.94162
1050 | 17.5 | feeder2_1716 | 0.32211 | 0.94142 | 0.32217 | 0.94167
1050 | 17.5 | feeder2_1537 | 0.32345 | 0.94635 | 0.32351 | 0.94661
1050 | 17.5 | feeder2_1645 | 0.32401 | 0.94496 | 0.32407 | 0.94521
1050 | 17.5 | feeder2_1561 | 0.32493 | 0.95284 | 0.32499 | 0.95309
1050 | 17.5 | feeder2_1657 | 0.32499 | 0.95288 | 0.32505 | 0.95314
1050 | 17.5 | feeder2_1570 | 0.32557 | 0.95562 | 0.32563 | 0.95588
1050 | 17.5 | feeder2_1756 | 0.35715 | 0.97782 | 0.3572 | 0.97806
1050 | 17.5 | feeder2_1588 | 0.32579 | 0.95671 | 0.32584 | 0.95696
1050 | 17.5 | feeder2_1628 | 0.32644 | 0.95672 | 0.32649 | 0.95697
1050 | 17.5 | feeder2_1598 | 0.32601 | 0.95805 | 0.32607 | 0.9583
1050 | 17.5 | feeder2_1816 | 0.31618 | 0.96536 | 0.31624 | 0.96563
1050 | 17.5 | feeder2_1765 | 0.32594 | 0.95808 | 0.326 | 0.95834
1050 | 17.5 | feeder2_1641 | 0.32689 | 0.96334 | 0.32695 | 0.9636
1050 | 17.5 | feeder2_1689 | 0.32579 | 0.96051 | 0.32585 | 0.96077
1050 | 17.5 | feeder2_1744 | 0.33303 | 0.96757 | 0.33309 | 0.96782
1050 | 17.5 | feeder2_1817 | 0.32577 | 0.96043 | 0.32583 | 0.9607
1050 | 17.5 | feeder2_1779 | 0.32473 | 0.96135 | 0.3248 | 0.96163
1050 | 17.5 | feeder2_1800 | 0.3238 | 0.95684 | 0.32385 | 0.95711
1050 | 17.5 | feeder2_1818 | 0.31835 | 0.95457 | 0.31842 | 0.95485
1050 | 17.5 | feeder2_1753 | 0.35239 | 0.98105 | 0.35245 | 0.9813
1050 | 17.5 | feeder2_1754 | 0.33306 | 0.9676 | 0.33312 | 0.96785
1080 | 18 | secondary | 0.10432 | 0.10242 | 0.10431 | 0.10241
1080 | 18 | feeder2_44 | 0.19443 | 0.53499 | 0.19443 | 0.53497
1080 | 18 | feeder2_45 | 0.19776 | 0.55148 | 0.19776 | 0.55146
1080 | 18 | feeder2_46 | 0.19636 | 0.53856 | 0.19637 | 0.53854
1080 | 18 | feeder2_51 | 0.20349 | 0.58063 | 0.2035 | 0.58061
1080 | 18 | feeder2_48 | 0.20072 | 0.54822 | 0.20072 | 0.54819
1080 | 18 | feeder2_52 | 0.20102 | 0.57937 | 0.20103 | 0.57935
1080 | 18 | feeder2_68 | 0.21987 | 0.66345 | 0.21987 | 0.66342
1080 | 18 | feeder2_69 | 0.228 | 0.68167 | 0.228 | 0.68164
1080 | 18 | feeder2_71 | 0.22188 | 0.67348 | 0.22188 | 0.67345
1080 | 18 | feeder2_72 | 0.23559 | 0.65559 | 0.2356 | 0.65556
1080 | 18 | feeder2_73 | 0.22815 | 0.70684 | 0.22815 | 0.70681
1080 | 18 | feeder2_74 | 0.2257 | 0.70566 | 0.2257 | 0.70563
1080 | 18 | feeder2_77 | 0.23361 | 0.73567 | 0.23362 | 0.73564
1080 | 18 | feeder2_79 | 0.25021 | 0.76374 | 0.25022 | 0.76371
1080 | 18 | feeder2_81 | 0.24021 | 0.77064 | 0.24022 | 0.77061
1080 | 18 | feeder2_82 | 0.24224 | 0.76729 | 0.24224 | 0.76726
1080 | 18 | feeder2_116 | 0.27031 | 0.93051 | 0.27032 | 0.93047
1080 | 18 | feeder2_119 | 0.26828 | 0.92954 | 0.26828 | 0.92951
1080 | 18 | feeder2_120 | 0.28175 | 0.99041 | 0.28175 | 0.99038
1080 | 18 | feeder2_248 | 0.27977 | 0.98943 | 0.27977 | 0.9894
1080 | 18 | feeder2_124 | 0.28893 | 1.0277 | 0.28893 | 1.0277
1080 | 18 | feeder2_282 | 0.29017 | 1.0256 | 0.29017 | 1.0256
1080 | 18 | feeder2_275 | 0.28658 | 1.0266 | 0.28659 | 1.0266
1080 | 18 | feeder2_151 | 0.30179 | 1.0948 | 0.30179 | 1.0948
1080 | 18 | feeder2_295 | 0.30332 | 1.0973 | 0.30332 | 1.0972
1080 | 18 | feeder2_311 | 0.30267 | 1.0961 | 0.30267 | 1.0961
1080 | 18 | feeder2_201 | 0.32222 | 1.2012 | 0.32223 | 1.2011
1080 | 18 | feeder2_314 | 0.32246 | 1.2007 | 0.32247 | 1.2006
1080 | 18 | feeder2_342 | 0.35148 | 1.3532 | 0.35149 | 1.3531
1080 | 18 | feeder2_368 | 0.35424 | 1.3715 | 0.35425 | 1.3715
1080 | 18 | feeder2_347 | 0.36131 | 1.3939 | 0.36131 | 1.3938
1080 | 18 | feeder2_353 | 0.36628 | 1.415 | 0.36628 | 1.4149
1080 | 18 | feeder2_518 | 0.36214 | 1.3922 | 0.36215 | 1.3922
1080 | 18 | feeder2_365 | 0.3718 | 1.4385 | 0.3718 | 1.4384
1080 | 18 | feeder2_653 | 0.36618 | 1.4149 | 0.36619 | 1.4149
1080 | 18 | feeder2_377 | 0.37381 | 1.4461 | 0.37382 | 1.446
1080 | 18 | feeder2_622 | 0.38322 | 1.4583 | 0.38323 | 1.4583
1080 | 18 | feeder2_451 | 0.35426 | 1.3715 | 0.35426 | 1.3714
1080 | 18 | feeder2_383 | 0.35876 | 1.4013 | 0.35877 | 1.4012
1080 | 18 | feeder2_385 | 0.37595 | 1.4539 | 0.37596 | 1.4539
1080 | 18 | feeder2_621 | 0.37552 | 1.4487 | 0.37552 | 1.4487
1080 | 18 | feeder2_611 | 0.35762 | 1.4019 | 0.35763 | 1.4018
1080 | 18 | feeder2_405 | 0.35907 | 1.4031 | 0.35907 | 1.4031
1080 | 18 | feeder2_461 | 0.38498 | 1.4874 | 0.38499 | 1.4874
1080 | 18 | feeder2_594 | 0.37468 | 1.4533 | 0.3747 | 1.4532
1080 | 18 | feeder2_732 | 0.35689 | 1.4019 | 0.35689 | 1.4019
1080 | 18 | feeder2_417 | 0.36147 | 1.4173 | 0.36148 | 1.4172
1080 | 18 | feeder2_663 | 0.36316 | 1.4205 | 0.36316 | 1.4204
1080 | 18 | feeder2_444 | 0.36309 | 1.427 | 0.36309 | 1.427
1080 | 18 | feeder2_759 | 0.36334 | 1.4261 | 0.36334 | 1.4261
1080 | 18 | feeder2_842 | 0.39484 | 1.4712 | 0.39485 | 1.4711
1080 | 18 | feeder2_459 | 0.36302 | 1.4279 | 0.36303 | 1.4279
1080 | 18 | feeder2_702 | 0.36331 | 1.4271 | 0.36332 | 1.427
1080 | 18 | feeder2_493 | 0.3628 | 1.4316 | 0.3628 | 1.4316
1080 | 18 | feeder2_651 | 0.38602 | 1.49 | 0.38602 | 1.49
1080 | 18 | feeder2_684 | 0.3918 | 1.5117 | 0.39181 | 1.5117
1080 | 18 | feeder2_674 | 0.35957 | 1.4314 | 0.35958 | 1.4314
1080 | 18 | feeder2_696 | 0.36606 | 1.4447 | 0.36607 | 1.4447
1080 | 18 | feeder2_681 | 0.35165 | 1.4313 | 0.35165 | 1.4313
1080 | 18 | feeder2_682 | 0.35819 | 1.4307 | 0.35819 | 1.4306
1080 | 18 | feeder2_728 | 0.39139 | 1.5099 | 0.39139 | 1.5098
1080 | 18 | feeder2_724 | 0.39958 | 1.5409 | 0.39958 | 1.5409
1080 | 18 | feeder2_703 | 0.3662 | 1.4449 | 0.36621 | 1.4449
1080 | 18 | feeder2_704 | 0.36948 | 1.4496 | 0.36949 | 1.4495
1080 | 18 | feeder2_754 | 0.40087 | 1.5395 | 0.40088 | 1.5394
1080 | 18 | feeder2_747 | 0.40266 | 1.5536 | 0.40267 | 1.5536
1080 | 18 | feeder2_828 | 0.3902 | 1.5094 | 0.39021 | 1.5093
1080 | 18 | feeder2_763 | 0.39122 | 1.5082 | 0.39123 | 1.5081
1080 | 18 | feeder2_836 | 0.40536 | 1.5599 | 0.40537 | 1.5598
1080 | 18 | feeder2_758 | 0.40481 | 1.5618 | 0.40482 | 1.5617
1080 | 18 | feeder2_788 | 0.40783 | 1.557 | 0.40783 | 1.557
1080 | 18 | feeder2_812 | 0.41167 | 1.5922 | 0.41168 | 1.5921
1080 | 18 | feeder2_947 | 0.39314 | 1.5047 | 0.39315 | 1.5046
1080 | 18 | feeder2_868 | 0.3915 | 1.5076 | 0.3915 | 1.5075
1080 | 18 | feeder2_785 | 0.39118 | 1.5083 | 0.39118 | 1.5082
1080 | 18 | feeder2_1176 | 0.39374 | 1.512 | 0.39375 | 1.5119
1080 | 18 | feeder2_846 | 0.38945 | 1.5072 | 0.38946 | 1.5071
1080 | 18 | feeder2_911 | 0.39117 | 1.5082 | 0.39118 | 1.5081
1080 | 18 | feeder2_1107 | 0.41341 | 1.5999 | 0.41342 | 1.5998
1080 | 18 | feeder2_920 | 0.41311 | 1.5986 | 0.41312 | 1.5985
1080 | 18 | feeder2_926 | 0.41533 | 1.6084 | 0.41534 | 1.6084
1080 | 18 | feeder2_1239 | 0.41302 | 1.5982 | 0.41303 | 1.5981
1080 | 18 | feeder2_933 | 0.4163 | 1.6132 | 0.41631 | 1.6131
1080 | 18 | feeder2_1146 | 0.41539 | 1.6065 | 0.41539 | 1.6064
1080 | 18 | feeder2_1124 | 0.41635 | 1.6133 | 0.41635 | 1.6132
1080 | 18 | feeder2_942 | 0.41875 | 1.6252 | 0.41876 | 1.6252
1080 | 18 | feeder2_952 | 0.42255 | 1.6441 | 0.42255 | 1.644
1080 | 18 | feeder2_965 | 0.41873 | 1.6251 | 0.41874 | 1.625
1080 | 18 | feeder2_961 | 0.42294 | 1.6464 | 0.42295 | 1.6463
1080 | 18 | feeder2_963 | 0.42255 | 1.644 | 0.42256 | 1.6439
1080 | 18 | feeder2_973 | 0.42513 | 1.659 | 0.42514 | 1.6589
1080 | 18 | feeder2_1128 | 0.42278 | 1.6456 | 0.42279 | 1.6455
1080 | 18 | feeder2_1113 | 0.42319 | 1.6432 | 0.4232 | 1.6431
1080 | 18 | feeder2_1143 | 0.42273 | 1.6426 | 0.42274 | 1.6425
1080 | 18 | feeder2_1238 | 0.41993 | 1.6226 | 0.41994 | 1.6225
1080 | 18 | feeder2_979 | 0.41873 | 1.6251 | 0.41873 | 1.625
1080 | 18 | feeder2_1236 | 0.42785 | 1.6753 | 0.42786 | 1.6752
1080 | 18 | feeder2_989 | 0.42513 | 1.659 | 0.42514 | 1.6589
1080 | 18 | feeder2_1196 | 0.41867 | 1.6251 | 0.41868 | 1.625
1080 | 18 | feeder2_1158 | 0.42723 | 1.662 | 0.42724 | 1.6619
1080 | 18 | feeder2_1122 | 0.41254 | 1.5953 | 0.41255 | 1.5952
1080 | 18 | feeder2_1258 | 0.41989 | 1.6093 | 0.4199 | 1.6093
1080 | 18 | feeder2_1303 | 0.41279 | 1.5947 | 0.41279 | 1.5947
1080 | 18 | feeder2_1138 | 0.41187 | 1.5918 | 0.41188 | 1.5917
1080 | 18 | feeder2_1304 | 0.41044 | 1.591 | 0.41045 | 1.5909
1080 | 18 | feeder2_1212 | 0.41065 | 1.5852 | 0.41066 | 1.5852
1080 | 18 | feeder2_1311 | 0.41182 | 1.583 | 0.41182 | 1.5829
1080 | 18 | feeder2_1290 | 0.40933 | 1.5788 | 0.40934 | 1.5787
1080 | 18 | feeder2_1325 | 0.42826 | 1.6812 | 0.42827 | 1.6811
1080 | 18 | feeder2_1248 | 0.42791 | 1.6754 | 0.42791 | 1.6753
1080 | 18 | feeder2_1249 | 0.42014 | 1.6222 | 0.42015 | 1.6221
1080 | 18 | feeder2_1250 | 0.4203 | 1.6219 | 0.42031 | 1.6218
1080 | 18 | feeder2_1366 | 0.43997 | 1.6929 | 0.43998 | 1.6928
1080 | 18 | feeder2_1266 | 0.42032 | 1.61 | 0.42033 | 1.6099
1080 | 18 | feeder2_1372 | 0.40934 | 1.5787 | 0.40935 | 1.5787
1080 | 18 | feeder2_1363 | 0.40793 | 1.5719 | 0.40793 | 1.5718
1080 | 18 | feeder2_1446 | 0.42848 | 1.6807 | 0.42849 | 1.6806
1080 | 18 | feeder2_1502 | 0.42882 | 1.6883 | 0.42883 | 1.6882
1080 | 18 | feeder2_1428 | 0.40784 | 1.5718 | 0.40785 | 1.5718
1080 | 18 | feeder2_1380 | 0.40624 | 1.5637 | 0.40625 | 1.5636
1080 | 18 | feeder2_1550 | 0.40622 | 1.5634 | 0.40623 | 1.5633
1080 | 18 | feeder2_1386 | 0.40548 | 1.5598 | 0.40549 | 1.5597
1080 | 18 | feeder2_1551 | 0.40433 | 1.5592 | 0.40434 | 1.5591
1080 | 18 | feeder2_1400 | 0.40516 | 1.5581 | 0.40516 | 1.558
1080 | 18 | feeder2_1552 | 0.40128 | 1.5559 | 0.40129 | 1.5558
1080 | 18 | feeder2_1408 | 0.40479 | 1.556 | 0.40479 | 1.5559
1080 | 18 | feeder2_1553 | 0.39961 | 1.5566 | 0.39961 | 1.5565
1080 | 18 | feeder2_1416 | 0.40485 | 1.5549 | 0.40486 | 1.5548
1080 | 18 | feeder2_1530 | 0.40817 | 1.5512 | 0.40818 | 1.5511
1080 | 18 | feeder2_1425 | 0.40473 | 1.5547 | 0.40474 | 1.5546
1080 | 18 | feeder2_1589 | 0.40239 | 1.5536 | 0.4024 | 1.5535
1080 | 18 | feeder2_1435 | 0.40474 | 1.5548 | 0.40476 | 1.5547
1080 | 18 | feeder2_1621 | 0.40467 | 1.5557 | 0.40468 | 1.5556
1080 | 18 | feeder2_1564 | 0.40473 | 1.5547 | 0.40474 | 1.5546
1080 | 18 | feeder2_1704 | 0.4326 | 1.6948 | 0.43261 | 1.6947
1080 | 18 | feeder2_1525 | 0.4285 | 1.6878 | 0.42851 | 1.6877
1080 | 18 | feeder2_1716 | 0.42829 | 1.6898 | 0.42829 | 1.6897
1080 | 18 | feeder2_1537 | 0.42811 | 1.6869 | 0.42812 | 1.6868
1080 | 18 | feeder2_1645 | 0.42808 | 1.6869 | 0.42809 | 1.6868
1080 | 18 | feeder2_1561 | 0.42767 | 1.6859 | 0.42767 | 1.6858
1080 | 18 | feeder2_1657 | 0.42849 | 1.685 | 0.4285 | 1.6848
1080 | 18 | feeder2_1570 | 0.42745 | 1.6856 | 0.42746 | 1.6855
1080 | 18 | feeder2_1756 | 0.4297 | 1.6815 | 0.42971 | 1.6814
1080 | 18 | feeder2_1588 | 0.42727 | 1.6857 | 0.42728 | 1.6856
1080 | 18 | feeder2_1628 | 0.42742 | 1.6854 | 0.42743 | 1.6852
1080 | 18 | feeder2_1598 | 0.42706 | 1.6858 | 0.42706 | 1.6857
1080 | 18 | feeder2_1816 | 0.43157 | 1.6925 | 0.43158 | 1.6924
1080 | 18 | feeder2_1765 | 0.42866 | 1.6881 | 0.42866 | 1.688
1080 | 18 | feeder2_1641 | 0.4254 | 1.6832 | 0.42541 | 1.6831
1080 | 18 | feeder2_1689 | 0.42404 | 1.6814 | 0.42405 | 1.6813
1080 | 18 | feeder2_1744 | 0.42552 | 1.6829 | 0.42553 | 1.6828
1080 | 18 | feeder2_1817 | 0.42403 | 1.6813 | 0.42404 | 1.6812
1080 | 18 | feeder2_1779 | 0.4246 | 1.682 | 0.42461 | 1.6819
1080 | 18 | feeder2_1800 | 0.41908 | 1.6793 | 0.41909 | 1.6792
1080 | 18 | feeder2_1818 | 0.41564 | 1.6724 | 0.41564 | 1.6723
1080 | 18 | feeder2_1753 | 0.42588 | 1.6822 | 0.42589 | 1.6821
1080 | 18 | feeder2_1754 | 0.42553 | 1.6829 | 0.42554 | 1.6828
1110 | 18.5 | secondary | 0.052348 | 0.028124 | 0.05235 | 0.028128
1110 | 18.5 | feeder2_44 | 0.097571 | 0.14691 | 0.097577 | 0.14694
1110 | 18.5 | feeder2_45 | 0.098871 | 0.14729 | 0.098874 | 0.14732
1110 | 18.5 | feeder2_46 | 0.10443 | 0.19777 | 0.10442 | 0.1978
1110 | 18.5 | feeder2_51 | 0.10113 | 0.14798 | 0.10113 | 0.14801
1110 | 18.5 | feeder2_48 | 0.099036 | 0.14721 | 0.099039 | 0.14724
1110 | 18.5 | feeder2_52 | 0.09778 | 0.1479 | 0.097786 | 0.14792
1110 | 18.5 | feeder2_68 | 0.1081 | 0.15091 | 0.10811 | 0.15095
1110 | 18.5 | feeder2_69 | 0.10832 | 0.1558 | 0.10833 | 0.15585
1110 | 18.5 | feeder2_71 | 0.109 | 0.15111 | 0.109 | 0.15116
1110 | 18.5 | feeder2_72 | 0.11429 | 0.1495 | 0.11429 | 0.14955
1110 | 18.5 | feeder2_73 | 0.11172 | 0.15194 | 0.11173 | 0.15198
1110 | 18.5 | feeder2_74 | 0.11083 | 0.15114 | 0.11084 | 0.15119
1110 | 18.5 | feeder2_77 | 0.11409 | 0.15286 | 0.11409 | 0.15291
1110 | 18.5 | feeder2_79 | 0.11487 | 0.17554 | 0.11488 | 0.17558
1110 | 18.5 | feeder2_81 | 0.11698 | 0.14633 | 0.11699 | 0.14638
1110 | 18.5 | feeder2_82 | 0.12164 | 0.1451 | 0.12165 | 0.14516
1110 | 18.5 | feeder2_116 | 0.1295 | 0.12304 | 0.12952 | 0.12315
1110 | 18.5 | feeder2_119 | 0.12888 | 0.12204 | 0.12889 | 0.12215
1110 | 18.5 | feeder2_120 | 0.13442 | 0.11793 | 0.13444 | 0.11806
1110 | 18.5 | feeder2_248 | 0.13304 | 0.11569 | 0.13305 | 0.11582
1110 | 18.5 | feeder2_124 | 0.1377 | 0.11689 | 0.13771 | 0.11705
1110 | 18.5 | feeder2_282 | 0.14071 | 0.11763 | 0.14072 | 0.11778
1110 | 18.5 | feeder2_275 | 0.13611 | 0.11489 | 0.13613 | 0.11505
1110 | 18.5 | feeder2_151 | 0.14342 | 0.1179 | 0.14343 | 0.11808
1110 | 18.5 | feeder2_295 | 0.14303 | 0.11937 | 0.14304 | 0.11955
1110 | 18.5 | feeder2_311 | 0.14321 | 0.11899 | 0.14322 | 0.11917
1110 | 18.5 | feeder2_201 | 0.15257 | 0.1229 | 0.15259 | 0.12311
1110 | 18.5 | feeder2_314 | 0.15652 | 0.12379 | 0.15654 | 0.12401
1110 | 18.5 | feeder2_342 | 0.16402 | 0.13834 | 0.16404 | 0.1386
1110 | 18.5 | feeder2_368 | 0.16264 | 0.13105 | 0.16266 | 0.13131
1110 | 18.5 | feeder2_347 | 0.17156 | 0.16218 | 0.17158 | 0.16245
1110 | 18.5 | feeder2_353 | 0.17502 | 0.17282 | 0.17504 | 0.1731
1110 | 18.5 | feeder2_518 | 0.17501 | 0.16493 | 0.17504 | 0.1652
1110 | 18.5 | feeder2_365 | 0.17886 | 0.18479 | 0.17889 | 0.18508
1110 | 18.5 | feeder2_653 | 0.17494 | 0.17273 | 0.17496 | 0.17301
1110 | 18.5 | feeder2_377 | 0.18072 | 0.19181 | 0.18075 | 0.1921
1110 | 18.5 | feeder2_622 | 0.17637 | 0.18522 | 0.17639 | 0.18551
1110 | 18.5 | feeder2_451 | 0.16331 | 0.13166 | 0.16334 | 0.13192
1110 | 18.5 | feeder2_383 | 0.16028 | 0.11873 | 0.1603 | 0.11899
1110 | 18.5 | feeder2_385 | 0.18283 | 0.20022 | 0.18285 | 0.20051
1110 | 18.5 | feeder2_621 | 0.18014 | 0.19181 | 0.18017 | 0.1921
1110 | 18.5 | feeder2_611 | 0.16007 | 0.1172 | 0.1601 | 0.11745
1110 | 18.5 | feeder2_405 | 0.16014 | 0.11804 | 0.16016 | 0.1183
1110 | 18.5 | feeder2_461 | 0.19211 | 0.24037 | 0.19214 | 0.24067
1110 | 18.5 | feeder2_594 | 0.18211 | 0.19808 | 0.18214 | 0.19837
1110 | 18.5 | feeder2_732 | 0.1404 | 0.08925 | 0.14043 | 0.089507
1110 | 18.5 | feeder2_417 | 0.16079 | 0.11908 | 0.16081 | 0.11934
1110 | 18.5 | feeder2_663 | 0.16056 | 0.11922 | 0.16058 | 0.11948
1110 | 18.5 | feeder2_444 | 0.16124 | 0.11992 | 0.16126 | 0.12018
1110 | 18.5 | feeder2_759 | 0.16807 | 0.12267 | 0.16809 | 0.12293
1110 | 18.5 | feeder2_842 | 0.16081 | 0.12029 | 0.16083 | 0.12054
1110 | 18.5 | feeder2_459 | 0.16126 | 0.12001 | 0.16129 | 0.12027
1110 | 18.5 | feeder2_702 | 0.16373 | 0.1213 | 0.16375 | 0.12156
1110 | 18.5 | feeder2_493 | 0.16109 | 0.11983 | 0.16111 | 0.12009
1110 | 18.5 | feeder2_651 | 0.19155 | 0.24002 | 0.19158 | 0.24033
1110 | 18.5 | feeder2_684 | 0.19967 | 0.27568 | 0.19971 | 0.276
1110 | 18.5 | feeder2_674 | 0.16067 | 0.11932 | 0.16069 | 0.11958
1110 | 18.5 | feeder2_696 | 0.16124 | 0.12189 | 0.16127 | 0.12215
1110 | 18.5 | feeder2_681 | 0.15983 | 0.11829 | 0.15986 | 0.11855
1110 | 18.5 | feeder2_682 | 0.16017 | 0.11878 | 0.16019 | 0.11904
1110 | 18.5 | feeder2_728 | 0.2 | 0.2798 | 0.20004 | 0.28011
1110 | 18.5 | feeder2_724 | 0.20767 | 0.30327 | 0.20771 | 0.3036
1110 | 18.5 | feeder2_703 | 0.16123 | 0.12192 | 0.16125 | 0.12218
1110 | 18.5 | feeder2_704 | 0.1604 | 0.12312 | 0.16042 | 0.12338
1110 | 18.5 | feeder2_754 | 0.20776 | 0.30336 | 0.20779 | 0.30369
1110 | 18.5 | feeder2_747 | 0.21093 | 0.31448 | 0.21097 | 0.31482
1110 | 18.5 | feeder2_828 | 0.19927 | 0.27898 | 0.19931 | 0.27929
1110 | 18.5 | feeder2_763 | 0.20094 | 0.28739 | 0.20098 | 0.2877
1110 | 18.5 | feeder2_836 | 0.20988 | 0.31312 | 0.20991 | 0.31346
1110 | 18.5 | feeder2_758 | 0.21363 | 0.32493 | 0.21366 | 0.32527
1110 | 18.5 | feeder2_788 | 0.21639 | 0.32734 | 0.21643 | 0.32768
1110 | 18.5 | feeder2_812 | 0.22121 | 0.35386 | 0.22126 | 0.35422
1110 | 18.5 | feeder2_947 | 0.20873 | 0.29513 | 0.20877 | 0.29543
1110 | 18.5 | feeder2_868 | 0.21024 | 0.2973 | 0.21027 | 0.2976
1110 | 18.5 | feeder2_785 | 0.19945 | 0.28338 | 0.19949 | 0.28368
1110 | 18.5 | feeder2_1176 | 0.19807 | 0.281 | 0.1981 | 0.28131
1110 | 18.5 | feeder2_846 | 0.19141 | 0.27595 | 0.19145 | 0.27625
1110 | 18.5 | feeder2_911 | 0.1999 | 0.28439 | 0.19993 | 0.28469
1110 | 18.5 | feeder2_1107 | 0.21688 | 0.32797 | 0.21692 | 0.32832
1110 | 18.5 | feeder2_920 | 0.22454 | 0.36916 | 0.22458 | 0.36953
1110 | 18.5 | feeder2_926 | 0.22957 | 0.39219 | 0.22961 | 0.39256
1110 | 18.5 | feeder2_1239 | 0.22445 | 0.36893 | 0.22449 | 0.36929
1110 | 18.5 | feeder2_933 | 0.23165 | 0.40194 | 0.23169 | 0.40232
1110 | 18.5 | feeder2_1146 | 0.23026 | 0.39431 | 0.2303 | 0.39468
1110 | 18.5 | feeder2_1124 | 0.23153 | 0.40181 | 0.23157 | 0.40219
1110 | 18.5 | feeder2_942 | 0.23689 | 0.42683 | 0.23693 | 0.42722
1110 | 18.5 | feeder2_952 | 0.24059 | 0.43949 | 0.24063 | 0.43989
1110 | 18.5 | feeder2_965 | 0.23742 | 0.42998 | 0.23746 | 0.43037
1110 | 18.5 | feeder2_961 | 0.24093 | 0.44069 | 0.24097 | 0.44109
1110 | 18.5 | feeder2_963 | 0.2406 | 0.43953 | 0.24065 | 0.43993
1110 | 18.5 | feeder2_973 | 0.24279 | 0.44733 | 0.24284 | 0.44774
1110 | 18.5 | feeder2_1128 | 0.24083 | 0.44043 | 0.24088 | 0.44083
1110 | 18.5 | feeder2_1113 | 0.24178 | 0.44028 | 0.24182 | 0.44069
1110 | 18.5 | feeder2_1143 | 0.24062 | 0.43966 | 0.24066 | 0.44007
1110 | 18.5 | feeder2_1238 | 0.28629 | 0.47943 | 0.28634 | 0.47981
1110 | 18.5 | feeder2_979 | 0.23741 | 0.42997 | 0.23745 | 0.43036
1110 | 18.5 | feeder2_1236 | 0.24549 | 0.45812 | 0.24553 | 0.45854
1110 | 18.5 | feeder2_989 | 0.24279 | 0.44732 | 0.24284 | 0.44774
1110 | 18.5 | feeder2_1196 | 0.23737 | 0.42994 | 0.23742 | 0.43033
1110 | 18.5 | feeder2_1158 | 0.24202 | 0.44679 | 0.24206 | 0.44721
1110 | 18.5 | feeder2_1122 | 0.21482 | 0.3215 | 0.21486 | 0.32184
1110 | 18.5 | feeder2_1258 | 0.21451 | 0.32484 | 0.21455 | 0.3252
1110 | 18.5 | feeder2_1303 | 0.21681 | 0.32362 | 0.21685 | 0.32397
1110 | 18.5 | feeder2_1138 | 0.21308 | 0.31593 | 0.21313 | 0.31628
1110 | 18.5 | feeder2_1304 | 0.21292 | 0.31435 | 0.21296 | 0.31469
1110 | 18.5 | feeder2_1212 | 0.20961 | 0.30629 | 0.20965 | 0.30662
1110 | 18.5 | feeder2_1311 | 0.21417 | 0.31093 | 0.21422 | 0.31126
1110 | 18.5 | feeder2_1290 | 0.20465 | 0.29222 | 0.20469 | 0.29253
1110 | 18.5 | feeder2_1325 | 0.24865 | 0.47644 | 0.2487 | 0.47689
1110 | 18.5 | feeder2_1248 | 0.24546 | 0.45811 | 0.24551 | 0.45853
1110 | 18.5 | feeder2_1249 | 0.29949 | 0.49299 | 0.29954 | 0.49338
1110 | 18.5 | feeder2_1250 | 0.28892 | 0.4817 | 0.28896 | 0.48209
1110 | 18.5 | feeder2_1366 | 0.24053 | 0.45646 | 0.24057 | 0.45689
1110 | 18.5 | feeder2_1266 | 0.21425 | 0.32446 | 0.21429 | 0.32482
1110 | 18.5 | feeder2_1372 | 0.2047 | 0.29228 | 0.20474 | 0.29259
1110 | 18.5 | feeder2_1363 | 0.19935 | 0.27942 | 0.1994 | 0.27971
1110 | 18.5 | feeder2_1446 | 0.26259 | 0.49025 | 0.26264 | 0.49069
1110 | 18.5 | feeder2_1502 | 0.24912 | 0.47855 | 0.24917 | 0.47901
1110 | 18.5 | feeder2_1428 | 0.1922 | 0.27491 | 0.19225 | 0.27519
1110 | 18.5 | feeder2_1380 | 0.19678 | 0.27193 | 0.19683 | 0.2722
1110 | 18.5 | feeder2_1550 | 0.19874 | 0.27399 | 0.19878 | 0.27426
1110 | 18.5 | feeder2_1386 | 0.19533 | 0.26754 | 0.19537 | 0.26781
1110 | 18.5 | feeder2_1551 | 0.19434 | 0.26358 | 0.19438 | 0.26385
1110 | 18.5 | feeder2_1400 | 0.19482 | 0.26636 | 0.19487 | 0.26663
1110 | 18.5 | feeder2_1552 | 0.19265 | 0.26512 | 0.19269 | 0.26538
1110 | 18.5 | feeder2_1408 | 0.19415 | 0.26446 | 0.1942 | 0.26472
1110 | 18.5 | feeder2_1553 | 0.1925 | 0.26384 | 0.19254 | 0.2641
1110 | 18.5 | feeder2_1416 | 0.19392 | 0.26357 | 0.19397 | 0.26383
1110 | 18.5 | feeder2_1530 | 0.19404 | 0.26369 | 0.19408 | 0.26395
1110 | 18.5 | feeder2_1425 | 0.19348 | 0.26184 | 0.19352 | 0.26209
1110 | 18.5 | feeder2_1589 | 0.19253 | 0.25814 | 0.19258 | 0.25839
1110 | 18.5 | feeder2_1435 | 0.19346 | 0.26181 | 0.1935 | 0.26207
1110 | 18.5 | feeder2_1621 | 0.19343 | 0.26171 | 0.19347 | 0.26197
1110 | 18.5 | feeder2_1564 | 0.19325 | 0.26163 | 0.1933 | 0.26188
1110 | 18.5 | feeder2_1704 | 0.24772 | 0.47897 | 0.24777 | 0.47943
1110 | 18.5 | feeder2_1525 | 0.24927 | 0.47902 | 0.24932 | 0.47949
1110 | 18.5 | feeder2_1716 | 0.24727 | 0.48011 | 0.24732 | 0.48057
1110 | 18.5 | feeder2_1537 | 0.24946 | 0.47942 | 0.24951 | 0.47989
1110 | 18.5 | feeder2_1645 | 0.24944 | 0.4794 | 0.24949 | 0.47987
1110 | 18.5 | feeder2_1561 | 0.24969 | 0.47989 | 0.24974 | 0.48036
1110 | 18.5 | feeder2_1657 | 0.25056 | 0.48043 | 0.25061 | 0.4809
1110 | 18.5 | feeder2_1570 | 0.24973 | 0.47994 | 0.24978 | 0.48042
1110 | 18.5 | feeder2_1756 | 0.25842 | 0.48795 | 0.25848 | 0.48842
1110 | 18.5 | feeder2_1588 | 0.24967 | 0.47946 | 0.24972 | 0.47994
1110 | 18.5 | feeder2_1628 | 0.25009 | 0.47991 | 0.25015 | 0.48039
1110 | 18.5 | feeder2_1598 | 0.24958 | 0.47871 | 0.24963 | 0.4792
1110 | 18.5 | feeder2_1816 | 0.24777 | 0.4774 | 0.24782 | 0.47788
1110 | 18.5 | feeder2_1765 | 0.2488 | 0.47801 | 0.24885 | 0.47849
1110 | 18.5 | feeder2_1641 | 0.24893 | 0.47614 | 0.24898 | 0.47663
1110 | 18.5 | feeder2_1689 | 0.24786 | 0.47182 | 0.24792 | 0.47233
1110 | 18.5 | feeder2_1744 | 0.25048 | 0.47739 | 0.25053 | 0.47788
1110 | 18.5 | feeder2_1817 | 0.24747 | 0.46949 | 0.24752 | 0.46999
1110 | 18.5 | feeder2_1779 | 0.24709 | 0.47204 | 0.24714 | 0.47255
1110 | 18.5 | feeder2_1800 | 0.24582 | 0.46967 | 0.24587 | 0.47017
1110 | 18.5 | feeder2_1818 | 0.24344 | 0.46724 | 0.24352 | 0.46777
1110 | 18.5 | feeder2_1753 | 0.25332 | 0.48035 | 0.25337 | 0.48084
1110 | 18.5 | feeder2_1754 | 0.25093 | 0.47761 | 0.25098 | 0.4781
1140 | 19 | secondary | 0.0064352 | 0.022316 | 0.0064282 | 0.022278
1140 | 19 | feeder2_44 | 0.012022 | 0.11684 | 0.012014 | 0.11664
1140 | 19 | feeder2_45 | 0.012278 | 0.12076 | 0.01227 | 0.12056
1140 | 19 | feeder2_46 | 0.011141 | 0.11384 | 0.011119 | 0.11364
1140 | 19 | feeder2_51 | 0.012771 | 0.127 | 0.012761 | 0.12678
1140 | 19 | feeder2_48 | 0.018488 | 0.12985 | 0.018536 | 0.12964
1140 | 19 | feeder2_52 | 0.014119 | 0.12822 | 0.01411 | 0.128
1140 | 19 | feeder2_68 | 0.014189 | 0.1448 | 0.014167 | 0.14456
1140 | 19 | feeder2_69 | 0.013275 | 0.14174 | 0.013243 | 0.14151
1140 | 19 | feeder2_71 | 0.014418 | 0.14737 | 0.014395 | 0.14713
1140 | 19 | feeder2_72 | 0.012329 | 0.14767 | 0.012322 | 0.14743
1140 | 19 | feeder2_73 | 0.015161 | 0.15553 | 0.015135 | 0.15529
1140 | 19 | feeder2_74 | 0.018303 | 0.15753 | 0.018283 | 0.15729
1140 | 19 | feeder2_77 | 0.01568 | 0.16225 | 0.015651 | 0.162
1140 | 19 | feeder2_79 | 0.016847 | 0.159 | 0.016813 | 0.15873
1140 | 19 | feeder2_81 | 0.016588 | 0.17423 | 0.016557 | 0.17396
1140 | 19 | feeder2_82 | 0.013541 | 0.17459 | 0.013522 | 0.17431
1140 | 19 | feeder2_116 | 0.021289 | 0.22999 | 0.021239 | 0.22966
1140 | 19 | feeder2_119 | 0.037832 | 0.24713 | 0.037797 | 0.24681
1140 | 19 | feeder2_120 | 0.020922 | 0.24124 | 0.020866 | 0.24088
1140 | 19 | feeder2_248 | 0.022641 | 0.24309 | 0.022588 | 0.24273
1140 | 19 | feeder2_124 | 0.020547 | 0.24741 | 0.020488 | 0.24704
1140 | 19 | feeder2_282 | 0.02042 | 0.24739 | 0.020363 | 0.24701
1140 | 19 | feeder2_275 | 0.035469 | 0.26281 | 0.035428 | 0.26245
1140 | 19 | feeder2_151 | 0.017594 | 0.24777 | 0.017528 | 0.24736
1140 | 19 | feeder2_295 | 0.017597 | 0.24768 | 0.017533 | 0.24728
1140 | 19 | feeder2_311 | 0.017657 | 0.24725 | 0.01759 | 0.24684
1140 | 19 | feeder2_201 | 0.013008 | 0.24911 | 0.012929 | 0.24866
1140 | 19 | feeder2_314 | 0.01232 | 0.24975 | 0.012238 | 0.2493
1140 | 19 | feeder2_342 | 0.008256 | 0.24989 | 0.0081564 | 0.24937
1140 | 19 | feeder2_368 | 0.0060901 | 0.25103 | 0.0059878 | 0.25049
1140 | 19 | feeder2_347 | 0.010421 | 0.24864 | 0.010324 | 0.24809
1140 | 19 | feeder2_353 | 0.012148 | 0.248 | 0.012051 | 0.24744
1140 | 19 | feeder2_518 | 0.008795 | 0.2494 | 0.0087132 | 0.24885
1140 | 19 | feeder2_365 | 0.014173 | 0.24747 | 0.01408 | 0.24691
1140 | 19 | feeder2_653 | 0.012134 | 0.2481 | 0.012036 | 0.24754
1140 | 19 | feeder2_377 | 0.014722 | 0.25014 | 0.014624 | 0.24957
1140 | 19 | feeder2_622 | 0.0288 | 0.23555 | 0.028721 | 0.235
1140 | 19 | feeder2_451 | 0.0099751 | 0.25268 | 0.010064 | 0.25214
1140 | 19 | feeder2_383 | 0.0061679 | 0.25324 | 0.006069 | 0.25271
1140 | 19 | feeder2_385 | 0.015349 | 0.25326 | 0.015254 | 0.25268
1140 | 19 | feeder2_621 | 0.014825 | 0.25006 | 0.01473 | 0.24948
1140 | 19 | feeder2_611 | 0.0065711 | 0.25438 | 0.0064718 | 0.25385
1140 | 19 | feeder2_405 | 0.0061633 | 0.25332 | 0.0060639 | 0.25279
1140 | 19 | feeder2_461 | 0.017745 | 0.26377 | 0.017646 | 0.26315
1140 | 19 | feeder2_594 | 0.01514 | 0.25451 | 0.015042 | 0.25393
1140 | 19 | feeder2_732 | 0.0079386 | 0.25731 | 0.0078518 | 0.25678
1140 | 19 | feeder2_417 | 0.0060475 | 0.25298 | 0.0059466 | 0.25245
1140 | 19 | feeder2_663 | 0.0090988 | 0.24988 | 0.0090034 | 0.24935
1140 | 19 | feeder2_444 | 0.0058106 | 0.25362 | 0.0057104 | 0.25308
1140 | 19 | feeder2_759 | 0.0048167 | 0.2534 | 0.00472 | 0.25286
1140 | 19 | feeder2_842 | 0.008168 | 0.25121 | 0.0080722 | 0.25068
1140 | 19 | feeder2_459 | 0.0057207 | 0.254 | 0.0056238 | 0.25347
1140 | 19 | feeder2_702 | 0.0051819 | 0.25649 | 0.0051288 | 0.25596
1140 | 19 | feeder2_493 | 0.0057325 | 0.25458 | 0.0056364 | 0.25405
1140 | 19 | feeder2_651 | 0.028964 | 0.25476 | 0.028873 | 0.25415
1140 | 19 | feeder2_684 | 0.017814 | 0.28194 | 0.017703 | 0.28128
1140 | 19 | feeder2_674 | 0.0055897 | 0.25495 | 0.0054881 | 0.25442
1140 | 19 | feeder2_696 | 0.0057552 | 0.25445 | 0.0056543 | 0.25392
1140 | 19 | feeder2_681 | 0.0056112 | 0.25502 | 0.0055103 | 0.25449
1140 | 19 | feeder2_682 | 0.0055784 | 0.25641 | 0.0054812 | 0.25589
1140 | 19 | feeder2_728 | 0.017484 | 0.28005 | 0.017373 | 0.27938
1140 | 19 | feeder2_724 | 0.018995 | 0.30504 | 0.018872 | 0.30435
1140 | 19 | feeder2_703 | 0.005888 | 0.2543 | 0.0057923 | 0.25378
1140 | 19 | feeder2_704 | 0.0057649 | 0.25444 | 0.0056661 | 0.25391
1140 | 19 | feeder2_754 | 0.011344 | 0.30346 | 0.011264 | 0.30276
1140 | 19 | feeder2_747 | 0.020806 | 0.31603 | 0.020678 | 0.31533
1140 | 19 | feeder2_828 | 0.017478 | 0.2801 | 0.017363 | 0.27944
1140 | 19 | feeder2_763 | 0.017034 | 0.27722 | 0.01693 | 0.27655
1140 | 19 | feeder2_836 | 0.024681 | 0.31253 | 0.024558 | 0.31184
1140 | 19 | feeder2_758 | 0.022228 | 0.327 | 0.022096 | 0.3263
1140 | 19 | feeder2_788 | 0.020106 | 0.32651 | 0.019977 | 0.32581
1140 | 19 | feeder2_812 | 0.027579 | 0.362 | 0.027436 | 0.36128
1140 | 19 | feeder2_947 | 0.015024 | 0.27857 | 0.014956 | 0.27788
1140 | 19 | feeder2_868 | 0.016977 | 0.2772 | 0.016875 | 0.27654
1140 | 19 | feeder2_785 | 0.017112 | 0.27542 | 0.017011 | 0.27476
1140 | 19 | feeder2_1176 | 0.024862 | 0.26779 | 0.024758 | 0.26712
1140 | 19 | feeder2_846 | 0.017095 | 0.27552 | 0.016993 | 0.27485
1140 | 19 | feeder2_911 | 0.016318 | 0.27471 | 0.016219 | 0.27404
1140 | 19 | feeder2_1107 | 0.033277 | 0.40104 | 0.033132 | 0.40032
1140 | 19 | feeder2_920 | 0.027685 | 0.36111 | 0.027543 | 0.36038
1140 | 19 | feeder2_926 | 0.027844 | 0.35963 | 0.027701 | 0.35889
1140 | 19 | feeder2_1239 | 0.02772 | 0.36135 | 0.027576 | 0.36062
1140 | 19 | feeder2_933 | 0.027994 | 0.35887 | 0.027848 | 0.35813
1140 | 19 | feeder2_1146 | 0.027527 | 0.36013 | 0.027383 | 0.35939
1140 | 19 | feeder2_1124 | 0.036048 | 0.35152 | 0.035905 | 0.35078
1140 | 19 | feeder2_942 | 0.027577 | 0.36333 | 0.027432 | 0.36257
1140 | 19 | feeder2_952 | 0.027682 | 0.36906 | 0.027528 | 0.36827
1140 | 19 | feeder2_965 | 0.027487 | 0.36344 | 0.027338 | 0.36267
1140 | 19 | feeder2_961 | 0.027724 | 0.36964 | 0.02757 | 0.36885
1140 | 19 | feeder2_963 | 0.027675 | 0.36907 | 0.027519 | 0.36828
1140 | 19 | feeder2_973 | 0.027883 | 0.37183 | 0.027725 | 0.37103
1140 | 19 | feeder2_1128 | 0.027842 | 0.37119 | 0.027682 | 0.3704
1140 | 19 | feeder2_1113 | 0.027282 | 0.36935 | 0.027125 | 0.36856
1140 | 19 | feeder2_1143 | 0.027648 | 0.36901 | 0.027492 | 0.36822
1140 | 19 | feeder2_1238 | 0.02272 | 0.36423 | 0.02258 | 0.36346
1140 | 19 | feeder2_979 | 0.027488 | 0.36357 | 0.02734 | 0.36281
1140 | 19 | feeder2_1236 | 0.027974 | 0.37682 | 0.027809 | 0.37598
1140 | 19 | feeder2_989 | 0.027885 | 0.37182 | 0.027725 | 0.37101
1140 | 19 | feeder2_1196 | 0.027092 | 0.36409 | 0.026941 | 0.36333
1140 | 19 | feeder2_1158 | 0.030009 | 0.36973 | 0.029851 | 0.36894
1140 | 19 | feeder2_1122 | 0.035354 | 0.41929 | 0.035209 | 0.41857
1140 | 19 | feeder2_1258 | 0.036788 | 0.39718 | 0.036641 | 0.39646
1140 | 19 | feeder2_1303 | 0.032804 | 0.41985 | 0.032659 | 0.41912
1140 | 19 | feeder2_1138 | 0.037315 | 0.43358 | 0.037171 | 0.43287
1140 | 19 | feeder2_1304 | 0.044874 | 0.44663 | 0.044737 | 0.44592
1140 | 19 | feeder2_1212 | 0.039649 | 0.45299 | 0.039504 | 0.45228
1140 | 19 | feeder2_1311 | 0.036434 | 0.45339 | 0.036288 | 0.45267
1140 | 19 | feeder2_1290 | 0.043278 | 0.47695 | 0.043135 | 0.47623
1140 | 19 | feeder2_1325 | 0.028109 | 0.38442 | 0.02794 | 0.38356
1140 | 19 | feeder2_1248 | 0.027977 | 0.37681 | 0.027812 | 0.37598
1140 | 19 | feeder2_1249 | 0.022014 | 0.36462 | 0.021875 | 0.36384
1140 | 19 | feeder2_1250 | 0.021529 | 0.3639 | 0.021391 | 0.36312
1140 | 19 | feeder2_1366 | 0.028884 | 0.37588 | 0.028721 | 0.37505
1140 | 19 | feeder2_1266 | 0.038241 | 0.39562 | 0.038098 | 0.39491
1140 | 19 | feeder2_1372 | 0.042095 | 0.47758 | 0.041949 | 0.47686
1140 | 19 | feeder2_1363 | 0.047752 | 0.50197 | 0.047611 | 0.50126
1140 | 19 | feeder2_1446 | 0.025996 | 0.38428 | 0.025829 | 0.38341
1140 | 19 | feeder2_1502 | 0.029002 | 0.39348 | 0.028827 | 0.39258
1140 | 19 | feeder2_1428 | 0.049052 | 0.504 | 0.04891 | 0.50328
1140 | 19 | feeder2_1380 | 0.052664 | 0.52912 | 0.052524 | 0.52842
1140 | 19 | feeder2_1550 | 0.051841 | 0.52979 | 0.051701 | 0.52908
1140 | 19 | feeder2_1386 | 0.055217 | 0.54211 | 0.055078 | 0.54141
1140 | 19 | feeder2_1551 | 0.055088 | 0.54267 | 0.054952 | 0.54198
1140 | 19 | feeder2_1400 | 0.056414 | 0.54814 | 0.056274 | 0.54744
1140 | 19 | feeder2_1552 | 0.059185 | 0.55228 | 0.059051 | 0.55159
1140 | 19 | feeder2_1408 | 0.058466 | 0.55846 | 0.058331 | 0.55776
1140 | 19 | feeder2_1553 | 0.059944 | 0.56055 | 0.059807 | 0.55986
1140 | 19 | feeder2_1416 | 0.059443 | 0.56336 | 0.059308 | 0.56266
1140 | 19 | feeder2_1530 | 0.059325 | 0.56331 | 0.059188 | 0.56262
1140 | 19 | feeder2_1425 | 0.061319 | 0.57273 | 0.061183 | 0.57204
1140 | 19 | feeder2_1589 | 0.061373 | 0.57281 | 0.061237 | 0.57212
1140 | 19 | feeder2_1435 | 0.061696 | 0.57462 | 0.061561 | 0.57393
1140 | 19 | feeder2_1621 | 0.061719 | 0.57453 | 0.061582 | 0.57384
1140 | 19 | feeder2_1564 | 0.066183 | 0.59695 | 0.066048 | 0.59626
1140 | 19 | feeder2_1704 | 0.03025 | 0.39204 | 0.030074 | 0.39114
1140 | 19 | feeder2_1525 | 0.029225 | 0.39631 | 0.029047 | 0.3954
1140 | 19 | feeder2_1716 | 0.03231 | 0.39292 | 0.032134 | 0.39202
1140 | 19 | feeder2_1537 | 0.029428 | 0.39997 | 0.029249 | 0.39905
1140 | 19 | feeder2_1645 | 0.028945 | 0.40034 | 0.028764 | 0.39942
1140 | 19 | feeder2_1561 | 0.029673 | 0.40387 | 0.029493 | 0.40294
1140 | 19 | feeder2_1657 | 0.028888 | 0.40365 | 0.028705 | 0.40272
1140 | 19 | feeder2_1570 | 0.029821 | 0.40563 | 0.029636 | 0.40469
1140 | 19 | feeder2_1756 | 0.024083 | 0.40659 | 0.023904 | 0.40564
1140 | 19 | feeder2_1588 | 0.030051 | 0.40726 | 0.029866 | 0.40631
1140 | 19 | feeder2_1628 | 0.029814 | 0.40718 | 0.029629 | 0.40623
1140 | 19 | feeder2_1598 | 0.030357 | 0.40934 | 0.030173 | 0.40839
1140 | 19 | feeder2_1816 | 0.030501 | 0.40913 | 0.030314 | 0.40818
1140 | 19 | feeder2_1765 | 0.030955 | 0.40853 | 0.03077 | 0.40758
1140 | 19 | feeder2_1641 | 0.031903 | 0.41995 | 0.031713 | 0.41897
1140 | 19 | feeder2_1689 | 0.034198 | 0.42959 | 0.034003 | 0.4286
1140 | 19 | feeder2_1744 | 0.029135 | 0.41987 | 0.028946 | 0.41889
1140 | 19 | feeder2_1817 | 0.034635 | 0.43191 | 0.034442 | 0.43091
1140 | 19 | feeder2_1779 | 0.034878 | 0.42888 | 0.034683 | 0.42789
1140 | 19 | feeder2_1800 | 0.043676 | 0.44523 | 0.043495 | 0.44424
1140 | 19 | feeder2_1818 | 0.035713 | 0.42377 | 0.035488 | 0.42273
1140 | 19 | feeder2_1753 | 0.025419 | 0.42081 | 0.025229 | 0.41982
1140 | 19 | feeder2_1754 | 0.02805 | 0.41962 | 0.027861 | 0.41863
1170 | 19.5 | secondary | 0.034112 | 0.042174 | 0.034108 | 0.042158
1170 | 19.5 | feeder2_44 | 0.063783 | 0.221 | 0.063784 | 0.22094
1170 | 19.5 | feeder2_45 | 0.064578 | 0.22689 | 0.064577 | 0.22682
1170 | 19.5 | feeder2_46 | 0.089648 | 0.23235 | 0.089645 | 0.23229
1170 | 19.5 | feeder2_51 | 0.066051 | 0.23745 | 0.066049 | 0.23737
1170 | 19.5 | feeder2_48 | 0.062797 | 0.22475 | 0.062793 | 0.22468
1170 | 19.5 | feeder2_52 | 0.066484 | 0.23881 | 0.066484 | 0.23873
1170 | 19.5 | feeder2_68 | 0.070166 | 0.26685 | 0.070162 | 0.26676
1170 | 19.5 | feeder2_69 | 0.072232 | 0.26864 | 0.072231 | 0.26855
1170 | 19.5 | feeder2_71 | 0.070715 | 0.27064 | 0.070717 | 0.27055
1170 | 19.5 | feeder2_72 | 0.067302 | 0.26678 | 0.067301 | 0.26669
1170 | 19.5 | feeder2_73 | 0.072548 | 0.28298 | 0.072548 | 0.28288
1170 | 19.5 | feeder2_74 | 0.071004 | 0.28561 | 0.071002 | 0.28552
1170 | 19.5 | feeder2_77 | 0.074151 | 0.29317 | 0.074153 | 0.29307
1170 | 19.5 | feeder2_79 | 0.076852 | 0.29354 | 0.076856 | 0.29344
1170 | 19.5 | feeder2_81 | 0.076558 | 0.30906 | 0.076562 | 0.30895
1170 | 19.5 | feeder2_82 | 0.073378 | 0.30535 | 0.073378 | 0.30524
1170 | 19.5 | feeder2_116 | 0.088659 | 0.38464 | 0.088659 | 0.38449
1170 | 19.5 | feeder2_119 | 0.092854 | 0.39414 | 0.092866 | 0.39399
1170 | 19.5 | feeder2_120 | 0.092009 | 0.40854 | 0.092014 | 0.40839
1170 | 19.5 | feeder2_248 | 0.091611 | 0.41211 | 0.091616 | 0.41195
1170 | 19.5 | feeder2_124 | 0.093929 | 0.42195 | 0.093933 | 0.42179
1170 | 19.5 | feeder2_282 | 0.091948 | 0.4198 | 0.091953 | 0.41963
1170 | 19.5 | feeder2_275 | 0.093122 | 0.42374 | 0.093126 | 0.42358
1170 | 19.5 | feeder2_151 | 0.097533 | 0.44558 | 0.097536 | 0.4454
1170 | 19.5 | feeder2_295 | 0.098554 | 0.44626 | 0.098558 | 0.44608
1170 | 19.5 | feeder2_311 | 0.098325 | 0.44614 | 0.098329 | 0.44597
1170 | 19.5 | feeder2_201 | 0.10335 | 0.4831 | 0.10336 | 0.4829
1170 | 19.5 | feeder2_314 | 0.10327 | 0.48301 | 0.10327 | 0.48281
1170 | 19.5 | feeder2_342 | 0.1117 | 0.53682 | 0.11171 | 0.53659
1170 | 19.5 | feeder2_368 | 0.11226 | 0.53896 | 0.11226 | 0.53874
1170 | 19.5 | feeder2_347 | 0.11518 | 0.55926 | 0.11518 | 0.55902
1170 | 19.5 | feeder2_353 | 0.11713 | 0.57151 | 0.11714 | 0.57127
1170 | 19.5 | feeder2_518 | 0.11328 | 0.55722 | 0.11328 | 0.55699
1170 | 19.5 | feeder2_365 | 0.11927 | 0.58506 | 0.11928 | 0.58481
1170 | 19.5 | feeder2_653 | 0.11726 | 0.57164 | 0.11726 | 0.57139
1170 | 19.5 | feeder2_377 | 0.12028 | 0.59027 | 0.12028 | 0.59001
1170 | 19.5 | feeder2_622 | 0.12917 | 0.59256 | 0.12916 | 0.59231
1170 | 19.5 | feeder2_451 | 0.11049 | 0.53712 | 0.11049 | 0.5369
1170 | 19.5 | feeder2_383 | 0.11355 | 0.54393 | 0.11356 | 0.54371
1170 | 19.5 | feeder2_385 | 0.12144 | 0.596 | 0.12144 | 0.59573
1170 | 19.5 | feeder2_621 | 0.1213 | 0.59103 | 0.1213 | 0.59076
1170 | 19.5 | feeder2_611 | 0.11397 | 0.54455 | 0.11397 | 0.54433
1170 | 19.5 | feeder2_405 | 0.11362 | 0.54422 | 0.11363 | 0.54399
1170 | 19.5 | feeder2_461 | 0.12575 | 0.61585 | 0.12576 | 0.61555
1170 | 19.5 | feeder2_594 | 0.1214 | 0.59826 | 0.1214 | 0.598
1170 | 19.5 | feeder2_732 | 0.11469 | 0.54638 | 0.11469 | 0.54616
1170 | 19.5 | feeder2_417 | 0.11401 | 0.54597 | 0.11402 | 0.54575
1170 | 19.5 | feeder2_663 | 0.11696 | 0.54689 | 0.11696 | 0.54668
1170 | 19.5 | feeder2_444 | 0.11411 | 0.54696 | 0.11411 | 0.54674
1170 | 19.5 | feeder2_759 | 0.11183 | 0.54458 | 0.11184 | 0.54436
1170 | 19.5 | feeder2_842 | 0.12352 | 0.55363 | 0.12352 | 0.55342
1170 | 19.5 | feeder2_459 | 0.11409 | 0.54701 | 0.11409 | 0.5468
1170 | 19.5 | feeder2_702 | 0.11273 | 0.54554 | 0.11273 | 0.54532
1170 | 19.5 | feeder2_493 | 0.11417 | 0.54781 | 0.11417 | 0.5476
1170 | 19.5 | feeder2_651 | 0.12756 | 0.61663 | 0.12757 | 0.61634
1170 | 19.5 | feeder2_684 | 0.12924 | 0.63119 | 0.12925 | 0.63088
1170 | 19.5 | feeder2_674 | 0.11412 | 0.54836 | 0.11412 | 0.54814
1170 | 19.5 | feeder2_696 | 0.11419 | 0.54792 | 0.11419 | 0.5477
1170 | 19.5 | feeder2_681 | 0.11444 | 0.54888 | 0.11444 | 0.54866
1170 | 19.5 | feeder2_682 | 0.11346 | 0.54985 | 0.11346 | 0.54963
1170 | 19.5 | feeder2_728 | 0.12904 | 0.63134 | 0.12905 | 0.63102
1170 | 19.5 | feeder2_724 | 0.13332 | 0.6469 | 0.13334 | 0.64656
1170 | 19.5 | feeder2_703 | 0.11431 | 0.54802 | 0.11431 | 0.5478
1170 | 19.5 | feeder2_704 | 0.1142 | 0.54793 | 0.1142 | 0.54771
1170 | 19.5 | feeder2_754 | 0.13239 | 0.64593 | 0.1324 | 0.64558
1170 | 19.5 | feeder2_747 | 0.13513 | 0.65392 | 0.13514 | 0.65357
1170 | 19.5 | feeder2_828 | 0.12933 | 0.63177 | 0.12934 | 0.63146
1170 | 19.5 | feeder2_763 | 0.12853 | 0.63098 | 0.12855 | 0.63067
1170 | 19.5 | feeder2_836 | 0.14082 | 0.65462 | 0.14084 | 0.65428
1170 | 19.5 | feeder2_758 | 0.13643 | 0.65946 | 0.13645 | 0.6591
1170 | 19.5 | feeder2_788 | 0.13362 | 0.65653 | 0.13363 | 0.65617
1170 | 19.5 | feeder2_812 | 0.14132 | 0.68088 | 0.14134 | 0.68049
1170 | 19.5 | feeder2_947 | 0.12419 | 0.62643 | 0.1242 | 0.62612
1170 | 19.5 | feeder2_868 | 0.12819 | 0.63059 | 0.1282 | 0.63028
1170 | 19.5 | feeder2_785 | 0.12859 | 0.63205 | 0.1286 | 0.63173
1170 | 19.5 | feeder2_1176 | 0.13169 | 0.63499 | 0.13169 | 0.63467
1170 | 19.5 | feeder2_846 | 0.12828 | 0.63284 | 0.12829 | 0.63252
1170 | 19.5 | feeder2_911 | 0.12856 | 0.63194 | 0.12857 | 0.63163
1170 | 19.5 | feeder2_1107 | 0.14661 | 0.70096 | 0.14663 | 0.70056
1170 | 19.5 | feeder2_920 | 0.14129 | 0.68166 | 0.14131 | 0.68126
1170 | 19.5 | feeder2_926 | 0.14116 | 0.68259 | 0.14118 | 0.68219
1170 | 19.5 | feeder2_1239 | 0.1414 | 0.68195 | 0.14142 | 0.68156
1170 | 19.5 | feeder2_933 | 0.1412 | 0.68353 | 0.14122 | 0.68313
1170 | 19.5 | feeder2_1146 | 0.14073 | 0.68012 | 0.14075 | 0.67972
1170 | 19.5 | feeder2_1124 | 0.14163 | 0.68409 | 0.14164 | 0.68369
1170 | 19.5 | feeder2_942 | 0.14131 | 0.68534 | 0.14134 | 0.68493
1170 | 19.5 | feeder2_952 | 0.14073 | 0.68198 | 0.14075 | 0.68157
1170 | 19.5 | feeder2_965 | 0.14141 | 0.68614 | 0.14143 | 0.68572
1170 | 19.5 | feeder2_961 | 0.14071 | 0.68185 | 0.14073 | 0.68143
1170 | 19.5 | feeder2_963 | 0.14072 | 0.68194 | 0.14074 | 0.68151
1170 | 19.5 | feeder2_973 | 0.14054 | 0.68054 | 0.14056 | 0.68012
1170 | 19.5 | feeder2_1128 | 0.14078 | 0.68302 | 0.1408 | 0.6826
1170 | 19.5 | feeder2_1113 | 0.13971 | 0.68089 | 0.13973 | 0.68047
1170 | 19.5 | feeder2_1143 | 0.1407 | 0.6818 | 0.14072 | 0.68137
1170 | 19.5 | feeder2_1238 | 0.13612 | 0.68091 | 0.13614 | 0.6805
1170 | 19.5 | feeder2_979 | 0.14164 | 0.68764 | 0.14166 | 0.68722
1170 | 19.5 | feeder2_1236 | 0.1401 | 0.67799 | 0.14011 | 0.67755
1170 | 19.5 | feeder2_989 | 0.14055 | 0.68055 | 0.14057 | 0.68012
1170 | 19.5 | feeder2_1196 | 0.1427 | 0.69428 | 0.14273 | 0.69387
1170 | 19.5 | feeder2_1158 | 0.1432 | 0.68104 | 0.14321 | 0.68061
1170 | 19.5 | feeder2_1122 | 0.14866 | 0.70841 | 0.14869 | 0.70801
1170 | 19.5 | feeder2_1258 | 0.14842 | 0.70166 | 0.14844 | 0.70127
1170 | 19.5 | feeder2_1303 | 0.14686 | 0.70656 | 0.14688 | 0.70616
1170 | 19.5 | feeder2_1138 | 0.15042 | 0.71516 | 0.15045 | 0.71475
1170 | 19.5 | feeder2_1304 | 0.15653 | 0.72283 | 0.15655 | 0.72242
1170 | 19.5 | feeder2_1212 | 0.1525 | 0.72426 | 0.15253 | 0.72385
1170 | 19.5 | feeder2_1311 | 0.14811 | 0.72023 | 0.14813 | 0.71982
1170 | 19.5 | feeder2_1290 | 0.15591 | 0.73949 | 0.15594 | 0.73907
1170 | 19.5 | feeder2_1325 | 0.13919 | 0.67454 | 0.13921 | 0.67409
1170 | 19.5 | feeder2_1248 | 0.14011 | 0.67799 | 0.14012 | 0.67755
1170 | 19.5 | feeder2_1249 | 0.13549 | 0.68026 | 0.13551 | 0.67985
1170 | 19.5 | feeder2_1250 | 0.13394 | 0.67882 | 0.13395 | 0.6784
1170 | 19.5 | feeder2_1366 | 0.14287 | 0.6777 | 0.14288 | 0.67727
1170 | 19.5 | feeder2_1266 | 0.1489 | 0.70203 | 0.14891 | 0.70164
1170 | 19.5 | feeder2_1372 | 0.15532 | 0.73883 | 0.15535 | 0.73841
1170 | 19.5 | feeder2_1363 | 0.15978 | 0.75723 | 0.15981 | 0.75681
1170 | 19.5 | feeder2_1446 | 0.1373 | 0.67257 | 0.13732 | 0.67212
1170 | 19.5 | feeder2_1502 | 0.13866 | 0.67336 | 0.13868 | 0.6729
1170 | 19.5 | feeder2_1428 | 0.16043 | 0.75968 | 0.16046 | 0.75926
1170 | 19.5 | feeder2_1380 | 0.16392 | 0.77559 | 0.16395 | 0.77516
1170 | 19.5 | feeder2_1550 | 0.16116 | 0.77279 | 0.16119 | 0.77236
1170 | 19.5 | feeder2_1386 | 0.1662 | 0.78619 | 0.16623 | 0.78576
1170 | 19.5 | feeder2_1551 | 0.16628 | 0.78628 | 0.16631 | 0.78585
1170 | 19.5 | feeder2_1400 | 0.16728 | 0.79125 | 0.16731 | 0.79082
1170 | 19.5 | feeder2_1552 | 0.16921 | 0.79622 | 0.16924 | 0.79579
1170 | 19.5 | feeder2_1408 | 0.16907 | 0.79936 | 0.1691 | 0.79893
1170 | 19.5 | feeder2_1553 | 0.18147 | 0.81695 | 0.18151 | 0.81651
1170 | 19.5 | feeder2_1416 | 0.1691 | 0.79997 | 0.16913 | 0.79954
1170 | 19.5 | feeder2_1530 | 0.1676 | 0.7993 | 0.16763 | 0.79886
1170 | 19.5 | feeder2_1425 | 0.16938 | 0.80161 | 0.16941 | 0.80117
1170 | 19.5 | feeder2_1589 | 0.16897 | 0.80357 | 0.169 | 0.80314
1170 | 19.5 | feeder2_1435 | 0.16942 | 0.80175 | 0.16946 | 0.80131
1170 | 19.5 | feeder2_1621 | 0.16946 | 0.80178 | 0.16949 | 0.80135
1170 | 19.5 | feeder2_1564 | 0.16996 | 0.80335 | 0.16999 | 0.80292
1170 | 19.5 | feeder2_1704 | 0.13987 | 0.67454 | 0.13989 | 0.67408
1170 | 19.5 | feeder2_1525 | 0.13852 | 0.67258 | 0.13854 | 0.67211
1170 | 19.5 | feeder2_1716 | 0.14489 | 0.67212 | 0.14491 | 0.67166
1170 | 19.5 | feeder2_1537 | 0.13824 | 0.67168 | 0.13825 | 0.67121
1170 | 19.5 | feeder2_1645 | 0.13826 | 0.6717 | 0.13827 | 0.67123
1170 | 19.5 | feeder2_1561 | 0.13791 | 0.67065 | 0.13793 | 0.67018
1170 | 19.5 | feeder2_1657 | 0.13707 | 0.66978 | 0.13709 | 0.6693
1170 | 19.5 | feeder2_1570 | 0.13781 | 0.67043 | 0.13783 | 0.66995
1170 | 19.5 | feeder2_1756 | 0.12966 | 0.66193 | 0.12968 | 0.66144
1170 | 19.5 | feeder2_1588 | 0.13783 | 0.67077 | 0.13785 | 0.67029
1170 | 19.5 | feeder2_1628 | 0.13725 | 0.67017 | 0.13727 | 0.66969
1170 | 19.5 | feeder2_1598 | 0.13789 | 0.67139 | 0.13791 | 0.67091
1170 | 19.5 | feeder2_1816 | 0.13803 | 0.67156 | 0.13805 | 0.67107
1170 | 19.5 | feeder2_1765 | 0.13893 | 0.67237 | 0.13895 | 0.67189
1170 | 19.5 | feeder2_1641 | 0.13819 | 0.67385 | 0.13821 | 0.67335
1170 | 19.5 | feeder2_1689 | 0.13871 | 0.6774 | 0.13872 | 0.67689
1170 | 19.5 | feeder2_1744 | 0.13732 | 0.67294 | 0.13733 | 0.67244
1170 | 19.5 | feeder2_1817 | 0.13916 | 0.6784 | 0.13918 | 0.67788
1170 | 19.5 | feeder2_1779 | 0.13963 | 0.67833 | 0.13964 | 0.67782
1170 | 19.5 | feeder2_1800 | 0.13878 | 0.67831 | 0.13879 | 0.6778
1170 | 19.5 | feeder2_1818 | 0.13902 | 0.6785 | 0.13902 | 0.67797
1170 | 19.5 | feeder2_1753 | 0.13471 | 0.67022 | 0.13472 | 0.66972
1170 | 19.5 | feeder2_1754 | 0.13728 | 0.6729 | 0.1373 | 0.6724
1200 | 20 | secondary | 0.028526 | 0.028802 | 0.028487 | 0.028841
1200 | 20 | feeder2_44 | 0.053413 | 0.15114 | 0.053339 | 0.15136
1200 | 20 | feeder2_45 | 0.05454 | 0.15714 | 0.054462 | 0.15737
1200 | 20 | feeder2_46 | 0.051923 | 0.13633 | 0.051859 | 0.13656
1200 | 20 | feeder2_51 | 0.056584 | 0.16714 | 0.056512 | 0.16738
1200 | 20 | feeder2_48 | 0.05077 | 0.16045 | 0.0507 | 0.16066
1200 | 20 | feeder2_52 | 0.059242 | 0.16935 | 0.059167 | 0.16959
1200 | 20 | feeder2_68 | 0.062209 | 0.19446 | 0.062123 | 0.19473
1200 | 20 | feeder2_69 | 0.061019 | 0.1924 | 0.06094 | 0.19267
1200 | 20 | feeder2_71 | 0.062981 | 0.19818 | 0.0629 | 0.19845
1200 | 20 | feeder2_72 | 0.061933 | 0.19857 | 0.06185 | 0.19883
1200 | 20 | feeder2_73 | 0.065395 | 0.20984 | 0.065311 | 0.21013
1200 | 20 | feeder2_74 | 0.085834 | 0.226 | 0.085751 | 0.2263
1200 | 20 | feeder2_77 | 0.066856 | 0.21716 | 0.06677 | 0.21746
1200 | 20 | feeder2_79 | 0.065621 | 0.21473 | 0.065534 | 0.21502
1200 | 20 | feeder2_81 | 0.069378 | 0.22963 | 0.069288 | 0.22994
1200 | 20 | feeder2_82 | 0.061084 | 0.23849 | 0.060992 | 0.23877
1200 | 20 | feeder2_116 | 0.080563 | 0.28177 | 0.080458 | 0.28218
1200 | 20 | feeder2_119 | 0.091252 | 0.28949 | 0.091142 | 0.28991
1200 | 20 | feeder2_120 | 0.083519 | 0.29668 | 0.083406 | 0.29712
1200 | 20 | feeder2_248 | 0.085385 | 0.2982 | 0.085273 | 0.29865
1200 | 20 | feeder2_124 | 0.085209 | 0.30521 | 0.085092 | 0.30567
1200 | 20 | feeder2_282 | 0.0843 | 0.30554 | 0.084185 | 0.306
1200 | 20 | feeder2_275 | 0.089356 | 0.30601 | 0.089238 | 0.30648
1200 | 20 | feeder2_151 | 0.087387 | 0.3192 | 0.087263 | 0.3197
1200 | 20 | feeder2_295 | 0.086477 | 0.31769 | 0.086356 | 0.31819
1200 | 20 | feeder2_311 | 0.086721 | 0.31805 | 0.086597 | 0.31854
1200 | 20 | feeder2_201 | 0.091789 | 0.34611 | 0.091651 | 0.34665
1200 | 20 | feeder2_314 | 0.090426 | 0.34741 | 0.090293 | 0.34795
1200 | 20 | feeder2_342 | 0.098538 | 0.38191 | 0.098387 | 0.38253
1200 | 20 | feeder2_368 | 0.1021 | 0.39066 | 0.10195 | 0.39129
1200 | 20 | feeder2_347 | 0.097664 | 0.3836 | 0.097505 | 0.38423
1200 | 20 | feeder2_353 | 0.097264 | 0.38447 | 0.097105 | 0.3851
1200 | 20 | feeder2_518 | 0.096847 | 0.38417 | 0.096687 | 0.38479
1200 | 20 | feeder2_365 | 0.096707 | 0.38471 | 0.096537 | 0.38535
1200 | 20 | feeder2_653 | 0.099213 | 0.38599 | 0.099054 | 0.38662
1200 | 20 | feeder2_377 | 0.097194 | 0.38874 | 0.097029 | 0.38937
1200 | 20 | feeder2_622 | 0.088797 | 0.36963 | 0.088631 | 0.37027
1200 | 20 | feeder2_451 | 0.10184 | 0.39062 | 0.10168 | 0.39125
1200 | 20 | feeder2_383 | 0.10793 | 0.40527 | 0.10778 | 0.40591
1200 | 20 | feeder2_385 | 0.097911 | 0.39403 | 0.097738 | 0.39467
1200 | 20 | feeder2_621 | 0.096035 | 0.38707 | 0.095865 | 0.38771
1200 | 20 | feeder2_611 | 0.11045 | 0.40664 | 0.1103 | 0.40729
1200 | 20 | feeder2_405 | 0.10825 | 0.40611 | 0.10811 | 0.40675
1200 | 20 | feeder2_461 | 0.10091 | 0.41482 | 0.10073 | 0.41545
1200 | 20 | feeder2_594 | 0.099099 | 0.39492 | 0.098925 | 0.39556
1200 | 20 | feeder2_732 | 0.13501 | 0.4289 | 0.13486 | 0.42957
1200 | 20 | feeder2_417 | 0.10919 | 0.40731 | 0.10905 | 0.40796
1200 | 20 | feeder2_663 | 0.10851 | 0.40408 | 0.10836 | 0.40472
1200 | 20 | feeder2_444 | 0.11005 | 0.40922 | 0.10991 | 0.40987
1200 | 20 | feeder2_759 | 0.10933 | 0.40925 | 0.10918 | 0.4099
1200 | 20 | feeder2_842 | 0.10792 | 0.40462 | 0.10777 | 0.40527
1200 | 20 | feeder2_459 | 0.11041 | 0.41016 | 0.11026 | 0.41081
1200 | 20 | feeder2_702 | 0.10945 | 0.41044 | 0.1093 | 0.41108
1200 | 20 | feeder2_493 | 0.11182 | 0.4137 | 0.11168 | 0.41435
1200 | 20 | feeder2_651 | 0.098642 | 0.4092 | 0.098453 | 0.40983
1200 | 20 | feeder2_684 | 0.10501 | 0.43934 | 0.10482 | 0.43997
1200 | 20 | feeder2_674 | 0.11527 | 0.4166 | 0.11512 | 0.41725
1200 | 20 | feeder2_696 | 0.11186 | 0.41056 | 0.11171 | 0.41121
1200 | 20 | feeder2_681 | 0.11669 | 0.4178 | 0.11654 | 0.41845
1200 | 20 | feeder2_682 | 0.12734 | 0.42684 | 0.1272 | 0.42749
1200 | 20 | feeder2_728 | 0.10487 | 0.44056 | 0.10468 | 0.44118
1200 | 20 | feeder2_724 | 0.10974 | 0.46243 | 0.10954 | 0.46305
1200 | 20 | feeder2_703 | 0.11283 | 0.40808 | 0.11269 | 0.40872
1200 | 20 | feeder2_704 | 0.11206 | 0.4101 | 0.11191 | 0.41075
1200 | 20 | feeder2_754 | 0.10871 | 0.4641 | 0.10851 | 0.46473
1200 | 20 | feeder2_747 | 0.11177 | 0.47121 | 0.11156 | 0.47184
1200 | 20 | feeder2_828 | 0.10562 | 0.44111 | 0.10542 | 0.44174
1200 | 20 | feeder2_763 | 0.10442 | 0.44147 | 0.10423 | 0.4421
1200 | 20 | feeder2_836 | 0.10685 | 0.46491 | 0.10664 | 0.46554
1200 | 20 | feeder2_758 | 0.11414 | 0.48164 | 0.11393 | 0.48226
1200 | 20 | feeder2_788 | 0.11417 | 0.48303 | 0.11396 | 0.48365
1200 | 20 | feeder2_812 | 0.12117 | 0.51266 | 0.12095 | 0.51328
1200 | 20 | feeder2_947 | 0.10393 | 0.44367 | 0.10374 | 0.44429
1200 | 20 | feeder2_868 | 0.10393 | 0.44208 | 0.10374 | 0.4427
1200 | 20 | feeder2_785 | 0.10416 | 0.44125 | 0.10396 | 0.44188
1200 | 20 | feeder2_1176 | 0.1005 | 0.4367 | 0.10031 | 0.43732
1200 | 20 | feeder2_846 | 0.10485 | 0.4411 | 0.10466 | 0.44173
1200 | 20 | feeder2_911 | 0.10386 | 0.44289 | 0.10367 | 0.44352
1200 | 20 | feeder2_1107 | 0.12336 | 0.52406 | 0.12315 | 0.5247
1200 | 20 | feeder2_920 | 0.12257 | 0.5183 | 0.12235 | 0.51892
1200 | 20 | feeder2_926 | 0.12453 | 0.52672 | 0.12431 | 0.52732
1200 | 20 | feeder2_1239 | 0.12279 | 0.51846 | 0.12258 | 0.51908
1200 | 20 | feeder2_933 | 0.12536 | 0.53006 | 0.12514 | 0.53067
1200 | 20 | feeder2_1146 | 0.12474 | 0.52873 | 0.12452 | 0.52933
1200 | 20 | feeder2_1124 | 0.1247 | 0.52936 | 0.12448 | 0.52997
1200 | 20 | feeder2_942 | 0.12765 | 0.5393 | 0.12742 | 0.53989
1200 | 20 | feeder2_952 | 0.13016 | 0.5518 | 0.12993 | 0.55238
1200 | 20 | feeder2_965 | 0.12777 | 0.53949 | 0.12754 | 0.54009
1200 | 20 | feeder2_961 | 0.13042 | 0.55299 | 0.13019 | 0.55357
1200 | 20 | feeder2_963 | 0.13017 | 0.55184 | 0.12993 | 0.55242
1200 | 20 | feeder2_973 | 0.13134 | 0.55647 | 0.1311 | 0.55703
1200 | 20 | feeder2_1128 | 0.13127 | 0.55831 | 0.13104 | 0.55891
1200 | 20 | feeder2_1113 | 0.12997 | 0.55285 | 0.12974 | 0.55343
1200 | 20 | feeder2_1143 | 0.13019 | 0.55189 | 0.12995 | 0.55247
1200 | 20 | feeder2_1238 | 0.12799 | 0.541 | 0.12776 | 0.54159
1200 | 20 | feeder2_979 | 0.1279 | 0.53965 | 0.12768 | 0.54024
1200 | 20 | feeder2_1236 | 0.13319 | 0.56397 | 0.13295 | 0.56448
1200 | 20 | feeder2_989 | 0.13133 | 0.55646 | 0.1311 | 0.55701
1200 | 20 | feeder2_1196 | 0.13115 | 0.54 | 0.13092 | 0.54061
1200 | 20 | feeder2_1158 | 0.12967 | 0.55453 | 0.12944 | 0.55508
1200 | 20 | feeder2_1122 | 0.12593 | 0.53668 | 0.12572 | 0.53733
1200 | 20 | feeder2_1258 | 0.11515 | 0.51407 | 0.11493 | 0.51471
1200 | 20 | feeder2_1303 | 0.12675 | 0.54385 | 0.12654 | 0.54447
1200 | 20 | feeder2_1138 | 0.12739 | 0.54466 | 0.12718 | 0.54532
1200 | 20 | feeder2_1304 | 0.13469 | 0.54833 | 0.13447 | 0.549
1200 | 20 | feeder2_1212 | 0.12964 | 0.55824 | 0.12942 | 0.55891
1200 | 20 | feeder2_1311 | 0.1284 | 0.56122 | 0.12819 | 0.56189
1200 | 20 | feeder2_1290 | 0.13229 | 0.57302 | 0.13207 | 0.57372
1200 | 20 | feeder2_1325 | 0.13657 | 0.57777 | 0.13633 | 0.57824
1200 | 20 | feeder2_1248 | 0.13318 | 0.56396 | 0.13294 | 0.56447
1200 | 20 | feeder2_1249 | 0.12802 | 0.54116 | 0.12779 | 0.54175
1200 | 20 | feeder2_1250 | 0.12811 | 0.54167 | 0.12788 | 0.54226
1200 | 20 | feeder2_1366 | 0.13185 | 0.56206 | 0.13161 | 0.56257
1200 | 20 | feeder2_1266 | 0.10846 | 0.50568 | 0.10825 | 0.50633
1200 | 20 | feeder2_1372 | 0.13242 | 0.57321 | 0.1322 | 0.57392
1200 | 20 | feeder2_1363 | 0.13502 | 0.58903 | 0.13481 | 0.58976
1200 | 20 | feeder2_1446 | 0.13987 | 0.58597 | 0.13963 | 0.58642
1200 | 20 | feeder2_1502 | 0.13815 | 0.58472 | 0.1379 | 0.58518
1200 | 20 | feeder2_1428 | 0.13643 | 0.58995 | 0.13621 | 0.59068
1200 | 20 | feeder2_1380 | 0.1381 | 0.60722 | 0.13788 | 0.60798
1200 | 20 | feeder2_1550 | 0.1378 | 0.60837 | 0.13758 | 0.60912
1200 | 20 | feeder2_1386 | 0.13951 | 0.6158 | 0.13929 | 0.61656
1200 | 20 | feeder2_1551 | 0.14123 | 0.61541 | 0.14101 | 0.61618
1200 | 20 | feeder2_1400 | 0.14009 | 0.61996 | 0.13986 | 0.62074
1200 | 20 | feeder2_1552 | 0.14268 | 0.62169 | 0.14246 | 0.62247
1200 | 20 | feeder2_1408 | 0.1411 | 0.62764 | 0.14088 | 0.62843
1200 | 20 | feeder2_1553 | 0.1589 | 0.64124 | 0.15868 | 0.64205
1200 | 20 | feeder2_1416 | 0.14109 | 0.62837 | 0.14087 | 0.62916
1200 | 20 | feeder2_1530 | 0.13972 | 0.63 | 0.1395 | 0.63078
1200 | 20 | feeder2_1425 | 0.14114 | 0.62895 | 0.14092 | 0.62973
1200 | 20 | feeder2_1589 | 0.14121 | 0.629 | 0.141 | 0.62979
1200 | 20 | feeder2_1435 | 0.14115 | 0.62905 | 0.14093 | 0.62984
1200 | 20 | feeder2_1621 | 0.14104 | 0.62892 | 0.14082 | 0.62972
1200 | 20 | feeder2_1564 | 0.1413 | 0.6305 | 0.14108 | 0.63128
1200 | 20 | feeder2_1704 | 0.13569 | 0.58208 | 0.13544 | 0.58254
1200 | 20 | feeder2_1525 | 0.13877 | 0.58754 | 0.13853 | 0.58799
1200 | 20 | feeder2_1716 | 0.13542 | 0.58396 | 0.13517 | 0.58442
1200 | 20 | feeder2_1537 | 0.13959 | 0.59126 | 0.13934 | 0.59171
1200 | 20 | feeder2_1645 | 0.13962 | 0.59128 | 0.13936 | 0.59173
1200 | 20 | feeder2_1561 | 0.14053 | 0.5955 | 0.14028 | 0.59594
1200 | 20 | feeder2_1657 | 0.1403 | 0.59715 | 0.14004 | 0.59759
1200 | 20 | feeder2_1570 | 0.1409 | 0.59695 | 0.14065 | 0.59739
1200 | 20 | feeder2_1756 | 0.14093 | 0.60416 | 0.14068 | 0.60459
1200 | 20 | feeder2_1588 | 0.14119 | 0.59788 | 0.14094 | 0.59832
1200 | 20 | feeder2_1628 | 0.1409 | 0.59913 | 0.14065 | 0.59957
1200 | 20 | feeder2_1598 | 0.14154 | 0.59871 | 0.14129 | 0.59915
1200 | 20 | feeder2_1816 | 0.13993 | 0.59673 | 0.13967 | 0.59716
1200 | 20 | feeder2_1765 | 0.13953 | 0.59658 | 0.13927 | 0.59702
1200 | 20 | feeder2_1641 | 0.14368 | 0.60451 | 0.14342 | 0.60495
1200 | 20 | feeder2_1689 | 0.14384 | 0.60154 | 0.14358 | 0.60201
1200 | 20 | feeder2_1744 | 0.14521 | 0.61004 | 0.14495 | 0.61046
1200 | 20 | feeder2_1817 | 0.14385 | 0.60159 | 0.14358 | 0.60206
1200 | 20 | feeder2_1779 | 0.14218 | 0.59978 | 0.14191 | 0.60025
1200 | 20 | feeder2_1800 | 0.15179 | 0.60099 | 0.15152 | 0.60148
1200 | 20 | feeder2_1818 | 0.13944 | 0.59843 | 0.13912 | 0.59891
1200 | 20 | feeder2_1753 | 0.15335 | 0.62505 | 0.1531 | 0.62544
1200 | 20 | feeder2_1754 | 0.1449 | 0.61065 | 0.14464 | 0.61108
1230 | 20.5 | secondary | 0.028735 | 0.0294 | 0.028719 | 0.029412
1230 | 20.5 | feeder2_44 | 0.053788 | 0.15424 | 0.053763 | 0.15431
1230 | 20.5 | feeder2_45 | 0.05489 | 0.15951 | 0.054866 | 0.15959
1230 | 20.5 | feeder2_46 | 0.047104 | 0.15053 | 0.047077 | 0.1506
1230 | 20.5 | feeder2_51 | 0.056746 | 0.1684 | 0.056714 | 0.16848
1230 | 20.5 | feeder2_48 | 0.055859 | 0.1616 | 0.055838 | 0.16167
1230 | 20.5 | feeder2_52 | 0.079101 | 0.16436 | 0.079077 | 0.16445
1230 | 20.5 | feeder2_68 | 0.061661 | 0.19481 | 0.061628 | 0.19489
1230 | 20.5 | feeder2_69 | 0.060342 | 0.19368 | 0.060316 | 0.19377
1230 | 20.5 | feeder2_71 | 0.062342 | 0.19837 | 0.062314 | 0.19846
1230 | 20.5 | feeder2_72 | 0.063174 | 0.20013 | 0.063141 | 0.20022
1230 | 20.5 | feeder2_73 | 0.064453 | 0.20934 | 0.064426 | 0.20944
1230 | 20.5 | feeder2_74 | 0.072294 | 0.20535 | 0.072266 | 0.20545
1230 | 20.5 | feeder2_77 | 0.066215 | 0.21925 | 0.06618 | 0.21935
1230 | 20.5 | feeder2_79 | 0.063847 | 0.21722 | 0.063823 | 0.21732
1230 | 20.5 | feeder2_81 | 0.069232 | 0.23581 | 0.069203 | 0.23591
1230 | 20.5 | feeder2_82 | 0.071073 | 0.24014 | 0.071037 | 0.24024
1230 | 20.5 | feeder2_116 | 0.082639 | 0.30622 | 0.0826 | 0.30633
1230 | 20.5 | feeder2_119 | 0.082662 | 0.3062 | 0.082624 | 0.30632
1230 | 20.5 | feeder2_120 | 0.087824 | 0.33249 | 0.087785 | 0.33261
1230 | 20.5 | feeder2_248 | 0.088427 | 0.33209 | 0.088388 | 0.33222
1230 | 20.5 | feeder2_124 | 0.091099 | 0.34878 | 0.091063 | 0.34891
1230 | 20.5 | feeder2_282 | 0.092922 | 0.35165 | 0.092884 | 0.35178
1230 | 20.5 | feeder2_275 | 0.091174 | 0.34874 | 0.091135 | 0.34887
1230 | 20.5 | feeder2_151 | 0.096551 | 0.37554 | 0.096512 | 0.37567
1230 | 20.5 | feeder2_295 | 0.094682 | 0.37417 | 0.09464 | 0.3743
1230 | 20.5 | feeder2_311 | 0.096143 | 0.37519 | 0.096096 | 0.37532
1230 | 20.5 | feeder2_201 | 0.10634 | 0.42298 | 0.10629 | 0.42312
1230 | 20.5 | feeder2_314 | 0.10641 | 0.42306 | 0.10636 | 0.42321
1230 | 20.5 | feeder2_342 | 0.12047 | 0.49045 | 0.12042 | 0.49061
1230 | 20.5 | feeder2_368 | 0.12259 | 0.4931 | 0.12254 | 0.49326
1230 | 20.5 | feeder2_347 | 0.12478 | 0.51879 | 0.12473 | 0.51895
1230 | 20.5 | feeder2_353 | 0.12674 | 0.53187 | 0.12668 | 0.53204
1230 | 20.5 | feeder2_518 | 0.12639 | 0.52092 | 0.12634 | 0.52108
1230 | 20.5 | feeder2_365 | 0.12901 | 0.54659 | 0.12895 | 0.54676
1230 | 20.5 | feeder2_653 | 0.12697 | 0.53141 | 0.12692 | 0.53158
1230 | 20.5 | feeder2_377 | 0.1304 | 0.55492 | 0.13035 | 0.5551
1230 | 20.5 | feeder2_622 | 0.12606 | 0.5456 | 0.126 | 0.54577
1230 | 20.5 | feeder2_451 | 0.12375 | 0.4944 | 0.1237 | 0.49456
1230 | 20.5 | feeder2_383 | 0.12573 | 0.49642 | 0.12567 | 0.49658
1230 | 20.5 | feeder2_385 | 0.13211 | 0.56506 | 0.13206 | 0.56523
1230 | 20.5 | feeder2_621 | 0.1285 | 0.55355 | 0.12844 | 0.55372
1230 | 20.5 | feeder2_611 | 0.12738 | 0.49462 | 0.12733 | 0.49478
1230 | 20.5 | feeder2_405 | 0.12591 | 0.49671 | 0.12585 | 0.49688
1230 | 20.5 | feeder2_461 | 0.13937 | 0.60676 | 0.13931 | 0.60695
1230 | 20.5 | feeder2_594 | 0.13224 | 0.5647 | 0.13219 | 0.56487
1230 | 20.5 | feeder2_732 | 0.1323 | 0.48997 | 0.13225 | 0.49013
1230 | 20.5 | feeder2_417 | 0.12704 | 0.5003 | 0.12699 | 0.50046
1230 | 20.5 | feeder2_663 | 0.12452 | 0.49831 | 0.12447 | 0.49847
1230 | 20.5 | feeder2_444 | 0.12809 | 0.50369 | 0.12804 | 0.50385
1230 | 20.5 | feeder2_759 | 0.14394 | 0.52639 | 0.14389 | 0.52655
1230 | 20.5 | feeder2_842 | 0.12505 | 0.50162 | 0.125 | 0.50179
1230 | 20.5 | feeder2_459 | 0.12815 | 0.5036 | 0.1281 | 0.50376
1230 | 20.5 | feeder2_702 | 0.12958 | 0.50556 | 0.12953 | 0.50572
1230 | 20.5 | feeder2_493 | 0.12818 | 0.50252 | 0.12813 | 0.50269
1230 | 20.5 | feeder2_651 | 0.13693 | 0.60529 | 0.13687 | 0.60547
1230 | 20.5 | feeder2_684 | 0.14582 | 0.64272 | 0.14576 | 0.64292
1230 | 20.5 | feeder2_674 | 0.12894 | 0.5017 | 0.1289 | 0.50186
1230 | 20.5 | feeder2_696 | 0.12815 | 0.50239 | 0.1281 | 0.50256
1230 | 20.5 | feeder2_681 | 0.12924 | 0.50138 | 0.12919 | 0.50155
1230 | 20.5 | feeder2_682 | 0.13183 | 0.49881 | 0.13178 | 0.49898
1230 | 20.5 | feeder2_728 | 0.14572 | 0.6432 | 0.14566 | 0.6434
1230 | 20.5 | feeder2_724 | 0.15272 | 0.67852 | 0.15265 | 0.67873
1230 | 20.5 | feeder2_703 | 0.12798 | 0.50225 | 0.12793 | 0.50242
1230 | 20.5 | feeder2_704 | 0.12814 | 0.50238 | 0.12808 | 0.50255
1230 | 20.5 | feeder2_754 | 0.1536 | 0.67954 | 0.15353 | 0.67974
1230 | 20.5 | feeder2_747 | 0.15544 | 0.69263 | 0.15537 | 0.69284
1230 | 20.5 | feeder2_828 | 0.14583 | 0.64283 | 0.14577 | 0.64302
1230 | 20.5 | feeder2_763 | 0.14568 | 0.64436 | 0.14562 | 0.64455
1230 | 20.5 | feeder2_836 | 0.14033 | 0.68245 | 0.14026 | 0.68265
1230 | 20.5 | feeder2_758 | 0.15873 | 0.71001 | 0.15867 | 0.71023
1230 | 20.5 | feeder2_788 | 0.16117 | 0.71294 | 0.16111 | 0.71315
1230 | 20.5 | feeder2_812 | 0.1681 | 0.7602 | 0.16803 | 0.76043
1230 | 20.5 | feeder2_947 | 0.1496 | 0.6492 | 0.14953 | 0.64939
1230 | 20.5 | feeder2_868 | 0.14574 | 0.64444 | 0.14567 | 0.64463
1230 | 20.5 | feeder2_785 | 0.14536 | 0.64401 | 0.14529 | 0.6442
1230 | 20.5 | feeder2_1176 | 0.1395 | 0.64266 | 0.13945 | 0.64284
1230 | 20.5 | feeder2_846 | 0.14536 | 0.64398 | 0.14529 | 0.64418
1230 | 20.5 | feeder2_911 | 0.14539 | 0.64411 | 0.14532 | 0.64431
1230 | 20.5 | feeder2_1107 | 0.17142 | 0.7811 | 0.17135 | 0.78134
1230 | 20.5 | feeder2_920 | 0.16982 | 0.76862 | 0.16975 | 0.76886
1230 | 20.5 | feeder2_926 | 0.17245 | 0.78132 | 0.17238 | 0.78156
1230 | 20.5 | feeder2_1239 | 0.16975 | 0.76846 | 0.16968 | 0.7687
1230 | 20.5 | feeder2_933 | 0.17291 | 0.78361 | 0.17283 | 0.78385
1230 | 20.5 | feeder2_1146 | 0.17579 | 0.79705 | 0.17571 | 0.79728
1230 | 20.5 | feeder2_1124 | 0.17227 | 0.78293 | 0.1722 | 0.78317
1230 | 20.5 | feeder2_942 | 0.17412 | 0.79009 | 0.17405 | 0.79033
1230 | 20.5 | feeder2_952 | 0.17538 | 0.79698 | 0.1753 | 0.79723
1230 | 20.5 | feeder2_965 | 0.1742 | 0.79043 | 0.17413 | 0.79068
1230 | 20.5 | feeder2_961 | 0.17522 | 0.79636 | 0.17515 | 0.79662
1230 | 20.5 | feeder2_963 | 0.17544 | 0.79727 | 0.17536 | 0.79752
1230 | 20.5 | feeder2_973 | 0.17461 | 0.79435 | 0.17453 | 0.7946
1230 | 20.5 | feeder2_1128 | 0.1749 | 0.79425 | 0.17482 | 0.7945
1230 | 20.5 | feeder2_1113 | 0.18086 | 0.80415 | 0.18079 | 0.80441
1230 | 20.5 | feeder2_1143 | 0.17547 | 0.7974 | 0.17539 | 0.79766
1230 | 20.5 | feeder2_1238 | 0.17968 | 0.79969 | 0.17961 | 0.79994
1230 | 20.5 | feeder2_979 | 0.17414 | 0.79013 | 0.17407 | 0.79037
1230 | 20.5 | feeder2_1236 | 0.1739 | 0.79256 | 0.17383 | 0.79282
1230 | 20.5 | feeder2_989 | 0.17461 | 0.79434 | 0.17453 | 0.79459
1230 | 20.5 | feeder2_1196 | 0.17484 | 0.7886 | 0.17477 | 0.78885
1230 | 20.5 | feeder2_1158 | 0.17292 | 0.79312 | 0.17285 | 0.79338
1230 | 20.5 | feeder2_1122 | 0.17296 | 0.79034 | 0.17289 | 0.79059
1230 | 20.5 | feeder2_1258 | 0.16959 | 0.78005 | 0.16952 | 0.78029
1230 | 20.5 | feeder2_1303 | 0.17386 | 0.79139 | 0.17379 | 0.79164
1230 | 20.5 | feeder2_1138 | 0.1741 | 0.79733 | 0.17403 | 0.79757
1230 | 20.5 | feeder2_1304 | 0.1741 | 0.79732 | 0.17403 | 0.79757
1230 | 20.5 | feeder2_1212 | 0.17653 | 0.81228 | 0.17646 | 0.81253
1230 | 20.5 | feeder2_1311 | 0.17674 | 0.81468 | 0.17667 | 0.81494
1230 | 20.5 | feeder2_1290 | 0.17929 | 0.82892 | 0.17922 | 0.82918
1230 | 20.5 | feeder2_1325 | 0.17333 | 0.79083 | 0.17325 | 0.7911
1230 | 20.5 | feeder2_1248 | 0.17389 | 0.79255 | 0.17382 | 0.79282
1230 | 20.5 | feeder2_1249 | 0.18057 | 0.8011 | 0.18049 | 0.80135
1230 | 20.5 | feeder2_1250 | 0.1815 | 0.80281 | 0.18142 | 0.80306
1230 | 20.5 | feeder2_1366 | 0.17298 | 0.79166 | 0.1729 | 0.79192
1230 | 20.5 | feeder2_1266 | 0.16911 | 0.77962 | 0.16903 | 0.77986
1230 | 20.5 | feeder2_1372 | 0.18677 | 0.83805 | 0.1867 | 0.83831
1230 | 20.5 | feeder2_1363 | 0.17951 | 0.83471 | 0.17944 | 0.83498
1230 | 20.5 | feeder2_1446 | 0.17523 | 0.79479 | 0.17515 | 0.79506
1230 | 20.5 | feeder2_1502 | 0.17173 | 0.78357 | 0.17165 | 0.78385
1230 | 20.5 | feeder2_1428 | 0.17973 | 0.8344 | 0.17965 | 0.83467
1230 | 20.5 | feeder2_1380 | 0.17998 | 0.84274 | 0.17991 | 0.84301
1230 | 20.5 | feeder2_1550 | 0.18599 | 0.85279 | 0.18592 | 0.85307
1230 | 20.5 | feeder2_1386 | 0.17926 | 0.84192 | 0.17919 | 0.8422
1230 | 20.5 | feeder2_1551 | 0.17927 | 0.84191 | 0.1792 | 0.84219
1230 | 20.5 | feeder2_1400 | 0.17893 | 0.84159 | 0.17886 | 0.84188
1230 | 20.5 | feeder2_1552 | 0.17959 | 0.84096 | 0.17952 | 0.84125
1230 | 20.5 | feeder2_1408 | 0.17836 | 0.84123 | 0.17829 | 0.84152
1230 | 20.5 | feeder2_1553 | 0.18255 | 0.83883 | 0.18248 | 0.83913
1230 | 20.5 | feeder2_1416 | 0.17842 | 0.84128 | 0.17835 | 0.84157
1230 | 20.5 | feeder2_1530 | 0.17845 | 0.84282 | 0.17837 | 0.84311
1230 | 20.5 | feeder2_1425 | 0.17842 | 0.84055 | 0.17835 | 0.84084
1230 | 20.5 | feeder2_1589 | 0.18012 | 0.83881 | 0.18004 | 0.83911
1230 | 20.5 | feeder2_1435 | 0.1784 | 0.84056 | 0.17833 | 0.84085
1230 | 20.5 | feeder2_1621 | 0.17829 | 0.84045 | 0.17821 | 0.84074
1230 | 20.5 | feeder2_1564 | 0.17819 | 0.84082 | 0.17811 | 0.84111
1230 | 20.5 | feeder2_1704 | 0.1698 | 0.78193 | 0.16971 | 0.7822
1230 | 20.5 | feeder2_1525 | 0.1714 | 0.78237 | 0.17132 | 0.78265
1230 | 20.5 | feeder2_1716 | 0.16856 | 0.77988 | 0.16847 | 0.78016
1230 | 20.5 | feeder2_1537 | 0.17108 | 0.78145 | 0.171 | 0.78173
1230 | 20.5 | feeder2_1645 | 0.17187 | 0.78045 | 0.17179 | 0.78073
1230 | 20.5 | feeder2_1561 | 0.17068 | 0.78095 | 0.1706 | 0.78123
1230 | 20.5 | feeder2_1657 | 0.17184 | 0.78283 | 0.17175 | 0.78311
1230 | 20.5 | feeder2_1570 | 0.17042 | 0.78028 | 0.17033 | 0.78056
1230 | 20.5 | feeder2_1756 | 0.17152 | 0.78465 | 0.17143 | 0.78493
1230 | 20.5 | feeder2_1588 | 0.17012 | 0.77935 | 0.17004 | 0.77963
1230 | 20.5 | feeder2_1628 | 0.17079 | 0.78013 | 0.1707 | 0.78042
1230 | 20.5 | feeder2_1598 | 0.1697 | 0.77795 | 0.16961 | 0.77824
1230 | 20.5 | feeder2_1816 | 0.16596 | 0.77861 | 0.16587 | 0.77889
1230 | 20.5 | feeder2_1765 | 0.1691 | 0.77736 | 0.16901 | 0.77764
1230 | 20.5 | feeder2_1641 | 0.16792 | 0.77133 | 0.16783 | 0.77163
1230 | 20.5 | feeder2_1689 | 0.16622 | 0.76486 | 0.16613 | 0.76516
1230 | 20.5 | feeder2_1744 | 0.1684 | 0.77187 | 0.16831 | 0.77217
1230 | 20.5 | feeder2_1817 | 0.16631 | 0.76357 | 0.16622 | 0.76387
1230 | 20.5 | feeder2_1779 | 0.16051 | 0.76204 | 0.16041 | 0.76234
1230 | 20.5 | feeder2_1800 | 0.16607 | 0.76201 | 0.16598 | 0.76231
1230 | 20.5 | feeder2_1818 | 0.16054 | 0.76346 | 0.16043 | 0.76377
1230 | 20.5 | feeder2_1753 | 0.16978 | 0.77341 | 0.1697 | 0.77371
1230 | 20.5 | feeder2_1754 | 0.16844 | 0.77191 | 0.16835 | 0.7722
1260 | 21 | secondary | 0.0083671 | 0.0062333 | 0.0083795 | 0.006244
1260 | 21 | feeder2_44 | 0.015574 | 0.032516 | 0.015596 | 0.032571
1260 | 21 | feeder2_45 | 0.015813 | 0.033119 | 0.015838 | 0.033183
1260 | 21 | feeder2_46 | 0.015413 | 0.03745 | 0.01543 | 0.03751
1260 | 21 | feeder2_51 | 0.016153 | 0.034439 | 0.016178 | 0.0345
1260 | 21 | feeder2_48 | 0.018886 | 0.03116 | 0.018913 | 0.031235
1260 | 21 | feeder2_52 | 0.014626 | 0.034718 | 0.014659 | 0.034754
1260 | 21 | feeder2_68 | 0.017511 | 0.03854 | 0.017537 | 0.038615
1260 | 21 | feeder2_69 | 0.01737 | 0.039992 | 0.017395 | 0.040071
1260 | 21 | feeder2_71 | 0.017685 | 0.039015 | 0.017713 | 0.039088
1260 | 21 | feeder2_72 | 0.019338 | 0.038085 | 0.019367 | 0.038171
1260 | 21 | feeder2_73 | 0.018205 | 0.040601 | 0.018236 | 0.04068
1260 | 21 | feeder2_74 | 0.015954 | 0.039104 | 0.015986 | 0.039173
1260 | 21 | feeder2_77 | 0.018757 | 0.042271 | 0.018787 | 0.042363
1260 | 21 | feeder2_79 | 0.018554 | 0.046232 | 0.018579 | 0.046318
1260 | 21 | feeder2_81 | 0.01951 | 0.043454 | 0.019542 | 0.043547
1260 | 21 | feeder2_82 | 0.04493 | 0.036497 | 0.044962 | 0.036692
1260 | 21 | feeder2_116 | 0.019308 | 0.065585 | 0.019337 | 0.065622
1260 | 21 | feeder2_119 | 0.01925 | 0.065568 | 0.019278 | 0.065609
1260 | 21 | feeder2_120 | 0.019526 | 0.074753 | 0.019552 | 0.074774
1260 | 21 | feeder2_248 | 0.016987 | 0.0757 | 0.017019 | 0.075708
1260 | 21 | feeder2_124 | 0.020052 | 0.080284 | 0.020075 | 0.080303
1260 | 21 | feeder2_282 | 0.022313 | 0.077869 | 0.022342 | 0.077897
1260 | 21 | feeder2_275 | 0.018311 | 0.079994 | 0.018337 | 0.080004
1260 | 21 | feeder2_151 | 0.02125 | 0.091646 | 0.021275 | 0.091656
1260 | 21 | feeder2_295 | 0.021809 | 0.093437 | 0.021828 | 0.09345
1260 | 21 | feeder2_311 | 0.021822 | 0.09307 | 0.021844 | 0.093082
1260 | 21 | feeder2_201 | 0.022841 | 0.10611 | 0.022863 | 0.1061
1260 | 21 | feeder2_314 | 0.023671 | 0.10527 | 0.023691 | 0.10526
1260 | 21 | feeder2_342 | 0.025302 | 0.1286 | 0.025314 | 0.12857
1260 | 21 | feeder2_368 | 0.025187 | 0.12841 | 0.0252 | 0.12838
1260 | 21 | feeder2_347 | 0.026929 | 0.14002 | 0.026937 | 0.13999
1260 | 21 | feeder2_353 | 0.027818 | 0.14629 | 0.027822 | 0.14626
1260 | 21 | feeder2_518 | 0.027439 | 0.13884 | 0.027447 | 0.13881
1260 | 21 | feeder2_365 | 0.028875 | 0.15327 | 0.028877 | 0.15324
1260 | 21 | feeder2_653 | 0.027501 | 0.14627 | 0.02751 | 0.14624
1260 | 21 | feeder2_377 | 0.029373 | 0.15663 | 0.029376 | 0.15659
1260 | 21 | feeder2_622 | 0.030139 | 0.1549 | 0.030143 | 0.15487
1260 | 21 | feeder2_451 | 0.025691 | 0.12719 | 0.025705 | 0.12717
1260 | 21 | feeder2_383 | 0.025016 | 0.12905 | 0.025032 | 0.12901
1260 | 21 | feeder2_385 | 0.029817 | 0.15986 | 0.029819 | 0.15982
1260 | 21 | feeder2_621 | 0.030712 | 0.15843 | 0.030712 | 0.15839
1260 | 21 | feeder2_611 | 0.02298 | 0.12898 | 0.022993 | 0.12895
1260 | 21 | feeder2_405 | 0.025034 | 0.1291 | 0.025045 | 0.12907
1260 | 21 | feeder2_461 | 0.032538 | 0.17183 | 0.032538 | 0.17178
1260 | 21 | feeder2_594 | 0.027439 | 0.16076 | 0.027436 | 0.16071
1260 | 21 | feeder2_732 | 0.023364 | 0.13125 | 0.023383 | 0.13121
1260 | 21 | feeder2_417 | 0.025308 | 0.12908 | 0.025317 | 0.12905
1260 | 21 | feeder2_663 | 0.026538 | 0.13096 | 0.026543 | 0.13093
1260 | 21 | feeder2_444 | 0.025373 | 0.12846 | 0.025385 | 0.12843
1260 | 21 | feeder2_759 | 0.028584 | 0.12416 | 0.028602 | 0.12413
1260 | 21 | feeder2_842 | 0.025427 | 0.12855 | 0.025442 | 0.12852
1260 | 21 | feeder2_459 | 0.025359 | 0.12851 | 0.025374 | 0.12848
1260 | 21 | feeder2_702 | 0.026335 | 0.12663 | 0.026355 | 0.1266
1260 | 21 | feeder2_493 | 0.025283 | 0.1294 | 0.025292 | 0.12937
1260 | 21 | feeder2_651 | 0.033779 | 0.17336 | 0.033773 | 0.17331
1260 | 21 | feeder2_684 | 0.034418 | 0.17975 | 0.034412 | 0.1797
1260 | 21 | feeder2_674 | 0.024445 | 0.12935 | 0.024459 | 0.12931
1260 | 21 | feeder2_696 | 0.026034 | 0.13257 | 0.026045 | 0.13254
1260 | 21 | feeder2_681 | 0.023321 | 0.1293 | 0.023336 | 0.12926
1260 | 21 | feeder2_682 | 0.022683 | 0.12924 | 0.022698 | 0.12919
1260 | 21 | feeder2_728 | 0.034282 | 0.17959 | 0.034272 | 0.17953
1260 | 21 | feeder2_724 | 0.03667 | 0.18827 | 0.036664 | 0.18821
1260 | 21 | feeder2_703 | 0.028358 | 0.13613 | 0.028363 | 0.13611
1260 | 21 | feeder2_704 | 0.026162 | 0.13276 | 0.026174 | 0.13273
1260 | 21 | feeder2_754 | 0.036876 | 0.18696 | 0.036866 | 0.18692
1260 | 21 | feeder2_747 | 0.037677 | 0.1924 | 0.037663 | 0.19235
1260 | 21 | feeder2_828 | 0.033329 | 0.17964 | 0.033323 | 0.17958
1260 | 21 | feeder2_763 | 0.034429 | 0.1794 | 0.034426 | 0.17935
1260 | 21 | feeder2_836 | 0.050331 | 0.20612 | 0.050301 | 0.20608
1260 | 21 | feeder2_758 | 0.037133 | 0.18966 | 0.037122 | 0.1896
1260 | 21 | feeder2_788 | 0.039756 | 0.18512 | 0.039753 | 0.18505
1260 | 21 | feeder2_812 | 0.03549 | 0.18727 | 0.035474 | 0.18717
1260 | 21 | feeder2_947 | 0.035038 | 0.17674 | 0.035041 | 0.17669
1260 | 21 | feeder2_868 | 0.035009 | 0.17823 | 0.035011 | 0.17817
1260 | 21 | feeder2_785 | 0.034507 | 0.18065 | 0.034503 | 0.18059
1260 | 21 | feeder2_1176 | 0.038954 | 0.18575 | 0.038941 | 0.1857
1260 | 21 | feeder2_846 | 0.033063 | 0.18113 | 0.03306 | 0.18107
1260 | 21 | feeder2_911 | 0.0345 | 0.18057 | 0.034495 | 0.18051
1260 | 21 | feeder2_1107 | 0.033851 | 0.18786 | 0.033826 | 0.1877
1260 | 21 | feeder2_920 | 0.035549 | 0.18682 | 0.035534 | 0.18672
1260 | 21 | feeder2_926 | 0.035727 | 0.18633 | 0.035709 | 0.18626
1260 | 21 | feeder2_1239 | 0.035442 | 0.18673 | 0.035421 | 0.18664
1260 | 21 | feeder2_933 | 0.035862 | 0.18665 | 0.035842 | 0.18658
1260 | 21 | feeder2_1146 | 0.035464 | 0.18405 | 0.035448 | 0.18398
1260 | 21 | feeder2_1124 | 0.036733 | 0.18757 | 0.036715 | 0.18751
1260 | 21 | feeder2_942 | 0.036019 | 0.18667 | 0.035998 | 0.18661
1260 | 21 | feeder2_952 | 0.037038 | 0.19045 | 0.037018 | 0.19043
1260 | 21 | feeder2_965 | 0.035917 | 0.18622 | 0.035901 | 0.18616
1260 | 21 | feeder2_961 | 0.037184 | 0.19114 | 0.037163 | 0.19112
1260 | 21 | feeder2_963 | 0.037031 | 0.1904 | 0.037014 | 0.19038
1260 | 21 | feeder2_973 | 0.038039 | 0.19508 | 0.038019 | 0.19507
1260 | 21 | feeder2_1128 | 0.037049 | 0.19079 | 0.037031 | 0.19077
1260 | 21 | feeder2_1113 | 0.0371 | 0.18942 | 0.037082 | 0.1894
1260 | 21 | feeder2_1143 | 0.036841 | 0.18934 | 0.036818 | 0.18932
1260 | 21 | feeder2_1238 | 0.03654 | 0.18021 | 0.036538 | 0.18017
1260 | 21 | feeder2_979 | 0.035848 | 0.1861 | 0.035828 | 0.18605
1260 | 21 | feeder2_1236 | 0.039289 | 0.20103 | 0.039268 | 0.20104
1260 | 21 | feeder2_989 | 0.038039 | 0.19508 | 0.038023 | 0.19508
1260 | 21 | feeder2_1196 | 0.033518 | 0.18591 | 0.033491 | 0.18584
1260 | 21 | feeder2_1158 | 0.038177 | 0.19523 | 0.038152 | 0.19523
1260 | 21 | feeder2_1122 | 0.032749 | 0.18692 | 0.032721 | 0.18673
1260 | 21 | feeder2_1258 | 0.036277 | 0.1899 | 0.036241 | 0.18975
1260 | 21 | feeder2_1303 | 0.032516 | 0.18526 | 0.03249 | 0.18507
1260 | 21 | feeder2_1138 | 0.031998 | 0.18712 | 0.031962 | 0.1869
1260 | 21 | feeder2_1304 | 0.031963 | 0.18713 | 0.031929 | 0.18691
1260 | 21 | feeder2_1212 | 0.030528 | 0.18863 | 0.030489 | 0.18836
1260 | 21 | feeder2_1311 | 0.030496 | 0.18851 | 0.030459 | 0.18824
1260 | 21 | feeder2_1290 | 0.028973 | 0.19258 | 0.028924 | 0.19226
1260 | 21 | feeder2_1325 | 0.04003 | 0.20541 | 0.040007 | 0.20545
1260 | 21 | feeder2_1248 | 0.039303 | 0.20104 | 0.039283 | 0.20106
1260 | 21 | feeder2_1249 | 0.036736 | 0.17934 | 0.03674 | 0.1793
1260 | 21 | feeder2_1250 | 0.037079 | 0.17814 | 0.037088 | 0.1781
1260 | 21 | feeder2_1366 | 0.043031 | 0.20546 | 0.042997 | 0.20549
1260 | 21 | feeder2_1266 | 0.037159 | 0.19071 | 0.037124 | 0.19056
1260 | 21 | feeder2_1372 | 0.029203 | 0.19046 | 0.029156 | 0.19013
1260 | 21 | feeder2_1363 | 0.028023 | 0.20216 | 0.027963 | 0.20178
1260 | 21 | feeder2_1446 | 0.041021 | 0.20413 | 0.041004 | 0.20417
1260 | 21 | feeder2_1502 | 0.040733 | 0.21225 | 0.040709 | 0.21231
1260 | 21 | feeder2_1428 | 0.025757 | 0.20449 | 0.025692 | 0.2041
1260 | 21 | feeder2_1380 | 0.027906 | 0.21264 | 0.027838 | 0.21221
1260 | 21 | feeder2_1550 | 0.027791 | 0.21198 | 0.027723 | 0.21155
1260 | 21 | feeder2_1386 | 0.028109 | 0.21879 | 0.028033 | 0.21834
1260 | 21 | feeder2_1551 | 0.027037 | 0.21998 | 0.026961 | 0.21953
1260 | 21 | feeder2_1400 | 0.028291 | 0.22158 | 0.028214 | 0.22113
1260 | 21 | feeder2_1552 | 0.028256 | 0.22169 | 0.028176 | 0.22124
1260 | 21 | feeder2_1408 | 0.028745 | 0.22758 | 0.028665 | 0.22711
1260 | 21 | feeder2_1553 | 0.029397 | 0.24268 | 0.029299 | 0.24219
1260 | 21 | feeder2_1416 | 0.028806 | 0.22784 | 0.028723 | 0.22737
1260 | 21 | feeder2_1530 | 0.02917 | 0.22694 | 0.029095 | 0.22646
1260 | 21 | feeder2_1425 | 0.029008 | 0.2289 | 0.028928 | 0.22843
1260 | 21 | feeder2_1589 | 0.028786 | 0.22954 | 0.028699 | 0.22907
1260 | 21 | feeder2_1435 | 0.029044 | 0.22906 | 0.028961 | 0.22859
1260 | 21 | feeder2_1621 | 0.030394 | 0.22967 | 0.030311 | 0.2292
1260 | 21 | feeder2_1564 | 0.029243 | 0.23015 | 0.02916 | 0.22967
1260 | 21 | feeder2_1704 | 0.042675 | 0.21483 | 0.042645 | 0.21491
1260 | 21 | feeder2_1525 | 0.040663 | 0.21301 | 0.040642 | 0.21307
1260 | 21 | feeder2_1716 | 0.043885 | 0.21733 | 0.043845 | 0.21741
1260 | 21 | feeder2_1537 | 0.040405 | 0.21313 | 0.04038 | 0.2132
1260 | 21 | feeder2_1645 | 0.038818 | 0.21425 | 0.038799 | 0.21431
1260 | 21 | feeder2_1561 | 0.040319 | 0.21273 | 0.040294 | 0.21281
1260 | 21 | feeder2_1657 | 0.040325 | 0.21176 | 0.040304 | 0.21183
1260 | 21 | feeder2_1570 | 0.040319 | 0.21278 | 0.040295 | 0.21286
1260 | 21 | feeder2_1756 | 0.040307 | 0.21262 | 0.040289 | 0.21269
1260 | 21 | feeder2_1588 | 0.04032 | 0.21283 | 0.040297 | 0.21291
1260 | 21 | feeder2_1628 | 0.04033 | 0.21204 | 0.04031 | 0.21212
1260 | 21 | feeder2_1598 | 0.040355 | 0.21311 | 0.04033 | 0.21318
1260 | 21 | feeder2_1816 | 0.0407 | 0.21349 | 0.040682 | 0.21357
1260 | 21 | feeder2_1765 | 0.042582 | 0.21565 | 0.042552 | 0.21573
1260 | 21 | feeder2_1641 | 0.040257 | 0.21315 | 0.040237 | 0.21323
1260 | 21 | feeder2_1689 | 0.040335 | 0.21405 | 0.040312 | 0.21412
1260 | 21 | feeder2_1744 | 0.040222 | 0.21256 | 0.040204 | 0.21264
1260 | 21 | feeder2_1817 | 0.040327 | 0.21401 | 0.040301 | 0.21408
1260 | 21 | feeder2_1779 | 0.040606 | 0.21441 | 0.040581 | 0.21448
1260 | 21 | feeder2_1800 | 0.038318 | 0.21333 | 0.038293 | 0.21339
1260 | 21 | feeder2_1818 | 0.041845 | 0.21553 | 0.041838 | 0.21559
1260 | 21 | feeder2_1753 | 0.040223 | 0.21081 | 0.040216 | 0.21089
1260 | 21 | feeder2_1754 | 0.04022 | 0.21254 | 0.040198 | 0.21262
1290 | 21.5 | secondary | 0.034532 | 0.031829 | 0.034514 | 0.031809
1290 | 21.5 | feeder2_44 | 0.064316 | 0.16614 | 0.064286 | 0.16604
1290 | 21.5 | feeder2_45 | 0.065446 | 0.17136 | 0.065417 | 0.17125
1290 | 21.5 | feeder2_46 | 0.060999 | 0.16694 | 0.060969 | 0.16683
1290 | 21.5 | feeder2_51 | 0.067335 | 0.18011 | 0.067304 | 0.17999
1290 | 21.5 | feeder2_48 | 0.067749 | 0.17334 | 0.067714 | 0.17323
1290 | 21.5 | feeder2_52 | 0.067981 | 0.17006 | 0.067948 | 0.16994
1290 | 21.5 | feeder2_68 | 0.073096 | 0.20851 | 0.073063 | 0.20838
1290 | 21.5 | feeder2_69 | 0.07166 | 0.20887 | 0.071622 | 0.20873
1290 | 21.5 | feeder2_71 | 0.073866 | 0.21228 | 0.073832 | 0.21215
1290 | 21.5 | feeder2_72 | 0.076901 | 0.21493 | 0.076866 | 0.2148
1290 | 21.5 | feeder2_73 | 0.076204 | 0.22374 | 0.076169 | 0.2236
1290 | 21.5 | feeder2_74 | 0.075056 | 0.2208 | 0.07502 | 0.22066
1290 | 21.5 | feeder2_77 | 0.078302 | 0.23401 | 0.078266 | 0.23387
1290 | 21.5 | feeder2_79 | 0.074292 | 0.23632 | 0.074254 | 0.23618
1290 | 21.5 | feeder2_81 | 0.081797 | 0.24964 | 0.081755 | 0.24949
1290 | 21.5 | feeder2_82 | 0.10513 | 0.26965 | 0.10509 | 0.26951
1290 | 21.5 | feeder2_116 | 0.092227 | 0.29726 | 0.092182 | 0.29706
1290 | 21.5 | feeder2_119 | 0.092624 | 0.29469 | 0.092578 | 0.29449
1290 | 21.5 | feeder2_120 | 0.096267 | 0.31633 | 0.096217 | 0.31612
1290 | 21.5 | feeder2_248 | 0.09519 | 0.31425 | 0.095143 | 0.31404
1290 | 21.5 | feeder2_124 | 0.098941 | 0.32887 | 0.098891 | 0.32865
1290 | 21.5 | feeder2_282 | 0.10268 | 0.33199 | 0.10262 | 0.33176
1290 | 21.5 | feeder2_275 | 0.097673 | 0.32616 | 0.097625 | 0.32594
1290 | 21.5 | feeder2_151 | 0.10353 | 0.35036 | 0.10347 | 0.35012
1290 | 21.5 | feeder2_295 | 0.10215 | 0.35075 | 0.10209 | 0.3505
1290 | 21.5 | feeder2_311 | 0.10262 | 0.35053 | 0.10256 | 0.35029
1290 | 21.5 | feeder2_201 | 0.11128 | 0.38597 | 0.11122 | 0.3857
1290 | 21.5 | feeder2_314 | 0.11185 | 0.38609 | 0.11179 | 0.38582
1290 | 21.5 | feeder2_342 | 0.12199 | 0.43613 | 0.12193 | 0.43582
1290 | 21.5 | feeder2_368 | 0.12282 | 0.43851 | 0.12276 | 0.4382
1290 | 21.5 | feeder2_347 | 0.12589 | 0.45632 | 0.12583 | 0.45599
1290 | 21.5 | feeder2_353 | 0.12771 | 0.46572 | 0.12764 | 0.46537
1290 | 21.5 | feeder2_518 | 0.12724 | 0.45748 | 0.12717 | 0.45715
1290 | 21.5 | feeder2_365 | 0.12975 | 0.47631 | 0.12968 | 0.47596
1290 | 21.5 | feeder2_653 | 0.12753 | 0.46542 | 0.12746 | 0.46507
1290 | 21.5 | feeder2_377 | 0.13085 | 0.4821 | 0.13078 | 0.48173
1290 | 21.5 | feeder2_622 | 0.12904 | 0.47638 | 0.12897 | 0.47602
1290 | 21.5 | feeder2_451 | 0.12507 | 0.43969 | 0.12501 | 0.43938
1290 | 21.5 | feeder2_383 | 0.12359 | 0.44125 | 0.12352 | 0.44094
1290 | 21.5 | feeder2_385 | 0.13211 | 0.48871 | 0.13204 | 0.48834
1290 | 21.5 | feeder2_621 | 0.12953 | 0.48251 | 0.12946 | 0.48214
1290 | 21.5 | feeder2_611 | 0.12346 | 0.44104 | 0.1234 | 0.44073
1290 | 21.5 | feeder2_405 | 0.12364 | 0.44143 | 0.12357 | 0.44112
1290 | 21.5 | feeder2_461 | 0.13774 | 0.51784 | 0.13767 | 0.51744
1290 | 21.5 | feeder2_594 | 0.13128 | 0.48735 | 0.13121 | 0.48698
1290 | 21.5 | feeder2_732 | 0.12345 | 0.44111 | 0.12339 | 0.4408
1290 | 21.5 | feeder2_417 | 0.12405 | 0.44287 | 0.12398 | 0.44256
1290 | 21.5 | feeder2_663 | 0.12332 | 0.4429 | 0.12326 | 0.44259
1290 | 21.5 | feeder2_444 | 0.12436 | 0.44401 | 0.1243 | 0.44369
1290 | 21.5 | feeder2_759 | 0.13122 | 0.44855 | 0.13116 | 0.44824
1290 | 21.5 | feeder2_842 | 0.12432 | 0.44398 | 0.12426 | 0.44367
1290 | 21.5 | feeder2_459 | 0.12435 | 0.44409 | 0.12428 | 0.44378
1290 | 21.5 | feeder2_702 | 0.12768 | 0.44612 | 0.12762 | 0.44581
1290 | 21.5 | feeder2_493 | 0.12389 | 0.44352 | 0.12382 | 0.44321
1290 | 21.5 | feeder2_651 | 0.13694 | 0.51808 | 0.13687 | 0.51768
1290 | 21.5 | feeder2_684 | 0.14232 | 0.54146 | 0.14224 | 0.54104
1290 | 21.5 | feeder2_674 | 0.12345 | 0.44283 | 0.12339 | 0.44252
1290 | 21.5 | feeder2_696 | 0.12333 | 0.44483 | 0.12327 | 0.44452
1290 | 21.5 | feeder2_681 | 0.12297 | 0.44203 | 0.1229 | 0.44172
1290 | 21.5 | feeder2_682 | 0.12241 | 0.4412 | 0.12234 | 0.44088
1290 | 21.5 | feeder2_728 | 0.14235 | 0.54056 | 0.14227 | 0.54014
1290 | 21.5 | feeder2_724 | 0.1471 | 0.56772 | 0.14701 | 0.56727
1290 | 21.5 | feeder2_703 | 0.1211 | 0.44559 | 0.12103 | 0.44527
1290 | 21.5 | feeder2_704 | 0.12253 | 0.44537 | 0.12247 | 0.44505
1290 | 21.5 | feeder2_754 | 0.14817 | 0.56868 | 0.14809 | 0.56823
1290 | 21.5 | feeder2_747 | 0.14894 | 0.5779 | 0.14886 | 0.57744
1290 | 21.5 | feeder2_828 | 0.1417 | 0.53927 | 0.14162 | 0.53886
1290 | 21.5 | feeder2_763 | 0.14282 | 0.54107 | 0.14274 | 0.54065
1290 | 21.5 | feeder2_836 | 0.14246 | 0.58044 | 0.14237 | 0.57997
1290 | 21.5 | feeder2_758 | 0.15057 | 0.58619 | 0.15048 | 0.58573
1290 | 21.5 | feeder2_788 | 0.15389 | 0.58846 | 0.1538 | 0.588
1290 | 21.5 | feeder2_812 | 0.15471 | 0.60877 | 0.15462 | 0.60829
1290 | 21.5 | feeder2_947 | 0.14583 | 0.54369 | 0.14575 | 0.54328
1290 | 21.5 | feeder2_868 | 0.14462 | 0.54239 | 0.14454 | 0.54196
1290 | 21.5 | feeder2_785 | 0.14257 | 0.53979 | 0.14249 | 0.53937
1290 | 21.5 | feeder2_1176 | 0.14054 | 0.54006 | 0.14046 | 0.53964
1290 | 21.5 | feeder2_846 | 0.14181 | 0.53747 | 0.14173 | 0.53705
1290 | 21.5 | feeder2_911 | 0.1426 | 0.53988 | 0.14251 | 0.53946
1290 | 21.5 | feeder2_1107 | 0.15536 | 0.60508 | 0.15527 | 0.6046
1290 | 21.5 | feeder2_920 | 0.1557 | 0.61616 | 0.15561 | 0.61568
1290 | 21.5 | feeder2_926 | 0.15734 | 0.62794 | 0.15724 | 0.62745
1290 | 21.5 | feeder2_1239 | 0.15551 | 0.61529 | 0.15541 | 0.61481
1290 | 21.5 | feeder2_933 | 0.15792 | 0.63261 | 0.15783 | 0.63212
1290 | 21.5 | feeder2_1146 | 0.158 | 0.63054 | 0.1579 | 0.63005
1290 | 21.5 | feeder2_1124 | 0.15666 | 0.63343 | 0.15656 | 0.63294
1290 | 21.5 | feeder2_942 | 0.15954 | 0.64381 | 0.15945 | 0.64331
1290 | 21.5 | feeder2_952 | 0.16157 | 0.6613 | 0.16148 | 0.66078
1290 | 21.5 | feeder2_965 | 0.15959 | 0.64368 | 0.1595 | 0.64319
1290 | 21.5 | feeder2_961 | 0.16169 | 0.66281 | 0.16159 | 0.66229
1290 | 21.5 | feeder2_963 | 0.16159 | 0.66138 | 0.16149 | 0.66087
1290 | 21.5 | feeder2_973 | 0.16248 | 0.67151 | 0.16238 | 0.67098
1290 | 21.5 | feeder2_1128 | 0.16142 | 0.66164 | 0.16132 | 0.66113
1290 | 21.5 | feeder2_1113 | 0.16294 | 0.66242 | 0.16284 | 0.6619
1290 | 21.5 | feeder2_1143 | 0.16224 | 0.66371 | 0.16215 | 0.6632
1290 | 21.5 | feeder2_1238 | 0.16746 | 0.64946 | 0.16736 | 0.64897
1290 | 21.5 | feeder2_979 | 0.15951 | 0.64301 | 0.15941 | 0.64251
1290 | 21.5 | feeder2_1236 | 0.16384 | 0.68365 | 0.16373 | 0.68311
1290 | 21.5 | feeder2_989 | 0.16248 | 0.67151 | 0.16237 | 0.67098
1290 | 21.5 | feeder2_1196 | 0.15938 | 0.64019 | 0.15928 | 0.63969
1290 | 21.5 | feeder2_1158 | 0.16122 | 0.67256 | 0.16112 | 0.67204
1290 | 21.5 | feeder2_1122 | 0.15571 | 0.60359 | 0.15562 | 0.60313
1290 | 21.5 | feeder2_1258 | 0.1503 | 0.6063 | 0.1502 | 0.60582
1290 | 21.5 | feeder2_1303 | 0.17288 | 0.61841 | 0.17279 | 0.61795
1290 | 21.5 | feeder2_1138 | 0.15481 | 0.597 | 0.15472 | 0.59654
1290 | 21.5 | feeder2_1304 | 0.15495 | 0.59519 | 0.15485 | 0.59473
1290 | 21.5 | feeder2_1212 | 0.15307 | 0.58467 | 0.15298 | 0.58422
1290 | 21.5 | feeder2_1311 | 0.15565 | 0.5863 | 0.15556 | 0.58586
1290 | 21.5 | feeder2_1290 | 0.15042 | 0.56814 | 0.15033 | 0.5677
1290 | 21.5 | feeder2_1325 | 0.16593 | 0.69921 | 0.16582 | 0.69865
1290 | 21.5 | feeder2_1248 | 0.16383 | 0.68365 | 0.16372 | 0.68312
1290 | 21.5 | feeder2_1249 | 0.16877 | 0.65028 | 0.16868 | 0.64979
1290 | 21.5 | feeder2_1250 | 0.16983 | 0.65158 | 0.16973 | 0.65109
1290 | 21.5 | feeder2_1366 | 0.1619 | 0.68514 | 0.16179 | 0.68459
1290 | 21.5 | feeder2_1266 | 0.14584 | 0.60767 | 0.14574 | 0.60718
1290 | 21.5 | feeder2_1372 | 0.15242 | 0.5698 | 0.15233 | 0.56936
1290 | 21.5 | feeder2_1363 | 0.14705 | 0.5481 | 0.14696 | 0.54768
1290 | 21.5 | feeder2_1446 | 0.16609 | 0.69936 | 0.16598 | 0.6988
1290 | 21.5 | feeder2_1502 | 0.16824 | 0.71651 | 0.16813 | 0.71592
1290 | 21.5 | feeder2_1428 | 0.14606 | 0.54595 | 0.14597 | 0.54552
1290 | 21.5 | feeder2_1380 | 0.14371 | 0.52729 | 0.14362 | 0.52687
1290 | 21.5 | feeder2_1550 | 0.14614 | 0.52911 | 0.14605 | 0.52869
1290 | 21.5 | feeder2_1386 | 0.14181 | 0.51619 | 0.14172 | 0.51578
1290 | 21.5 | feeder2_1551 | 0.14228 | 0.51503 | 0.14219 | 0.51462
1290 | 21.5 | feeder2_1400 | 0.14091 | 0.51121 | 0.14082 | 0.5108
1290 | 21.5 | feeder2_1552 | 0.14175 | 0.5093 | 0.14166 | 0.50889
1290 | 21.5 | feeder2_1408 | 0.13909 | 0.50193 | 0.139 | 0.50152
1290 | 21.5 | feeder2_1553 | 0.13246 | 0.48578 | 0.13237 | 0.48539
1290 | 21.5 | feeder2_1416 | 0.13891 | 0.50053 | 0.13882 | 0.50012
1290 | 21.5 | feeder2_1530 | 0.13915 | 0.50076 | 0.13907 | 0.50035
1290 | 21.5 | feeder2_1425 | 0.13854 | 0.49773 | 0.13845 | 0.49733
1290 | 21.5 | feeder2_1589 | 0.13897 | 0.49469 | 0.13889 | 0.49428
1290 | 21.5 | feeder2_1435 | 0.13849 | 0.49746 | 0.1384 | 0.49705
1290 | 21.5 | feeder2_1621 | 0.13613 | 0.49814 | 0.13604 | 0.49773
1290 | 21.5 | feeder2_1564 | 0.13817 | 0.49381 | 0.13808 | 0.4934
1290 | 21.5 | feeder2_1704 | 0.16626 | 0.71745 | 0.16614 | 0.71686
1290 | 21.5 | feeder2_1525 | 0.1689 | 0.72071 | 0.16878 | 0.72012
1290 | 21.5 | feeder2_1716 | 0.16581 | 0.72225 | 0.16569 | 0.72166
1290 | 21.5 | feeder2_1537 | 0.16967 | 0.72524 | 0.16956 | 0.72465
1290 | 21.5 | feeder2_1645 | 0.1699 | 0.72451 | 0.16979 | 0.72392
1290 | 21.5 | feeder2_1561 | 0.17057 | 0.7308 | 0.17046 | 0.7302
1290 | 21.5 | feeder2_1657 | 0.17071 | 0.73093 | 0.1706 | 0.73033
1290 | 21.5 | feeder2_1570 | 0.17095 | 0.73316 | 0.17084 | 0.73257
1290 | 21.5 | feeder2_1756 | 0.17596 | 0.73616 | 0.17585 | 0.73557
1290 | 21.5 | feeder2_1588 | 0.17123 | 0.73516 | 0.17111 | 0.73456
1290 | 21.5 | feeder2_1628 | 0.17229 | 0.73612 | 0.17217 | 0.73552
1290 | 21.5 | feeder2_1598 | 0.17152 | 0.73739 | 0.17141 | 0.73679
1290 | 21.5 | feeder2_1816 | 0.17139 | 0.73734 | 0.17127 | 0.73673
1290 | 21.5 | feeder2_1765 | 0.17001 | 0.73744 | 0.16989 | 0.73684
1290 | 21.5 | feeder2_1641 | 0.17295 | 0.74849 | 0.17283 | 0.74788
1290 | 21.5 | feeder2_1689 | 0.17171 | 0.74657 | 0.17159 | 0.74594
1290 | 21.5 | feeder2_1744 | 0.18076 | 0.75527 | 0.18064 | 0.75466
1290 | 21.5 | feeder2_1817 | 0.17169 | 0.7465 | 0.17157 | 0.74587
1290 | 21.5 | feeder2_1779 | 0.17025 | 0.74742 | 0.17012 | 0.74678
1290 | 21.5 | feeder2_1800 | 0.17101 | 0.7426 | 0.17089 | 0.74196
1290 | 21.5 | feeder2_1818 | 0.16429 | 0.74365 | 0.16414 | 0.74298
1290 | 21.5 | feeder2_1753 | 0.20546 | 0.77688 | 0.20534 | 0.77628
1290 | 21.5 | feeder2_1754 | 0.18079 | 0.7553 | 0.18067 | 0.75469
1320 | 22 | secondary | 0.031927 | 0.013971 | 0.031937 | 0.013964
1320 | 22 | feeder2_44 | 0.059443 | 0.072901 | 0.059462 | 0.072851
1320 | 22 | feeder2_45 | 0.06041 | 0.074833 | 0.060432 | 0.074778
1320 | 22 | feeder2_46 | 0.059178 | 0.07661 | 0.059193 | 0.076578
1320 | 22 | feeder2_51 | 0.061985 | 0.078641 | 0.062007 | 0.078584
1320 | 22 | feeder2_48 | 0.063658 | 0.072194 | 0.063673 | 0.072135
1320 | 22 | feeder2_52 | 0.058968 | 0.079969 | 0.05899 | 0.079907
1320 | 22 | feeder2_68 | 0.06669 | 0.089028 | 0.06671 | 0.08896
1320 | 22 | feeder2_69 | 0.067015 | 0.090215 | 0.067037 | 0.09015
1320 | 22 | feeder2_71 | 0.0673 | 0.090335 | 0.067321 | 0.090266
1320 | 22 | feeder2_72 | 0.069197 | 0.087714 | 0.069219 | 0.087648
1320 | 22 | feeder2_73 | 0.069191 | 0.094734 | 0.069212 | 0.094662
1320 | 22 | feeder2_74 | 0.066816 | 0.0972 | 0.06684 | 0.09712
1320 | 22 | feeder2_77 | 0.070924 | 0.098174 | 0.070949 | 0.098099
1320 | 22 | feeder2_79 | 0.070999 | 0.098425 | 0.071024 | 0.098351
1320 | 22 | feeder2_81 | 0.073646 | 0.10351 | 0.073673 | 0.10342
1320 | 22 | feeder2_82 | 0.087031 | 0.085563 | 0.087058 | 0.085488
1320 | 22 | feeder2_116 | 0.084892 | 0.14617 | 0.084921 | 0.14605
1320 | 22 | feeder2_119 | 0.084141 | 0.14652 | 0.08417 | 0.1464
1320 | 22 | feeder2_120 | 0.08925 | 0.16182 | 0.08928 | 0.1617
1320 | 22 | feeder2_248 | 0.08877 | 0.16202 | 0.088797 | 0.16189
1320 | 22 | feeder2_124 | 0.091992 | 0.1714 | 0.092018 | 0.17126
1320 | 22 | feeder2_282 | 0.094837 | 0.16726 | 0.094864 | 0.16713
1320 | 22 | feeder2_275 | 0.064063 | 0.18528 | 0.064096 | 0.1851
1320 | 22 | feeder2_151 | 0.10054 | 0.18551 | 0.10057 | 0.1854
1320 | 22 | feeder2_295 | 0.1013 | 0.18733 | 0.10133 | 0.18722
1320 | 22 | feeder2_311 | 0.10127 | 0.18704 | 0.1013 | 0.18693
1320 | 22 | feeder2_201 | 0.11371 | 0.20687 | 0.11375 | 0.20679
1320 | 22 | feeder2_314 | 0.11511 | 0.20562 | 0.11514 | 0.20554
1320 | 22 | feeder2_342 | 0.13187 | 0.24378 | 0.13191 | 0.24375
1320 | 22 | feeder2_368 | 0.13199 | 0.2447 | 0.13203 | 0.24466
1320 | 22 | feeder2_347 | 0.14069 | 0.26134 | 0.14073 | 0.26132
1320 | 22 | feeder2_353 | 0.14506 | 0.27095 | 0.1451 | 0.27095
1320 | 22 | feeder2_518 | 0.14168 | 0.25994 | 0.14172 | 0.25992
1320 | 22 | feeder2_365 | 0.15001 | 0.28179 | 0.15004 | 0.28179
1320 | 22 | feeder2_653 | 0.14414 | 0.27093 | 0.14418 | 0.27092
1320 | 22 | feeder2_377 | 0.15262 | 0.28734 | 0.15266 | 0.28735
1320 | 22 | feeder2_622 | 0.15063 | 0.28323 | 0.15067 | 0.28323
1320 | 22 | feeder2_451 | 0.1333 | 0.24282 | 0.13334 | 0.24278
1320 | 22 | feeder2_383 | 0.13203 | 0.24763 | 0.13207 | 0.2476
1320 | 22 | feeder2_385 | 0.15548 | 0.29284 | 0.15553 | 0.29286
1320 | 22 | feeder2_621 | 0.15352 | 0.28993 | 0.15356 | 0.28994
1320 | 22 | feeder2_611 | 0.13116 | 0.24766 | 0.13119 | 0.24762
1320 | 22 | feeder2_405 | 0.13204 | 0.24782 | 0.13208 | 0.24778
1320 | 22 | feeder2_461 | 0.16719 | 0.31559 | 0.16723 | 0.31562
1320 | 22 | feeder2_594 | 0.15516 | 0.29282 | 0.15521 | 0.29283
1320 | 22 | feeder2_732 | 0.13047 | 0.25051 | 0.13051 | 0.25047
1320 | 22 | feeder2_417 | 0.13231 | 0.24868 | 0.13234 | 0.24864
1320 | 22 | feeder2_663 | 0.13244 | 0.2506 | 0.13247 | 0.25057
1320 | 22 | feeder2_444 | 0.13242 | 0.24869 | 0.13245 | 0.24866
1320 | 22 | feeder2_759 | 0.13388 | 0.24652 | 0.13392 | 0.24649
1320 | 22 | feeder2_842 | 0.13252 | 0.24887 | 0.13255 | 0.24884
1320 | 22 | feeder2_459 | 0.13244 | 0.24881 | 0.13248 | 0.24878
1320 | 22 | feeder2_702 | 0.13488 | 0.24591 | 0.13492 | 0.24588
1320 | 22 | feeder2_493 | 0.13232 | 0.25041 | 0.13236 | 0.25038
1320 | 22 | feeder2_651 | 0.16726 | 0.31579 | 0.16731 | 0.31583
1320 | 22 | feeder2_684 | 0.17667 | 0.33418 | 0.17672 | 0.33423
1320 | 22 | feeder2_674 | 0.13162 | 0.25077 | 0.13166 | 0.25074
1320 | 22 | feeder2_696 | 0.13297 | 0.25378 | 0.13301 | 0.25376
1320 | 22 | feeder2_681 | 0.13077 | 0.25125 | 0.13081 | 0.25121
1320 | 22 | feeder2_682 | 0.13001 | 0.25157 | 0.13005 | 0.25153
1320 | 22 | feeder2_728 | 0.17653 | 0.33171 | 0.17658 | 0.33176
1320 | 22 | feeder2_724 | 0.18681 | 0.35931 | 0.18686 | 0.35939
1320 | 22 | feeder2_703 | 0.13322 | 0.25439 | 0.13325 | 0.25436
1320 | 22 | feeder2_704 | 0.13339 | 0.25483 | 0.13343 | 0.25479
1320 | 22 | feeder2_754 | 0.18832 | 0.35773 | 0.18837 | 0.35781
1320 | 22 | feeder2_747 | 0.1908 | 0.37056 | 0.19086 | 0.37064
1320 | 22 | feeder2_828 | 0.17516 | 0.33161 | 0.1752 | 0.33166
1320 | 22 | feeder2_763 | 0.17693 | 0.32841 | 0.17698 | 0.32846
1320 | 22 | feeder2_836 | 0.19628 | 0.38555 | 0.19633 | 0.38565
1320 | 22 | feeder2_758 | 0.1931 | 0.37339 | 0.19316 | 0.37348
1320 | 22 | feeder2_788 | 0.19466 | 0.3714 | 0.19471 | 0.37149
1320 | 22 | feeder2_812 | 0.2001 | 0.38447 | 0.20016 | 0.38457
1320 | 22 | feeder2_947 | 0.17912 | 0.32554 | 0.17917 | 0.3256
1320 | 22 | feeder2_868 | 0.179 | 0.32597 | 0.17905 | 0.32602
1320 | 22 | feeder2_785 | 0.1768 | 0.32868 | 0.17685 | 0.32873
1320 | 22 | feeder2_1176 | 0.17847 | 0.33279 | 0.17852 | 0.33284
1320 | 22 | feeder2_846 | 0.174 | 0.32929 | 0.17404 | 0.32933
1320 | 22 | feeder2_911 | 0.17725 | 0.32699 | 0.1773 | 0.32704
1320 | 22 | feeder2_1107 | 0.1977 | 0.38105 | 0.19776 | 0.38114
1320 | 22 | feeder2_920 | 0.20272 | 0.38855 | 0.20278 | 0.38866
1320 | 22 | feeder2_926 | 0.20682 | 0.39445 | 0.20688 | 0.39457
1320 | 22 | feeder2_1239 | 0.2025 | 0.38884 | 0.20256 | 0.38895
1320 | 22 | feeder2_933 | 0.20851 | 0.39802 | 0.20857 | 0.39815
1320 | 22 | feeder2_1146 | 0.20741 | 0.39002 | 0.20747 | 0.39015
1320 | 22 | feeder2_1124 | 0.20899 | 0.39925 | 0.20905 | 0.39938
1320 | 22 | feeder2_942 | 0.2126 | 0.40596 | 0.21266 | 0.4061
1320 | 22 | feeder2_952 | 0.21787 | 0.42379 | 0.21793 | 0.42393
1320 | 22 | feeder2_965 | 0.2127 | 0.40518 | 0.21276 | 0.40531
1320 | 22 | feeder2_961 | 0.21837 | 0.42624 | 0.21844 | 0.42639
1320 | 22 | feeder2_963 | 0.21788 | 0.42367 | 0.21795 | 0.42382
1320 | 22 | feeder2_973 | 0.22124 | 0.43928 | 0.2213 | 0.43943
1320 | 22 | feeder2_1128 | 0.21806 | 0.42627 | 0.21812 | 0.42642
1320 | 22 | feeder2_1113 | 0.21964 | 0.42175 | 0.21971 | 0.4219
1320 | 22 | feeder2_1143 | 0.21813 | 0.42144 | 0.2182 | 0.42159
1320 | 22 | feeder2_1238 | 0.22425 | 0.39264 | 0.22431 | 0.39278
1320 | 22 | feeder2_979 | 0.21269 | 0.40516 | 0.21275 | 0.4053
1320 | 22 | feeder2_1236 | 0.22525 | 0.45705 | 0.22531 | 0.45722
1320 | 22 | feeder2_989 | 0.22124 | 0.43929 | 0.22131 | 0.43945
1320 | 22 | feeder2_1196 | 0.21251 | 0.40511 | 0.21257 | 0.40525
1320 | 22 | feeder2_1158 | 0.22194 | 0.4412 | 0.22201 | 0.44136
1320 | 22 | feeder2_1122 | 0.19662 | 0.37892 | 0.19667 | 0.37901
1320 | 22 | feeder2_1258 | 0.19817 | 0.38208 | 0.19822 | 0.38216
1320 | 22 | feeder2_1303 | 0.19703 | 0.37836 | 0.19708 | 0.37844
1320 | 22 | feeder2_1138 | 0.19577 | 0.37744 | 0.19582 | 0.37752
1320 | 22 | feeder2_1304 | 0.19521 | 0.37735 | 0.19527 | 0.37742
1320 | 22 | feeder2_1212 | 0.19406 | 0.3745 | 0.19411 | 0.37456
1320 | 22 | feeder2_1311 | 0.19582 | 0.37224 | 0.19588 | 0.37231
1320 | 22 | feeder2_1290 | 0.19185 | 0.37275 | 0.19191 | 0.3728
1320 | 22 | feeder2_1325 | 0.23064 | 0.48088 | 0.23071 | 0.48106
1320 | 22 | feeder2_1248 | 0.22525 | 0.45705 | 0.22531 | 0.45722
1320 | 22 | feeder2_1249 | 0.22557 | 0.39121 | 0.22564 | 0.39135
1320 | 22 | feeder2_1250 | 0.22923 | 0.3873 | 0.22928 | 0.38744
1320 | 22 | feeder2_1366 | 0.22552 | 0.45757 | 0.22558 | 0.45774
1320 | 22 | feeder2_1266 | 0.19839 | 0.38253 | 0.19845 | 0.38262
1320 | 22 | feeder2_1372 | 0.19242 | 0.37197 | 0.19248 | 0.37202
1320 | 22 | feeder2_1363 | 0.18946 | 0.37213 | 0.18952 | 0.37216
1320 | 22 | feeder2_1446 | 0.23216 | 0.47931 | 0.23222 | 0.47949
1320 | 22 | feeder2_1502 | 0.23637 | 0.50979 | 0.23644 | 0.50998
1320 | 22 | feeder2_1428 | 0.1873 | 0.37199 | 0.18735 | 0.37201
1320 | 22 | feeder2_1380 | 0.18728 | 0.37222 | 0.18734 | 0.37224
1320 | 22 | feeder2_1550 | 0.18891 | 0.36997 | 0.18897 | 0.36999
1320 | 22 | feeder2_1386 | 0.18618 | 0.37342 | 0.18624 | 0.37342
1320 | 22 | feeder2_1551 | 0.18521 | 0.37488 | 0.18527 | 0.37488
1320 | 22 | feeder2_1400 | 0.18574 | 0.3737 | 0.18579 | 0.3737
1320 | 22 | feeder2_1552 | 0.183 | 0.37362 | 0.18305 | 0.37362
1320 | 22 | feeder2_1408 | 0.18512 | 0.37449 | 0.18518 | 0.37448
1320 | 22 | feeder2_1553 | 0.18043 | 0.37582 | 0.18048 | 0.37581
1320 | 22 | feeder2_1416 | 0.18506 | 0.37472 | 0.18511 | 0.37472
1320 | 22 | feeder2_1530 | 0.18531 | 0.37434 | 0.18537 | 0.37434
1320 | 22 | feeder2_1425 | 0.18492 | 0.37536 | 0.18498 | 0.37536
1320 | 22 | feeder2_1589 | 0.18468 | 0.37535 | 0.18473 | 0.37535
1320 | 22 | feeder2_1435 | 0.1849 | 0.3755 | 0.18495 | 0.37549
1320 | 22 | feeder2_1621 | 0.18499 | 0.37716 | 0.18505 | 0.37715
1320 | 22 | feeder2_1564 | 0.18432 | 0.37504 | 0.18438 | 0.37503
1320 | 22 | feeder2_1704 | 0.23726 | 0.51191 | 0.23733 | 0.51211
1320 | 22 | feeder2_1525 | 0.23771 | 0.51643 | 0.23778 | 0.51662
1320 | 22 | feeder2_1716 | 0.23782 | 0.51665 | 0.23788 | 0.51685
1320 | 22 | feeder2_1537 | 0.23921 | 0.52383 | 0.23928 | 0.52404
1320 | 22 | feeder2_1645 | 0.23863 | 0.52441 | 0.2387 | 0.52461
1320 | 22 | feeder2_1561 | 0.24102 | 0.53195 | 0.24109 | 0.53216
1320 | 22 | feeder2_1657 | 0.24134 | 0.53156 | 0.24141 | 0.53176
1320 | 22 | feeder2_1570 | 0.2418 | 0.53555 | 0.24186 | 0.53575
1320 | 22 | feeder2_1756 | 0.24494 | 0.53178 | 0.24501 | 0.53199
1320 | 22 | feeder2_1588 | 0.24251 | 0.53912 | 0.24258 | 0.53933
1320 | 22 | feeder2_1628 | 0.24356 | 0.53798 | 0.24363 | 0.53819
1320 | 22 | feeder2_1598 | 0.24338 | 0.54396 | 0.24345 | 0.54417
1320 | 22 | feeder2_1816 | 0.24359 | 0.54435 | 0.24366 | 0.54456
1320 | 22 | feeder2_1765 | 0.245 | 0.54767 | 0.24507 | 0.54788
1320 | 22 | feeder2_1641 | 0.24732 | 0.56586 | 0.24739 | 0.56608
1320 | 22 | feeder2_1689 | 0.25046 | 0.58616 | 0.25054 | 0.58638
1320 | 22 | feeder2_1744 | 0.24831 | 0.56478 | 0.24838 | 0.565
1320 | 22 | feeder2_1817 | 0.25045 | 0.58611 | 0.25052 | 0.58634
1320 | 22 | feeder2_1779 | 0.25122 | 0.58786 | 0.25128 | 0.58808
1320 | 22 | feeder2_1800 | 0.24843 | 0.58546 | 0.2485 | 0.58568
1320 | 22 | feeder2_1818 | 0.26836 | 0.62381 | 0.26844 | 0.62405
1320 | 22 | feeder2_1753 | 0.24882 | 0.5641 | 0.2489 | 0.56432
1320 | 22 | feeder2_1754 | 0.24889 | 0.56419 | 0.24896 | 0.5644
1350 | 22.5 | secondary | 0.00076628 | 0.0047505 | 0.00077049 | 0.004748
1350 | 22.5 | feeder2_44 | 0.0014263 | 0.024781 | 0.0014349 | 0.02475
1350 | 22.5 | feeder2_45 | 0.0013651 | 0.024861 | 0.001375 | 0.024827
1350 | 22.5 | feeder2_46 | 0.0081268 | 0.033253 | 0.0081482 | 0.033228
1350 | 22.5 | feeder2_51 | 0.0012749 | 0.025008 | 0.0012796 | 0.02497
1350 | 22.5 | feeder2_48 | 0.001835 | 0.024787 | 0.0018366 | 0.024755
1350 | 22.5 | feeder2_52 | 0.0045269 | 0.023298 | 0.0045057 | 0.023287
1350 | 22.5 | feeder2_68 | 0.0015162 | 0.026661 | 0.0015095 | 0.026613
1350 | 22.5 | feeder2_69 | 0.0028028 | 0.028833 | 0.0028212 | 0.028791
1350 | 22.5 | feeder2_71 | 0.0015415 | 0.026805 | 0.001533 | 0.026755
1350 | 22.5 | feeder2_72 | 0.0046274 | 0.027401 | 0.004612 | 0.027331
1350 | 22.5 | feeder2_73 | 0.0015839 | 0.027198 | 0.0015733 | 0.027139
1350 | 22.5 | feeder2_74 | 0.0053278 | 0.021299 | 0.005305 | 0.021253
1350 | 22.5 | feeder2_77 | 0.0018429 | 0.028582 | 0.0018294 | 0.028514
1350 | 22.5 | feeder2_79 | 0.0017714 | 0.028919 | 0.0017691 | 0.028855
1350 | 22.5 | feeder2_81 | 0.0022482 | 0.030757 | 0.0022333 | 0.030683
1350 | 22.5 | feeder2_82 | 0.002805 | 0.030853 | 0.0027899 | 0.03077
1350 | 22.5 | feeder2_116 | 0.003988 | 0.041306 | 0.0039672 | 0.041183
1350 | 22.5 | feeder2_119 | 0.0033442 | 0.038909 | 0.0033105 | 0.038792
1350 | 22.5 | feeder2_120 | 0.0048903 | 0.046806 | 0.0048698 | 0.046665
1350 | 22.5 | feeder2_248 | 0.0056259 | 0.045418 | 0.0055923 | 0.045286
1350 | 22.5 | feeder2_124 | 0.0055221 | 0.050888 | 0.0055009 | 0.050742
1350 | 22.5 | feeder2_282 | 0.011074 | 0.053498 | 0.011053 | 0.053333
1350 | 22.5 | feeder2_275 | 0.0052919 | 0.050084 | 0.0052664 | 0.049937
1350 | 22.5 | feeder2_151 | 0.0061868 | 0.05687 | 0.0061704 | 0.056711
1350 | 22.5 | feeder2_295 | 0.0063529 | 0.059309 | 0.006363 | 0.059161
1350 | 22.5 | feeder2_311 | 0.006063 | 0.058253 | 0.0060639 | 0.058095
1350 | 22.5 | feeder2_201 | 0.0068978 | 0.062808 | 0.0068759 | 0.062614
1350 | 22.5 | feeder2_314 | 0.0070094 | 0.062892 | 0.0069884 | 0.062693
1350 | 22.5 | feeder2_342 | 0.0079219 | 0.072294 | 0.0078944 | 0.072049
1350 | 22.5 | feeder2_368 | 0.0077893 | 0.071781 | 0.0077657 | 0.071549
1350 | 22.5 | feeder2_347 | 0.0086302 | 0.080302 | 0.008588 | 0.080018
1350 | 22.5 | feeder2_353 | 0.0088686 | 0.084094 | 0.0088238 | 0.083797
1350 | 22.5 | feeder2_518 | 0.011048 | 0.082332 | 0.011007 | 0.082045
1350 | 22.5 | feeder2_365 | 0.0092711 | 0.089148 | 0.0092225 | 0.088834
1350 | 22.5 | feeder2_653 | 0.0086114 | 0.083366 | 0.0085637 | 0.083063
1350 | 22.5 | feeder2_377 | 0.009613 | 0.091815 | 0.0095619 | 0.091496
1350 | 22.5 | feeder2_622 | 0.0070111 | 0.090453 | 0.0069638 | 0.090138
1350 | 22.5 | feeder2_451 | 0.0095289 | 0.073074 | 0.009505 | 0.072843
1350 | 22.5 | feeder2_383 | 0.0077137 | 0.071154 | 0.0077048 | 0.070948
1350 | 22.5 | feeder2_385 | 0.010151 | 0.095299 | 0.010097 | 0.094971
1350 | 22.5 | feeder2_621 | 0.0070636 | 0.091866 | 0.0070274 | 0.091546
1350 | 22.5 | feeder2_611 | 0.0070417 | 0.069686 | 0.0070208 | 0.069486
1350 | 22.5 | feeder2_405 | 0.0077504 | 0.071257 | 0.0077446 | 0.071055
1350 | 22.5 | feeder2_461 | 0.012679 | 0.11498 | 0.012613 | 0.11463
1350 | 22.5 | feeder2_594 | 0.011069 | 0.093829 | 0.011012 | 0.093498
1350 | 22.5 | feeder2_732 | 0.0074284 | 0.069973 | 0.0074086 | 0.069776
1350 | 22.5 | feeder2_417 | 0.0082116 | 0.072511 | 0.0082129 | 0.072321
1350 | 22.5 | feeder2_663 | 0.0082772 | 0.072583 | 0.008277 | 0.072403
1350 | 22.5 | feeder2_444 | 0.0086719 | 0.073632 | 0.0086798 | 0.073456
1350 | 22.5 | feeder2_759 | 0.012445 | 0.073065 | 0.012447 | 0.072876
1350 | 22.5 | feeder2_842 | 0.0094848 | 0.074882 | 0.0095009 | 0.074713
1350 | 22.5 | feeder2_459 | 0.0087792 | 0.074019 | 0.0087903 | 0.073844
1350 | 22.5 | feeder2_702 | 0.009128 | 0.074374 | 0.0091286 | 0.074204
1350 | 22.5 | feeder2_493 | 0.0092844 | 0.075559 | 0.0093033 | 0.075399
1350 | 22.5 | feeder2_651 | 0.012495 | 0.11492 | 0.012436 | 0.11456
1350 | 22.5 | feeder2_684 | 0.015047 | 0.13351 | 0.01498 | 0.13314
1350 | 22.5 | feeder2_674 | 0.0078658 | 0.07417 | 0.0078829 | 0.074013
1350 | 22.5 | feeder2_696 | 0.013132 | 0.087801 | 0.013156 | 0.087687
1350 | 22.5 | feeder2_681 | 0.0064891 | 0.072886 | 0.006496 | 0.072739
1350 | 22.5 | feeder2_682 | 0.0041242 | 0.070395 | 0.0041398 | 0.070241
1350 | 22.5 | feeder2_728 | 0.015461 | 0.13497 | 0.015394 | 0.13461
1350 | 22.5 | feeder2_724 | 0.017151 | 0.15013 | 0.017084 | 0.14974
1350 | 22.5 | feeder2_703 | 0.013606 | 0.088379 | 0.013632 | 0.088263
1350 | 22.5 | feeder2_704 | 0.017691 | 0.092921 | 0.017728 | 0.092813
1350 | 22.5 | feeder2_754 | 0.017363 | 0.15042 | 0.017291 | 0.15003
1350 | 22.5 | feeder2_747 | 0.017977 | 0.15687 | 0.017907 | 0.15647
1350 | 22.5 | feeder2_828 | 0.016111 | 0.13374 | 0.016046 | 0.13338
1350 | 22.5 | feeder2_763 | 0.016148 | 0.13881 | 0.016085 | 0.13844
1350 | 22.5 | feeder2_836 | 0.013978 | 0.15468 | 0.013907 | 0.15429
1350 | 22.5 | feeder2_758 | 0.01896 | 0.1639 | 0.018891 | 0.16351
1350 | 22.5 | feeder2_788 | 0.020947 | 0.16745 | 0.020878 | 0.16706
1350 | 22.5 | feeder2_812 | 0.021187 | 0.18141 | 0.02111 | 0.181
1350 | 22.5 | feeder2_947 | 0.020393 | 0.14447 | 0.020324 | 0.1441
1350 | 22.5 | feeder2_868 | 0.018108 | 0.14149 | 0.018043 | 0.14112
1350 | 22.5 | feeder2_785 | 0.015801 | 0.13801 | 0.015734 | 0.13765
1350 | 22.5 | feeder2_1176 | 0.010884 | 0.1388 | 0.010821 | 0.13844
1350 | 22.5 | feeder2_846 | 0.016904 | 0.13624 | 0.016841 | 0.13587
1350 | 22.5 | feeder2_911 | 0.015827 | 0.13812 | 0.015762 | 0.13775
1350 | 22.5 | feeder2_1107 | 0.025021 | 0.19823 | 0.024945 | 0.19784
1350 | 22.5 | feeder2_920 | 0.020786 | 0.18192 | 0.020708 | 0.1815
1350 | 22.5 | feeder2_926 | 0.020222 | 0.18292 | 0.020144 | 0.18249
1350 | 22.5 | feeder2_1239 | 0.02075 | 0.18167 | 0.020674 | 0.18126
1350 | 22.5 | feeder2_933 | 0.019968 | 0.18334 | 0.01989 | 0.18291
1350 | 22.5 | feeder2_1146 | 0.020253 | 0.18306 | 0.020179 | 0.18264
1350 | 22.5 | feeder2_1124 | 0.018946 | 0.18264 | 0.018865 | 0.18221
1350 | 22.5 | feeder2_942 | 0.019464 | 0.18517 | 0.019381 | 0.18472
1350 | 22.5 | feeder2_952 | 0.018384 | 0.18627 | 0.018306 | 0.18581
1350 | 22.5 | feeder2_965 | 0.019509 | 0.18538 | 0.019429 | 0.18494
1350 | 22.5 | feeder2_961 | 0.018214 | 0.18612 | 0.018135 | 0.18565
1350 | 22.5 | feeder2_963 | 0.018395 | 0.18633 | 0.018313 | 0.18587
1350 | 22.5 | feeder2_973 | 0.017446 | 0.18608 | 0.017363 | 0.1856
1350 | 22.5 | feeder2_1128 | 0.018015 | 0.18488 | 0.017928 | 0.18442
1350 | 22.5 | feeder2_1113 | 0.018446 | 0.18639 | 0.018366 | 0.18593
1350 | 22.5 | feeder2_1143 | 0.019162 | 0.19033 | 0.019079 | 0.18988
1350 | 22.5 | feeder2_1238 | 0.02321 | 0.19039 | 0.023128 | 0.18995
1350 | 22.5 | feeder2_979 | 0.019485 | 0.18525 | 0.019405 | 0.18481
1350 | 22.5 | feeder2_1236 | 0.016383 | 0.18647 | 0.016293 | 0.18598
1350 | 22.5 | feeder2_989 | 0.017446 | 0.18608 | 0.017359 | 0.1856
1350 | 22.5 | feeder2_1196 | 0.01982 | 0.18461 | 0.019743 | 0.18417
1350 | 22.5 | feeder2_1158 | 0.017056 | 0.18581 | 0.01697 | 0.18533
1350 | 22.5 | feeder2_1122 | 0.026614 | 0.20538 | 0.026541 | 0.20499
1350 | 22.5 | feeder2_1258 | 0.024508 | 0.19787 | 0.024434 | 0.19748
1350 | 22.5 | feeder2_1303 | 0.026701 | 0.2055 | 0.026627 | 0.20511
1350 | 22.5 | feeder2_1138 | 0.027872 | 0.21108 | 0.027792 | 0.2107
1350 | 22.5 | feeder2_1304 | 0.0286 | 0.21047 | 0.028528 | 0.21009
1350 | 22.5 | feeder2_1212 | 0.030578 | 0.22376 | 0.030504 | 0.22338
1350 | 22.5 | feeder2_1311 | 0.032392 | 0.22706 | 0.032313 | 0.22668
1350 | 22.5 | feeder2_1290 | 0.033438 | 0.23709 | 0.033369 | 0.23672
1350 | 22.5 | feeder2_1325 | 0.015391 | 0.18698 | 0.015306 | 0.18647
1350 | 22.5 | feeder2_1248 | 0.016375 | 0.18647 | 0.016286 | 0.18598
1350 | 22.5 | feeder2_1249 | 0.023862 | 0.19123 | 0.023783 | 0.19078
1350 | 22.5 | feeder2_1250 | 0.024399 | 0.19191 | 0.024322 | 0.19146
1350 | 22.5 | feeder2_1366 | 0.014392 | 0.18714 | 0.014307 | 0.18664
1350 | 22.5 | feeder2_1266 | 0.024446 | 0.19782 | 0.02437 | 0.19743
1350 | 22.5 | feeder2_1372 | 0.039713 | 0.24686 | 0.03964 | 0.24649
1350 | 22.5 | feeder2_1363 | 0.033893 | 0.2386 | 0.033821 | 0.23825
1350 | 22.5 | feeder2_1446 | 0.01558 | 0.18758 | 0.01549 | 0.18706
1350 | 22.5 | feeder2_1502 | 0.014203 | 0.18701 | 0.014116 | 0.18647
1350 | 22.5 | feeder2_1428 | 0.034154 | 0.2385 | 0.034081 | 0.23814
1350 | 22.5 | feeder2_1380 | 0.034639 | 0.2417 | 0.034567 | 0.24136
1350 | 22.5 | feeder2_1550 | 0.035992 | 0.24451 | 0.03592 | 0.24417
1350 | 22.5 | feeder2_1386 | 0.034814 | 0.24231 | 0.034742 | 0.24198
1350 | 22.5 | feeder2_1551 | 0.034891 | 0.24232 | 0.03482 | 0.24199
1350 | 22.5 | feeder2_1400 | 0.034918 | 0.2427 | 0.034851 | 0.24238
1350 | 22.5 | feeder2_1552 | 0.035258 | 0.24274 | 0.035194 | 0.24242
1350 | 22.5 | feeder2_1408 | 0.035169 | 0.2437 | 0.035105 | 0.24338
1350 | 22.5 | feeder2_1553 | 0.047952 | 0.24336 | 0.047896 | 0.24307
1350 | 22.5 | feeder2_1416 | 0.035163 | 0.24415 | 0.0351 | 0.24384
1350 | 22.5 | feeder2_1530 | 0.034354 | 0.24948 | 0.034284 | 0.24916
1350 | 22.5 | feeder2_1425 | 0.03498 | 0.24221 | 0.034911 | 0.2419
1350 | 22.5 | feeder2_1589 | 0.036957 | 0.24057 | 0.036887 | 0.24026
1350 | 22.5 | feeder2_1435 | 0.034908 | 0.24196 | 0.034842 | 0.24165
1350 | 22.5 | feeder2_1621 | 0.031558 | 0.23927 | 0.031491 | 0.23895
1350 | 22.5 | feeder2_1564 | 0.034954 | 0.24239 | 0.034893 | 0.24208
1350 | 22.5 | feeder2_1704 | 0.01142 | 0.18684 | 0.011333 | 0.1863
1350 | 22.5 | feeder2_1525 | 0.014078 | 0.18724 | 0.013989 | 0.1867
1350 | 22.5 | feeder2_1716 | 0.011398 | 0.1888 | 0.011304 | 0.18826
1350 | 22.5 | feeder2_1537 | 0.014035 | 0.1873 | 0.013946 | 0.18675
1350 | 22.5 | feeder2_1645 | 0.014 | 0.18726 | 0.013912 | 0.18671
1350 | 22.5 | feeder2_1561 | 0.013998 | 0.1874 | 0.013905 | 0.18684
1350 | 22.5 | feeder2_1657 | 0.014604 | 0.18828 | 0.014513 | 0.18772
1350 | 22.5 | feeder2_1570 | 0.013929 | 0.18721 | 0.013841 | 0.18665
1350 | 22.5 | feeder2_1756 | 0.019481 | 0.19345 | 0.019393 | 0.19289
1350 | 22.5 | feeder2_1588 | 0.013781 | 0.18663 | 0.013687 | 0.18607
1350 | 22.5 | feeder2_1628 | 0.01441 | 0.18735 | 0.01432 | 0.18679
1350 | 22.5 | feeder2_1598 | 0.01355 | 0.18569 | 0.013462 | 0.18513
1350 | 22.5 | feeder2_1816 | 0.013287 | 0.18551 | 0.013196 | 0.18494
1350 | 22.5 | feeder2_1765 | 0.010599 | 0.18433 | 0.010516 | 0.18376
1350 | 22.5 | feeder2_1641 | 0.012588 | 0.18198 | 0.012493 | 0.1814
1350 | 22.5 | feeder2_1689 | 0.011735 | 0.17868 | 0.011642 | 0.17808
1350 | 22.5 | feeder2_1744 | 0.012686 | 0.18209 | 0.01259 | 0.18151
1350 | 22.5 | feeder2_1817 | 0.011824 | 0.17729 | 0.011726 | 0.17668
1350 | 22.5 | feeder2_1779 | 0.010314 | 0.17805 | 0.01022 | 0.17745
1350 | 22.5 | feeder2_1800 | 0.011808 | 0.17641 | 0.011706 | 0.17581
1350 | 22.5 | feeder2_1818 | 0.0066707 | 0.17821 | 0.0065542 | 0.17759
1350 | 22.5 | feeder2_1753 | 0.012851 | 0.18227 | 0.012758 | 0.18169
1350 | 22.5 | feeder2_1754 | 0.012719 | 0.18213 | 0.012624 | 0.18155
1380 | 23 | secondary | 0.024008 | 0.032122 | 0.023991 | 0.032112
1380 | 23 | feeder2_44 | 0.0447 | 0.16761 | 0.044669 | 0.16756
1380 | 23 | feeder2_45 | 0.045492 | 0.17291 | 0.045463 | 0.17286
1380 | 23 | feeder2_46 | 0.04395 | 0.16713 | 0.043927 | 0.16708
1380 | 23 | feeder2_51 | 0.046854 | 0.18203 | 0.046823 | 0.18197
1380 | 23 | feeder2_48 | 0.045671 | 0.17356 | 0.045647 | 0.17351
1380 | 23 | feeder2_52 | 0.070056 | 0.17116 | 0.070035 | 0.17113
1380 | 23 | feeder2_68 | 0.050316 | 0.21148 | 0.050281 | 0.2114
1380 | 23 | feeder2_69 | 0.050141 | 0.21136 | 0.05011 | 0.21129
1380 | 23 | feeder2_71 | 0.050795 | 0.21539 | 0.050758 | 0.21532
1380 | 23 | feeder2_72 | 0.050897 | 0.21564 | 0.050868 | 0.21557
1380 | 23 | feeder2_73 | 0.05231 | 0.22763 | 0.05227 | 0.22756
1380 | 23 | feeder2_74 | 0.056787 | 0.2243 | 0.056757 | 0.22423
1380 | 23 | feeder2_77 | 0.053617 | 0.23857 | 0.053578 | 0.23849
1380 | 23 | feeder2_79 | 0.052307 | 0.23921 | 0.052272 | 0.23912
1380 | 23 | feeder2_81 | 0.055931 | 0.25578 | 0.055891 | 0.25568
1380 | 23 | feeder2_82 | 0.056184 | 0.25639 | 0.056147 | 0.25629
1380 | 23 | feeder2_116 | 0.067044 | 0.33265 | 0.066993 | 0.33252
1380 | 23 | feeder2_119 | 0.06955 | 0.32979 | 0.069504 | 0.32965
1380 | 23 | feeder2_120 | 0.07131 | 0.3627 | 0.071258 | 0.36255
1380 | 23 | feeder2_248 | 0.071486 | 0.36245 | 0.07143 | 0.36229
1380 | 23 | feeder2_124 | 0.074009 | 0.38131 | 0.073957 | 0.38114
1380 | 23 | feeder2_282 | 0.074112 | 0.38146 | 0.07406 | 0.3813
1380 | 23 | feeder2_275 | 0.078656 | 0.37611 | 0.078601 | 0.37594
1380 | 23 | feeder2_151 | 0.078433 | 0.41696 | 0.078372 | 0.41678
1380 | 23 | feeder2_295 | 0.078336 | 0.41691 | 0.078277 | 0.41672
1380 | 23 | feeder2_311 | 0.075985 | 0.41566 | 0.075924 | 0.41548
1380 | 23 | feeder2_201 | 0.086618 | 0.47838 | 0.086553 | 0.47816
1380 | 23 | feeder2_314 | 0.087023 | 0.47895 | 0.086957 | 0.47873
1380 | 23 | feeder2_342 | 0.098486 | 0.56449 | 0.098413 | 0.56424
1380 | 23 | feeder2_368 | 0.098089 | 0.56635 | 0.098014 | 0.56609
1380 | 23 | feeder2_347 | 0.10452 | 0.60362 | 0.10444 | 0.60336
1380 | 23 | feeder2_353 | 0.10728 | 0.62184 | 0.1072 | 0.62157
1380 | 23 | feeder2_518 | 0.10575 | 0.60605 | 0.10567 | 0.60579
1380 | 23 | feeder2_365 | 0.11041 | 0.64248 | 0.11032 | 0.64221
1380 | 23 | feeder2_653 | 0.10752 | 0.62093 | 0.10744 | 0.62066
1380 | 23 | feeder2_377 | 0.1123 | 0.65346 | 0.11221 | 0.65318
1380 | 23 | feeder2_622 | 0.10744 | 0.64377 | 0.10735 | 0.64349
1380 | 23 | feeder2_451 | 0.098764 | 0.56711 | 0.098692 | 0.56685
1380 | 23 | feeder2_383 | 0.097338 | 0.569 | 0.097261 | 0.56873
1380 | 23 | feeder2_385 | 0.11448 | 0.66614 | 0.11439 | 0.66586
1380 | 23 | feeder2_621 | 0.1122 | 0.6534 | 0.11212 | 0.65312
1380 | 23 | feeder2_611 | 0.097359 | 0.56887 | 0.097282 | 0.5686
1380 | 23 | feeder2_405 | 0.097294 | 0.56918 | 0.097218 | 0.56891
1380 | 23 | feeder2_461 | 0.12338 | 0.71801 | 0.12329 | 0.71772
1380 | 23 | feeder2_594 | 0.11452 | 0.66597 | 0.11443 | 0.66569
1380 | 23 | feeder2_732 | 0.097329 | 0.56897 | 0.097251 | 0.56871
1380 | 23 | feeder2_417 | 0.09698 | 0.57061 | 0.096908 | 0.57034
1380 | 23 | feeder2_663 | 0.095818 | 0.57119 | 0.095738 | 0.57092
1380 | 23 | feeder2_444 | 0.096865 | 0.5716 | 0.09679 | 0.57133
1380 | 23 | feeder2_759 | 0.11532 | 0.59442 | 0.11525 | 0.59415
1380 | 23 | feeder2_842 | 0.091188 | 0.56932 | 0.091111 | 0.56905
1380 | 23 | feeder2_459 | 0.096524 | 0.57066 | 0.096447 | 0.57039
1380 | 23 | feeder2_702 | 0.097203 | 0.57148 | 0.097128 | 0.57121
1380 | 23 | feeder2_493 | 0.095147 | 0.5668 | 0.095071 | 0.56652
1380 | 23 | feeder2_651 | 0.12319 | 0.71791 | 0.12311 | 0.71761
1380 | 23 | feeder2_684 | 0.13065 | 0.7605 | 0.13056 | 0.76019
1380 | 23 | feeder2_674 | 0.095427 | 0.56593 | 0.095351 | 0.56566
1380 | 23 | feeder2_696 | 0.091361 | 0.55947 | 0.091286 | 0.55918
1380 | 23 | feeder2_681 | 0.095941 | 0.56527 | 0.095865 | 0.56499
1380 | 23 | feeder2_682 | 0.095926 | 0.56335 | 0.095852 | 0.56308
1380 | 23 | feeder2_728 | 0.13082 | 0.76149 | 0.13072 | 0.76119
1380 | 23 | feeder2_724 | 0.13768 | 0.80183 | 0.13758 | 0.80151
1380 | 23 | feeder2_703 | 0.088884 | 0.55845 | 0.088806 | 0.55816
1380 | 23 | feeder2_704 | 0.085986 | 0.55772 | 0.085907 | 0.55743
1380 | 23 | feeder2_754 | 0.1379 | 0.80212 | 0.13781 | 0.8018
1380 | 23 | feeder2_747 | 0.14052 | 0.81858 | 0.14042 | 0.81826
1380 | 23 | feeder2_828 | 0.13082 | 0.76147 | 0.13073 | 0.76116
1380 | 23 | feeder2_763 | 0.13107 | 0.76298 | 0.13097 | 0.76268
1380 | 23 | feeder2_836 | 0.13503 | 0.8168 | 0.13493 | 0.81648
1380 | 23 | feeder2_758 | 0.14337 | 0.83406 | 0.14327 | 0.83373
1380 | 23 | feeder2_788 | 0.14366 | 0.83443 | 0.14356 | 0.83411
1380 | 23 | feeder2_812 | 0.15207 | 0.88142 | 0.15196 | 0.88109
1380 | 23 | feeder2_947 | 0.13399 | 0.76856 | 0.1339 | 0.76825
1380 | 23 | feeder2_868 | 0.13124 | 0.7632 | 0.13114 | 0.7629
1380 | 23 | feeder2_785 | 0.13092 | 0.76252 | 0.13083 | 0.76221
1380 | 23 | feeder2_1176 | 0.12772 | 0.7606 | 0.12763 | 0.76029
1380 | 23 | feeder2_846 | 0.13095 | 0.76239 | 0.13086 | 0.76208
1380 | 23 | feeder2_911 | 0.13095 | 0.76262 | 0.13086 | 0.76231
1380 | 23 | feeder2_1107 | 0.15107 | 0.87779 | 0.15096 | 0.87746
1380 | 23 | feeder2_920 | 0.15479 | 0.89578 | 0.15468 | 0.89545
1380 | 23 | feeder2_926 | 0.1589 | 0.91739 | 0.15879 | 0.91704
1380 | 23 | feeder2_1239 | 0.15472 | 0.89554 | 0.15462 | 0.8952
1380 | 23 | feeder2_933 | 0.16069 | 0.92674 | 0.16058 | 0.92639
1380 | 23 | feeder2_1146 | 0.15905 | 0.91842 | 0.15895 | 0.91807
1380 | 23 | feeder2_1124 | 0.16035 | 0.92639 | 0.16024 | 0.92605
1380 | 23 | feeder2_942 | 0.16524 | 0.95075 | 0.16513 | 0.95039
1380 | 23 | feeder2_952 | 0.16437 | 0.95135 | 0.16425 | 0.95098
1380 | 23 | feeder2_965 | 0.16623 | 0.95527 | 0.16612 | 0.95491
1380 | 23 | feeder2_961 | 0.16421 | 0.95109 | 0.1641 | 0.95072
1380 | 23 | feeder2_963 | 0.16438 | 0.95142 | 0.16427 | 0.95104
1380 | 23 | feeder2_973 | 0.16352 | 0.95042 | 0.16341 | 0.95005
1380 | 23 | feeder2_1128 | 0.16395 | 0.94986 | 0.16383 | 0.94949
1380 | 23 | feeder2_1113 | 0.16442 | 0.95182 | 0.1643 | 0.95145
1380 | 23 | feeder2_1143 | 0.16512 | 0.95494 | 0.16501 | 0.95456
1380 | 23 | feeder2_1238 | 0.22784 | 1.0317 | 0.22772 | 1.0314
1380 | 23 | feeder2_979 | 0.16623 | 0.955 | 0.16612 | 0.95464
1380 | 23 | feeder2_1236 | 0.16252 | 0.94954 | 0.1624 | 0.94914
1380 | 23 | feeder2_989 | 0.16352 | 0.95042 | 0.16341 | 0.95005
1380 | 23 | feeder2_1196 | 0.16703 | 0.95381 | 0.16692 | 0.95345
1380 | 23 | feeder2_1158 | 0.1634 | 0.95032 | 0.16329 | 0.94994
1380 | 23 | feeder2_1122 | 0.15103 | 0.87625 | 0.15093 | 0.87593
1380 | 23 | feeder2_1258 | 0.14934 | 0.87827 | 0.14924 | 0.87795
1380 | 23 | feeder2_1303 | 0.15103 | 0.87739 | 0.15092 | 0.87707
1380 | 23 | feeder2_1138 | 0.15095 | 0.87464 | 0.15085 | 0.87433
1380 | 23 | feeder2_1304 | 0.15231 | 0.8728 | 0.15221 | 0.87249
1380 | 23 | feeder2_1212 | 0.15075 | 0.87278 | 0.15065 | 0.87247
1380 | 23 | feeder2_1311 | 0.15077 | 0.8739 | 0.15067 | 0.8736
1380 | 23 | feeder2_1290 | 0.1504 | 0.86967 | 0.1503 | 0.86937
1380 | 23 | feeder2_1325 | 0.16128 | 0.94891 | 0.16116 | 0.94851
1380 | 23 | feeder2_1248 | 0.16251 | 0.94954 | 0.1624 | 0.94914
1380 | 23 | feeder2_1249 | 0.24691 | 1.054 | 0.24679 | 1.0537
1380 | 23 | feeder2_1250 | 0.22789 | 1.0318 | 0.22777 | 1.0314
1380 | 23 | feeder2_1366 | 0.16149 | 0.94904 | 0.16138 | 0.94864
1380 | 23 | feeder2_1266 | 0.14861 | 0.87854 | 0.14851 | 0.87821
1380 | 23 | feeder2_1372 | 0.15165 | 0.8722 | 0.15155 | 0.8719
1380 | 23 | feeder2_1363 | 0.14939 | 0.86296 | 0.14929 | 0.86268
1380 | 23 | feeder2_1446 | 0.16141 | 0.94908 | 0.16129 | 0.94868
1380 | 23 | feeder2_1502 | 0.15985 | 0.94799 | 0.15972 | 0.94757
1380 | 23 | feeder2_1428 | 0.15069 | 0.86147 | 0.15059 | 0.86118
1380 | 23 | feeder2_1380 | 0.148 | 0.85742 | 0.1479 | 0.85714
1380 | 23 | feeder2_1550 | 0.14779 | 0.85884 | 0.1477 | 0.85857
1380 | 23 | feeder2_1386 | 0.14726 | 0.85404 | 0.14716 | 0.85377
1380 | 23 | feeder2_1551 | 0.14742 | 0.85379 | 0.14733 | 0.85352
1380 | 23 | feeder2_1400 | 0.14692 | 0.85249 | 0.14682 | 0.85223
1380 | 23 | feeder2_1552 | 0.14694 | 0.85245 | 0.14684 | 0.85219
1380 | 23 | feeder2_1408 | 0.14624 | 0.84935 | 0.14614 | 0.84909
1380 | 23 | feeder2_1553 | 0.15162 | 0.84343 | 0.15153 | 0.84318
1380 | 23 | feeder2_1416 | 0.14611 | 0.84878 | 0.14602 | 0.84852
1380 | 23 | feeder2_1530 | 0.14629 | 0.84903 | 0.1462 | 0.84877
1380 | 23 | feeder2_1425 | 0.14583 | 0.84756 | 0.14573 | 0.8473
1380 | 23 | feeder2_1589 | 0.14589 | 0.84748 | 0.1458 | 0.84721
1380 | 23 | feeder2_1435 | 0.14577 | 0.84733 | 0.14568 | 0.84706
1380 | 23 | feeder2_1621 | 0.14266 | 0.84504 | 0.14256 | 0.84478
1380 | 23 | feeder2_1564 | 0.14566 | 0.84735 | 0.14556 | 0.84709
1380 | 23 | feeder2_1704 | 0.15958 | 0.94783 | 0.15945 | 0.9474
1380 | 23 | feeder2_1525 | 0.15949 | 0.94783 | 0.15937 | 0.9474
1380 | 23 | feeder2_1716 | 0.15931 | 0.9477 | 0.15918 | 0.94727
1380 | 23 | feeder2_1537 | 0.1591 | 0.94766 | 0.15897 | 0.94723
1380 | 23 | feeder2_1645 | 0.15908 | 0.94765 | 0.15895 | 0.94721
1380 | 23 | feeder2_1561 | 0.15866 | 0.94749 | 0.15853 | 0.94705
1380 | 23 | feeder2_1657 | 0.15878 | 0.94764 | 0.15865 | 0.9472
1380 | 23 | feeder2_1570 | 0.15847 | 0.94737 | 0.15833 | 0.94693
1380 | 23 | feeder2_1756 | 0.15871 | 0.94942 | 0.15858 | 0.94898
1380 | 23 | feeder2_1588 | 0.15826 | 0.94713 | 0.15813 | 0.94669
1380 | 23 | feeder2_1628 | 0.1589 | 0.94793 | 0.15877 | 0.94749
1380 | 23 | feeder2_1598 | 0.15795 | 0.94659 | 0.15783 | 0.94614
1380 | 23 | feeder2_1816 | 0.15765 | 0.94633 | 0.15752 | 0.94589
1380 | 23 | feeder2_1765 | 0.15405 | 0.94401 | 0.15392 | 0.94356
1380 | 23 | feeder2_1641 | 0.1567 | 0.94538 | 0.15657 | 0.94492
1380 | 23 | feeder2_1689 | 0.15548 | 0.9434 | 0.15535 | 0.94294
1380 | 23 | feeder2_1744 | 0.15678 | 0.94593 | 0.15664 | 0.94547
1380 | 23 | feeder2_1817 | 0.15547 | 0.94338 | 0.15534 | 0.9429
1380 | 23 | feeder2_1779 | 0.15444 | 0.94386 | 0.15431 | 0.94339
1380 | 23 | feeder2_1800 | 0.15574 | 0.94203 | 0.1556 | 0.94156
1380 | 23 | feeder2_1818 | 0.14828 | 0.93607 | 0.14813 | 0.93557
1380 | 23 | feeder2_1753 | 0.1569 | 0.94752 | 0.15677 | 0.94706
1380 | 23 | feeder2_1754 | 0.1568 | 0.94597 | 0.15667 | 0.94551
1410 | 23.5 | secondary | 0.019541 | 0.021944 | 0.019531 | 0.021927
1410 | 23.5 | feeder2_44 | 0.036365 | 0.11445 | 0.036354 | 0.11437
1410 | 23.5 | feeder2_45 | 0.036983 | 0.11801 | 0.036974 | 0.11793
1410 | 23.5 | feeder2_46 | 0.037036 | 0.11473 | 0.037026 | 0.11465
1410 | 23.5 | feeder2_51 | 0.03807 | 0.12428 | 0.03806 | 0.1242
1410 | 23.5 | feeder2_48 | 0.036977 | 0.11737 | 0.036964 | 0.11729
1410 | 23.5 | feeder2_52 | 0.033942 | 0.12778 | 0.033931 | 0.12769
1410 | 23.5 | feeder2_68 | 0.04132 | 0.14093 | 0.041308 | 0.14083
1410 | 23.5 | feeder2_69 | 0.041482 | 0.14101 | 0.041473 | 0.14092
1410 | 23.5 | feeder2_71 | 0.041749 | 0.14314 | 0.041737 | 0.14304
1410 | 23.5 | feeder2_72 | 0.041724 | 0.14289 | 0.041712 | 0.14279
1410 | 23.5 | feeder2_73 | 0.043097 | 0.15008 | 0.043081 | 0.14998
1410 | 23.5 | feeder2_74 | 0.03752 | 0.15475 | 0.0375 | 0.15464
1410 | 23.5 | feeder2_77 | 0.044356 | 0.15546 | 0.044343 | 0.15535
1410 | 23.5 | feeder2_79 | 0.044697 | 0.15562 | 0.044682 | 0.15552
1410 | 23.5 | feeder2_81 | 0.046314 | 0.16393 | 0.046299 | 0.16383
1410 | 23.5 | feeder2_82 | 0.046295 | 0.16333 | 0.046279 | 0.16322
1410 | 23.5 | feeder2_116 | 0.055164 | 0.20317 | 0.055154 | 0.20305
1410 | 23.5 | feeder2_119 | 0.053025 | 0.20464 | 0.05301 | 0.20451
1410 | 23.5 | feeder2_120 | 0.058571 | 0.21727 | 0.058557 | 0.21714
1410 | 23.5 | feeder2_248 | 0.058168 | 0.21752 | 0.058154 | 0.21739
1410 | 23.5 | feeder2_124 | 0.060685 | 0.22593 | 0.060675 | 0.2258
1410 | 23.5 | feeder2_282 | 0.060666 | 0.22577 | 0.060653 | 0.22564
1410 | 23.5 | feeder2_275 | 0.059481 | 0.22719 | 0.059467 | 0.22706
1410 | 23.5 | feeder2_151 | 0.064545 | 0.24039 | 0.064532 | 0.24026
1410 | 23.5 | feeder2_295 | 0.064638 | 0.24046 | 0.064627 | 0.24033
1410 | 23.5 | feeder2_311 | 0.066624 | 0.24178 | 0.066613 | 0.24165
1410 | 23.5 | feeder2_201 | 0.070343 | 0.26271 | 0.070334 | 0.26257
1410 | 23.5 | feeder2_314 | 0.071993 | 0.26039 | 0.071985 | 0.26025
1410 | 23.5 | feeder2_342 | 0.078447 | 0.29984 | 0.078436 | 0.29969
1410 | 23.5 | feeder2_368 | 0.082219 | 0.30794 | 0.082206 | 0.30781
1410 | 23.5 | feeder2_347 | 0.077101 | 0.30356 | 0.077089 | 0.30338
1410 | 23.5 | feeder2_353 | 0.076615 | 0.30713 | 0.076607 | 0.30693
1410 | 23.5 | feeder2_518 | 0.076961 | 0.30069 | 0.076955 | 0.30051
1410 | 23.5 | feeder2_365 | 0.076153 | 0.31095 | 0.076141 | 0.31073
1410 | 23.5 | feeder2_653 | 0.075403 | 0.30783 | 0.075386 | 0.30763
1410 | 23.5 | feeder2_377 | 0.075807 | 0.3131 | 0.075797 | 0.31288
1410 | 23.5 | feeder2_622 | 0.077104 | 0.3107 | 0.077089 | 0.31049
1410 | 23.5 | feeder2_451 | 0.083355 | 0.30571 | 0.083348 | 0.30558
1410 | 23.5 | feeder2_383 | 0.088238 | 0.32362 | 0.088222 | 0.32352
1410 | 23.5 | feeder2_385 | 0.075403 | 0.31563 | 0.075388 | 0.31539
1410 | 23.5 | feeder2_621 | 0.075907 | 0.31317 | 0.075889 | 0.31294
1410 | 23.5 | feeder2_611 | 0.088061 | 0.32369 | 0.088052 | 0.32358
1410 | 23.5 | feeder2_405 | 0.088617 | 0.32462 | 0.088607 | 0.32452
1410 | 23.5 | feeder2_461 | 0.073825 | 0.32634 | 0.073812 | 0.32605
1410 | 23.5 | feeder2_594 | 0.075147 | 0.3158 | 0.075129 | 0.31556
1410 | 23.5 | feeder2_732 | 0.088339 | 0.32473 | 0.088322 | 0.32463
1410 | 23.5 | feeder2_417 | 0.091482 | 0.33227 | 0.091468 | 0.33218
1410 | 23.5 | feeder2_663 | 0.091632 | 0.3324 | 0.091623 | 0.33231
1410 | 23.5 | feeder2_444 | 0.093648 | 0.33815 | 0.093638 | 0.33806
1410 | 23.5 | feeder2_759 | 0.093263 | 0.33432 | 0.093248 | 0.33424
1410 | 23.5 | feeder2_842 | 0.1199 | 0.35919 | 0.11988 | 0.35914
1410 | 23.5 | feeder2_459 | 0.093963 | 0.33916 | 0.093949 | 0.33908
1410 | 23.5 | feeder2_702 | 0.09376 | 0.3375 | 0.093748 | 0.33742
1410 | 23.5 | feeder2_493 | 0.095242 | 0.34367 | 0.095224 | 0.34359
1410 | 23.5 | feeder2_651 | 0.074013 | 0.32644 | 0.073994 | 0.32614
1410 | 23.5 | feeder2_684 | 0.072512 | 0.33568 | 0.072496 | 0.33534
1410 | 23.5 | feeder2_674 | 0.094429 | 0.34394 | 0.094415 | 0.34386
1410 | 23.5 | feeder2_696 | 0.099674 | 0.35609 | 0.099657 | 0.35603
1410 | 23.5 | feeder2_681 | 0.094365 | 0.34396 | 0.094347 | 0.34388
1410 | 23.5 | feeder2_682 | 0.091201 | 0.34509 | 0.09118 | 0.345
1410 | 23.5 | feeder2_728 | 0.072594 | 0.334 | 0.072581 | 0.33366
1410 | 23.5 | feeder2_724 | 0.07128 | 0.34975 | 0.071256 | 0.34936
1410 | 23.5 | feeder2_703 | 0.10363 | 0.35937 | 0.10361 | 0.35931
1410 | 23.5 | feeder2_704 | 0.10392 | 0.3596 | 0.1039 | 0.35954
1410 | 23.5 | feeder2_754 | 0.071229 | 0.34946 | 0.071211 | 0.34908
1410 | 23.5 | feeder2_747 | 0.07082 | 0.35581 | 0.070795 | 0.35541
1410 | 23.5 | feeder2_828 | 0.072555 | 0.33402 | 0.072541 | 0.33369
1410 | 23.5 | feeder2_763 | 0.072735 | 0.33147 | 0.072716 | 0.33113
1410 | 23.5 | feeder2_836 | 0.075332 | 0.35754 | 0.075309 | 0.35714
1410 | 23.5 | feeder2_758 | 0.069974 | 0.36018 | 0.069945 | 0.35976
1410 | 23.5 | feeder2_788 | 0.069904 | 0.35981 | 0.069876 | 0.35939
1410 | 23.5 | feeder2_812 | 0.067516 | 0.37486 | 0.067486 | 0.37438
1410 | 23.5 | feeder2_947 | 0.072301 | 0.3251 | 0.072299 | 0.32476
1410 | 23.5 | feeder2_868 | 0.072707 | 0.33126 | 0.072694 | 0.33092
1410 | 23.5 | feeder2_785 | 0.073001 | 0.33147 | 0.072984 | 0.33113
1410 | 23.5 | feeder2_1176 | 0.076106 | 0.3331 | 0.076087 | 0.33276
1410 | 23.5 | feeder2_846 | 0.072797 | 0.33163 | 0.072785 | 0.33129
1410 | 23.5 | feeder2_911 | 0.073215 | 0.33046 | 0.073197 | 0.33011
1410 | 23.5 | feeder2_1107 | 0.065623 | 0.3909 | 0.065585 | 0.3904
1410 | 23.5 | feeder2_920 | 0.067392 | 0.37479 | 0.067357 | 0.3743
1410 | 23.5 | feeder2_926 | 0.067237 | 0.37433 | 0.067209 | 0.37383
1410 | 23.5 | feeder2_1239 | 0.067357 | 0.37521 | 0.06732 | 0.37472
1410 | 23.5 | feeder2_933 | 0.067174 | 0.37416 | 0.06714 | 0.37365
1410 | 23.5 | feeder2_1146 | 0.067212 | 0.37418 | 0.067181 | 0.37367
1410 | 23.5 | feeder2_1124 | 0.068093 | 0.37376 | 0.068061 | 0.37326
1410 | 23.5 | feeder2_942 | 0.06675 | 0.37399 | 0.066718 | 0.37346
1410 | 23.5 | feeder2_952 | 0.066468 | 0.37583 | 0.066434 | 0.37528
1410 | 23.5 | feeder2_965 | 0.066706 | 0.37372 | 0.06667 | 0.37319
1410 | 23.5 | feeder2_961 | 0.066479 | 0.3763 | 0.066447 | 0.37574
1410 | 23.5 | feeder2_963 | 0.066459 | 0.37577 | 0.066428 | 0.37522
1410 | 23.5 | feeder2_973 | 0.066643 | 0.3776 | 0.066618 | 0.37704
1410 | 23.5 | feeder2_1128 | 0.066296 | 0.37835 | 0.066265 | 0.37779
1410 | 23.5 | feeder2_1113 | 0.066436 | 0.37571 | 0.066401 | 0.37516
1410 | 23.5 | feeder2_1143 | 0.065879 | 0.37196 | 0.065847 | 0.37141
1410 | 23.5 | feeder2_1238 | 0.067222 | 0.36842 | 0.067201 | 0.36789
1410 | 23.5 | feeder2_979 | 0.066697 | 0.37382 | 0.066671 | 0.3733
1410 | 23.5 | feeder2_1236 | 0.066865 | 0.37948 | 0.066834 | 0.37891
1410 | 23.5 | feeder2_989 | 0.066643 | 0.3776 | 0.066618 | 0.37704
1410 | 23.5 | feeder2_1196 | 0.066199 | 0.37433 | 0.066169 | 0.3738
1410 | 23.5 | feeder2_1158 | 0.066788 | 0.37767 | 0.066755 | 0.37711
1410 | 23.5 | feeder2_1122 | 0.064808 | 0.39748 | 0.064769 | 0.39697
1410 | 23.5 | feeder2_1258 | 0.066117 | 0.39062 | 0.06608 | 0.39012
1410 | 23.5 | feeder2_1303 | 0.064755 | 0.39736 | 0.064718 | 0.39685
1410 | 23.5 | feeder2_1138 | 0.064192 | 0.40279 | 0.064148 | 0.40226
1410 | 23.5 | feeder2_1304 | 0.063013 | 0.4042 | 0.062966 | 0.40368
1410 | 23.5 | feeder2_1212 | 0.062987 | 0.41313 | 0.062946 | 0.4126
1410 | 23.5 | feeder2_1311 | 0.064624 | 0.41216 | 0.064587 | 0.41162
1410 | 23.5 | feeder2_1290 | 0.061586 | 0.42717 | 0.061534 | 0.42662
1410 | 23.5 | feeder2_1325 | 0.066873 | 0.38179 | 0.066843 | 0.38119
1410 | 23.5 | feeder2_1248 | 0.066871 | 0.37949 | 0.066839 | 0.37891
1410 | 23.5 | feeder2_1249 | 0.067472 | 0.3669 | 0.067458 | 0.36637
1410 | 23.5 | feeder2_1250 | 0.06721 | 0.36836 | 0.067189 | 0.36783
1410 | 23.5 | feeder2_1366 | 0.068209 | 0.3796 | 0.06818 | 0.37903
1410 | 23.5 | feeder2_1266 | 0.066181 | 0.39065 | 0.066137 | 0.39015
1410 | 23.5 | feeder2_1372 | 0.060703 | 0.42537 | 0.060656 | 0.42483
1410 | 23.5 | feeder2_1363 | 0.060738 | 0.445 | 0.060677 | 0.44444
1410 | 23.5 | feeder2_1446 | 0.066838 | 0.38163 | 0.066807 | 0.38103
1410 | 23.5 | feeder2_1502 | 0.06692 | 0.3846 | 0.066894 | 0.38398
1410 | 23.5 | feeder2_1428 | 0.06046 | 0.44541 | 0.060403 | 0.44485
1410 | 23.5 | feeder2_1380 | 0.059978 | 0.46623 | 0.059908 | 0.46566
1410 | 23.5 | feeder2_1550 | 0.060397 | 0.46594 | 0.060328 | 0.46537
1410 | 23.5 | feeder2_1386 | 0.059731 | 0.47685 | 0.059656 | 0.47628
1410 | 23.5 | feeder2_1551 | 0.056358 | 0.48073 | 0.056284 | 0.48016
1410 | 23.5 | feeder2_1400 | 0.059748 | 0.48102 | 0.059672 | 0.48044
1410 | 23.5 | feeder2_1552 | 0.059687 | 0.48117 | 0.059617 | 0.48059
1410 | 23.5 | feeder2_1408 | 0.059818 | 0.48958 | 0.059739 | 0.489
1410 | 23.5 | feeder2_1553 | 0.052638 | 0.50628 | 0.052532 | 0.50569
1410 | 23.5 | feeder2_1416 | 0.059883 | 0.49055 | 0.059803 | 0.48997
1410 | 23.5 | feeder2_1530 | 0.059738 | 0.49032 | 0.059663 | 0.48974
1410 | 23.5 | feeder2_1425 | 0.060032 | 0.49253 | 0.059955 | 0.49196
1410 | 23.5 | feeder2_1589 | 0.05993 | 0.49274 | 0.059849 | 0.49216
1410 | 23.5 | feeder2_1435 | 0.060062 | 0.49292 | 0.059985 | 0.49233
1410 | 23.5 | feeder2_1621 | 0.06353 | 0.49361 | 0.063453 | 0.49303
1410 | 23.5 | feeder2_1564 | 0.059748 | 0.49631 | 0.059666 | 0.49573
1410 | 23.5 | feeder2_1704 | 0.067196 | 0.38468 | 0.067165 | 0.38406
1410 | 23.5 | feeder2_1525 | 0.06691 | 0.38528 | 0.066885 | 0.38465
1410 | 23.5 | feeder2_1716 | 0.06764 | 0.38407 | 0.067607 | 0.38345
1410 | 23.5 | feeder2_1537 | 0.066847 | 0.38621 | 0.066821 | 0.38557
1410 | 23.5 | feeder2_1645 | 0.065854 | 0.38726 | 0.065828 | 0.38662
1410 | 23.5 | feeder2_1561 | 0.06689 | 0.38667 | 0.066859 | 0.38602
1410 | 23.5 | feeder2_1657 | 0.06686 | 0.38653 | 0.06683 | 0.38588
1410 | 23.5 | feeder2_1570 | 0.066914 | 0.3869 | 0.066887 | 0.38625
1410 | 23.5 | feeder2_1756 | 0.070854 | 0.38471 | 0.070836 | 0.38404
1410 | 23.5 | feeder2_1588 | 0.06692 | 0.3873 | 0.066896 | 0.38665
1410 | 23.5 | feeder2_1628 | 0.066762 | 0.38656 | 0.066738 | 0.3859
1410 | 23.5 | feeder2_1598 | 0.06696 | 0.38802 | 0.066933 | 0.38736
1410 | 23.5 | feeder2_1816 | 0.067322 | 0.38818 | 0.067302 | 0.38752
1410 | 23.5 | feeder2_1765 | 0.07071 | 0.3893 | 0.07068 | 0.38865
1410 | 23.5 | feeder2_1641 | 0.066751 | 0.39075 | 0.066726 | 0.39007
1410 | 23.5 | feeder2_1689 | 0.066529 | 0.39381 | 0.066505 | 0.39311
1410 | 23.5 | feeder2_1744 | 0.067293 | 0.39037 | 0.067271 | 0.38968
1410 | 23.5 | feeder2_1817 | 0.066525 | 0.39386 | 0.066493 | 0.39316
1410 | 23.5 | feeder2_1779 | 0.066738 | 0.39338 | 0.066713 | 0.39268
1410 | 23.5 | feeder2_1800 | 0.061929 | 0.39855 | 0.0619 | 0.39785
1410 | 23.5 | feeder2_1818 | 0.069083 | 0.3926 | 0.069081 | 0.39187
1410 | 23.5 | feeder2_1753 | 0.067238 | 0.39019 | 0.067213 | 0.38951
1410 | 23.5 | feeder2_1754 | 0.067684 | 0.39014 | 0.06766 | 0.38946
1440 | 24 | secondary | 0.020634 | 0.019178 | 0.020607 | 0.019146
1440 | 24 | feeder2_44 | 0.038399 | 0.10002 | 0.038347 | 0.099858
1440 | 24 | feeder2_45 | 0.039005 | 0.10342 | 0.038948 | 0.10324
1440 | 24 | feeder2_46 | 0.040474 | 0.096718 | 0.040421 | 0.096549
1440 | 24 | feeder2_51 | 0.040076 | 0.10939 | 0.040022 | 0.10921
1440 | 24 | feeder2_48 | 0.038806 | 0.10294 | 0.038751 | 0.10277
1440 | 24 | feeder2_52 | 0.034208 | 0.11709 | 0.034155 | 0.11692
1440 | 24 | feeder2_68 | 0.043364 | 0.12336 | 0.043303 | 0.12315
1440 | 24 | feeder2_69 | 0.04354 | 0.12333 | 0.043483 | 0.12313
1440 | 24 | feeder2_71 | 0.043798 | 0.12521 | 0.043735 | 0.125
1440 | 24 | feeder2_72 | 0.043701 | 0.12501 | 0.043639 | 0.1248
1440 | 24 | feeder2_73 | 0.045161 | 0.13103 | 0.0451 | 0.13081
1440 | 24 | feeder2_74 | 0.040663 | 0.13921 | 0.040595 | 0.13899
1440 | 24 | feeder2_77 | 0.046364 | 0.13481 | 0.046295 | 0.13458
1440 | 24 | feeder2_79 | 0.048257 | 0.13137 | 0.048193 | 0.13115
1440 | 24 | feeder2_81 | 0.047996 | 0.14202 | 0.047923 | 0.14178
1440 | 24 | feeder2_82 | 0.047807 | 0.14157 | 0.047742 | 0.14133
1440 | 24 | feeder2_116 | 0.055432 | 0.17492 | 0.055355 | 0.17461
1440 | 24 | feeder2_119 | 0.052204 | 0.18007 | 0.052122 | 0.17977
1440 | 24 | feeder2_120 | 0.058308 | 0.18443 | 0.058229 | 0.18411
1440 | 24 | feeder2_248 | 0.057993 | 0.18491 | 0.057906 | 0.18457
1440 | 24 | feeder2_124 | 0.060093 | 0.19012 | 0.060006 | 0.18977
1440 | 24 | feeder2_282 | 0.060038 | 0.18999 | 0.059956 | 0.18965
1440 | 24 | feeder2_275 | 0.058854 | 0.19131 | 0.058771 | 0.19096
1440 | 24 | feeder2_151 | 0.06338 | 0.19932 | 0.063289 | 0.19895
1440 | 24 | feeder2_295 | 0.06348 | 0.19932 | 0.06339 | 0.19894
1440 | 24 | feeder2_311 | 0.065674 | 0.1991 | 0.06559 | 0.19872
1440 | 24 | feeder2_201 | 0.068271 | 0.21468 | 0.068174 | 0.21427
1440 | 24 | feeder2_314 | 0.068394 | 0.21354 | 0.068301 | 0.21313
1440 | 24 | feeder2_342 | 0.075648 | 0.23919 | 0.075545 | 0.23872
1440 | 24 | feeder2_368 | 0.078825 | 0.23984 | 0.07872 | 0.23935
1440 | 24 | feeder2_347 | 0.074954 | 0.25125 | 0.074844 | 0.25077
1440 | 24 | feeder2_353 | 0.074816 | 0.25891 | 0.074703 | 0.25843
1440 | 24 | feeder2_518 | 0.074311 | 0.24928 | 0.074205 | 0.24881
1440 | 24 | feeder2_365 | 0.074703 | 0.267 | 0.074591 | 0.26652
1440 | 24 | feeder2_653 | 0.073846 | 0.26032 | 0.073732 | 0.25984
1440 | 24 | feeder2_377 | 0.074608 | 0.27154 | 0.074492 | 0.27106
1440 | 24 | feeder2_622 | 0.075374 | 0.26688 | 0.075257 | 0.2664
1440 | 24 | feeder2_451 | 0.078754 | 0.23961 | 0.078645 | 0.23912
1440 | 24 | feeder2_383 | 0.084002 | 0.24234 | 0.083896 | 0.24183
1440 | 24 | feeder2_385 | 0.074492 | 0.27689 | 0.074373 | 0.27641
1440 | 24 | feeder2_621 | 0.074713 | 0.27152 | 0.074591 | 0.27104
1440 | 24 | feeder2_611 | 0.083849 | 0.24254 | 0.083742 | 0.24202
1440 | 24 | feeder2_405 | 0.084327 | 0.24254 | 0.084222 | 0.24203
1440 | 24 | feeder2_461 | 0.074059 | 0.29912 | 0.07393 | 0.29865
1440 | 24 | feeder2_594 | 0.074277 | 0.27721 | 0.074151 | 0.27673
1440 | 24 | feeder2_732 | 0.078626 | 0.24824 | 0.07852 | 0.24772
1440 | 24 | feeder2_417 | 0.087129 | 0.24294 | 0.087024 | 0.24242
1440 | 24 | feeder2_663 | 0.087706 | 0.24194 | 0.087596 | 0.24141
1440 | 24 | feeder2_444 | 0.089178 | 0.24372 | 0.089072 | 0.24319
1440 | 24 | feeder2_759 | 0.089715 | 0.23957 | 0.08961 | 0.23904
1440 | 24 | feeder2_842 | 0.11421 | 0.24756 | 0.1141 | 0.24701
1440 | 24 | feeder2_459 | 0.089487 | 0.24404 | 0.089386 | 0.24351
1440 | 24 | feeder2_702 | 0.089946 | 0.24139 | 0.089838 | 0.24087
1440 | 24 | feeder2_493 | 0.090746 | 0.24644 | 0.09064 | 0.2459
1440 | 24 | feeder2_651 | 0.074258 | 0.29905 | 0.074127 | 0.29857
1440 | 24 | feeder2_684 | 0.073673 | 0.31838 | 0.073533 | 0.31791
1440 | 24 | feeder2_674 | 0.089931 | 0.2474 | 0.089827 | 0.24687
1440 | 24 | feeder2_696 | 0.095025 | 0.25001 | 0.094921 | 0.24947
1440 | 24 | feeder2_681 | 0.089878 | 0.24746 | 0.089771 | 0.24693
1440 | 24 | feeder2_682 | 0.086723 | 0.2513 | 0.086612 | 0.25077
1440 | 24 | feeder2_728 | 0.073689 | 0.31692 | 0.073555 | 0.31645
1440 | 24 | feeder2_724 | 0.073359 | 0.34228 | 0.073218 | 0.34182
1440 | 24 | feeder2_703 | 0.098333 | 0.25068 | 0.098223 | 0.25013
1440 | 24 | feeder2_704 | 0.09952 | 0.25092 | 0.099409 | 0.25037
1440 | 24 | feeder2_754 | 0.07326 | 0.34212 | 0.073116 | 0.34165
1440 | 24 | feeder2_747 | 0.073265 | 0.35233 | 0.073117 | 0.35187
1440 | 24 | feeder2_828 | 0.073657 | 0.31697 | 0.073523 | 0.3165
1440 | 24 | feeder2_763 | 0.073722 | 0.31468 | 0.07359 | 0.31421
1440 | 24 | feeder2_836 | 0.073482 | 0.35223 | 0.073336 | 0.35177
1440 | 24 | feeder2_758 | 0.073168 | 0.36109 | 0.073023 | 0.36063
1440 | 24 | feeder2_788 | 0.074586 | 0.36196 | 0.074445 | 0.36151
1440 | 24 | feeder2_812 | 0.072967 | 0.38757 | 0.072808 | 0.38711
1440 | 24 | feeder2_947 | 0.072148 | 0.31128 | 0.072017 | 0.31082
1440 | 24 | feeder2_868 | 0.073991 | 0.31474 | 0.07386 | 0.31427
1440 | 24 | feeder2_785 | 0.073934 | 0.31415 | 0.073799 | 0.31368
1440 | 24 | feeder2_1176 | 0.078964 | 0.30922 | 0.07883 | 0.30874
1440 | 24 | feeder2_846 | 0.073075 | 0.3149 | 0.072935 | 0.31443
1440 | 24 | feeder2_911 | 0.073915 | 0.31407 | 0.073782 | 0.3136
1440 | 24 | feeder2_1107 | 0.07136 | 0.4125 | 0.071205 | 0.41203
1440 | 24 | feeder2_920 | 0.073403 | 0.38817 | 0.073245 | 0.3877
1440 | 24 | feeder2_926 | 0.074062 | 0.38894 | 0.073901 | 0.38847
1440 | 24 | feeder2_1239 | 0.073398 | 0.38835 | 0.073239 | 0.38788
1440 | 24 | feeder2_933 | 0.074355 | 0.38911 | 0.074194 | 0.38864
1440 | 24 | feeder2_1146 | 0.074071 | 0.38987 | 0.073911 | 0.38941
1440 | 24 | feeder2_1124 | 0.074505 | 0.38903 | 0.074344 | 0.38856
1440 | 24 | feeder2_942 | 0.07507 | 0.3896 | 0.074909 | 0.38913
1440 | 24 | feeder2_952 | 0.076565 | 0.38816 | 0.076398 | 0.38768
1440 | 24 | feeder2_965 | 0.075013 | 0.38989 | 0.074848 | 0.38942
1440 | 24 | feeder2_961 | 0.076753 | 0.38801 | 0.076583 | 0.38753
1440 | 24 | feeder2_963 | 0.07656 | 0.38816 | 0.076392 | 0.38768
1440 | 24 | feeder2_973 | 0.07781 | 0.38507 | 0.077635 | 0.38457
1440 | 24 | feeder2_1128 | 0.076655 | 0.39179 | 0.076486 | 0.39132
1440 | 24 | feeder2_1113 | 0.077196 | 0.38868 | 0.077029 | 0.3882
1440 | 24 | feeder2_1143 | 0.076152 | 0.38676 | 0.07598 | 0.38628
1440 | 24 | feeder2_1238 | 0.078289 | 0.39187 | 0.078127 | 0.39142
1440 | 24 | feeder2_979 | 0.074968 | 0.39017 | 0.074801 | 0.3897
1440 | 24 | feeder2_1236 | 0.079171 | 0.38182 | 0.078997 | 0.38131
1440 | 24 | feeder2_989 | 0.077812 | 0.38506 | 0.077639 | 0.38457
1440 | 24 | feeder2_1196 | 0.073737 | 0.39131 | 0.073567 | 0.39083
1440 | 24 | feeder2_1158 | 0.078485 | 0.38373 | 0.078313 | 0.38324
1440 | 24 | feeder2_1122 | 0.07076 | 0.42229 | 0.070603 | 0.42183
1440 | 24 | feeder2_1258 | 0.071665 | 0.41235 | 0.071508 | 0.41188
1440 | 24 | feeder2_1303 | 0.070689 | 0.42221 | 0.070535 | 0.42175
1440 | 24 | feeder2_1138 | 0.070326 | 0.43004 | 0.070164 | 0.42957
1440 | 24 | feeder2_1304 | 0.068483 | 0.43385 | 0.068328 | 0.43338
1440 | 24 | feeder2_1212 | 0.06949 | 0.44335 | 0.069337 | 0.44289
1440 | 24 | feeder2_1311 | 0.070073 | 0.44395 | 0.069912 | 0.44349
1440 | 24 | feeder2_1290 | 0.068634 | 0.45944 | 0.068478 | 0.45897
1440 | 24 | feeder2_1325 | 0.080717 | 0.37824 | 0.080532 | 0.37771
1440 | 24 | feeder2_1248 | 0.079178 | 0.38182 | 0.079003 | 0.38131
1440 | 24 | feeder2_1249 | 0.078475 | 0.3918 | 0.078315 | 0.39135
1440 | 24 | feeder2_1250 | 0.080483 | 0.39352 | 0.080328 | 0.39308
1440 | 24 | feeder2_1366 | 0.080803 | 0.3807 | 0.080625 | 0.38019
1440 | 24 | feeder2_1266 | 0.07173 | 0.41233 | 0.07157 | 0.41186
1440 | 24 | feeder2_1372 | 0.067667 | 0.45847 | 0.06751 | 0.458
1440 | 24 | feeder2_1363 | 0.068315 | 0.47822 | 0.068159 | 0.47775
1440 | 24 | feeder2_1446 | 0.082195 | 0.37941 | 0.08201 | 0.37889
1440 | 24 | feeder2_1502 | 0.082432 | 0.37304 | 0.082242 | 0.37249
1440 | 24 | feeder2_1428 | 0.068112 | 0.47876 | 0.06796 | 0.47829
1440 | 24 | feeder2_1380 | 0.068147 | 0.50021 | 0.067994 | 0.49973
1440 | 24 | feeder2_1550 | 0.068395 | 0.50061 | 0.068239 | 0.50014
1440 | 24 | feeder2_1386 | 0.068197 | 0.51079 | 0.068046 | 0.51031
1440 | 24 | feeder2_1551 | 0.066652 | 0.51341 | 0.066502 | 0.51293
1440 | 24 | feeder2_1400 | 0.068259 | 0.5152 | 0.068103 | 0.51472
1440 | 24 | feeder2_1552 | 0.066529 | 0.51655 | 0.066379 | 0.51606
1440 | 24 | feeder2_1408 | 0.068545 | 0.52358 | 0.068393 | 0.5231
1440 | 24 | feeder2_1553 | 0.064396 | 0.54223 | 0.064254 | 0.54174
1440 | 24 | feeder2_1416 | 0.068559 | 0.52379 | 0.068402 | 0.5233
1440 | 24 | feeder2_1530 | 0.068386 | 0.52364 | 0.068235 | 0.52316
1440 | 24 | feeder2_1425 | 0.068613 | 0.52426 | 0.068456 | 0.52377
1440 | 24 | feeder2_1589 | 0.066817 | 0.52567 | 0.066665 | 0.52518
1440 | 24 | feeder2_1435 | 0.068648 | 0.52421 | 0.068492 | 0.52372
1440 | 24 | feeder2_1621 | 0.070829 | 0.52315 | 0.070678 | 0.52266
1440 | 24 | feeder2_1564 | 0.068669 | 0.52458 | 0.068515 | 0.52409
1440 | 24 | feeder2_1704 | 0.083772 | 0.37054 | 0.083583 | 0.36999
1440 | 24 | feeder2_1525 | 0.082698 | 0.37262 | 0.082507 | 0.37206
1440 | 24 | feeder2_1716 | 0.084993 | 0.36763 | 0.084799 | 0.36706
1440 | 24 | feeder2_1537 | 0.08286 | 0.3729 | 0.082669 | 0.37234
1440 | 24 | feeder2_1645 | 0.082821 | 0.37301 | 0.082624 | 0.37244
1440 | 24 | feeder2_1561 | 0.083042 | 0.37317 | 0.082846 | 0.37259
1440 | 24 | feeder2_1657 | 0.082988 | 0.37309 | 0.08279 | 0.37251
1440 | 24 | feeder2_1570 | 0.083127 | 0.37331 | 0.082931 | 0.37273
1440 | 24 | feeder2_1756 | 0.084747 | 0.3745 | 0.084553 | 0.37393
1440 | 24 | feeder2_1588 | 0.083207 | 0.37338 | 0.083008 | 0.37279
1440 | 24 | feeder2_1628 | 0.083138 | 0.37328 | 0.082942 | 0.3727
1440 | 24 | feeder2_1598 | 0.083316 | 0.37351 | 0.083123 | 0.37292
1440 | 24 | feeder2_1816 | 0.083684 | 0.37337 | 0.083487 | 0.37278
1440 | 24 | feeder2_1765 | 0.087302 | 0.37149 | 0.0871 | 0.37089
1440 | 24 | feeder2_1641 | 0.083462 | 0.37494 | 0.083261 | 0.37433
1440 | 24 | feeder2_1689 | 0.083617 | 0.37629 | 0.083405 | 0.37565
1440 | 24 | feeder2_1744 | 0.083414 | 0.37488 | 0.083209 | 0.37426
1440 | 24 | feeder2_1817 | 0.083616 | 0.37638 | 0.083409 | 0.37574
1440 | 24 | feeder2_1779 | 0.083936 | 0.37559 | 0.083725 | 0.37496
1440 | 24 | feeder2_1800 | 0.080665 | 0.37991 | 0.080457 | 0.37927
1440 | 24 | feeder2_1818 | 0.087227 | 0.37336 | 0.086995 | 0.37271
1440 | 24 | feeder2_1753 | 0.083329 | 0.37477 | 0.083126 | 0.37415
1440 | 24 | feeder2_1754 | 0.0834 | 0.37486 | 0.0832 | 0.37425

## Line_loading
Time_sample | Line | Phase | I_limit_A | OPF_I_A | DSS_I_A | OPF_loading_percent | DSS_loading_percent
30 | feeder2_line1 | 1 | 354.6 | 70.037 | 70.0343 | 19.751 | 19.7502
30 | feeder2_line1 | 2 | 354.6 | 87.466 | 87.4645 | 24.6661 | 24.6657
30 | feeder2_line1 | 3 | 354.6 | 76.9801 | 76.9855 | 21.709 | 21.7105
30 | feeder2_line2 | 1 | 354.6 | 70.7652 | 70.7623 | 19.9563 | 19.9555
30 | feeder2_line2 | 2 | 354.6 | 87.4661 | 87.4645 | 24.6661 | 24.6657
30 | feeder2_line2 | 3 | 354.6 | 76.9802 | 76.9855 | 21.709 | 21.7105
30 | feeder2_line3 | 1 | 80.1 | 1.4318 | 1.4318 | 1.7875 | 1.7875
30 | feeder2_line3 | 2 | 80.1 | 5.7232e-07 | 1.0576e-06 | 7.1451e-07 | 1.3204e-06
30 | feeder2_line3 | 3 | 80.1 | 5.7175e-07 | 1.0566e-06 | 7.138e-07 | 1.3191e-06
30 | feeder2_line4 | 1 | 354.6 | 70.7653 | 70.7623 | 19.9564 | 19.9555
30 | feeder2_line4 | 2 | 354.6 | 87.7366 | 87.7349 | 24.7424 | 24.7419
30 | feeder2_line4 | 3 | 354.6 | 76.9804 | 76.9855 | 21.7091 | 21.7105
30 | feeder2_line5 | 1 | 80.1 | 5.7166e-07 | 9.975e-07 | 7.1369e-07 | 1.2453e-06
30 | feeder2_line5 | 2 | 80.1 | 0.27933 | 0.27933 | 0.34872 | 0.34872
30 | feeder2_line5 | 3 | 80.1 | 5.7179e-07 | 9.9773e-07 | 7.1384e-07 | 1.2456e-06
30 | feeder2_line6 | 1 | 80.1 | 5.7171e-07 | 1.1735e-06 | 7.1375e-07 | 1.4651e-06
30 | feeder2_line6 | 2 | 80.1 | 5.7245e-07 | 1.175e-06 | 7.1467e-07 | 1.467e-06
30 | feeder2_line6 | 3 | 80.1 | 1.474 | 1.474 | 1.8402 | 1.8402
30 | feeder2_line7 | 1 | 354.6 | 70.7654 | 70.7623 | 19.9564 | 19.9555
30 | feeder2_line7 | 2 | 354.6 | 87.7368 | 87.7349 | 24.7425 | 24.7419
30 | feeder2_line7 | 3 | 354.6 | 77.4751 | 77.4801 | 21.8486 | 21.85
30 | feeder2_line8 | 1 | 80.1 | 0.07269 | 0.07269 | 0.090749 | 0.090749
30 | feeder2_line8 | 2 | 80.1 | 5.727e-07 | 1.1335e-06 | 7.1498e-07 | 1.4151e-06
30 | feeder2_line8 | 3 | 80.1 | 5.7199e-07 | 1.1321e-06 | 7.1409e-07 | 1.4134e-06
30 | feeder2_line9 | 1 | 354.6 | 70.8369 | 70.8337 | 19.9766 | 19.9757
30 | feeder2_line9 | 2 | 354.6 | 87.7368 | 87.7349 | 24.7425 | 24.7419
30 | feeder2_line9 | 3 | 354.6 | 77.4752 | 77.4801 | 21.8486 | 21.85
30 | feeder2_line10 | 1 | 80.1 | 8.4534e-07 | 1.4945e-06 | 1.0554e-06 | 1.8658e-06
30 | feeder2_line10 | 2 | 80.1 | 0.072517 | 0.072517 | 0.090533 | 0.090533
30 | feeder2_line10 | 3 | 80.1 | 8.4554e-07 | 1.4949e-06 | 1.0556e-06 | 1.8663e-06
30 | feeder2_line11 | 1 | 354.6 | 70.8369 | 70.8337 | 19.9766 | 19.9757
30 | feeder2_line11 | 2 | 354.6 | 87.808 | 87.806 | 24.7625 | 24.762
30 | feeder2_line11 | 3 | 354.6 | 77.4752 | 77.4801 | 21.8486 | 21.85
30 | feeder2_line12 | 1 | 80.1 | 5.4701e-07 | 9.9142e-07 | 6.8291e-07 | 1.2377e-06
30 | feeder2_line12 | 2 | 80.1 | 5.4802e-07 | 9.9299e-07 | 6.8417e-07 | 1.2397e-06
30 | feeder2_line12 | 3 | 80.1 | 0.061828 | 0.061828 | 0.077188 | 0.077189
30 | feeder2_line13 | 1 | 354.6 | 70.8369 | 70.8337 | 19.9766 | 19.9757
30 | feeder2_line13 | 2 | 354.6 | 87.8079 | 87.806 | 24.7625 | 24.762
30 | feeder2_line13 | 3 | 354.6 | 77.5354 | 77.5403 | 21.8656 | 21.867
30 | feeder2_line14 | 1 | 80.1 | 0.27523 | 0.27523 | 0.34361 | 0.34361
30 | feeder2_line14 | 2 | 80.1 | 2.9886e-07 | 6.476e-07 | 3.7311e-07 | 8.0849e-07
30 | feeder2_line14 | 3 | 80.1 | 2.9853e-07 | 6.4672e-07 | 3.727e-07 | 8.074e-07
30 | feeder2_line15 | 1 | 354.6 | 71.104 | 71.1008 | 20.0519 | 20.051
30 | feeder2_line15 | 2 | 354.6 | 87.808 | 87.806 | 24.7625 | 24.762
30 | feeder2_line15 | 3 | 354.6 | 77.5354 | 77.5403 | 21.8656 | 21.867
30 | feeder2_line16 | 1 | 80.1 | 5.7204e-07 | 1.0306e-06 | 7.1415e-07 | 1.2866e-06
30 | feeder2_line16 | 2 | 80.1 | 0.25458 | 0.25458 | 0.31783 | 0.31783
30 | feeder2_line16 | 3 | 80.1 | 5.7221e-07 | 1.0309e-06 | 7.1436e-07 | 1.287e-06
30 | feeder2_line17 | 1 | 354.6 | 71.104 | 71.1008 | 20.0519 | 20.051
30 | feeder2_line17 | 2 | 354.6 | 88.0533 | 88.0514 | 24.8317 | 24.8312
30 | feeder2_line17 | 3 | 354.6 | 77.5354 | 77.5404 | 21.8656 | 21.867
30 | feeder2_line18 | 1 | 80.1 | 5.4744e-07 | 7.3813e-07 | 6.8344e-07 | 9.2151e-07
30 | feeder2_line18 | 2 | 80.1 | 5.4886e-07 | 7.3976e-07 | 6.8522e-07 | 9.2355e-07
30 | feeder2_line18 | 3 | 80.1 | 1.4139 | 1.4139 | 1.7652 | 1.7652
30 | feeder2_line19 | 1 | 354.6 | 71.104 | 71.1008 | 20.0519 | 20.051
30 | feeder2_line19 | 2 | 354.6 | 88.0533 | 88.0514 | 24.8317 | 24.8312
30 | feeder2_line19 | 3 | 354.6 | 78.3319 | 78.3367 | 22.0902 | 22.0916
30 | feeder2_line20 | 1 | 99 | 5.4756e-07 | 8.8517e-07 | 5.5309e-07 | 8.9411e-07
30 | feeder2_line20 | 2 | 99 | 5.4909e-07 | 8.8727e-07 | 5.5463e-07 | 8.9624e-07
30 | feeder2_line20 | 3 | 99 | 1.5839 | 1.5839 | 1.5999 | 1.5999
30 | feeder2_line21 | 1 | 354.6 | 71.1041 | 71.1008 | 20.0519 | 20.051
30 | feeder2_line21 | 2 | 354.6 | 88.0535 | 88.0514 | 24.8318 | 24.8312
30 | feeder2_line21 | 3 | 354.6 | 79.113 | 79.1177 | 22.3105 | 22.3118
30 | feeder2_line22 | 1 | 99 | 5.7259e-07 | 1.0149e-06 | 5.7837e-07 | 1.0251e-06
30 | feeder2_line22 | 2 | 99 | 0.093671 | 0.093671 | 0.094617 | 0.094617
30 | feeder2_line22 | 3 | 99 | 5.7282e-07 | 1.0153e-06 | 5.7861e-07 | 1.0256e-06
30 | feeder2_line23 | 1 | 99 | 5.7258e-07 | 9.5002e-07 | 5.7837e-07 | 9.5961e-07
30 | feeder2_line23 | 2 | 99 | 5.7402e-07 | 9.5236e-07 | 5.7982e-07 | 9.6198e-07
30 | feeder2_line23 | 3 | 99 | 0.12735 | 0.12736 | 0.12864 | 0.12864
30 | feeder2_line24 | 1 | 354.6 | 71.1042 | 71.1008 | 20.0519 | 20.051
30 | feeder2_line24 | 2 | 354.6 | 88.1452 | 88.1431 | 24.8576 | 24.857
30 | feeder2_line24 | 3 | 354.6 | 79.24 | 79.2447 | 22.3463 | 22.3476
30 | feeder2_line25 | 1 | 99 | 0.093947 | 0.093946 | 0.094896 | 0.094895
30 | feeder2_line25 | 2 | 99 | 4.9595e-08 | 6.9267e-07 | 5.0096e-08 | 6.9967e-07
30 | feeder2_line25 | 3 | 99 | 5.0032e-08 | 6.9117e-07 | 5.0538e-08 | 6.9816e-07
30 | feeder2_line26 | 1 | 99 | 0.2205 | 0.2205 | 0.22272 | 0.22272
30 | feeder2_line26 | 2 | 99 | 5.4946e-07 | 8.5818e-07 | 5.5501e-07 | 8.6685e-07
30 | feeder2_line26 | 3 | 99 | 5.4798e-07 | 8.5632e-07 | 5.5351e-07 | 8.6497e-07
30 | feeder2_line27 | 1 | 354.6 | 71.4107 | 71.4073 | 20.1384 | 20.1374
30 | feeder2_line27 | 2 | 354.6 | 88.1452 | 88.1431 | 24.8576 | 24.857
30 | feeder2_line27 | 3 | 354.6 | 79.24 | 79.2447 | 22.3463 | 22.3476
30 | feeder2_line28 | 1 | 99 | 2.54e-06 | 7.1077e-07 | 2.5656e-06 | 7.1795e-07
30 | feeder2_line28 | 2 | 99 | 0.10838 | 0.10838 | 0.10948 | 0.10948
30 | feeder2_line28 | 3 | 99 | 2.5409e-06 | 7.1117e-07 | 2.5665e-06 | 7.1835e-07
30 | feeder2_line29 | 1 | 354.6 | 71.4107 | 71.4073 | 20.1384 | 20.1374
30 | feeder2_line29 | 2 | 354.6 | 88.253 | 88.2508 | 24.888 | 24.8874
30 | feeder2_line29 | 3 | 354.6 | 79.24 | 79.2447 | 22.3463 | 22.3476
30 | feeder2_line30 | 1 | 266.4 | 11.3292 | 11.3289 | 4.2527 | 4.2526
30 | feeder2_line30 | 2 | 266.4 | 1.6427 | 1.6428 | 0.61661 | 0.61668
30 | feeder2_line30 | 3 | 266.4 | 1.5527 | 1.5528 | 0.58284 | 0.58289
30 | feeder2_line31 | 1 | 354.6 | 82.4084 | 82.4045 | 23.2398 | 23.2387
30 | feeder2_line31 | 2 | 354.6 | 89.0716 | 89.069 | 25.1189 | 25.1182
30 | feeder2_line31 | 3 | 354.6 | 80.1636 | 80.1679 | 22.6068 | 22.608
30 | feeder2_line32 | 1 | 354.6 | 82.4084 | 82.4045 | 23.2398 | 23.2387
30 | feeder2_line32 | 2 | 354.6 | 89.3226 | 89.32 | 25.1897 | 25.1889
30 | feeder2_line32 | 3 | 354.6 | 80.1637 | 80.1679 | 22.6068 | 22.608
30 | feeder2_line33 | 1 | 99 | 5.004e-08 | 6.8638e-07 | 5.0546e-08 | 6.9332e-07
30 | feeder2_line33 | 2 | 99 | 0.25778 | 0.25778 | 0.26039 | 0.26039
30 | feeder2_line33 | 3 | 99 | 5.0164e-08 | 6.8679e-07 | 5.0671e-08 | 6.9373e-07
30 | feeder2_line34 | 1 | 354.6 | 82.4084 | 82.4045 | 23.2398 | 23.2387
30 | feeder2_line34 | 2 | 354.6 | 89.3225 | 89.32 | 25.1897 | 25.1889
30 | feeder2_line34 | 3 | 354.6 | 80.4308 | 80.435 | 22.6821 | 22.6833
30 | feeder2_line35 | 1 | 99 | 2.9932e-07 | 7.6023e-07 | 3.0235e-07 | 7.6791e-07
30 | feeder2_line35 | 2 | 99 | 3.0021e-07 | 7.6283e-07 | 3.0324e-07 | 7.7054e-07
30 | feeder2_line35 | 3 | 99 | 0.27528 | 0.27529 | 0.27806 | 0.27807
30 | feeder2_line36 | 1 | 354.6 | 91.6216 | 91.6178 | 25.838 | 25.8369
30 | feeder2_line36 | 2 | 354.6 | 89.3225 | 89.32 | 25.1897 | 25.1889
30 | feeder2_line36 | 3 | 354.6 | 80.4307 | 80.435 | 22.6821 | 22.6833
30 | feeder2_line37 | 1 | 99 | 9.4353 | 9.4353 | 9.5306 | 9.5306
30 | feeder2_line37 | 2 | 99 | 3.0027e-07 | 8.4424e-07 | 3.033e-07 | 8.5277e-07
30 | feeder2_line37 | 3 | 99 | 2.9956e-07 | 8.4179e-07 | 3.0259e-07 | 8.5029e-07
30 | feeder2_line38 | 1 | 99 | 3.2414e-07 | 7.7573e-07 | 3.2741e-07 | 7.8357e-07
30 | feeder2_line38 | 2 | 99 | 0.21253 | 0.21253 | 0.21468 | 0.21467
30 | feeder2_line38 | 3 | 99 | 3.2443e-07 | 7.7631e-07 | 3.2771e-07 | 7.8415e-07
30 | feeder2_line39 | 1 | 266.4 | 11.3292 | 11.3289 | 4.2527 | 4.2526
30 | feeder2_line39 | 2 | 266.4 | 1.5051 | 1.5054 | 0.56499 | 0.56508
30 | feeder2_line39 | 3 | 266.4 | 1.5527 | 1.5528 | 0.58285 | 0.58289
30 | feeder2_line40 | 1 | 354.6 | 91.7147 | 91.7107 | 25.8643 | 25.8632
30 | feeder2_line40 | 2 | 354.6 | 89.3226 | 89.32 | 25.1897 | 25.1889
30 | feeder2_line40 | 3 | 354.6 | 80.4308 | 80.435 | 22.6821 | 22.6833
30 | feeder2_line41 | 1 | 99 | 0.093805 | 0.093804 | 0.094752 | 0.094751
30 | feeder2_line41 | 2 | 99 | 4.9629e-08 | 7.3782e-07 | 5.0131e-08 | 7.4528e-07
30 | feeder2_line41 | 3 | 99 | 5.0208e-08 | 7.3564e-07 | 5.0715e-08 | 7.4307e-07
30 | feeder2_line42 | 1 | 99 | 2.9909e-07 | 7.4867e-07 | 3.0211e-07 | 7.5623e-07
30 | feeder2_line42 | 2 | 99 | 3e-07 | 7.5131e-07 | 3.0303e-07 | 7.589e-07
30 | feeder2_line42 | 3 | 99 | 0.18992 | 0.18992 | 0.19184 | 0.19184
30 | feeder2_line43 | 1 | 266.4 | 11.3291 | 11.3289 | 4.2527 | 4.2526
30 | feeder2_line43 | 2 | 266.4 | 1.5052 | 1.5054 | 0.56503 | 0.56508
30 | feeder2_line43 | 3 | 266.4 | 1.4134 | 1.4135 | 0.53054 | 0.53058
30 | feeder2_line44 | 1 | 354.6 | 91.7147 | 91.7107 | 25.8643 | 25.8632
30 | feeder2_line44 | 2 | 354.6 | 89.3226 | 89.32 | 25.1897 | 25.1889
30 | feeder2_line44 | 3 | 354.6 | 81.2618 | 81.266 | 22.9165 | 22.9177
30 | feeder2_line45 | 1 | 99 | 5.006e-08 | 5.7997e-07 | 5.0565e-08 | 5.8583e-07
30 | feeder2_line45 | 2 | 99 | 4.9631e-08 | 5.8195e-07 | 5.0132e-08 | 5.8783e-07
30 | feeder2_line45 | 3 | 99 | 1.5848 | 1.5848 | 1.6008 | 1.6008
30 | feeder2_line46 | 1 | 99 | 5.7317e-07 | 1.3572e-06 | 5.7895e-07 | 1.3709e-06
30 | feeder2_line46 | 2 | 99 | 5.7521e-07 | 1.362e-06 | 5.8102e-07 | 1.3758e-06
30 | feeder2_line46 | 3 | 99 | 1.3134 | 1.3134 | 1.3266 | 1.3266
30 | feeder2_line47 | 1 | 266.4 | 11.3292 | 11.3289 | 4.2527 | 4.2526
30 | feeder2_line47 | 2 | 266.4 | 1.5054 | 1.5054 | 0.5651 | 0.56508
30 | feeder2_line47 | 3 | 266.4 | 0.17012 | 0.16985 | 0.063859 | 0.063759
30 | feeder2_line48 | 1 | 99 | 0.13644 | 0.13644 | 0.13782 | 0.13781
30 | feeder2_line48 | 2 | 99 | 4.9579e-08 | 7.3333e-07 | 5.008e-08 | 7.4074e-07
30 | feeder2_line48 | 3 | 99 | 5.0125e-08 | 7.3139e-07 | 5.0631e-08 | 7.3878e-07
30 | feeder2_line49 | 1 | 266.4 | 11.1957 | 11.1954 | 4.2026 | 4.2025
30 | feeder2_line49 | 2 | 266.4 | 1.5054 | 1.5054 | 0.56509 | 0.56508
30 | feeder2_line49 | 3 | 266.4 | 0.1701 | 0.16985 | 0.063852 | 0.063759
30 | feeder2_line50 | 1 | 99 | 5.731e-07 | 1.235e-06 | 5.7889e-07 | 1.2475e-06
30 | feeder2_line50 | 2 | 99 | 1.4776 | 1.4776 | 1.4926 | 1.4925
30 | feeder2_line50 | 3 | 99 | 5.7367e-07 | 1.2363e-06 | 5.7947e-07 | 1.2487e-06
30 | feeder2_line51 | 1 | 99 | 10.5401 | 10.54 | 10.6465 | 10.6465
30 | feeder2_line51 | 2 | 99 | 5.7519e-07 | 1.3456e-06 | 5.81e-07 | 1.3592e-06
30 | feeder2_line51 | 3 | 99 | 5.7365e-07 | 1.3421e-06 | 5.7945e-07 | 1.3556e-06
30 | feeder2_line52 | 1 | 266.4 | 0.65551 | 0.65541 | 0.24606 | 0.24603
30 | feeder2_line52 | 2 | 266.4 | 0.048831 | 0.048726 | 0.01833 | 0.018291
30 | feeder2_line52 | 3 | 266.4 | 0.16996 | 0.16985 | 0.0638 | 0.063759
30 | feeder2_line53 | 1 | 99 | 5.4809e-07 | 7.5377e-07 | 5.5362e-07 | 7.6138e-07
30 | feeder2_line53 | 2 | 99 | 0.048726 | 0.048726 | 0.049219 | 0.049218
30 | feeder2_line53 | 3 | 99 | 5.4861e-07 | 7.5451e-07 | 5.5415e-07 | 7.6213e-07
30 | feeder2_line54 | 1 | 266.4 | 0.65533 | 0.65541 | 0.246 | 0.24603
30 | feeder2_line54 | 2 | 266.4 | 8.5755e-05 | 4.6403e-06 | 3.219e-05 | 1.7419e-06
30 | feeder2_line54 | 3 | 266.4 | 0.16977 | 0.16985 | 0.063728 | 0.063758
30 | feeder2_line55 | 1 | 99 | 0.18102 | 0.18102 | 0.18285 | 0.18285
30 | feeder2_line55 | 2 | 99 | 4.966e-08 | 7.336e-07 | 5.0162e-08 | 7.4101e-07
30 | feeder2_line55 | 3 | 99 | 5.0268e-08 | 7.3129e-07 | 5.0775e-08 | 7.3867e-07
30 | feeder2_line56 | 1 | 354.6 | 91.8925 | 91.8885 | 25.9144 | 25.9133
30 | feeder2_line56 | 2 | 354.6 | 89.3226 | 89.32 | 25.1897 | 25.1889
30 | feeder2_line56 | 3 | 354.6 | 81.2619 | 81.266 | 22.9165 | 22.9177
30 | feeder2_line57 | 1 | 99 | 7.506e-07 | 1.544e-06 | 7.5818e-07 | 1.5596e-06
30 | feeder2_line57 | 2 | 99 | 7.4365e-07 | 1.5496e-06 | 7.5116e-07 | 1.5652e-06
30 | feeder2_line57 | 3 | 99 | 0.16985 | 0.16985 | 0.17156 | 0.17157
30 | feeder2_line58 | 1 | 266.4 | 0.6554 | 0.65541 | 0.24602 | 0.24603
30 | feeder2_line58 | 2 | 266.4 | 1.9022e-05 | 2.694e-06 | 7.1404e-06 | 1.0113e-06
30 | feeder2_line58 | 3 | 266.4 | 1.8962e-05 | 2.6874e-06 | 7.1181e-06 | 1.0088e-06
30 | feeder2_line59 | 1 | 99 | 5.0037e-08 | 5.3669e-07 | 5.0542e-08 | 5.4211e-07
30 | feeder2_line59 | 2 | 99 | 4.9575e-08 | 5.3864e-07 | 5.0076e-08 | 5.4409e-07
30 | feeder2_line59 | 3 | 99 | 0.10827 | 0.10827 | 0.10936 | 0.10936
30 | feeder2_line60 | 1 | 99 | 2.9906e-07 | 8.111e-07 | 3.0208e-07 | 8.1929e-07
30 | feeder2_line60 | 2 | 99 | 3e-07 | 8.1405e-07 | 3.0303e-07 | 8.2228e-07
30 | feeder2_line60 | 3 | 99 | 0.061718 | 0.061719 | 0.062341 | 0.062342
30 | feeder2_line61 | 1 | 266.4 | 0.19843 | 0.1986 | 0.074485 | 0.074549
30 | feeder2_line61 | 2 | 266.4 | 1.2533 | 1.2535 | 0.47045 | 0.47052
30 | feeder2_line61 | 3 | 266.4 | 1.0445 | 1.0447 | 0.39208 | 0.39216
30 | feeder2_line62 | 1 | 354.6 | 92.0881 | 92.0843 | 25.9696 | 25.9685
30 | feeder2_line62 | 2 | 354.6 | 90.2229 | 90.2204 | 25.4436 | 25.4429
30 | feeder2_line62 | 3 | 354.6 | 81.9302 | 81.9347 | 23.105 | 23.1062
30 | feeder2_line63 | 1 | 99 | 0.35986 | 0.35986 | 0.36349 | 0.36349
30 | feeder2_line63 | 2 | 99 | 5.7522e-07 | 1.2239e-06 | 5.8103e-07 | 1.2363e-06
30 | feeder2_line63 | 3 | 99 | 5.7367e-07 | 1.2207e-06 | 5.7947e-07 | 1.233e-06
30 | feeder2_line64 | 1 | 99 | 0.29557 | 0.29557 | 0.29855 | 0.29855
30 | feeder2_line64 | 2 | 99 | 5.5854e-12 | 3.224e-07 | 5.6418e-12 | 3.2565e-07
30 | feeder2_line64 | 3 | 99 | 7.3264e-12 | 3.2155e-07 | 7.4004e-12 | 3.248e-07
30 | feeder2_line65 | 1 | 99 | 5.0096e-08 | 6.429e-07 | 5.0602e-08 | 6.494e-07
30 | feeder2_line65 | 2 | 99 | 0.27962 | 0.27961 | 0.28244 | 0.28244
30 | feeder2_line65 | 3 | 99 | 5.0347e-08 | 6.4273e-07 | 5.0855e-08 | 6.4922e-07
30 | feeder2_line66 | 1 | 354.6 | 92.088 | 92.0843 | 25.9696 | 25.9685
30 | feeder2_line66 | 2 | 354.6 | 90.4958 | 90.4934 | 25.5205 | 25.5199
30 | feeder2_line66 | 3 | 354.6 | 81.9302 | 81.9347 | 23.105 | 23.1062
30 | feeder2_line67 | 1 | 99 | 2.5033e-08 | 3.6326e-07 | 2.5286e-08 | 3.6693e-07
30 | feeder2_line67 | 2 | 99 | 2.4844e-08 | 3.6442e-07 | 2.5095e-08 | 3.681e-07
30 | feeder2_line67 | 3 | 99 | 0.093741 | 0.093744 | 0.094688 | 0.094691
30 | feeder2_line68 | 1 | 266.4 | 0.19847 | 0.1986 | 0.074501 | 0.074549
30 | feeder2_line68 | 2 | 266.4 | 1.2533 | 1.2535 | 0.47047 | 0.47052
30 | feeder2_line68 | 3 | 266.4 | 0.97564 | 0.97579 | 0.36623 | 0.36629
30 | feeder2_line69 | 1 | 99 | 1.5594 | 1.5594 | 1.5751 | 1.5752
30 | feeder2_line69 | 2 | 99 | 2.5617e-06 | 6.6966e-07 | 2.5875e-06 | 6.7643e-07
30 | feeder2_line69 | 3 | 99 | 2.5473e-06 | 6.6733e-07 | 2.5731e-06 | 6.7408e-07
30 | feeder2_line70 | 1 | 354.6 | 92.8751 | 92.8714 | 26.1915 | 26.1905
30 | feeder2_line70 | 2 | 354.6 | 90.4958 | 90.4934 | 25.5205 | 25.5199
30 | feeder2_line70 | 3 | 354.6 | 81.9301 | 81.9347 | 23.1049 | 23.1062
30 | feeder2_line71 | 1 | 99 | 5.0101e-08 | 7.1753e-07 | 5.0607e-08 | 7.2477e-07
30 | feeder2_line71 | 2 | 99 | 1.4293 | 1.4293 | 1.4438 | 1.4437
30 | feeder2_line71 | 3 | 99 | 5.0379e-08 | 7.1723e-07 | 5.0887e-08 | 7.2447e-07
30 | feeder2_line72 | 1 | 354.6 | 92.8752 | 92.8714 | 26.1915 | 26.1905
30 | feeder2_line72 | 2 | 354.6 | 91.2522 | 91.2498 | 25.7338 | 25.7332
30 | feeder2_line72 | 3 | 354.6 | 81.9302 | 81.9347 | 23.105 | 23.1062
30 | feeder2_line73 | 1 | 99 | 5.9971e-07 | 1.5379e-06 | 6.0577e-07 | 1.5534e-06
30 | feeder2_line73 | 2 | 99 | 0.25785 | 0.25784 | 0.26045 | 0.26045
30 | feeder2_line73 | 3 | 99 | 5.9977e-07 | 1.5377e-06 | 6.0583e-07 | 1.5533e-06
30 | feeder2_line74 | 1 | 99 | 5.0076e-08 | 4.5867e-07 | 5.0581e-08 | 4.633e-07
30 | feeder2_line74 | 2 | 99 | 0.97671 | 0.97672 | 0.98657 | 0.98659
30 | feeder2_line74 | 3 | 99 | 5.0307e-08 | 4.5864e-07 | 5.0816e-08 | 4.6327e-07
30 | feeder2_line75 | 1 | 266.4 | 0.19857 | 0.1986 | 0.074538 | 0.074549
30 | feeder2_line75 | 2 | 266.4 | 0.089337 | 0.089369 | 0.033535 | 0.033547
30 | feeder2_line75 | 3 | 266.4 | 0.97573 | 0.9758 | 0.36626 | 0.36629
30 | feeder2_line76 | 1 | 99 | 0.1986 | 0.1986 | 0.20061 | 0.20061
30 | feeder2_line76 | 2 | 99 | 8.5239e-07 | 1.5915e-06 | 8.61e-07 | 1.6076e-06
30 | feeder2_line76 | 3 | 99 | 8.4935e-07 | 1.5863e-06 | 8.5793e-07 | 1.6023e-06
30 | feeder2_line77 | 1 | 99 | 2.5039e-08 | 5.7641e-07 | 2.5292e-08 | 5.8223e-07
30 | feeder2_line77 | 2 | 99 | 2.4839e-08 | 5.7826e-07 | 2.509e-08 | 5.841e-07
30 | feeder2_line77 | 3 | 99 | 0.97576 | 0.9758 | 0.98562 | 0.98565
30 | feeder2_line78 | 1 | 266.4 | 9.165e-12 | 9.5601e-07 | 3.4403e-12 | 3.5886e-07
30 | feeder2_line78 | 2 | 266.4 | 0.08937 | 0.089369 | 0.033547 | 0.033547
30 | feeder2_line78 | 3 | 266.4 | 4.8727e-12 | 9.5608e-07 | 1.8291e-12 | 3.5889e-07
30 | feeder2_line79 | 1 | 354.6 | 2.0599 | 2.0597 | 0.58092 | 0.58085
30 | feeder2_line79 | 2 | 354.6 | 1.9688 | 1.9685 | 0.55521 | 0.55512
30 | feeder2_line79 | 3 | 354.6 | 3.7362 | 3.7359 | 1.0536 | 1.0536
30 | feeder2_line80 | 1 | 354.6 | 94.2008 | 94.1964 | 26.5654 | 26.5641
30 | feeder2_line80 | 2 | 354.6 | 92.8553 | 92.8523 | 26.1859 | 26.1851
30 | feeder2_line80 | 3 | 354.6 | 84.7038 | 84.7077 | 23.8871 | 23.8882
30 | feeder2_line81 | 1 | 354.6 | 94.2007 | 94.1964 | 26.5653 | 26.5641
30 | feeder2_line81 | 2 | 354.6 | 92.8552 | 92.8523 | 26.1859 | 26.1851
30 | feeder2_line81 | 3 | 354.6 | 84.9502 | 84.9542 | 23.9566 | 23.9577
30 | feeder2_line82 | 1 | 354.6 | 2.0743e-11 | 7.3647e-07 | 5.8498e-12 | 2.0769e-07
30 | feeder2_line82 | 2 | 354.6 | 1.3571e-11 | 7.3841e-07 | 3.8272e-12 | 2.0824e-07
30 | feeder2_line82 | 3 | 354.6 | 0.25033 | 0.25033 | 0.070595 | 0.070596
30 | feeder2_line83 | 1 | 354.6 | 94.2009 | 94.1964 | 26.5654 | 26.5641
30 | feeder2_line83 | 2 | 354.6 | 93.3302 | 93.3271 | 26.3199 | 26.319
30 | feeder2_line83 | 3 | 354.6 | 84.9503 | 84.9542 | 23.9567 | 23.9577
30 | feeder2_line84 | 1 | 354.6 | 1.1777e-11 | 1.3018e-06 | 3.3212e-12 | 3.6711e-07
30 | feeder2_line84 | 2 | 354.6 | 0.98365 | 0.98361 | 0.2774 | 0.27739
30 | feeder2_line84 | 3 | 354.6 | 9.4256e-12 | 1.301e-06 | 2.6581e-12 | 3.6689e-07
30 | feeder2_line85 | 1 | 99 | 0.21253 | 0.21253 | 0.21468 | 0.21467
30 | feeder2_line85 | 2 | 99 | 4.9785e-08 | 4.6604e-07 | 5.0288e-08 | 4.7075e-07
30 | feeder2_line85 | 3 | 99 | 5.0464e-08 | 4.6426e-07 | 5.0973e-08 | 4.6895e-07
30 | feeder2_line86 | 1 | 354.6 | 94.4116 | 94.4069 | 26.6248 | 26.6235
30 | feeder2_line86 | 2 | 354.6 | 93.3303 | 93.3271 | 26.3199 | 26.319
30 | feeder2_line86 | 3 | 354.6 | 84.9505 | 84.9542 | 23.9567 | 23.9577
30 | feeder2_line87 | 1 | 354.6 | 94.4117 | 94.4069 | 26.6249 | 26.6235
30 | feeder2_line87 | 2 | 354.6 | 94.8039 | 94.8005 | 26.7354 | 26.7345
30 | feeder2_line87 | 3 | 354.6 | 85.7361 | 85.7397 | 24.1783 | 24.1793
30 | feeder2_line88 | 1 | 354.6 | 0.00011502 | 3.375e-06 | 3.2438e-05 | 9.5177e-07
30 | feeder2_line88 | 2 | 354.6 | 3.4311 | 3.431 | 0.96759 | 0.96756
30 | feeder2_line88 | 3 | 354.6 | 1.4497 | 1.4497 | 0.40883 | 0.40883
30 | feeder2_line89 | 1 | 354.6 | 94.4094 | 94.4069 | 26.6242 | 26.6235
30 | feeder2_line89 | 2 | 354.6 | 95.8769 | 95.8758 | 27.038 | 27.0377
30 | feeder2_line89 | 3 | 354.6 | 85.7338 | 85.7397 | 24.1776 | 24.1793
30 | feeder2_line90 | 1 | 354.6 | 0.00072677 | 2.0374e-06 | 0.00020495 | 5.7456e-07
30 | feeder2_line90 | 2 | 354.6 | 1.961 | 1.9609 | 0.55302 | 0.55299
30 | feeder2_line90 | 3 | 354.6 | 0.00072424 | 2.0361e-06 | 0.00020424 | 5.7421e-07
30 | feeder2_line91 | 1 | 354.6 | 94.4094 | 94.4069 | 26.6242 | 26.6235
30 | feeder2_line91 | 2 | 354.6 | 95.8768 | 95.8758 | 27.038 | 27.0377
30 | feeder2_line91 | 3 | 354.6 | 85.795 | 85.8009 | 24.1949 | 24.1965
30 | feeder2_line92 | 1 | 354.6 | 6.419e-12 | 1.0279e-06 | 1.8102e-12 | 2.8989e-07
30 | feeder2_line92 | 2 | 354.6 | 2.6822e-12 | 1.0307e-06 | 7.564e-13 | 2.9067e-07
30 | feeder2_line92 | 3 | 354.6 | 0.06158 | 0.061582 | 0.017366 | 0.017367
30 | feeder2_line93 | 1 | 99 | 2.5068e-08 | 3.4312e-07 | 2.5321e-08 | 3.4658e-07
30 | feeder2_line93 | 2 | 99 | 0.98384 | 0.98381 | 0.99378 | 0.99374
30 | feeder2_line93 | 3 | 99 | 2.5255e-08 | 3.4276e-07 | 2.551e-08 | 3.4622e-07
30 | feeder2_line94 | 1 | 354.6 | 2.5072e-06 | 1.6705e-06 | 7.0705e-07 | 4.711e-07
30 | feeder2_line94 | 2 | 354.6 | 0.978 | 0.978 | 0.2758 | 0.2758
30 | feeder2_line94 | 3 | 354.6 | 2.5257e-06 | 1.6691e-06 | 7.1227e-07 | 4.7071e-07
30 | feeder2_line95 | 1 | 99 | 3.5756e-06 | 2.6171e-06 | 3.6117e-06 | 2.6436e-06
30 | feeder2_line95 | 2 | 99 | 3.4311 | 3.431 | 3.4657 | 3.4656
30 | feeder2_line95 | 3 | 99 | 3.5737e-06 | 2.6147e-06 | 3.6098e-06 | 2.6412e-06
30 | feeder2_line96 | 1 | 354.6 | 0.00012148 | 6.2394e-07 | 3.4258e-05 | 1.7596e-07
30 | feeder2_line96 | 2 | 354.6 | 0.00012186 | 6.257e-07 | 3.4365e-05 | 1.7645e-07
30 | feeder2_line96 | 3 | 354.6 | 1.4497 | 1.4497 | 0.40881 | 0.40883
30 | feeder2_line97 | 1 | 354.6 | 95.1203 | 95.1176 | 26.8247 | 26.8239
30 | feeder2_line97 | 2 | 354.6 | 95.877 | 95.8758 | 27.0381 | 27.0377
30 | feeder2_line97 | 3 | 354.6 | 85.7952 | 85.8009 | 24.1949 | 24.1965
30 | feeder2_line98 | 1 | 354.6 | 1.3571 | 1.3562 | 0.3827 | 0.38245
30 | feeder2_line98 | 2 | 354.6 | 0.001715 | 6.2467e-07 | 0.00048365 | 1.7616e-07
30 | feeder2_line98 | 3 | 354.6 | 0.0016978 | 6.2406e-07 | 0.00047879 | 1.7599e-07
30 | feeder2_line99 | 1 | 99 | 2.5065e-08 | 4.485e-07 | 2.5319e-08 | 4.5303e-07
30 | feeder2_line99 | 2 | 99 | 2.4896e-08 | 4.4982e-07 | 2.5147e-08 | 4.5436e-07
30 | feeder2_line99 | 3 | 99 | 1.4497 | 1.4497 | 1.4643 | 1.4644
30 | feeder2_line100 | 1 | 99 | 1.3562 | 1.3562 | 1.3699 | 1.3699
30 | feeder2_line100 | 2 | 99 | 2.4912e-08 | 6.1788e-07 | 2.5164e-08 | 6.2412e-07
30 | feeder2_line100 | 3 | 99 | 2.5266e-08 | 6.1536e-07 | 2.5521e-08 | 6.2158e-07
30 | feeder2_line101 | 1 | 354.6 | 0.97679 | 0.9766 | 0.27546 | 0.27541
30 | feeder2_line101 | 2 | 354.6 | 1.9688 | 1.9685 | 0.55521 | 0.55512
30 | feeder2_line101 | 3 | 354.6 | 3.7361 | 3.7359 | 1.0536 | 1.0536
30 | feeder2_line102 | 1 | 99 | 1.0922 | 1.0921 | 1.1032 | 1.1032
30 | feeder2_line102 | 2 | 99 | 2.3517e-06 | 8.83e-07 | 2.3755e-06 | 8.9192e-07
30 | feeder2_line102 | 3 | 99 | 2.3333e-06 | 8.7972e-07 | 2.3569e-06 | 8.8861e-07
30 | feeder2_line103 | 1 | 99 | 5.5058e-07 | 8.0576e-07 | 5.5614e-07 | 8.139e-07
30 | feeder2_line103 | 2 | 99 | 0.096187 | 0.096186 | 0.097158 | 0.097157
30 | feeder2_line103 | 3 | 99 | 5.5001e-07 | 8.0521e-07 | 5.5556e-07 | 8.1334e-07
30 | feeder2_line104 | 1 | 354.6 | 0.97678 | 0.9766 | 0.27546 | 0.27541
30 | feeder2_line104 | 2 | 354.6 | 1.8878 | 1.8875 | 0.53236 | 0.53229
30 | feeder2_line104 | 3 | 354.6 | 3.7361 | 3.7359 | 1.0536 | 1.0536
30 | feeder2_line105 | 1 | 99 | 2.5525e-06 | 7.4141e-07 | 2.5783e-06 | 7.489e-07
30 | feeder2_line105 | 2 | 99 | 2.5637e-06 | 7.4366e-07 | 2.5896e-06 | 7.5117e-07
30 | feeder2_line105 | 3 | 99 | 1.4153 | 1.4153 | 1.4296 | 1.4296
30 | feeder2_line106 | 1 | 354.6 | 0.97675 | 0.9766 | 0.27545 | 0.27541
30 | feeder2_line106 | 2 | 354.6 | 1.8877 | 1.8875 | 0.53235 | 0.53229
30 | feeder2_line106 | 3 | 354.6 | 2.3462 | 2.346 | 0.66165 | 0.6616
30 | feeder2_line107 | 1 | 99 | 3.2539e-07 | 9.0351e-07 | 3.2868e-07 | 9.1264e-07
30 | feeder2_line107 | 2 | 99 | 1.4077 | 1.4077 | 1.4219 | 1.4219
30 | feeder2_line107 | 3 | 99 | 3.2542e-07 | 9.0286e-07 | 3.2871e-07 | 9.1198e-07
30 | feeder2_line108 | 1 | 354.6 | 0.97676 | 0.9766 | 0.27545 | 0.27541
30 | feeder2_line108 | 2 | 354.6 | 0.55581 | 0.55556 | 0.15674 | 0.15667
30 | feeder2_line108 | 3 | 354.6 | 2.3462 | 2.346 | 0.66165 | 0.6616
30 | feeder2_line109 | 1 | 354.6 | 95.3574 | 95.3535 | 26.8915 | 26.8905
30 | feeder2_line109 | 2 | 354.6 | 95.8782 | 95.8758 | 27.0384 | 27.0377
30 | feeder2_line109 | 3 | 354.6 | 85.7964 | 85.8009 | 24.1953 | 24.1965
30 | feeder2_line110 | 1 | 99 | 0.23677 | 0.23596 | 0.23916 | 0.23834
30 | feeder2_line110 | 2 | 99 | 0.00081077 | 9.146e-07 | 0.00081896 | 9.2384e-07
30 | feeder2_line110 | 3 | 99 | 0.00080483 | 9.1085e-07 | 0.00081296 | 9.2006e-07
30 | feeder2_line111 | 1 | 99 | 2.5062e-08 | 3.8306e-07 | 2.5315e-08 | 3.8693e-07
30 | feeder2_line111 | 2 | 99 | 1.0354 | 1.0353 | 1.0458 | 1.0458
30 | feeder2_line111 | 3 | 99 | 2.5244e-08 | 3.8271e-07 | 2.5499e-08 | 3.8657e-07
30 | feeder2_line112 | 1 | 99 | 3.2566e-07 | 9.2048e-07 | 3.2895e-07 | 9.2978e-07
30 | feeder2_line112 | 2 | 99 | 2.3967 | 2.3966 | 2.4209 | 2.4208
30 | feeder2_line112 | 3 | 99 | 3.2567e-07 | 9.1966e-07 | 3.2896e-07 | 9.2895e-07
30 | feeder2_line113 | 1 | 99 | 0.12828 | 0.12828 | 0.12958 | 0.12958
30 | feeder2_line113 | 2 | 99 | 3.2665e-07 | 9.1134e-07 | 3.2995e-07 | 9.2054e-07
30 | feeder2_line113 | 3 | 99 | 3.2597e-07 | 9.0753e-07 | 3.2926e-07 | 9.1669e-07
30 | feeder2_line114 | 1 | 99 | 0.09644 | 0.096438 | 0.097414 | 0.097412
30 | feeder2_line114 | 2 | 99 | 2.4884e-08 | 4.3908e-07 | 2.5135e-08 | 4.4352e-07
30 | feeder2_line114 | 3 | 99 | 2.5211e-08 | 4.3745e-07 | 2.5465e-08 | 4.4187e-07
30 | feeder2_line115 | 1 | 99 | 2.5049e-08 | 5.6383e-07 | 2.5302e-08 | 5.6952e-07
30 | feeder2_line115 | 2 | 99 | 0.33268 | 0.33268 | 0.33604 | 0.33604
30 | feeder2_line115 | 3 | 99 | 2.5213e-08 | 5.6342e-07 | 2.5468e-08 | 5.6911e-07
30 | feeder2_line116 | 1 | 354.6 | 0.97677 | 0.9766 | 0.27546 | 0.27541
30 | feeder2_line116 | 2 | 354.6 | 0.22316 | 0.22291 | 0.062933 | 0.062862
30 | feeder2_line116 | 3 | 354.6 | 2.3462 | 2.346 | 0.66165 | 0.6616
30 | feeder2_line117 | 1 | 99 | 5.0184e-08 | 6.4528e-07 | 5.0691e-08 | 6.5179e-07
30 | feeder2_line117 | 2 | 99 | 1.3178 | 1.3178 | 1.3312 | 1.3312
30 | feeder2_line117 | 3 | 99 | 5.0597e-08 | 6.4442e-07 | 5.1109e-08 | 6.5093e-07
30 | feeder2_line118 | 1 | 354.6 | 95.3574 | 95.3535 | 26.8915 | 26.8905
30 | feeder2_line118 | 2 | 354.6 | 96.5762 | 96.5737 | 27.2353 | 27.2346
30 | feeder2_line118 | 3 | 354.6 | 85.7964 | 85.8009 | 24.1953 | 24.1965
30 | feeder2_line119 | 1 | 99 | 2.5053e-08 | 6.067e-07 | 2.5306e-08 | 6.1283e-07
30 | feeder2_line119 | 2 | 99 | 2.4873e-08 | 6.0856e-07 | 2.5124e-08 | 6.1471e-07
30 | feeder2_line119 | 3 | 99 | 0.54558 | 0.54559 | 0.55109 | 0.5511
30 | feeder2_line120 | 1 | 354.6 | 0.97677 | 0.97661 | 0.27546 | 0.27541
30 | feeder2_line120 | 2 | 354.6 | 0.22316 | 0.22291 | 0.062934 | 0.062862
30 | feeder2_line120 | 3 | 354.6 | 1.8676 | 1.8675 | 0.52669 | 0.52664
30 | feeder2_line121 | 1 | 99 | 3.2539e-07 | 9.3949e-07 | 3.2867e-07 | 9.4897e-07
30 | feeder2_line121 | 2 | 99 | 0.043772 | 0.043772 | 0.044214 | 0.044214
30 | feeder2_line121 | 3 | 99 | 3.254e-07 | 9.3877e-07 | 3.2869e-07 | 9.4826e-07
30 | feeder2_line122 | 1 | 354.6 | 0.97674 | 0.97661 | 0.27545 | 0.27541
30 | feeder2_line122 | 2 | 354.6 | 0.17938 | 0.17914 | 0.050587 | 0.050518
30 | feeder2_line122 | 3 | 354.6 | 1.8676 | 1.8675 | 0.52668 | 0.52664
30 | feeder2_line123 | 1 | 99 | 5.7561e-07 | 9.7352e-07 | 5.8142e-07 | 9.8335e-07
30 | feeder2_line123 | 2 | 99 | 5.7741e-07 | 9.7653e-07 | 5.8325e-07 | 9.864e-07
30 | feeder2_line123 | 3 | 99 | 0.10849 | 0.10849 | 0.10959 | 0.10959
30 | feeder2_line124 | 1 | 354.6 | 0.97678 | 0.97661 | 0.27546 | 0.27541
30 | feeder2_line124 | 2 | 354.6 | 0.17929 | 0.17914 | 0.050561 | 0.050518
30 | feeder2_line124 | 3 | 354.6 | 1.788 | 1.7878 | 0.50422 | 0.50418
30 | feeder2_line125 | 1 | 99 | 5.7561e-07 | 9.0498e-07 | 5.8142e-07 | 9.1413e-07
30 | feeder2_line125 | 2 | 99 | 5.7741e-07 | 9.0778e-07 | 5.8324e-07 | 9.1695e-07
30 | feeder2_line125 | 3 | 99 | 1.355 | 1.3551 | 1.3687 | 1.3687
30 | feeder2_line126 | 1 | 354.6 | 0.97691 | 0.97661 | 0.2755 | 0.27541
30 | feeder2_line126 | 2 | 354.6 | 0.17945 | 0.17914 | 0.050606 | 0.050518
30 | feeder2_line126 | 3 | 354.6 | 0.58771 | 0.58741 | 0.16574 | 0.16565
30 | feeder2_line127 | 1 | 99 | 5.756e-07 | 1.0834e-06 | 5.8142e-07 | 1.0943e-06
30 | feeder2_line127 | 2 | 99 | 5.7741e-07 | 1.0868e-06 | 5.8324e-07 | 1.0977e-06
30 | feeder2_line127 | 3 | 99 | 0.21251 | 0.21252 | 0.21466 | 0.21466
30 | feeder2_line128 | 1 | 354.6 | 0.97689 | 0.97661 | 0.27549 | 0.27541
30 | feeder2_line128 | 2 | 354.6 | 0.17936 | 0.17914 | 0.050582 | 0.050518
30 | feeder2_line128 | 3 | 354.6 | 0.37513 | 0.37491 | 0.10579 | 0.10573
30 | feeder2_line129 | 1 | 99 | 5.5055e-07 | 8.7848e-07 | 5.5611e-07 | 8.8735e-07
30 | feeder2_line129 | 2 | 99 | 0.17914 | 0.17914 | 0.18095 | 0.18095
30 | feeder2_line129 | 3 | 99 | 5.4994e-07 | 8.7782e-07 | 5.5549e-07 | 8.8668e-07
30 | feeder2_line130 | 1 | 354.6 | 0.97693 | 0.97661 | 0.2755 | 0.27541
30 | feeder2_line130 | 2 | 354.6 | 0.00031007 | 4.6627e-06 | 8.7441e-05 | 1.3149e-06
30 | feeder2_line130 | 3 | 354.6 | 0.37514 | 0.37491 | 0.10579 | 0.10573
30 | feeder2_line131 | 1 | 99 | 5.756e-07 | 9.7365e-07 | 5.8141e-07 | 9.8349e-07
30 | feeder2_line131 | 2 | 99 | 5.7741e-07 | 9.7669e-07 | 5.8324e-07 | 9.8655e-07
30 | feeder2_line131 | 3 | 99 | 0.16243 | 0.16243 | 0.16407 | 0.16407
30 | feeder2_line132 | 1 | 354.6 | 0.97675 | 0.97661 | 0.27545 | 0.27541
30 | feeder2_line132 | 2 | 354.6 | 0.00012649 | 2.9313e-06 | 3.5672e-05 | 8.2666e-07
30 | feeder2_line132 | 3 | 354.6 | 0.21259 | 0.21252 | 0.059951 | 0.059931
30 | feeder2_line133 | 1 | 99 | 0.97662 | 0.97661 | 0.98649 | 0.98648
30 | feeder2_line133 | 2 | 99 | 3.0114e-07 | 9.8448e-07 | 3.0418e-07 | 9.9442e-07
30 | feeder2_line133 | 3 | 99 | 3.0018e-07 | 9.8069e-07 | 3.0321e-07 | 9.906e-07
30 | feeder2_line134 | 1 | 354.6 | 4.6442e-12 | 1.7898e-06 | 1.3097e-12 | 5.0474e-07
30 | feeder2_line134 | 2 | 354.6 | 5.6886e-12 | 1.7949e-06 | 1.6042e-12 | 5.0618e-07
30 | feeder2_line134 | 3 | 354.6 | 0.21251 | 0.21252 | 0.05993 | 0.059931
30 | feeder2_line135 | 1 | 99 | 1.429 | 1.429 | 1.4435 | 1.4435
30 | feeder2_line135 | 2 | 99 | 4.9877e-08 | 5.9005e-07 | 5.0381e-08 | 5.9601e-07
30 | feeder2_line135 | 3 | 99 | 5.0636e-08 | 5.8738e-07 | 5.1147e-08 | 5.9331e-07
30 | feeder2_line136 | 1 | 354.6 | 96.216 | 96.2122 | 27.1337 | 27.1326
30 | feeder2_line136 | 2 | 354.6 | 96.5762 | 96.5737 | 27.2352 | 27.2346
30 | feeder2_line136 | 3 | 354.6 | 85.7964 | 85.8009 | 24.1953 | 24.1965
30 | feeder2_line137 | 1 | 99 | 1.192 | 1.1919 | 1.204 | 1.204
30 | feeder2_line137 | 2 | 99 | 8.5653e-07 | 1.5894e-06 | 8.6518e-07 | 1.6054e-06
30 | feeder2_line137 | 3 | 99 | 8.5231e-07 | 1.5821e-06 | 8.6092e-07 | 1.5981e-06
30 | feeder2_line138 | 1 | 354.6 | 96.8192 | 96.8152 | 27.3038 | 27.3027
30 | feeder2_line138 | 2 | 354.6 | 96.5762 | 96.5737 | 27.2353 | 27.2346
30 | feeder2_line138 | 3 | 354.6 | 85.7964 | 85.8009 | 24.1953 | 24.1965
30 | feeder2_line139 | 1 | 99 | 5.0213e-08 | 4.9378e-07 | 5.0721e-08 | 4.9876e-07
30 | feeder2_line139 | 2 | 99 | 4.9881e-08 | 4.9529e-07 | 5.0385e-08 | 5.003e-07
30 | feeder2_line139 | 3 | 99 | 12.9836 | 12.9838 | 13.1148 | 13.115
30 | feeder2_line140 | 1 | 354.6 | 96.8193 | 96.8152 | 27.3038 | 27.3027
30 | feeder2_line140 | 2 | 354.6 | 96.5763 | 96.5737 | 27.2353 | 27.2346
30 | feeder2_line140 | 3 | 354.6 | 98.3296 | 98.3342 | 27.7297 | 27.731
30 | feeder2_line141 | 1 | 99 | 2.5372e-06 | 4.8852e-07 | 2.5629e-06 | 4.9345e-07
30 | feeder2_line141 | 2 | 99 | 0.18985 | 0.18985 | 0.19177 | 0.19177
30 | feeder2_line141 | 3 | 99 | 2.5295e-06 | 4.8774e-07 | 2.555e-06 | 4.9267e-07
30 | feeder2_line142 | 1 | 354.6 | 96.8191 | 96.8152 | 27.3037 | 27.3027
30 | feeder2_line142 | 2 | 354.6 | 96.7649 | 96.7625 | 27.2885 | 27.2878
30 | feeder2_line142 | 3 | 354.6 | 98.3294 | 98.3342 | 27.7297 | 27.731
30 | feeder2_line143 | 1 | 99 | 8.5415e-07 | 1.736e-06 | 8.6278e-07 | 1.7535e-06
30 | feeder2_line143 | 2 | 99 | 1.4079 | 1.4079 | 1.4221 | 1.4221
30 | feeder2_line143 | 3 | 99 | 8.5266e-07 | 1.7332e-06 | 8.6127e-07 | 1.7508e-06
30 | feeder2_line144 | 1 | 354.6 | 96.8189 | 96.8152 | 27.3037 | 27.3027
30 | feeder2_line144 | 2 | 354.6 | 97.8098 | 97.8075 | 27.5831 | 27.5825
30 | feeder2_line144 | 3 | 354.6 | 98.3292 | 98.3342 | 27.7296 | 27.731
30 | feeder2_line145 | 1 | 99 | 2.5124e-08 | 4.8679e-07 | 2.5378e-08 | 4.9171e-07
30 | feeder2_line145 | 2 | 99 | 0.25083 | 0.25083 | 0.25337 | 0.25337
30 | feeder2_line145 | 3 | 99 | 2.534e-08 | 4.8603e-07 | 2.5596e-08 | 4.9094e-07
30 | feeder2_line146 | 1 | 354.6 | 96.8188 | 96.8152 | 27.3037 | 27.3027
30 | feeder2_line146 | 2 | 354.6 | 98.0589 | 98.0568 | 27.6534 | 27.6528
30 | feeder2_line146 | 3 | 354.6 | 98.3291 | 98.3342 | 27.7296 | 27.731
30 | feeder2_line147 | 1 | 99 | 0.10757 | 0.10757 | 0.10866 | 0.10865
30 | feeder2_line147 | 2 | 99 | 1.1594e-06 | 2.2523e-06 | 1.1711e-06 | 2.2751e-06
30 | feeder2_line147 | 3 | 99 | 1.154e-06 | 2.2419e-06 | 1.1656e-06 | 2.2646e-06
30 | feeder2_line148 | 1 | 99 | 0.22049 | 0.22048 | 0.22271 | 0.22271
30 | feeder2_line148 | 2 | 99 | 6.0466e-07 | 1.5092e-06 | 6.1076e-07 | 1.5245e-06
30 | feeder2_line148 | 3 | 99 | 6.0233e-07 | 1.5023e-06 | 6.0841e-07 | 1.5174e-06
30 | feeder2_line149 | 1 | 354.6 | 97.1458 | 97.1421 | 27.3959 | 27.3948
30 | feeder2_line149 | 2 | 354.6 | 98.0591 | 98.0568 | 27.6534 | 27.6528
30 | feeder2_line149 | 3 | 354.6 | 98.3293 | 98.3342 | 27.7296 | 27.731
30 | feeder2_line150 | 1 | 354.6 | 97.1459 | 97.1421 | 27.3959 | 27.3948
30 | feeder2_line150 | 2 | 354.6 | 98.2439 | 98.2415 | 27.7055 | 27.7049
30 | feeder2_line150 | 3 | 354.6 | 98.3294 | 98.3342 | 27.7297 | 27.731
30 | feeder2_line151 | 1 | 99 | 9.8102e-06 | 1.7875e-06 | 9.9093e-06 | 1.8055e-06
30 | feeder2_line151 | 2 | 99 | 0.1847 | 0.18471 | 0.18657 | 0.18657
30 | feeder2_line151 | 3 | 99 | 9.7717e-06 | 1.7847e-06 | 9.8704e-06 | 1.8027e-06
30 | feeder2_line152 | 1 | 354.6 | 4.6341e-12 | 1.1915e-06 | 1.3068e-12 | 3.36e-07
30 | feeder2_line152 | 2 | 354.6 | 1.1736e-11 | 1.1949e-06 | 3.3095e-12 | 3.3696e-07
30 | feeder2_line152 | 3 | 354.6 | 0.076746 | 0.076749 | 0.021643 | 0.021644
30 | feeder2_line153 | 1 | 99 | 0.043755 | 0.043753 | 0.044197 | 0.044195
30 | feeder2_line153 | 2 | 99 | 4.9947e-08 | 5.9796e-07 | 5.0451e-08 | 6.04e-07
30 | feeder2_line153 | 3 | 99 | 5.0731e-08 | 5.9518e-07 | 5.1243e-08 | 6.012e-07
30 | feeder2_line154 | 1 | 99 | 5.7843e-07 | 8.8703e-07 | 5.8427e-07 | 8.9599e-07
30 | feeder2_line154 | 2 | 99 | 5.8024e-07 | 8.8978e-07 | 5.861e-07 | 8.9877e-07
30 | feeder2_line154 | 3 | 99 | 1.2431 | 1.2432 | 1.2557 | 1.2557
30 | feeder2_line155 | 1 | 99 | 97.1893 | 97.1856 | 98.171 | 98.1672
30 | feeder2_line155 | 2 | 99 | 98.2438 | 98.2415 | 99.2361 | 99.2338
30 | feeder2_line155 | 3 | 99 | 99 | 99.0049 | 100 | 100.005
30 | feeder2_line156 | 1 | 99 | 6.0332e-07 | 1.1672e-06 | 6.0942e-07 | 1.179e-06
30 | feeder2_line156 | 2 | 99 | 0.095937 | 0.095936 | 0.096906 | 0.096905
30 | feeder2_line156 | 3 | 99 | 6.0262e-07 | 1.1654e-06 | 6.0871e-07 | 1.1771e-06
30 | feeder2_line157 | 1 | 99 | 2.5142e-08 | 2.5338e-07 | 2.5396e-08 | 2.5594e-07
30 | feeder2_line157 | 2 | 99 | 0.088931 | 0.08893 | 0.08983 | 0.089828
30 | feeder2_line157 | 3 | 99 | 2.5355e-08 | 2.53e-07 | 2.5612e-08 | 2.5555e-07
60 | feeder2_line1 | 1 | 354.6 | 79.7008 | 79.7015 | 22.4762 | 22.4764
60 | feeder2_line1 | 2 | 354.6 | 87.9885 | 87.9927 | 24.8135 | 24.8146
60 | feeder2_line1 | 3 | 354.6 | 82.0334 | 82.0307 | 23.1341 | 23.1333
60 | feeder2_line2 | 1 | 354.6 | 80.5696 | 80.5702 | 22.7213 | 22.7214
60 | feeder2_line2 | 2 | 354.6 | 87.9887 | 87.9927 | 24.8135 | 24.8146
60 | feeder2_line2 | 3 | 354.6 | 82.0336 | 82.0307 | 23.1341 | 23.1333
60 | feeder2_line3 | 1 | 80.1 | 1.573 | 1.573 | 1.9637 | 1.9638
60 | feeder2_line3 | 2 | 80.1 | 5.7223e-07 | 1.0575e-06 | 7.144e-07 | 1.3202e-06
60 | feeder2_line3 | 3 | 80.1 | 5.7228e-07 | 1.0576e-06 | 7.1445e-07 | 1.3203e-06
60 | feeder2_line4 | 1 | 354.6 | 80.5698 | 80.5702 | 22.7213 | 22.7214
60 | feeder2_line4 | 2 | 354.6 | 88.7522 | 88.7561 | 25.0288 | 25.0299
60 | feeder2_line4 | 3 | 354.6 | 82.0337 | 82.0307 | 23.1342 | 23.1333
60 | feeder2_line5 | 1 | 80.1 | 5.7222e-07 | 9.9848e-07 | 7.1438e-07 | 1.2465e-06
60 | feeder2_line5 | 2 | 80.1 | 1.5294 | 1.5294 | 1.9093 | 1.9093
60 | feeder2_line5 | 3 | 80.1 | 5.7232e-07 | 9.9866e-07 | 7.1451e-07 | 1.2468e-06
60 | feeder2_line6 | 1 | 80.1 | 5.723e-07 | 1.1747e-06 | 7.1448e-07 | 1.4666e-06
60 | feeder2_line6 | 2 | 80.1 | 5.7236e-07 | 1.1749e-06 | 7.1455e-07 | 1.4667e-06
60 | feeder2_line6 | 3 | 80.1 | 0.085332 | 0.085329 | 0.10653 | 0.10653
60 | feeder2_line7 | 1 | 354.6 | 80.5699 | 80.5702 | 22.7214 | 22.7214
60 | feeder2_line7 | 2 | 354.6 | 88.7523 | 88.7561 | 25.0289 | 25.0299
60 | feeder2_line7 | 3 | 354.6 | 82.1188 | 82.1157 | 23.1582 | 23.1573
60 | feeder2_line8 | 1 | 80.1 | 0.072583 | 0.072583 | 0.090615 | 0.090615
60 | feeder2_line8 | 2 | 80.1 | 5.7257e-07 | 1.1333e-06 | 7.1482e-07 | 1.4148e-06
60 | feeder2_line8 | 3 | 80.1 | 5.7259e-07 | 1.1333e-06 | 7.1484e-07 | 1.4148e-06
60 | feeder2_line9 | 1 | 354.6 | 80.6421 | 80.6423 | 22.7417 | 22.7418
60 | feeder2_line9 | 2 | 354.6 | 88.7524 | 88.7561 | 25.0289 | 25.0299
60 | feeder2_line9 | 3 | 354.6 | 82.1189 | 82.1157 | 23.1582 | 23.1573
60 | feeder2_line10 | 1 | 80.1 | 8.4635e-07 | 1.4962e-06 | 1.0566e-06 | 1.8679e-06
60 | feeder2_line10 | 2 | 80.1 | 0.072572 | 0.072573 | 0.090602 | 0.090602
60 | feeder2_line10 | 3 | 80.1 | 8.4646e-07 | 1.4965e-06 | 1.0567e-06 | 1.8682e-06
60 | feeder2_line11 | 1 | 354.6 | 80.6421 | 80.6423 | 22.7417 | 22.7418
60 | feeder2_line11 | 2 | 354.6 | 88.8241 | 88.8278 | 25.0491 | 25.0502
60 | feeder2_line11 | 3 | 354.6 | 82.1189 | 82.1157 | 23.1582 | 23.1573
60 | feeder2_line12 | 1 | 80.1 | 5.4773e-07 | 9.9262e-07 | 6.8381e-07 | 1.2392e-06
60 | feeder2_line12 | 2 | 80.1 | 5.4781e-07 | 9.9277e-07 | 6.8391e-07 | 1.2394e-06
60 | feeder2_line12 | 3 | 80.1 | 0.061769 | 0.061769 | 0.077115 | 0.077115
60 | feeder2_line13 | 1 | 354.6 | 80.642 | 80.6423 | 22.7417 | 22.7418
60 | feeder2_line13 | 2 | 354.6 | 88.8241 | 88.8278 | 25.0491 | 25.0502
60 | feeder2_line13 | 3 | 354.6 | 82.1804 | 82.1773 | 23.1755 | 23.1746
60 | feeder2_line14 | 1 | 80.1 | 1.5991 | 1.5991 | 1.9964 | 1.9964
60 | feeder2_line14 | 2 | 80.1 | 2.9884e-07 | 6.4746e-07 | 3.7308e-07 | 8.0831e-07
60 | feeder2_line14 | 3 | 80.1 | 2.9884e-07 | 6.4744e-07 | 3.7309e-07 | 8.0829e-07
60 | feeder2_line15 | 1 | 354.6 | 81.4986 | 81.4989 | 22.9833 | 22.9833
60 | feeder2_line15 | 2 | 354.6 | 88.8241 | 88.8278 | 25.0491 | 25.0502
60 | feeder2_line15 | 3 | 354.6 | 82.1804 | 82.1773 | 23.1755 | 23.1746
60 | feeder2_line16 | 1 | 80.1 | 5.7279e-07 | 1.0319e-06 | 7.151e-07 | 1.2883e-06
60 | feeder2_line16 | 2 | 80.1 | 1.0252 | 1.0252 | 1.2799 | 1.2799
60 | feeder2_line16 | 3 | 80.1 | 5.7287e-07 | 1.0321e-06 | 7.1519e-07 | 1.2885e-06
60 | feeder2_line17 | 1 | 354.6 | 81.4987 | 81.4989 | 22.9833 | 22.9833
60 | feeder2_line17 | 2 | 354.6 | 89.3921 | 89.3958 | 25.2093 | 25.2103
60 | feeder2_line17 | 3 | 354.6 | 82.1804 | 82.1773 | 23.1755 | 23.1746
60 | feeder2_line18 | 1 | 80.1 | 5.4842e-07 | 7.3934e-07 | 6.8467e-07 | 9.2302e-07
60 | feeder2_line18 | 2 | 80.1 | 5.4857e-07 | 7.3954e-07 | 6.8485e-07 | 9.2327e-07
60 | feeder2_line18 | 3 | 80.1 | 0.49168 | 0.49168 | 0.61383 | 0.61383
60 | feeder2_line19 | 1 | 354.6 | 81.4987 | 81.4989 | 22.9833 | 22.9833
60 | feeder2_line19 | 2 | 354.6 | 89.3922 | 89.3958 | 25.2093 | 25.2103
60 | feeder2_line19 | 3 | 354.6 | 82.6656 | 82.6624 | 23.3123 | 23.3114
60 | feeder2_line20 | 1 | 99 | 5.486e-07 | 8.8672e-07 | 5.5415e-07 | 8.9568e-07
60 | feeder2_line20 | 2 | 99 | 5.4877e-07 | 8.8699e-07 | 5.5431e-07 | 8.9595e-07
60 | feeder2_line20 | 3 | 99 | 0.35663 | 0.35662 | 0.36023 | 0.36023
60 | feeder2_line21 | 1 | 354.6 | 81.4988 | 81.4989 | 22.9833 | 22.9833
60 | feeder2_line21 | 2 | 354.6 | 89.3923 | 89.3958 | 25.2093 | 25.2103
60 | feeder2_line21 | 3 | 354.6 | 83.0186 | 83.0153 | 23.4119 | 23.411
60 | feeder2_line22 | 1 | 99 | 5.7364e-07 | 1.0167e-06 | 5.7943e-07 | 1.027e-06
60 | feeder2_line22 | 2 | 99 | 0.093758 | 0.09376 | 0.094705 | 0.094707
60 | feeder2_line22 | 3 | 99 | 5.7365e-07 | 1.0168e-06 | 5.7944e-07 | 1.027e-06
60 | feeder2_line23 | 1 | 99 | 5.7364e-07 | 9.5174e-07 | 5.7943e-07 | 9.6135e-07
60 | feeder2_line23 | 2 | 99 | 5.7382e-07 | 9.5206e-07 | 5.7962e-07 | 9.6167e-07
60 | feeder2_line23 | 3 | 99 | 0.12723 | 0.12723 | 0.12852 | 0.12852
60 | feeder2_line24 | 1 | 354.6 | 81.4988 | 81.4989 | 22.9833 | 22.9833
60 | feeder2_line24 | 2 | 354.6 | 89.485 | 89.4885 | 25.2355 | 25.2365
60 | feeder2_line24 | 3 | 354.6 | 83.1458 | 83.1425 | 23.4478 | 23.4468
60 | feeder2_line25 | 1 | 99 | 0.093755 | 0.093755 | 0.094702 | 0.094702
60 | feeder2_line25 | 2 | 99 | 4.986e-08 | 6.9244e-07 | 5.0364e-08 | 6.9943e-07
60 | feeder2_line25 | 3 | 99 | 5.0012e-08 | 6.922e-07 | 5.0517e-08 | 6.9919e-07
60 | feeder2_line26 | 1 | 99 | 0.22049 | 0.22049 | 0.22272 | 0.22272
60 | feeder2_line26 | 2 | 99 | 5.4912e-07 | 8.579e-07 | 5.5466e-07 | 8.6656e-07
60 | feeder2_line26 | 3 | 99 | 5.4884e-07 | 8.5759e-07 | 5.5438e-07 | 8.6625e-07
60 | feeder2_line27 | 1 | 354.6 | 81.8101 | 81.8101 | 23.0711 | 23.0711
60 | feeder2_line27 | 2 | 354.6 | 89.485 | 89.4885 | 25.2355 | 25.2365
60 | feeder2_line27 | 3 | 354.6 | 83.1458 | 83.1425 | 23.4478 | 23.4468
60 | feeder2_line28 | 1 | 99 | 2.5468e-06 | 7.123e-07 | 2.5725e-06 | 7.1949e-07
60 | feeder2_line28 | 2 | 99 | 0.10848 | 0.10848 | 0.10957 | 0.10957
60 | feeder2_line28 | 3 | 99 | 2.5455e-06 | 7.1228e-07 | 2.5712e-06 | 7.1948e-07
60 | feeder2_line29 | 1 | 354.6 | 81.8101 | 81.8101 | 23.0711 | 23.0711
60 | feeder2_line29 | 2 | 354.6 | 89.5934 | 89.5968 | 25.266 | 25.267
60 | feeder2_line29 | 3 | 354.6 | 83.1459 | 83.1425 | 23.4478 | 23.4468
60 | feeder2_line30 | 1 | 266.4 | 12.7561 | 12.7559 | 4.7883 | 4.7882
60 | feeder2_line30 | 2 | 266.4 | 1.5008 | 1.501 | 0.56336 | 0.56343
60 | feeder2_line30 | 3 | 266.4 | 1.4833 | 1.4833 | 0.55678 | 0.55681
60 | feeder2_line31 | 1 | 354.6 | 94.011 | 94.0107 | 26.5118 | 26.5117
60 | feeder2_line31 | 2 | 354.6 | 90.4321 | 90.4352 | 25.5026 | 25.5034
60 | feeder2_line31 | 3 | 354.6 | 84.1678 | 84.1641 | 23.736 | 23.7349
60 | feeder2_line32 | 1 | 354.6 | 94.0111 | 94.0107 | 26.5119 | 26.5117
60 | feeder2_line32 | 2 | 354.6 | 90.6857 | 90.6888 | 25.5741 | 25.5749
60 | feeder2_line32 | 3 | 354.6 | 84.1678 | 84.1641 | 23.736 | 23.7349
60 | feeder2_line33 | 1 | 99 | 4.9912e-08 | 6.8816e-07 | 5.0416e-08 | 6.9511e-07
60 | feeder2_line33 | 2 | 99 | 0.25774 | 0.25774 | 0.26034 | 0.26034
60 | feeder2_line33 | 3 | 99 | 5.0153e-08 | 6.8799e-07 | 5.0659e-08 | 6.9494e-07
60 | feeder2_line34 | 1 | 354.6 | 94.011 | 94.0107 | 26.5119 | 26.5117
60 | feeder2_line34 | 2 | 354.6 | 90.6857 | 90.6888 | 25.5741 | 25.5749
60 | feeder2_line34 | 3 | 354.6 | 84.4406 | 84.4369 | 23.8129 | 23.8119
60 | feeder2_line35 | 1 | 99 | 3.0006e-07 | 7.6226e-07 | 3.0309e-07 | 7.6996e-07
60 | feeder2_line35 | 2 | 99 | 3.0017e-07 | 7.6252e-07 | 3.032e-07 | 7.7022e-07
60 | feeder2_line35 | 3 | 99 | 0.27536 | 0.27536 | 0.27814 | 0.27814
60 | feeder2_line36 | 1 | 354.6 | 94.0389 | 94.0386 | 26.5197 | 26.5196
60 | feeder2_line36 | 2 | 354.6 | 90.6856 | 90.6888 | 25.5741 | 25.5749
60 | feeder2_line36 | 3 | 354.6 | 84.4406 | 84.4369 | 23.8129 | 23.8119
60 | feeder2_line37 | 1 | 99 | 0.028018 | 0.028013 | 0.028301 | 0.028296
60 | feeder2_line37 | 2 | 99 | 3.0024e-07 | 8.4391e-07 | 3.0328e-07 | 8.5243e-07
60 | feeder2_line37 | 3 | 99 | 3.0009e-07 | 8.433e-07 | 3.0312e-07 | 8.5182e-07
60 | feeder2_line38 | 1 | 99 | 3.2474e-07 | 7.7761e-07 | 3.2802e-07 | 7.8546e-07
60 | feeder2_line38 | 2 | 99 | 1.4152 | 1.4152 | 1.4295 | 1.4295
60 | feeder2_line38 | 3 | 99 | 3.2491e-07 | 7.7763e-07 | 3.2819e-07 | 7.8548e-07
60 | feeder2_line39 | 1 | 266.4 | 12.7561 | 12.7559 | 4.7883 | 4.7882
60 | feeder2_line39 | 2 | 266.4 | 0.13411 | 0.13374 | 0.050341 | 0.050204
60 | feeder2_line39 | 3 | 266.4 | 1.4833 | 1.4833 | 0.55678 | 0.55681
60 | feeder2_line40 | 1 | 354.6 | 94.1323 | 94.1319 | 26.5461 | 26.5459
60 | feeder2_line40 | 2 | 354.6 | 90.6857 | 90.6888 | 25.5741 | 25.5749
60 | feeder2_line40 | 3 | 354.6 | 84.4407 | 84.4369 | 23.8129 | 23.8119
60 | feeder2_line41 | 1 | 99 | 0.093529 | 0.09353 | 0.094474 | 0.094474
60 | feeder2_line41 | 2 | 99 | 4.998e-08 | 7.3753e-07 | 5.0485e-08 | 7.4498e-07
60 | feeder2_line41 | 3 | 99 | 5.0202e-08 | 7.3697e-07 | 5.0709e-08 | 7.4442e-07
60 | feeder2_line42 | 1 | 99 | 2.9975e-07 | 7.5046e-07 | 3.0278e-07 | 7.5804e-07
60 | feeder2_line42 | 2 | 99 | 2.9996e-07 | 7.5103e-07 | 3.0299e-07 | 7.5861e-07
60 | feeder2_line42 | 3 | 99 | 1.2577 | 1.2576 | 1.2704 | 1.2703
60 | feeder2_line43 | 1 | 266.4 | 12.756 | 12.7559 | 4.7883 | 4.7882
60 | feeder2_line43 | 2 | 266.4 | 0.13399 | 0.13374 | 0.050298 | 0.050203
60 | feeder2_line43 | 3 | 266.4 | 0.33193 | 0.33165 | 0.1246 | 0.12449
60 | feeder2_line44 | 1 | 354.6 | 94.1324 | 94.1319 | 26.5461 | 26.5459
60 | feeder2_line44 | 2 | 354.6 | 90.6857 | 90.6888 | 25.5741 | 25.5749
60 | feeder2_line44 | 3 | 354.6 | 84.7947 | 84.7908 | 23.9128 | 23.9117
60 | feeder2_line45 | 1 | 99 | 4.9923e-08 | 5.8159e-07 | 5.0427e-08 | 5.8746e-07
60 | feeder2_line45 | 2 | 99 | 4.9978e-08 | 5.8173e-07 | 5.0483e-08 | 5.876e-07
60 | feeder2_line45 | 3 | 99 | 0.35685 | 0.35684 | 0.36045 | 0.36044
60 | feeder2_line46 | 1 | 99 | 5.7454e-07 | 1.3604e-06 | 5.8035e-07 | 1.3742e-06
60 | feeder2_line46 | 2 | 99 | 5.7498e-07 | 1.3615e-06 | 5.8079e-07 | 1.3752e-06
60 | feeder2_line46 | 3 | 99 | 0.16255 | 0.16254 | 0.16419 | 0.16419
60 | feeder2_line47 | 1 | 266.4 | 12.7561 | 12.7559 | 4.7883 | 4.7882
60 | feeder2_line47 | 2 | 266.4 | 0.13399 | 0.13374 | 0.050295 | 0.050203
60 | feeder2_line47 | 3 | 266.4 | 0.16987 | 0.1696 | 0.063766 | 0.063664
60 | feeder2_line48 | 1 | 99 | 2.2739 | 2.2739 | 2.2968 | 2.2969
60 | feeder2_line48 | 2 | 99 | 4.9899e-08 | 7.3305e-07 | 5.0403e-08 | 7.4045e-07
60 | feeder2_line48 | 3 | 99 | 5.0101e-08 | 7.3264e-07 | 5.0607e-08 | 7.4004e-07
60 | feeder2_line49 | 1 | 266.4 | 11.2284 | 11.2282 | 4.2149 | 4.2148
60 | feeder2_line49 | 2 | 266.4 | 0.13397 | 0.13374 | 0.050288 | 0.050203
60 | feeder2_line49 | 3 | 266.4 | 0.16986 | 0.1696 | 0.063759 | 0.063664
60 | feeder2_line50 | 1 | 99 | 5.7447e-07 | 1.238e-06 | 5.8028e-07 | 1.2505e-06
60 | feeder2_line50 | 2 | 99 | 0.084946 | 0.084962 | 0.085804 | 0.08582
60 | feeder2_line50 | 3 | 99 | 5.7466e-07 | 1.2384e-06 | 5.8046e-07 | 1.2509e-06
60 | feeder2_line51 | 1 | 99 | 10.5722 | 10.5722 | 10.679 | 10.679
60 | feeder2_line51 | 2 | 99 | 5.7496e-07 | 1.3451e-06 | 5.8077e-07 | 1.3587e-06
60 | feeder2_line51 | 3 | 99 | 5.7464e-07 | 1.3444e-06 | 5.8044e-07 | 1.3579e-06
60 | feeder2_line52 | 1 | 266.4 | 0.65614 | 0.65605 | 0.2463 | 0.24626
60 | feeder2_line52 | 2 | 266.4 | 0.048887 | 0.048783 | 0.018351 | 0.018312
60 | feeder2_line52 | 3 | 266.4 | 0.16972 | 0.1696 | 0.063707 | 0.063664
60 | feeder2_line53 | 1 | 99 | 5.4951e-07 | 7.5555e-07 | 5.5506e-07 | 7.6318e-07
60 | feeder2_line53 | 2 | 99 | 0.048782 | 0.048783 | 0.049275 | 0.049276
60 | feeder2_line53 | 3 | 99 | 5.4961e-07 | 7.558e-07 | 5.5516e-07 | 7.6344e-07
60 | feeder2_line54 | 1 | 266.4 | 0.65596 | 0.65605 | 0.24623 | 0.24626
60 | feeder2_line54 | 2 | 266.4 | 8.5754e-05 | 4.6389e-06 | 3.219e-05 | 1.7413e-06
60 | feeder2_line54 | 3 | 266.4 | 0.16952 | 0.1696 | 0.063635 | 0.063664
60 | feeder2_line55 | 1 | 99 | 0.1812 | 0.1812 | 0.18303 | 0.18303
60 | feeder2_line55 | 2 | 99 | 5.0024e-08 | 7.3333e-07 | 5.0529e-08 | 7.4073e-07
60 | feeder2_line55 | 3 | 99 | 5.0265e-08 | 7.3269e-07 | 5.0773e-08 | 7.4009e-07
60 | feeder2_line56 | 1 | 354.6 | 94.3123 | 94.3118 | 26.5968 | 26.5967
60 | feeder2_line56 | 2 | 354.6 | 90.6858 | 90.6888 | 25.5741 | 25.5749
60 | feeder2_line56 | 3 | 354.6 | 84.7947 | 84.7908 | 23.9128 | 23.9117
60 | feeder2_line57 | 1 | 99 | 7.489e-07 | 1.5476e-06 | 7.5646e-07 | 1.5632e-06
60 | feeder2_line57 | 2 | 99 | 7.484e-07 | 1.549e-06 | 7.5596e-07 | 1.5646e-06
60 | feeder2_line57 | 3 | 99 | 0.1696 | 0.1696 | 0.17131 | 0.17131
60 | feeder2_line58 | 1 | 266.4 | 0.65603 | 0.65605 | 0.24626 | 0.24626
60 | feeder2_line58 | 2 | 266.4 | 1.9008e-05 | 2.6933e-06 | 7.1352e-06 | 1.011e-06
60 | feeder2_line58 | 3 | 266.4 | 1.8991e-05 | 2.6919e-06 | 7.1287e-06 | 1.0105e-06
60 | feeder2_line59 | 1 | 99 | 4.9931e-08 | 5.3796e-07 | 5.0435e-08 | 5.434e-07
60 | feeder2_line59 | 2 | 99 | 4.9896e-08 | 5.3845e-07 | 5.04e-08 | 5.4389e-07
60 | feeder2_line59 | 3 | 99 | 0.10811 | 0.10811 | 0.1092 | 0.1092
60 | feeder2_line60 | 1 | 99 | 2.9972e-07 | 8.1303e-07 | 3.0274e-07 | 8.2124e-07
60 | feeder2_line60 | 2 | 99 | 2.9997e-07 | 8.1376e-07 | 3.03e-07 | 8.2198e-07
60 | feeder2_line60 | 3 | 99 | 0.061628 | 0.061627 | 0.06225 | 0.06225
60 | feeder2_line61 | 1 | 266.4 | 0.19841 | 0.19858 | 0.074478 | 0.074543
60 | feeder2_line61 | 2 | 266.4 | 2.6207 | 2.6209 | 0.98373 | 0.98381
60 | feeder2_line61 | 3 | 266.4 | 1.0447 | 1.0449 | 0.39214 | 0.39221
60 | feeder2_line62 | 1 | 354.6 | 94.5097 | 94.5094 | 26.6525 | 26.6524
60 | feeder2_line62 | 2 | 354.6 | 92.2156 | 92.2188 | 26.0055 | 26.0064
60 | feeder2_line62 | 3 | 354.6 | 85.532 | 85.5283 | 24.1207 | 24.1197
60 | feeder2_line63 | 1 | 99 | 0.36007 | 0.36007 | 0.36371 | 0.36371
60 | feeder2_line63 | 2 | 99 | 5.7499e-07 | 1.2235e-06 | 5.808e-07 | 1.2358e-06
60 | feeder2_line63 | 3 | 99 | 5.7466e-07 | 1.2228e-06 | 5.8046e-07 | 1.2351e-06
60 | feeder2_line64 | 1 | 99 | 0.29598 | 0.29598 | 0.29897 | 0.29897
60 | feeder2_line64 | 2 | 99 | 9.7129e-12 | 3.2229e-07 | 9.811e-12 | 3.2555e-07
60 | feeder2_line64 | 3 | 99 | 6.7917e-12 | 3.221e-07 | 6.8604e-12 | 3.2536e-07
60 | feeder2_line65 | 1 | 99 | 4.9954e-08 | 6.4482e-07 | 5.0459e-08 | 6.5134e-07
60 | feeder2_line65 | 2 | 99 | 1.5326 | 1.5326 | 1.548 | 1.548
60 | feeder2_line65 | 3 | 99 | 5.0348e-08 | 6.4406e-07 | 5.0856e-08 | 6.5056e-07
60 | feeder2_line66 | 1 | 354.6 | 94.5096 | 94.5094 | 26.6525 | 26.6524
60 | feeder2_line66 | 2 | 354.6 | 93.0663 | 93.0695 | 26.2454 | 26.2463
60 | feeder2_line66 | 3 | 354.6 | 85.5319 | 85.5283 | 24.1207 | 24.1197
60 | feeder2_line67 | 1 | 99 | 2.4969e-08 | 3.6433e-07 | 2.5221e-08 | 3.6801e-07
60 | feeder2_line67 | 2 | 99 | 2.5025e-08 | 3.6429e-07 | 2.5278e-08 | 3.6797e-07
60 | feeder2_line67 | 3 | 99 | 0.093566 | 0.093565 | 0.094511 | 0.09451
60 | feeder2_line68 | 1 | 266.4 | 0.19845 | 0.19858 | 0.074493 | 0.074543
60 | feeder2_line68 | 2 | 266.4 | 2.6207 | 2.6209 | 0.98375 | 0.98381
60 | feeder2_line68 | 3 | 266.4 | 0.97601 | 0.97614 | 0.36637 | 0.36642
60 | feeder2_line69 | 1 | 99 | 1.5611 | 1.5611 | 1.5769 | 1.5769
60 | feeder2_line69 | 2 | 99 | 2.5583e-06 | 6.6946e-07 | 2.5842e-06 | 6.7623e-07
60 | feeder2_line69 | 3 | 99 | 2.5534e-06 | 6.6873e-07 | 2.5792e-06 | 6.7549e-07
60 | feeder2_line70 | 1 | 354.6 | 95.3849 | 95.3848 | 26.8993 | 26.8993
60 | feeder2_line70 | 2 | 354.6 | 93.0662 | 93.0695 | 26.2454 | 26.2463
60 | feeder2_line70 | 3 | 354.6 | 85.5318 | 85.5283 | 24.1207 | 24.1197
60 | feeder2_line71 | 1 | 99 | 4.9968e-08 | 7.1971e-07 | 5.0472e-08 | 7.2698e-07
60 | feeder2_line71 | 2 | 99 | 0.32448 | 0.3245 | 0.32775 | 0.32778
60 | feeder2_line71 | 3 | 99 | 5.0378e-08 | 7.1875e-07 | 5.0887e-08 | 7.2601e-07
60 | feeder2_line72 | 1 | 354.6 | 95.385 | 95.3848 | 26.8993 | 26.8993
60 | feeder2_line72 | 2 | 354.6 | 93.3869 | 93.3901 | 26.3358 | 26.3368
60 | feeder2_line72 | 3 | 354.6 | 85.5319 | 85.5283 | 24.1207 | 24.1197
60 | feeder2_line73 | 1 | 99 | 6.0134e-07 | 1.5424e-06 | 6.0742e-07 | 1.558e-06
60 | feeder2_line73 | 2 | 99 | 0.25779 | 0.2578 | 0.2604 | 0.2604
60 | feeder2_line73 | 3 | 99 | 6.0092e-07 | 1.5408e-06 | 6.0699e-07 | 1.5564e-06
60 | feeder2_line74 | 1 | 99 | 4.994e-08 | 4.6003e-07 | 5.0444e-08 | 4.6467e-07
60 | feeder2_line74 | 2 | 99 | 0.97644 | 0.97647 | 0.98631 | 0.98634
60 | feeder2_line74 | 3 | 99 | 5.0307e-08 | 4.5955e-07 | 5.0816e-08 | 4.6419e-07
60 | feeder2_line75 | 1 | 266.4 | 0.19855 | 0.19858 | 0.07453 | 0.074543
60 | feeder2_line75 | 2 | 266.4 | 1.4803 | 1.4803 | 0.55566 | 0.55566
60 | feeder2_line75 | 3 | 266.4 | 0.9761 | 0.97614 | 0.3664 | 0.36642
60 | feeder2_line76 | 1 | 99 | 0.19858 | 0.19858 | 0.20059 | 0.20059
60 | feeder2_line76 | 2 | 99 | 8.5195e-07 | 1.5909e-06 | 8.6056e-07 | 1.607e-06
60 | feeder2_line76 | 3 | 99 | 8.5106e-07 | 1.5894e-06 | 8.5966e-07 | 1.6055e-06
60 | feeder2_line77 | 1 | 99 | 2.4971e-08 | 5.781e-07 | 2.5223e-08 | 5.8394e-07
60 | feeder2_line77 | 2 | 99 | 2.5029e-08 | 5.7803e-07 | 2.5281e-08 | 5.8387e-07
60 | feeder2_line77 | 3 | 99 | 0.97614 | 0.97615 | 0.986 | 0.98601
60 | feeder2_line78 | 1 | 266.4 | 8.3297e-12 | 9.5866e-07 | 3.1268e-12 | 3.5986e-07
60 | feeder2_line78 | 2 | 266.4 | 1.4803 | 1.4803 | 0.55567 | 0.55566
60 | feeder2_line78 | 3 | 266.4 | 1.0809e-11 | 9.5792e-07 | 4.0576e-12 | 3.5958e-07
60 | feeder2_line79 | 1 | 354.6 | 1.3192 | 1.3189 | 0.37201 | 0.37193
60 | feeder2_line79 | 2 | 354.6 | 1.4806 | 1.4804 | 0.41755 | 0.41747
60 | feeder2_line79 | 3 | 354.6 | 2.8029 | 2.8025 | 0.79044 | 0.79033
60 | feeder2_line80 | 1 | 354.6 | 96.4337 | 96.4329 | 27.1951 | 27.1948
60 | feeder2_line80 | 2 | 354.6 | 94.5546 | 94.5573 | 26.6651 | 26.6659
60 | feeder2_line80 | 3 | 354.6 | 88.0047 | 88.0005 | 24.818 | 24.8168
60 | feeder2_line81 | 1 | 354.6 | 96.4336 | 96.4329 | 27.195 | 27.1948
60 | feeder2_line81 | 2 | 354.6 | 94.5545 | 94.5573 | 26.6651 | 26.6659
60 | feeder2_line81 | 3 | 354.6 | 88.2538 | 88.2496 | 24.8883 | 24.8871
60 | feeder2_line82 | 1 | 354.6 | 2.4032e-11 | 7.386e-07 | 6.7773e-12 | 2.0829e-07
60 | feeder2_line82 | 2 | 354.6 | 1.2758e-11 | 7.3842e-07 | 3.5979e-12 | 2.0824e-07
60 | feeder2_line82 | 3 | 354.6 | 0.25046 | 0.25045 | 0.070631 | 0.07063
60 | feeder2_line83 | 1 | 354.6 | 96.4338 | 96.4329 | 27.1951 | 27.1948
60 | feeder2_line83 | 2 | 354.6 | 94.6705 | 94.6731 | 26.6978 | 26.6986
60 | feeder2_line83 | 3 | 354.6 | 88.254 | 88.2496 | 24.8883 | 24.8871
60 | feeder2_line84 | 1 | 354.6 | 1.195e-11 | 1.3057e-06 | 3.37e-12 | 3.6821e-07
60 | feeder2_line84 | 2 | 354.6 | 0.11576 | 0.11578 | 0.032646 | 0.032651
60 | feeder2_line84 | 3 | 354.6 | 6.755e-12 | 1.3038e-06 | 1.905e-12 | 3.6769e-07
60 | feeder2_line85 | 1 | 99 | 1.4174 | 1.4174 | 1.4317 | 1.4317
60 | feeder2_line85 | 2 | 99 | 5.016e-08 | 4.6595e-07 | 5.0667e-08 | 4.7065e-07
60 | feeder2_line85 | 3 | 99 | 5.0464e-08 | 4.6532e-07 | 5.0974e-08 | 4.7002e-07
60 | feeder2_line86 | 1 | 354.6 | 97.2666 | 97.2656 | 27.43 | 27.4297
60 | feeder2_line86 | 2 | 354.6 | 94.6706 | 94.6731 | 26.6979 | 26.6986
60 | feeder2_line86 | 3 | 354.6 | 88.2541 | 88.2496 | 24.8884 | 24.8871
60 | feeder2_line87 | 1 | 354.6 | 97.2668 | 97.2656 | 27.43 | 27.4297
60 | feeder2_line87 | 2 | 354.6 | 95.4202 | 95.4226 | 26.9093 | 26.9099
60 | feeder2_line87 | 3 | 354.6 | 89.1265 | 89.1218 | 25.1344 | 25.1331
60 | feeder2_line88 | 1 | 354.6 | 0.0001156 | 3.3857e-06 | 3.2601e-05 | 9.5479e-07
60 | feeder2_line88 | 2 | 354.6 | 1.4891 | 1.4891 | 0.41994 | 0.41993
60 | feeder2_line88 | 3 | 354.6 | 1.4508 | 1.4507 | 0.40912 | 0.40912
60 | feeder2_line89 | 1 | 354.6 | 97.2645 | 97.2656 | 27.4294 | 27.4297
60 | feeder2_line89 | 2 | 354.6 | 96.1181 | 96.1228 | 27.1061 | 27.1074
60 | feeder2_line89 | 3 | 354.6 | 89.1242 | 89.1218 | 25.1337 | 25.1331
60 | feeder2_line90 | 1 | 354.6 | 0.00072975 | 2.0434e-06 | 0.0002058 | 5.7626e-07
60 | feeder2_line90 | 2 | 354.6 | 1.0483 | 1.0483 | 0.29562 | 0.29564
60 | feeder2_line90 | 3 | 354.6 | 0.00072653 | 2.0407e-06 | 0.00020489 | 5.755e-07
60 | feeder2_line91 | 1 | 354.6 | 97.2644 | 97.2656 | 27.4293 | 27.4297
60 | feeder2_line91 | 2 | 354.6 | 96.1181 | 96.1228 | 27.1061 | 27.1074
60 | feeder2_line91 | 3 | 354.6 | 89.1856 | 89.1833 | 25.151 | 25.1504
60 | feeder2_line92 | 1 | 354.6 | 3.9243e-12 | 1.0311e-06 | 1.1067e-12 | 2.9078e-07
60 | feeder2_line92 | 2 | 354.6 | 3.9243e-12 | 1.0307e-06 | 1.1067e-12 | 2.9068e-07
60 | feeder2_line92 | 3 | 354.6 | 0.061462 | 0.061461 | 0.017333 | 0.017332
60 | feeder2_line93 | 1 | 99 | 2.5006e-08 | 3.4422e-07 | 2.5258e-08 | 3.477e-07
60 | feeder2_line93 | 2 | 99 | 0.11569 | 0.11571 | 0.11686 | 0.11688
60 | feeder2_line93 | 3 | 99 | 2.5259e-08 | 3.4356e-07 | 2.5515e-08 | 3.4703e-07
60 | feeder2_line94 | 1 | 354.6 | 2.5006e-06 | 1.6757e-06 | 7.052e-07 | 4.7255e-07
60 | feeder2_line94 | 2 | 354.6 | 0.97767 | 0.97768 | 0.27571 | 0.27571
60 | feeder2_line94 | 3 | 354.6 | 2.5261e-06 | 1.6729e-06 | 7.1237e-07 | 4.7178e-07
60 | feeder2_line95 | 1 | 99 | 3.5901e-06 | 2.6254e-06 | 3.6264e-06 | 2.652e-06
60 | feeder2_line95 | 2 | 99 | 1.4891 | 1.4891 | 1.5041 | 1.5041
60 | feeder2_line95 | 3 | 99 | 3.5807e-06 | 2.6207e-06 | 3.6168e-06 | 2.6472e-06
60 | feeder2_line96 | 1 | 354.6 | 0.00012188 | 6.2572e-07 | 3.4372e-05 | 1.7646e-07
60 | feeder2_line96 | 2 | 354.6 | 0.00012179 | 6.2559e-07 | 3.4346e-05 | 1.7642e-07
60 | feeder2_line96 | 3 | 354.6 | 1.4507 | 1.4507 | 0.40911 | 0.40912
60 | feeder2_line97 | 1 | 354.6 | 97.4184 | 97.4194 | 27.4728 | 27.473
60 | feeder2_line97 | 2 | 354.6 | 96.1182 | 96.1228 | 27.1061 | 27.1074
60 | feeder2_line97 | 3 | 354.6 | 89.1857 | 89.1833 | 25.1511 | 25.1504
60 | feeder2_line98 | 1 | 354.6 | 0.15603 | 0.15429 | 0.044 | 0.043511
60 | feeder2_line98 | 2 | 354.6 | 0.0017092 | 6.2268e-07 | 0.000482 | 1.756e-07
60 | feeder2_line98 | 3 | 354.6 | 0.0017074 | 6.2217e-07 | 0.00048149 | 1.7546e-07
60 | feeder2_line99 | 1 | 99 | 2.5e-08 | 4.4993e-07 | 2.5252e-08 | 4.5448e-07
60 | feeder2_line99 | 2 | 99 | 2.5092e-08 | 4.4975e-07 | 2.5345e-08 | 4.5429e-07
60 | feeder2_line99 | 3 | 99 | 1.4507 | 1.4507 | 1.4654 | 1.4654
60 | feeder2_line100 | 1 | 99 | 0.15431 | 0.15429 | 0.15587 | 0.15585
60 | feeder2_line100 | 2 | 99 | 2.5108e-08 | 6.1777e-07 | 2.5362e-08 | 6.2401e-07
60 | feeder2_line100 | 3 | 99 | 2.5271e-08 | 6.1682e-07 | 2.5527e-08 | 6.2305e-07
60 | feeder2_line101 | 1 | 354.6 | 0.9777 | 0.97752 | 0.27572 | 0.27567
60 | feeder2_line101 | 2 | 354.6 | 1.4806 | 1.4804 | 0.41755 | 0.41747
60 | feeder2_line101 | 3 | 354.6 | 2.8029 | 2.8025 | 0.79043 | 0.79033
60 | feeder2_line102 | 1 | 99 | 0.44876 | 0.44875 | 0.45329 | 0.45329
60 | feeder2_line102 | 2 | 99 | 2.3464e-06 | 8.8281e-07 | 2.3701e-06 | 8.9173e-07
60 | feeder2_line102 | 3 | 99 | 2.3421e-06 | 8.8167e-07 | 2.3657e-06 | 8.9058e-07
60 | feeder2_line103 | 1 | 99 | 5.5244e-07 | 8.0827e-07 | 5.5802e-07 | 8.1643e-07
60 | feeder2_line103 | 2 | 99 | 0.096265 | 0.096267 | 0.097238 | 0.09724
60 | feeder2_line103 | 3 | 99 | 5.5128e-07 | 8.0699e-07 | 5.5685e-07 | 8.1514e-07
60 | feeder2_line104 | 1 | 354.6 | 0.97769 | 0.97752 | 0.27572 | 0.27567
60 | feeder2_line104 | 2 | 354.6 | 1.406 | 1.4058 | 0.39651 | 0.39645
60 | feeder2_line104 | 3 | 354.6 | 2.8028 | 2.8025 | 0.79042 | 0.79033
60 | feeder2_line105 | 1 | 99 | 2.5623e-06 | 7.4371e-07 | 2.5882e-06 | 7.5122e-07
60 | feeder2_line105 | 2 | 99 | 2.5604e-06 | 7.435e-07 | 2.5863e-06 | 7.5101e-07
60 | feeder2_line105 | 3 | 99 | 0.4927 | 0.49269 | 0.49767 | 0.49766
60 | feeder2_line106 | 1 | 354.6 | 0.97766 | 0.97752 | 0.27571 | 0.27567
60 | feeder2_line106 | 2 | 354.6 | 1.406 | 1.4058 | 0.3965 | 0.39645
60 | feeder2_line106 | 3 | 354.6 | 2.3488 | 2.3485 | 0.66237 | 0.66231
60 | feeder2_line107 | 1 | 99 | 3.2619e-07 | 9.0631e-07 | 3.2949e-07 | 9.1546e-07
60 | feeder2_line107 | 2 | 99 | 0.98512 | 0.98514 | 0.99507 | 0.99509
60 | feeder2_line107 | 3 | 99 | 3.2606e-07 | 9.0486e-07 | 3.2936e-07 | 9.14e-07
60 | feeder2_line108 | 1 | 354.6 | 0.97767 | 0.97752 | 0.27571 | 0.27567
60 | feeder2_line108 | 2 | 354.6 | 0.55577 | 0.55553 | 0.15673 | 0.15666
60 | feeder2_line108 | 3 | 354.6 | 2.3488 | 2.3485 | 0.66237 | 0.66231
60 | feeder2_line109 | 1 | 354.6 | 97.6547 | 97.6544 | 27.5394 | 27.5393
60 | feeder2_line109 | 2 | 354.6 | 96.1195 | 96.1228 | 27.1064 | 27.1074
60 | feeder2_line109 | 3 | 354.6 | 89.1869 | 89.1833 | 25.1514 | 25.1504
60 | feeder2_line110 | 1 | 99 | 0.2361 | 0.2353 | 0.23849 | 0.23767
60 | feeder2_line110 | 2 | 99 | 0.0008095 | 9.1484e-07 | 0.00081767 | 9.2408e-07
60 | feeder2_line110 | 3 | 99 | 0.00080707 | 9.1296e-07 | 0.00081522 | 9.2219e-07
60 | feeder2_line111 | 1 | 99 | 2.5001e-08 | 3.8426e-07 | 2.5254e-08 | 3.8814e-07
60 | feeder2_line111 | 2 | 99 | 1.4663 | 1.4662 | 1.4811 | 1.4811
60 | feeder2_line111 | 3 | 99 | 2.5245e-08 | 3.8358e-07 | 2.55e-08 | 3.8746e-07
60 | feeder2_line112 | 1 | 99 | 3.2649e-07 | 9.2342e-07 | 3.2979e-07 | 9.3275e-07
60 | feeder2_line112 | 2 | 99 | 0.040625 | 0.040665 | 0.041035 | 0.041075
60 | feeder2_line112 | 3 | 99 | 3.2634e-07 | 9.2176e-07 | 3.2963e-07 | 9.3108e-07
60 | feeder2_line113 | 1 | 99 | 0.12794 | 0.12794 | 0.12923 | 0.12923
60 | feeder2_line113 | 2 | 99 | 3.2689e-07 | 9.1116e-07 | 3.3019e-07 | 9.2037e-07
60 | feeder2_line113 | 3 | 99 | 3.2667e-07 | 9.097e-07 | 3.2997e-07 | 9.1889e-07
60 | feeder2_line114 | 1 | 99 | 0.096221 | 0.096222 | 0.097193 | 0.097194
60 | feeder2_line114 | 2 | 99 | 2.5072e-08 | 4.3898e-07 | 2.5325e-08 | 4.4342e-07
60 | feeder2_line114 | 3 | 99 | 2.5213e-08 | 4.3842e-07 | 2.5468e-08 | 4.4285e-07
60 | feeder2_line115 | 1 | 99 | 2.4987e-08 | 5.6558e-07 | 2.5239e-08 | 5.7129e-07
60 | feeder2_line115 | 2 | 99 | 0.33254 | 0.33254 | 0.3359 | 0.3359
60 | feeder2_line115 | 3 | 99 | 2.5214e-08 | 5.6466e-07 | 2.5468e-08 | 5.7037e-07
60 | feeder2_line116 | 1 | 354.6 | 0.97768 | 0.97753 | 0.27571 | 0.27567
60 | feeder2_line116 | 2 | 354.6 | 0.22327 | 0.22302 | 0.062963 | 0.062893
60 | feeder2_line116 | 3 | 354.6 | 2.3488 | 2.3485 | 0.66238 | 0.66231
60 | feeder2_line117 | 1 | 99 | 5.005e-08 | 6.4746e-07 | 5.0555e-08 | 6.54e-07
60 | feeder2_line117 | 2 | 99 | 0.16238 | 0.1624 | 0.16402 | 0.16405
60 | feeder2_line117 | 3 | 99 | 5.0608e-08 | 6.46e-07 | 5.1119e-08 | 6.5252e-07
60 | feeder2_line118 | 1 | 354.6 | 97.6547 | 97.6544 | 27.5394 | 27.5393
60 | feeder2_line118 | 2 | 354.6 | 96.281 | 96.2844 | 27.152 | 27.153
60 | feeder2_line118 | 3 | 354.6 | 89.187 | 89.1833 | 25.1514 | 25.1504
60 | feeder2_line119 | 1 | 99 | 2.4988e-08 | 6.0857e-07 | 2.524e-08 | 6.1472e-07
60 | feeder2_line119 | 2 | 99 | 2.5067e-08 | 6.0842e-07 | 2.532e-08 | 6.1457e-07
60 | feeder2_line119 | 3 | 99 | 0.54603 | 0.54602 | 0.55154 | 0.55154
60 | feeder2_line120 | 1 | 354.6 | 0.97768 | 0.97753 | 0.27571 | 0.27567
60 | feeder2_line120 | 2 | 354.6 | 0.22327 | 0.22302 | 0.062963 | 0.062893
60 | feeder2_line120 | 3 | 354.6 | 1.8708 | 1.8706 | 0.52758 | 0.52752
60 | feeder2_line121 | 1 | 99 | 3.2619e-07 | 9.424e-07 | 3.2948e-07 | 9.5192e-07
60 | feeder2_line121 | 2 | 99 | 0.043835 | 0.043836 | 0.044278 | 0.044279
60 | feeder2_line121 | 3 | 99 | 3.2604e-07 | 9.4085e-07 | 3.2934e-07 | 9.5036e-07
60 | feeder2_line122 | 1 | 354.6 | 0.97765 | 0.97753 | 0.27571 | 0.27567
60 | feeder2_line122 | 2 | 354.6 | 0.17942 | 0.17918 | 0.050598 | 0.050532
60 | feeder2_line122 | 3 | 354.6 | 1.8708 | 1.8706 | 0.52757 | 0.52752
60 | feeder2_line123 | 1 | 99 | 5.7741e-07 | 9.7654e-07 | 5.8324e-07 | 9.864e-07
60 | feeder2_line123 | 2 | 99 | 5.7727e-07 | 9.7631e-07 | 5.831e-07 | 9.8617e-07
60 | feeder2_line123 | 3 | 99 | 0.1083 | 0.1083 | 0.1094 | 0.1094
60 | feeder2_line124 | 1 | 354.6 | 0.97769 | 0.97753 | 0.27572 | 0.27567
60 | feeder2_line124 | 2 | 354.6 | 0.17933 | 0.17918 | 0.050573 | 0.050532
60 | feeder2_line124 | 3 | 354.6 | 1.7916 | 1.7914 | 0.50524 | 0.50518
60 | feeder2_line125 | 1 | 99 | 5.7741e-07 | 9.0779e-07 | 5.8324e-07 | 9.1696e-07
60 | feeder2_line125 | 2 | 99 | 5.7727e-07 | 9.0758e-07 | 5.831e-07 | 9.1675e-07
60 | feeder2_line125 | 3 | 99 | 0.15483 | 0.15482 | 0.1564 | 0.15639
60 | feeder2_line126 | 1 | 354.6 | 0.97782 | 0.97753 | 0.27575 | 0.27567
60 | feeder2_line126 | 2 | 354.6 | 0.17949 | 0.17918 | 0.050618 | 0.050532
60 | feeder2_line126 | 3 | 354.6 | 1.6856 | 1.6853 | 0.47536 | 0.47527
60 | feeder2_line127 | 1 | 99 | 5.774e-07 | 1.0868e-06 | 5.8323e-07 | 1.0977e-06
60 | feeder2_line127 | 2 | 99 | 5.7726e-07 | 1.0865e-06 | 5.8309e-07 | 1.0975e-06
60 | feeder2_line127 | 3 | 99 | 0.21253 | 0.21253 | 0.21468 | 0.21467
60 | feeder2_line128 | 1 | 354.6 | 0.9778 | 0.97753 | 0.27575 | 0.27567
60 | feeder2_line128 | 2 | 354.6 | 0.17941 | 0.17918 | 0.050594 | 0.050532
60 | feeder2_line128 | 3 | 354.6 | 1.5293 | 1.529 | 0.43127 | 0.43119
60 | feeder2_line129 | 1 | 99 | 5.5241e-07 | 8.8121e-07 | 5.5799e-07 | 8.9011e-07
60 | feeder2_line129 | 2 | 99 | 0.17918 | 0.17918 | 0.18099 | 0.18099
60 | feeder2_line129 | 3 | 99 | 5.5121e-07 | 8.7975e-07 | 5.5678e-07 | 8.8864e-07
60 | feeder2_line130 | 1 | 354.6 | 0.97784 | 0.97753 | 0.27576 | 0.27567
60 | feeder2_line130 | 2 | 354.6 | 0.00031027 | 4.6622e-06 | 8.7499e-05 | 1.3148e-06
60 | feeder2_line130 | 3 | 354.6 | 1.5293 | 1.529 | 0.43128 | 0.43119
60 | feeder2_line131 | 1 | 99 | 5.774e-07 | 9.7667e-07 | 5.8323e-07 | 9.8654e-07
60 | feeder2_line131 | 2 | 99 | 5.7727e-07 | 9.7648e-07 | 5.831e-07 | 9.8634e-07
60 | feeder2_line131 | 3 | 99 | 0.16251 | 0.16251 | 0.16415 | 0.16415
60 | feeder2_line132 | 1 | 354.6 | 0.97766 | 0.97753 | 0.27571 | 0.27567
60 | feeder2_line132 | 2 | 354.6 | 0.00012636 | 2.9315e-06 | 3.5635e-05 | 8.2669e-07
60 | feeder2_line132 | 3 | 354.6 | 1.4158 | 1.4157 | 0.39928 | 0.39924
60 | feeder2_line133 | 1 | 99 | 0.97753 | 0.97754 | 0.98741 | 0.98741
60 | feeder2_line133 | 2 | 99 | 3.0116e-07 | 9.8427e-07 | 3.0421e-07 | 9.9422e-07
60 | feeder2_line133 | 3 | 99 | 3.0082e-07 | 9.8284e-07 | 3.0385e-07 | 9.9277e-07
60 | feeder2_line134 | 1 | 354.6 | 8.1519e-12 | 1.7951e-06 | 2.2989e-12 | 5.0623e-07
60 | feeder2_line134 | 2 | 354.6 | 1.3902e-11 | 1.7949e-06 | 3.9206e-12 | 5.0617e-07
60 | feeder2_line134 | 3 | 354.6 | 1.4157 | 1.4157 | 0.39924 | 0.39924
60 | feeder2_line135 | 1 | 99 | 0.32503 | 0.32502 | 0.32832 | 0.3283
60 | feeder2_line135 | 2 | 99 | 5.0294e-08 | 5.8991e-07 | 5.0802e-08 | 5.9587e-07
60 | feeder2_line135 | 3 | 99 | 5.0651e-08 | 5.8885e-07 | 5.1162e-08 | 5.948e-07
60 | feeder2_line136 | 1 | 354.6 | 97.9785 | 97.9782 | 27.6307 | 27.6306
60 | feeder2_line136 | 2 | 354.6 | 96.281 | 96.2844 | 27.152 | 27.153
60 | feeder2_line136 | 3 | 354.6 | 89.1869 | 89.1833 | 25.1514 | 25.1504
60 | feeder2_line137 | 1 | 99 | 0.085051 | 0.085036 | 0.08591 | 0.085895
60 | feeder2_line137 | 2 | 99 | 8.5621e-07 | 1.589e-06 | 8.6486e-07 | 1.6051e-06
60 | feeder2_line137 | 3 | 99 | 8.545e-07 | 1.5861e-06 | 8.6313e-07 | 1.6021e-06
60 | feeder2_line138 | 1 | 354.6 | 98.0636 | 98.0633 | 27.6547 | 27.6546
60 | feeder2_line138 | 2 | 354.6 | 96.281 | 96.2844 | 27.152 | 27.153
60 | feeder2_line138 | 3 | 354.6 | 89.187 | 89.1833 | 25.1514 | 25.1504
60 | feeder2_line139 | 1 | 99 | 5.0069e-08 | 4.955e-07 | 5.0575e-08 | 5.0051e-07
60 | feeder2_line139 | 2 | 99 | 5.0298e-08 | 4.9517e-07 | 5.0806e-08 | 5.0018e-07
60 | feeder2_line139 | 3 | 99 | 9.7423 | 9.7422 | 9.8407 | 9.8406
60 | feeder2_line140 | 1 | 354.6 | 98.0637 | 98.0633 | 27.6547 | 27.6546
60 | feeder2_line140 | 2 | 354.6 | 96.2811 | 96.2844 | 27.152 | 27.153
60 | feeder2_line140 | 3 | 354.6 | 98.8833 | 98.8794 | 27.8859 | 27.8848
60 | feeder2_line141 | 1 | 99 | 2.5484e-06 | 4.9021e-07 | 2.5741e-06 | 4.9517e-07
60 | feeder2_line141 | 2 | 99 | 1.2608 | 1.2608 | 1.2735 | 1.2735
60 | feeder2_line141 | 3 | 99 | 2.5368e-06 | 4.8898e-07 | 2.5624e-06 | 4.9392e-07
60 | feeder2_line142 | 1 | 354.6 | 98.0635 | 98.0633 | 27.6547 | 27.6546
60 | feeder2_line142 | 2 | 354.6 | 97.0021 | 97.0055 | 27.3554 | 27.3563
60 | feeder2_line142 | 3 | 354.6 | 98.8831 | 98.8794 | 27.8858 | 27.8848
60 | feeder2_line143 | 1 | 99 | 8.5724e-07 | 1.742e-06 | 8.659e-07 | 1.7596e-06
60 | feeder2_line143 | 2 | 99 | 0.98598 | 0.98599 | 0.99594 | 0.99595
60 | feeder2_line143 | 3 | 99 | 8.5487e-07 | 1.7377e-06 | 8.635e-07 | 1.7552e-06
60 | feeder2_line144 | 1 | 354.6 | 98.0633 | 98.0633 | 27.6546 | 27.6546
60 | feeder2_line144 | 2 | 354.6 | 97.5581 | 97.5617 | 27.5122 | 27.5132
60 | feeder2_line144 | 3 | 354.6 | 98.8829 | 98.8794 | 27.8858 | 27.8848
60 | feeder2_line145 | 1 | 99 | 2.5047e-08 | 4.8851e-07 | 2.53e-08 | 4.9344e-07
60 | feeder2_line145 | 2 | 99 | 0.25076 | 0.25076 | 0.25329 | 0.25329
60 | feeder2_line145 | 3 | 99 | 2.5346e-08 | 4.8727e-07 | 2.5602e-08 | 4.9219e-07
60 | feeder2_line146 | 1 | 354.6 | 98.0632 | 98.0633 | 27.6546 | 27.6546
60 | feeder2_line146 | 2 | 354.6 | 97.8077 | 97.8115 | 27.5826 | 27.5836
60 | feeder2_line146 | 3 | 354.6 | 98.8828 | 98.8794 | 27.8857 | 27.8848
60 | feeder2_line147 | 1 | 99 | 0.10723 | 0.10723 | 0.10831 | 0.10831
60 | feeder2_line147 | 2 | 99 | 1.1591e-06 | 2.2518e-06 | 1.1708e-06 | 2.2745e-06
60 | feeder2_line147 | 3 | 99 | 1.1569e-06 | 2.2476e-06 | 1.1686e-06 | 2.2704e-06
60 | feeder2_line148 | 1 | 99 | 0.22049 | 0.22049 | 0.22271 | 0.22271
60 | feeder2_line148 | 2 | 99 | 6.0472e-07 | 1.5089e-06 | 6.1082e-07 | 1.5241e-06
60 | feeder2_line148 | 3 | 99 | 6.0382e-07 | 1.5061e-06 | 6.0991e-07 | 1.5213e-06
60 | feeder2_line149 | 1 | 354.6 | 98.3904 | 98.3903 | 27.7469 | 27.7468
60 | feeder2_line149 | 2 | 354.6 | 97.8079 | 97.8115 | 27.5826 | 27.5836
60 | feeder2_line149 | 3 | 354.6 | 98.8829 | 98.8794 | 27.8858 | 27.8848
60 | feeder2_line150 | 1 | 354.6 | 98.3905 | 98.3903 | 27.7469 | 27.7468
60 | feeder2_line150 | 2 | 354.6 | 98.684 | 98.6875 | 27.8297 | 27.8306
60 | feeder2_line150 | 3 | 354.6 | 98.883 | 98.8794 | 27.8858 | 27.8848
60 | feeder2_line151 | 1 | 99 | 9.8549e-06 | 1.7938e-06 | 9.9544e-06 | 1.8119e-06
60 | feeder2_line151 | 2 | 99 | 1.5313 | 1.5313 | 1.5468 | 1.5468
60 | feeder2_line151 | 3 | 99 | 9.8033e-06 | 1.7893e-06 | 9.9024e-06 | 1.8074e-06
60 | feeder2_line152 | 1 | 354.6 | 1.7009e-11 | 1.1955e-06 | 4.7967e-12 | 3.3714e-07
60 | feeder2_line152 | 2 | 354.6 | 3.2982e-11 | 1.1949e-06 | 9.3012e-12 | 3.3696e-07
60 | feeder2_line152 | 3 | 354.6 | 0.076544 | 0.076542 | 0.021586 | 0.021585
60 | feeder2_line153 | 1 | 99 | 0.043555 | 0.043555 | 0.043995 | 0.043995
60 | feeder2_line153 | 2 | 99 | 5.0379e-08 | 5.9782e-07 | 5.0887e-08 | 6.0386e-07
60 | feeder2_line153 | 3 | 99 | 5.0748e-08 | 5.9673e-07 | 5.126e-08 | 6.0275e-07
60 | feeder2_line154 | 1 | 99 | 5.805e-07 | 8.902e-07 | 5.8637e-07 | 8.9919e-07
60 | feeder2_line154 | 2 | 99 | 5.8009e-07 | 8.8958e-07 | 5.8595e-07 | 8.9857e-07
60 | feeder2_line154 | 3 | 99 | 0.040557 | 0.040546 | 0.040967 | 0.040956
60 | feeder2_line155 | 1 | 99 | 98.4338 | 98.4337 | 99.4281 | 99.428
60 | feeder2_line155 | 2 | 99 | 98.6839 | 98.6875 | 99.6807 | 99.6843
60 | feeder2_line155 | 3 | 99 | 99 | 98.9964 | 100 | 99.9964
60 | feeder2_line156 | 1 | 99 | 6.0531e-07 | 1.1713e-06 | 6.1143e-07 | 1.1832e-06
60 | feeder2_line156 | 2 | 99 | 0.096023 | 0.096026 | 0.096993 | 0.096996
60 | feeder2_line156 | 3 | 99 | 6.0412e-07 | 1.1684e-06 | 6.1023e-07 | 1.1802e-06
60 | feeder2_line157 | 1 | 99 | 2.5047e-08 | 2.543e-07 | 2.53e-08 | 2.5687e-07
60 | feeder2_line157 | 2 | 99 | 1.4834 | 1.4833 | 1.4983 | 1.4983
60 | feeder2_line157 | 3 | 99 | 2.5364e-08 | 2.5365e-07 | 2.562e-08 | 2.5621e-07
90 | feeder2_line1 | 1 | 354.6 | 79.4041 | 79.4078 | 22.3926 | 22.3936
90 | feeder2_line1 | 2 | 354.6 | 86.4766 | 86.4767 | 24.3871 | 24.3871
90 | feeder2_line1 | 3 | 354.6 | 88.6451 | 88.6435 | 24.9986 | 24.9982
90 | feeder2_line2 | 1 | 354.6 | 79.7422 | 79.7457 | 22.4879 | 22.4889
90 | feeder2_line2 | 2 | 354.6 | 86.4768 | 86.4767 | 24.3871 | 24.3871
90 | feeder2_line2 | 3 | 354.6 | 88.6452 | 88.6435 | 24.9987 | 24.9982
90 | feeder2_line3 | 1 | 80.1 | 0.33975 | 0.33975 | 0.42415 | 0.42416
90 | feeder2_line3 | 2 | 80.1 | 5.7239e-07 | 1.0578e-06 | 7.146e-07 | 1.3206e-06
90 | feeder2_line3 | 3 | 80.1 | 5.7263e-07 | 1.0582e-06 | 7.1489e-07 | 1.3211e-06
90 | feeder2_line4 | 1 | 354.6 | 79.7423 | 79.7457 | 22.488 | 22.4889
90 | feeder2_line4 | 2 | 354.6 | 86.7527 | 86.7524 | 24.465 | 24.4649
90 | feeder2_line4 | 3 | 354.6 | 88.6454 | 88.6435 | 24.9987 | 24.9982
90 | feeder2_line5 | 1 | 80.1 | 5.7243e-07 | 9.9884e-07 | 7.1464e-07 | 1.247e-06
90 | feeder2_line5 | 2 | 80.1 | 0.27932 | 0.27932 | 0.34871 | 0.34871
90 | feeder2_line5 | 3 | 80.1 | 5.7268e-07 | 9.9927e-07 | 7.1495e-07 | 1.2475e-06
90 | feeder2_line6 | 1 | 80.1 | 5.7251e-07 | 1.1752e-06 | 7.1474e-07 | 1.4671e-06
90 | feeder2_line6 | 2 | 80.1 | 5.7251e-07 | 1.1752e-06 | 7.1475e-07 | 1.4671e-06
90 | feeder2_line6 | 3 | 80.1 | 1.26 | 1.2601 | 1.5731 | 1.5731
90 | feeder2_line7 | 1 | 354.6 | 79.7424 | 79.7457 | 22.488 | 22.4889
90 | feeder2_line7 | 2 | 354.6 | 86.7528 | 86.7524 | 24.465 | 24.4649
90 | feeder2_line7 | 3 | 354.6 | 89.3106 | 89.3086 | 25.1863 | 25.1857
90 | feeder2_line8 | 1 | 80.1 | 0.072569 | 0.072569 | 0.090598 | 0.090598
90 | feeder2_line8 | 2 | 80.1 | 5.7274e-07 | 1.1336e-06 | 7.1503e-07 | 1.4152e-06
90 | feeder2_line8 | 3 | 80.1 | 5.73e-07 | 1.1341e-06 | 7.1536e-07 | 1.4159e-06
90 | feeder2_line9 | 1 | 354.6 | 79.815 | 79.8183 | 22.5085 | 22.5094
90 | feeder2_line9 | 2 | 354.6 | 86.7529 | 86.7524 | 24.465 | 24.4649
90 | feeder2_line9 | 3 | 354.6 | 89.3107 | 89.3086 | 25.1863 | 25.1857
90 | feeder2_line10 | 1 | 80.1 | 8.4665e-07 | 1.4968e-06 | 1.057e-06 | 1.8686e-06
90 | feeder2_line10 | 2 | 80.1 | 0.072549 | 0.072549 | 0.090573 | 0.090573
90 | feeder2_line10 | 3 | 80.1 | 8.471e-07 | 1.4976e-06 | 1.0575e-06 | 1.8696e-06
90 | feeder2_line11 | 1 | 354.6 | 79.815 | 79.8183 | 22.5085 | 22.5094
90 | feeder2_line11 | 2 | 354.6 | 86.8251 | 86.8246 | 24.4854 | 24.4852
90 | feeder2_line11 | 3 | 354.6 | 89.3106 | 89.3086 | 25.1863 | 25.1857
90 | feeder2_line12 | 1 | 80.1 | 5.479e-07 | 9.9299e-07 | 6.8403e-07 | 1.2397e-06
90 | feeder2_line12 | 2 | 80.1 | 5.4796e-07 | 9.9305e-07 | 6.841e-07 | 1.2398e-06
90 | feeder2_line12 | 3 | 80.1 | 0.061728 | 0.061727 | 0.077063 | 0.077063
90 | feeder2_line13 | 1 | 354.6 | 79.815 | 79.8183 | 22.5084 | 22.5094
90 | feeder2_line13 | 2 | 354.6 | 86.825 | 86.8246 | 24.4853 | 24.4852
90 | feeder2_line13 | 3 | 354.6 | 89.3723 | 89.3703 | 25.2037 | 25.2031
90 | feeder2_line14 | 1 | 80.1 | 0.2753 | 0.2753 | 0.34369 | 0.3437
90 | feeder2_line14 | 2 | 80.1 | 2.9892e-07 | 6.4763e-07 | 3.7318e-07 | 8.0853e-07
90 | feeder2_line14 | 3 | 80.1 | 2.9907e-07 | 6.4796e-07 | 3.7338e-07 | 8.0894e-07
90 | feeder2_line15 | 1 | 354.6 | 80.0889 | 80.0922 | 22.5857 | 22.5866
90 | feeder2_line15 | 2 | 354.6 | 86.8251 | 86.8246 | 24.4854 | 24.4852
90 | feeder2_line15 | 3 | 354.6 | 89.3723 | 89.3703 | 25.2037 | 25.2031
90 | feeder2_line16 | 1 | 80.1 | 5.7301e-07 | 1.0323e-06 | 7.1537e-07 | 1.2888e-06
90 | feeder2_line16 | 2 | 80.1 | 0.25452 | 0.25452 | 0.31776 | 0.31775
90 | feeder2_line16 | 3 | 80.1 | 5.7336e-07 | 1.0329e-06 | 7.1581e-07 | 1.2896e-06
90 | feeder2_line17 | 1 | 354.6 | 80.089 | 80.0922 | 22.5857 | 22.5866
90 | feeder2_line17 | 2 | 354.6 | 87.0757 | 87.0752 | 24.556 | 24.5559
90 | feeder2_line17 | 3 | 354.6 | 89.3724 | 89.3703 | 25.2037 | 25.2031
90 | feeder2_line18 | 1 | 80.1 | 5.4858e-07 | 7.3962e-07 | 6.8487e-07 | 9.2337e-07
90 | feeder2_line18 | 2 | 80.1 | 5.487e-07 | 7.3972e-07 | 6.8501e-07 | 9.2349e-07
90 | feeder2_line18 | 3 | 80.1 | 0.49196 | 0.49196 | 0.61419 | 0.61418
90 | feeder2_line19 | 1 | 354.6 | 80.089 | 80.0922 | 22.5857 | 22.5866
90 | feeder2_line19 | 2 | 354.6 | 87.0757 | 87.0752 | 24.556 | 24.5559
90 | feeder2_line19 | 3 | 354.6 | 89.8617 | 89.8596 | 25.3417 | 25.3411
90 | feeder2_line20 | 1 | 99 | 5.4876e-07 | 8.8706e-07 | 5.5431e-07 | 8.9602e-07
90 | feeder2_line20 | 2 | 99 | 5.4889e-07 | 8.872e-07 | 5.5444e-07 | 8.9616e-07
90 | feeder2_line20 | 3 | 99 | 0.35675 | 0.35674 | 0.36035 | 0.36034
90 | feeder2_line21 | 1 | 354.6 | 80.0891 | 80.0922 | 22.5858 | 22.5866
90 | feeder2_line21 | 2 | 354.6 | 87.0758 | 87.0752 | 24.5561 | 24.5559
90 | feeder2_line21 | 3 | 354.6 | 90.2173 | 90.2151 | 25.442 | 25.4414
90 | feeder2_line22 | 1 | 99 | 5.7385e-07 | 1.0171e-06 | 5.7964e-07 | 1.0274e-06
90 | feeder2_line22 | 2 | 99 | 0.093744 | 0.093744 | 0.094691 | 0.094691
90 | feeder2_line22 | 3 | 99 | 5.7435e-07 | 1.018e-06 | 5.8015e-07 | 1.0283e-06
90 | feeder2_line23 | 1 | 99 | 5.7385e-07 | 9.521e-07 | 5.7964e-07 | 9.6172e-07
90 | feeder2_line23 | 2 | 99 | 5.7395e-07 | 9.5227e-07 | 5.7975e-07 | 9.6189e-07
90 | feeder2_line23 | 3 | 99 | 0.12712 | 0.12712 | 0.12841 | 0.12841
90 | feeder2_line24 | 1 | 354.6 | 80.0891 | 80.0922 | 22.5858 | 22.5866
90 | feeder2_line24 | 2 | 354.6 | 87.169 | 87.1684 | 24.5823 | 24.5822
90 | feeder2_line24 | 3 | 354.6 | 90.3439 | 90.3416 | 25.4777 | 25.4771
90 | feeder2_line25 | 1 | 99 | 0.09375 | 0.093751 | 0.094697 | 0.094698
90 | feeder2_line25 | 2 | 99 | 4.9883e-08 | 6.9258e-07 | 5.0387e-08 | 6.9958e-07
90 | feeder2_line25 | 3 | 99 | 4.9961e-08 | 6.931e-07 | 5.0465e-08 | 7.001e-07
90 | feeder2_line26 | 1 | 99 | 0.22049 | 0.22049 | 0.22272 | 0.22272
90 | feeder2_line26 | 2 | 99 | 5.4923e-07 | 8.5807e-07 | 5.5478e-07 | 8.6674e-07
90 | feeder2_line26 | 3 | 99 | 5.4961e-07 | 8.5871e-07 | 5.5517e-07 | 8.6738e-07
90 | feeder2_line27 | 1 | 354.6 | 80.4024 | 80.4054 | 22.6741 | 22.675
90 | feeder2_line27 | 2 | 354.6 | 87.169 | 87.1684 | 24.5824 | 24.5822
90 | feeder2_line27 | 3 | 354.6 | 90.3439 | 90.3416 | 25.4777 | 25.4771
90 | feeder2_line28 | 1 | 99 | 2.547e-06 | 7.1257e-07 | 2.5727e-06 | 7.1977e-07
90 | feeder2_line28 | 2 | 99 | 0.10847 | 0.10847 | 0.10956 | 0.10956
90 | feeder2_line28 | 3 | 99 | 2.5501e-06 | 7.1331e-07 | 2.5758e-06 | 7.2052e-07
90 | feeder2_line29 | 1 | 354.6 | 80.4024 | 80.4054 | 22.6741 | 22.675
90 | feeder2_line29 | 2 | 354.6 | 87.2775 | 87.2768 | 24.6129 | 24.6128
90 | feeder2_line29 | 3 | 354.6 | 90.3439 | 90.3416 | 25.4777 | 25.4771
90 | feeder2_line30 | 1 | 266.4 | 12.0054 | 12.0051 | 4.5065 | 4.5064
90 | feeder2_line30 | 2 | 266.4 | 1.4307 | 1.4309 | 0.53705 | 0.53712
90 | feeder2_line30 | 3 | 266.4 | 2.8835 | 2.8837 | 1.0824 | 1.0825
90 | feeder2_line31 | 1 | 354.6 | 92.224 | 92.2267 | 26.0079 | 26.0087
90 | feeder2_line31 | 2 | 354.6 | 88.134 | 88.1329 | 24.8545 | 24.8542
90 | feeder2_line31 | 3 | 354.6 | 92.1407 | 92.1381 | 25.9844 | 25.9837
90 | feeder2_line32 | 1 | 354.6 | 92.224 | 92.2267 | 26.0079 | 26.0087
90 | feeder2_line32 | 2 | 354.6 | 88.3892 | 88.3881 | 24.9264 | 24.9261
90 | feeder2_line32 | 3 | 354.6 | 92.1408 | 92.1381 | 25.9844 | 25.9837
90 | feeder2_line33 | 1 | 99 | 5.0068e-08 | 6.8841e-07 | 5.0573e-08 | 6.9536e-07
90 | feeder2_line33 | 2 | 99 | 0.25774 | 0.25774 | 0.26034 | 0.26034
90 | feeder2_line33 | 3 | 99 | 5.0068e-08 | 6.8921e-07 | 5.0573e-08 | 6.9618e-07
90 | feeder2_line34 | 1 | 354.6 | 92.224 | 92.2267 | 26.0079 | 26.0087
90 | feeder2_line34 | 2 | 354.6 | 88.3892 | 88.3881 | 24.9264 | 24.9261
90 | feeder2_line34 | 3 | 354.6 | 92.4156 | 92.413 | 26.0619 | 26.0612
90 | feeder2_line35 | 1 | 99 | 3.002e-07 | 7.6254e-07 | 3.0324e-07 | 7.7024e-07
90 | feeder2_line35 | 2 | 99 | 3.0022e-07 | 7.6261e-07 | 3.0325e-07 | 7.7032e-07
90 | feeder2_line35 | 3 | 99 | 0.27545 | 0.27545 | 0.27823 | 0.27823
90 | feeder2_line36 | 1 | 354.6 | 92.8577 | 92.8605 | 26.1866 | 26.1874
90 | feeder2_line36 | 2 | 354.6 | 88.3891 | 88.3881 | 24.9264 | 24.9261
90 | feeder2_line36 | 3 | 354.6 | 92.4156 | 92.413 | 26.0619 | 26.0612
90 | feeder2_line37 | 1 | 99 | 1.2354 | 1.2354 | 1.2479 | 1.2479
90 | feeder2_line37 | 2 | 99 | 3.0029e-07 | 8.44e-07 | 3.0332e-07 | 8.5253e-07
90 | feeder2_line37 | 3 | 99 | 3.0061e-07 | 8.4491e-07 | 3.0365e-07 | 8.5344e-07
90 | feeder2_line38 | 1 | 99 | 3.2496e-07 | 7.7791e-07 | 3.2825e-07 | 7.8576e-07
90 | feeder2_line38 | 2 | 99 | 0.21252 | 0.21252 | 0.21467 | 0.21467
90 | feeder2_line38 | 3 | 99 | 3.2533e-07 | 7.7891e-07 | 3.2861e-07 | 7.8678e-07
90 | feeder2_line39 | 1 | 266.4 | 12.0054 | 12.0051 | 4.5065 | 4.5064
90 | feeder2_line39 | 2 | 266.4 | 1.2897 | 1.29 | 0.48413 | 0.48423
90 | feeder2_line39 | 3 | 266.4 | 2.8835 | 2.8837 | 1.0824 | 1.0825
90 | feeder2_line40 | 1 | 354.6 | 92.9513 | 92.954 | 26.213 | 26.2138
90 | feeder2_line40 | 2 | 354.6 | 88.3892 | 88.3881 | 24.9264 | 24.9261
90 | feeder2_line40 | 3 | 354.6 | 92.4156 | 92.413 | 26.0619 | 26.0612
90 | feeder2_line41 | 1 | 99 | 0.093536 | 0.093538 | 0.094481 | 0.094483
90 | feeder2_line41 | 2 | 99 | 5.0027e-08 | 7.3759e-07 | 5.0532e-08 | 7.4505e-07
90 | feeder2_line41 | 3 | 99 | 5.0105e-08 | 7.3841e-07 | 5.0611e-08 | 7.4587e-07
90 | feeder2_line42 | 1 | 99 | 2.999e-07 | 7.5076e-07 | 3.0293e-07 | 7.5834e-07
90 | feeder2_line42 | 2 | 99 | 3.0002e-07 | 7.5115e-07 | 3.0305e-07 | 7.5874e-07
90 | feeder2_line42 | 3 | 99 | 1.2584 | 1.2584 | 1.2711 | 1.2711
90 | feeder2_line43 | 1 | 266.4 | 12.0053 | 12.0051 | 4.5065 | 4.5064
90 | feeder2_line43 | 2 | 266.4 | 1.2898 | 1.29 | 0.48416 | 0.48423
90 | feeder2_line43 | 3 | 266.4 | 1.626 | 1.6261 | 0.61038 | 0.61041
90 | feeder2_line44 | 1 | 354.6 | 92.9513 | 92.954 | 26.213 | 26.2138
90 | feeder2_line44 | 2 | 354.6 | 88.3892 | 88.3881 | 24.9265 | 24.9261
90 | feeder2_line44 | 3 | 354.6 | 92.7722 | 92.7695 | 26.1625 | 26.1617
90 | feeder2_line45 | 1 | 99 | 5.0091e-08 | 5.818e-07 | 5.0597e-08 | 5.8768e-07
90 | feeder2_line45 | 2 | 99 | 5.0041e-08 | 5.8176e-07 | 5.0546e-08 | 5.8764e-07
90 | feeder2_line45 | 3 | 99 | 0.35706 | 0.35705 | 0.36067 | 0.36065
90 | feeder2_line46 | 1 | 99 | 5.7476e-07 | 1.361e-06 | 5.8057e-07 | 1.3747e-06
90 | feeder2_line46 | 2 | 99 | 5.7507e-07 | 1.3617e-06 | 5.8088e-07 | 1.3755e-06
90 | feeder2_line46 | 3 | 99 | 1.5296 | 1.5296 | 1.5451 | 1.545
90 | feeder2_line47 | 1 | 266.4 | 12.0053 | 12.0051 | 4.5065 | 4.5064
90 | feeder2_line47 | 2 | 266.4 | 1.29 | 1.29 | 0.48423 | 0.48423
90 | feeder2_line47 | 3 | 266.4 | 0.16962 | 0.16935 | 0.063671 | 0.063569
90 | feeder2_line48 | 1 | 99 | 1.1287 | 1.1287 | 1.1401 | 1.1401
90 | feeder2_line48 | 2 | 99 | 4.9935e-08 | 7.3317e-07 | 5.0439e-08 | 7.4057e-07
90 | feeder2_line48 | 3 | 99 | 5.0031e-08 | 7.3383e-07 | 5.0536e-08 | 7.4124e-07
90 | feeder2_line49 | 1 | 266.4 | 11.2287 | 11.2284 | 4.215 | 4.2149
90 | feeder2_line49 | 2 | 266.4 | 1.29 | 1.29 | 0.48422 | 0.48423
90 | feeder2_line49 | 3 | 266.4 | 0.1696 | 0.16935 | 0.063664 | 0.063569
90 | feeder2_line50 | 1 | 99 | 5.747e-07 | 1.2385e-06 | 5.805e-07 | 1.251e-06
90 | feeder2_line50 | 2 | 99 | 1.2617 | 1.2617 | 1.2744 | 1.2745
90 | feeder2_line50 | 3 | 99 | 5.756e-07 | 1.2404e-06 | 5.8142e-07 | 1.2529e-06
90 | feeder2_line51 | 1 | 99 | 10.5724 | 10.5724 | 10.6792 | 10.6792
90 | feeder2_line51 | 2 | 99 | 5.7505e-07 | 1.3453e-06 | 5.8086e-07 | 1.3589e-06
90 | feeder2_line51 | 3 | 99 | 5.7558e-07 | 1.3466e-06 | 5.8139e-07 | 1.3602e-06
90 | feeder2_line52 | 1 | 266.4 | 0.65614 | 0.65605 | 0.2463 | 0.24627
90 | feeder2_line52 | 2 | 266.4 | 0.048884 | 0.04878 | 0.01835 | 0.018311
90 | feeder2_line52 | 3 | 266.4 | 0.16946 | 0.16935 | 0.063612 | 0.063569
90 | feeder2_line53 | 1 | 99 | 5.4966e-07 | 7.5586e-07 | 5.5522e-07 | 7.6349e-07
90 | feeder2_line53 | 2 | 99 | 0.04878 | 0.04878 | 0.049273 | 0.049273
90 | feeder2_line53 | 3 | 99 | 5.5058e-07 | 7.5703e-07 | 5.5615e-07 | 7.6468e-07
90 | feeder2_line54 | 1 | 266.4 | 0.65597 | 0.65605 | 0.24623 | 0.24627
90 | feeder2_line54 | 2 | 266.4 | 8.5777e-05 | 4.6397e-06 | 3.2198e-05 | 1.7416e-06
90 | feeder2_line54 | 3 | 266.4 | 0.16927 | 0.16935 | 0.06354 | 0.063569
90 | feeder2_line55 | 1 | 99 | 0.18119 | 0.1812 | 0.18303 | 0.18303
90 | feeder2_line55 | 2 | 99 | 5.0084e-08 | 7.3337e-07 | 5.059e-08 | 7.4078e-07
90 | feeder2_line55 | 3 | 99 | 5.0154e-08 | 7.3426e-07 | 5.066e-08 | 7.4168e-07
90 | feeder2_line56 | 1 | 354.6 | 93.1321 | 93.1348 | 26.264 | 26.2648
90 | feeder2_line56 | 2 | 354.6 | 88.3893 | 88.3881 | 24.9265 | 24.9261
90 | feeder2_line56 | 3 | 354.6 | 92.7722 | 92.7695 | 26.1625 | 26.1617
90 | feeder2_line57 | 1 | 99 | 7.5104e-07 | 1.5482e-06 | 7.5862e-07 | 1.5639e-06
90 | feeder2_line57 | 2 | 99 | 7.4895e-07 | 1.5492e-06 | 7.5652e-07 | 1.5649e-06
90 | feeder2_line57 | 3 | 99 | 0.16935 | 0.16935 | 0.17106 | 0.17106
90 | feeder2_line58 | 1 | 266.4 | 0.65603 | 0.65605 | 0.24626 | 0.24627
90 | feeder2_line58 | 2 | 266.4 | 1.9007e-05 | 2.6937e-06 | 7.1348e-06 | 1.0112e-06
90 | feeder2_line58 | 3 | 266.4 | 1.9027e-05 | 2.6962e-06 | 7.1421e-06 | 1.0121e-06
90 | feeder2_line59 | 1 | 99 | 5.007e-08 | 5.3817e-07 | 5.0575e-08 | 5.4361e-07
90 | feeder2_line59 | 2 | 99 | 4.9928e-08 | 5.3853e-07 | 5.0432e-08 | 5.4397e-07
90 | feeder2_line59 | 3 | 99 | 0.10795 | 0.10795 | 0.10904 | 0.10904
90 | feeder2_line60 | 1 | 99 | 2.9987e-07 | 8.1335e-07 | 3.029e-07 | 8.2157e-07
90 | feeder2_line60 | 2 | 99 | 3.0002e-07 | 8.1388e-07 | 3.0306e-07 | 8.221e-07
90 | feeder2_line60 | 3 | 99 | 0.061536 | 0.061535 | 0.062157 | 0.062157
90 | feeder2_line61 | 1 | 266.4 | 1.5496 | 1.5497 | 0.58167 | 0.58174
90 | feeder2_line61 | 2 | 266.4 | 0.63853 | 0.63871 | 0.23969 | 0.23976
90 | feeder2_line61 | 3 | 266.4 | 0.38466 | 0.38482 | 0.14439 | 0.14445
90 | feeder2_line62 | 1 | 354.6 | 94.0595 | 94.0625 | 26.5255 | 26.5264
90 | feeder2_line62 | 2 | 354.6 | 89.0223 | 89.0214 | 25.105 | 25.1047
90 | feeder2_line62 | 3 | 354.6 | 93.1565 | 93.154 | 26.2709 | 26.2702
90 | feeder2_line63 | 1 | 99 | 0.36007 | 0.36008 | 0.36371 | 0.36371
90 | feeder2_line63 | 2 | 99 | 5.7508e-07 | 1.2236e-06 | 5.8089e-07 | 1.236e-06
90 | feeder2_line63 | 3 | 99 | 5.756e-07 | 1.2248e-06 | 5.8141e-07 | 1.2371e-06
90 | feeder2_line64 | 1 | 99 | 0.29598 | 0.29599 | 0.29897 | 0.29897
90 | feeder2_line64 | 2 | 99 | 4.5688e-12 | 3.2234e-07 | 4.615e-12 | 3.256e-07
90 | feeder2_line64 | 3 | 99 | 3.4747e-12 | 3.2263e-07 | 3.5097e-12 | 3.2589e-07
90 | feeder2_line65 | 1 | 99 | 5.0147e-08 | 6.4509e-07 | 5.0653e-08 | 6.5161e-07
90 | feeder2_line65 | 2 | 99 | 0.27956 | 0.27956 | 0.28238 | 0.28238
90 | feeder2_line65 | 3 | 99 | 5.0221e-08 | 6.456e-07 | 5.0728e-08 | 6.5212e-07
90 | feeder2_line66 | 1 | 354.6 | 94.0595 | 94.0625 | 26.5255 | 26.5264
90 | feeder2_line66 | 2 | 354.6 | 89.2992 | 89.2983 | 25.1831 | 25.1828
90 | feeder2_line66 | 3 | 354.6 | 93.1565 | 93.154 | 26.2709 | 26.2702
90 | feeder2_line67 | 1 | 99 | 2.5069e-08 | 3.6445e-07 | 2.5323e-08 | 3.6813e-07
90 | feeder2_line67 | 2 | 99 | 2.5055e-08 | 3.6432e-07 | 2.5308e-08 | 3.68e-07
90 | feeder2_line67 | 3 | 99 | 0.093338 | 0.093337 | 0.094281 | 0.09428
90 | feeder2_line68 | 1 | 266.4 | 1.5496 | 1.5497 | 0.58169 | 0.58174
90 | feeder2_line68 | 2 | 266.4 | 0.63857 | 0.63871 | 0.2397 | 0.23976
90 | feeder2_line68 | 3 | 266.4 | 0.29142 | 0.29154 | 0.10939 | 0.10944
90 | feeder2_line69 | 1 | 99 | 0.21376 | 0.21377 | 0.21592 | 0.21593
90 | feeder2_line69 | 2 | 99 | 2.5577e-06 | 6.6943e-07 | 2.5835e-06 | 6.7619e-07
90 | feeder2_line69 | 3 | 99 | 2.5613e-06 | 6.7036e-07 | 2.5872e-06 | 6.7714e-07
90 | feeder2_line70 | 1 | 354.6 | 94.273 | 94.2761 | 26.5857 | 26.5866
90 | feeder2_line70 | 2 | 354.6 | 89.2991 | 89.2983 | 25.1831 | 25.1828
90 | feeder2_line70 | 3 | 354.6 | 93.1564 | 93.154 | 26.2708 | 26.2702
90 | feeder2_line71 | 1 | 99 | 5.0154e-08 | 7.2001e-07 | 5.0661e-08 | 7.2729e-07
90 | feeder2_line71 | 2 | 99 | 1.4286 | 1.4286 | 1.443 | 1.443
90 | feeder2_line71 | 3 | 99 | 5.0249e-08 | 7.2053e-07 | 5.0756e-08 | 7.2781e-07
90 | feeder2_line72 | 1 | 354.6 | 94.2731 | 94.2761 | 26.5858 | 26.5866
90 | feeder2_line72 | 2 | 354.6 | 90.1511 | 90.1502 | 25.4233 | 25.4231
90 | feeder2_line72 | 3 | 354.6 | 93.1565 | 93.154 | 26.2709 | 26.2702
90 | feeder2_line73 | 1 | 99 | 6.0163e-07 | 1.5429e-06 | 6.0771e-07 | 1.5585e-06
90 | feeder2_line73 | 2 | 99 | 0.25779 | 0.25779 | 0.26039 | 0.26039
90 | feeder2_line73 | 3 | 99 | 6.0219e-07 | 1.5443e-06 | 6.0827e-07 | 1.5599e-06
90 | feeder2_line74 | 1 | 99 | 5.0131e-08 | 4.6018e-07 | 5.0637e-08 | 4.6483e-07
90 | feeder2_line74 | 2 | 99 | 0.29153 | 0.29153 | 0.29447 | 0.29447
90 | feeder2_line74 | 3 | 99 | 5.0183e-08 | 4.6061e-07 | 5.0689e-08 | 4.6526e-07
90 | feeder2_line75 | 1 | 266.4 | 1.5497 | 1.5497 | 0.58172 | 0.58174
90 | feeder2_line75 | 2 | 266.4 | 0.089461 | 0.089494 | 0.033581 | 0.033594
90 | feeder2_line75 | 3 | 266.4 | 0.29152 | 0.29154 | 0.10943 | 0.10944
90 | feeder2_line76 | 1 | 99 | 1.5497 | 1.5497 | 1.5654 | 1.5654
90 | feeder2_line76 | 2 | 99 | 8.5198e-07 | 1.591e-06 | 8.6058e-07 | 1.6071e-06
90 | feeder2_line76 | 3 | 99 | 8.5309e-07 | 1.5931e-06 | 8.6171e-07 | 1.6092e-06
90 | feeder2_line77 | 1 | 99 | 2.5063e-08 | 5.783e-07 | 2.5317e-08 | 5.8414e-07
90 | feeder2_line77 | 2 | 99 | 2.5068e-08 | 5.7807e-07 | 2.5321e-08 | 5.8391e-07
90 | feeder2_line77 | 3 | 99 | 0.29156 | 0.29154 | 0.2945 | 0.29449
90 | feeder2_line78 | 1 | 266.4 | 1.3236e-11 | 9.5909e-07 | 4.9686e-12 | 3.6002e-07
90 | feeder2_line78 | 2 | 266.4 | 0.089494 | 0.089493 | 0.033594 | 0.033594
90 | feeder2_line78 | 3 | 266.4 | 2.195e-12 | 9.5997e-07 | 8.2395e-13 | 3.6035e-07
90 | feeder2_line79 | 1 | 354.6 | 1.6529 | 1.6526 | 0.46613 | 0.46606
90 | feeder2_line79 | 2 | 354.6 | 4.245 | 4.2448 | 1.1971 | 1.1971
90 | feeder2_line79 | 3 | 354.6 | 3.5474 | 3.5471 | 1.0004 | 1.0003
90 | feeder2_line80 | 1 | 354.6 | 95.5499 | 95.5524 | 26.9458 | 26.9465
90 | feeder2_line80 | 2 | 354.6 | 92.6612 | 92.6598 | 26.1312 | 26.1308
90 | feeder2_line80 | 3 | 354.6 | 96.1508 | 96.1477 | 27.1153 | 27.1144
90 | feeder2_line81 | 1 | 354.6 | 95.5499 | 95.5524 | 26.9458 | 26.9465
90 | feeder2_line81 | 2 | 354.6 | 92.6612 | 92.6598 | 26.1312 | 26.1308
90 | feeder2_line81 | 3 | 354.6 | 96.4012 | 96.3982 | 27.1859 | 27.185
90 | feeder2_line82 | 1 | 354.6 | 8.0788e-12 | 7.3898e-07 | 2.2783e-12 | 2.084e-07
90 | feeder2_line82 | 2 | 354.6 | 1.9859e-11 | 7.3835e-07 | 5.6005e-12 | 2.0822e-07
90 | feeder2_line82 | 3 | 354.6 | 0.25063 | 0.25063 | 0.070679 | 0.070679
90 | feeder2_line83 | 1 | 354.6 | 95.5501 | 95.5524 | 26.9459 | 26.9465
90 | feeder2_line83 | 2 | 354.6 | 93.8894 | 93.8878 | 26.4776 | 26.4771
90 | feeder2_line83 | 3 | 354.6 | 96.4014 | 96.3982 | 27.1859 | 27.185
90 | feeder2_line84 | 1 | 354.6 | 1.8637e-11 | 1.3064e-06 | 5.2557e-12 | 3.6841e-07
90 | feeder2_line84 | 2 | 354.6 | 2.3472 | 2.3471 | 0.66193 | 0.66191
90 | feeder2_line84 | 3 | 354.6 | 1.441e-11 | 1.3072e-06 | 4.0636e-12 | 3.6864e-07
90 | feeder2_line85 | 1 | 99 | 0.21256 | 0.21256 | 0.2147 | 0.21471
90 | feeder2_line85 | 2 | 99 | 5.0262e-08 | 4.6588e-07 | 5.077e-08 | 4.7059e-07
90 | feeder2_line85 | 3 | 99 | 5.0318e-08 | 4.6659e-07 | 5.0827e-08 | 4.713e-07
90 | feeder2_line86 | 1 | 354.6 | 95.7627 | 95.7649 | 27.0058 | 27.0065
90 | feeder2_line86 | 2 | 354.6 | 93.8896 | 93.8878 | 26.4776 | 26.4771
90 | feeder2_line86 | 3 | 354.6 | 96.4015 | 96.3982 | 27.186 | 27.185
90 | feeder2_line87 | 1 | 354.6 | 95.7629 | 95.7649 | 27.0059 | 27.0065
90 | feeder2_line87 | 2 | 354.6 | 94.0025 | 94.0005 | 26.5094 | 26.5089
90 | feeder2_line87 | 3 | 354.6 | 97.885 | 97.8815 | 27.6043 | 27.6033
90 | feeder2_line88 | 1 | 354.6 | 0.0001149 | 3.387e-06 | 3.2402e-05 | 9.5517e-07
90 | feeder2_line88 | 2 | 354.6 | 0.11302 | 0.11294 | 0.031874 | 0.031849
90 | feeder2_line88 | 3 | 354.6 | 2.4539 | 2.4538 | 0.69201 | 0.69199
90 | feeder2_line89 | 1 | 354.6 | 95.7606 | 95.7649 | 27.0052 | 27.0065
90 | feeder2_line89 | 2 | 354.6 | 95.4653 | 95.4656 | 26.922 | 26.9221
90 | feeder2_line89 | 3 | 354.6 | 97.8827 | 97.8815 | 27.6037 | 27.6033
90 | feeder2_line90 | 1 | 354.6 | 0.00072933 | 2.0456e-06 | 0.00020568 | 5.7687e-07
90 | feeder2_line90 | 2 | 354.6 | 2.4651 | 2.465 | 0.69519 | 0.69516
90 | feeder2_line90 | 3 | 354.6 | 0.00072952 | 2.0463e-06 | 0.00020573 | 5.7708e-07
90 | feeder2_line91 | 1 | 354.6 | 95.7605 | 95.7649 | 27.0052 | 27.0065
90 | feeder2_line91 | 2 | 354.6 | 95.4652 | 95.4656 | 26.9219 | 26.9221
90 | feeder2_line91 | 3 | 354.6 | 97.9438 | 97.9427 | 27.6209 | 27.6206
90 | feeder2_line92 | 1 | 354.6 | 8.2322e-12 | 1.0317e-06 | 2.3215e-12 | 2.9093e-07
90 | feeder2_line92 | 2 | 354.6 | 1.0069e-11 | 1.0306e-06 | 2.8394e-12 | 2.9065e-07
90 | feeder2_line92 | 3 | 354.6 | 0.061292 | 0.061291 | 0.017285 | 0.017285
90 | feeder2_line93 | 1 | 99 | 2.5114e-08 | 3.4437e-07 | 2.5368e-08 | 3.4785e-07
90 | feeder2_line93 | 2 | 99 | 2.3479 | 2.3478 | 2.3716 | 2.3715
90 | feeder2_line93 | 3 | 99 | 2.518e-08 | 3.4457e-07 | 2.5434e-08 | 3.4805e-07
90 | feeder2_line94 | 1 | 354.6 | 2.5117e-06 | 1.6765e-06 | 7.0831e-07 | 4.728e-07
90 | feeder2_line94 | 2 | 354.6 | 0.19459 | 0.1946 | 0.054877 | 0.054879
90 | feeder2_line94 | 3 | 354.6 | 2.5179e-06 | 1.6776e-06 | 7.1008e-07 | 4.7309e-07
90 | feeder2_line95 | 1 | 99 | 3.5917e-06 | 2.6266e-06 | 3.6279e-06 | 2.6532e-06
90 | feeder2_line95 | 2 | 99 | 0.11292 | 0.11294 | 0.11406 | 0.11408
90 | feeder2_line95 | 3 | 99 | 3.5928e-06 | 2.6281e-06 | 3.6291e-06 | 2.6547e-06
90 | feeder2_line96 | 1 | 354.6 | 0.00012191 | 6.2585e-07 | 3.4378e-05 | 1.7649e-07
90 | feeder2_line96 | 2 | 354.6 | 0.00012178 | 6.2563e-07 | 3.4342e-05 | 1.7643e-07
90 | feeder2_line96 | 3 | 354.6 | 2.4538 | 2.4538 | 0.69199 | 0.69199
90 | feeder2_line97 | 1 | 354.6 | 95.9137 | 95.918 | 27.0484 | 27.0496
90 | feeder2_line97 | 2 | 354.6 | 95.4654 | 95.4656 | 26.922 | 26.9221
90 | feeder2_line97 | 3 | 354.6 | 97.944 | 97.9427 | 27.621 | 27.6206
90 | feeder2_line98 | 1 | 354.6 | 0.15604 | 0.15434 | 0.044005 | 0.043525
90 | feeder2_line98 | 2 | 354.6 | 0.0017109 | 6.2332e-07 | 0.00048249 | 1.7578e-07
90 | feeder2_line98 | 3 | 354.6 | 0.0017154 | 6.2778e-07 | 0.00048376 | 1.7704e-07
90 | feeder2_line99 | 1 | 99 | 2.51e-08 | 4.5012e-07 | 2.5353e-08 | 4.5466e-07
90 | feeder2_line99 | 2 | 99 | 2.5137e-08 | 4.4968e-07 | 2.5391e-08 | 4.5422e-07
90 | feeder2_line99 | 3 | 99 | 2.4538 | 2.4538 | 2.4786 | 2.4786
90 | feeder2_line100 | 1 | 99 | 0.15433 | 0.15434 | 0.15589 | 0.1559
90 | feeder2_line100 | 2 | 99 | 2.5162e-08 | 6.1768e-07 | 2.5416e-08 | 6.2392e-07
90 | feeder2_line100 | 3 | 99 | 2.5187e-08 | 6.1868e-07 | 2.5442e-08 | 6.2493e-07
90 | feeder2_line101 | 1 | 354.6 | 0.19501 | 0.1946 | 0.054993 | 0.05488
90 | feeder2_line101 | 2 | 354.6 | 4.245 | 4.2448 | 1.1971 | 1.1971
90 | feeder2_line101 | 3 | 354.6 | 3.5474 | 3.5471 | 1.0004 | 1.0003
90 | feeder2_line102 | 1 | 99 | 1.5043 | 1.5043 | 1.5195 | 1.5195
90 | feeder2_line102 | 2 | 99 | 2.3466e-06 | 8.8268e-07 | 2.3703e-06 | 8.916e-07
90 | feeder2_line102 | 3 | 99 | 2.3507e-06 | 8.8395e-07 | 2.3745e-06 | 8.9288e-07
90 | feeder2_line103 | 1 | 99 | 5.5261e-07 | 8.0864e-07 | 5.5819e-07 | 8.1681e-07
90 | feeder2_line103 | 2 | 99 | 1.2621 | 1.2621 | 1.2749 | 1.2749
90 | feeder2_line103 | 3 | 99 | 5.5285e-07 | 8.0907e-07 | 5.5844e-07 | 8.1725e-07
90 | feeder2_line104 | 1 | 354.6 | 0.1949 | 0.1946 | 0.054965 | 0.05488
90 | feeder2_line104 | 2 | 354.6 | 2.9895 | 2.9893 | 0.84307 | 0.84301
90 | feeder2_line104 | 3 | 354.6 | 3.5473 | 3.5471 | 1.0004 | 1.0003
90 | feeder2_line105 | 1 | 99 | 2.5624e-06 | 7.4406e-07 | 2.5883e-06 | 7.5158e-07
90 | feeder2_line105 | 2 | 99 | 2.5594e-06 | 7.4338e-07 | 2.5852e-06 | 7.5089e-07
90 | feeder2_line105 | 3 | 99 | 0.49341 | 0.49339 | 0.49839 | 0.49838
90 | feeder2_line106 | 1 | 354.6 | 0.19485 | 0.1946 | 0.054949 | 0.05488
90 | feeder2_line106 | 2 | 354.6 | 2.9895 | 2.9893 | 0.84306 | 0.84301
90 | feeder2_line106 | 3 | 354.6 | 3.1241 | 3.1239 | 0.88103 | 0.88098
90 | feeder2_line107 | 1 | 99 | 3.2647e-07 | 9.0675e-07 | 3.2977e-07 | 9.1591e-07
90 | feeder2_line107 | 2 | 99 | 1.1998 | 1.1998 | 1.2119 | 1.2119
90 | feeder2_line107 | 3 | 99 | 3.2671e-07 | 9.0718e-07 | 3.3001e-07 | 9.1634e-07
90 | feeder2_line108 | 1 | 354.6 | 0.19484 | 0.1946 | 0.054946 | 0.05488
90 | feeder2_line108 | 2 | 354.6 | 1.8004 | 1.8002 | 0.50772 | 0.50768
90 | feeder2_line108 | 3 | 354.6 | 3.1241 | 3.1239 | 0.88103 | 0.88098
90 | feeder2_line109 | 1 | 354.6 | 96.7177 | 96.7208 | 27.2752 | 27.276
90 | feeder2_line109 | 2 | 354.6 | 95.4666 | 95.4656 | 26.9223 | 26.9221
90 | feeder2_line109 | 3 | 354.6 | 97.9452 | 97.9427 | 27.6213 | 27.6206
90 | feeder2_line110 | 1 | 99 | 1.1986 | 1.198 | 1.2107 | 1.2101
90 | feeder2_line110 | 2 | 99 | 0.00080905 | 9.1457e-07 | 0.00081722 | 9.2381e-07
90 | feeder2_line110 | 3 | 99 | 0.00081049 | 9.1592e-07 | 0.00081868 | 9.2517e-07
90 | feeder2_line111 | 1 | 99 | 2.5102e-08 | 3.8445e-07 | 2.5356e-08 | 3.8834e-07
90 | feeder2_line111 | 2 | 99 | 0.072493 | 0.0725 | 0.073225 | 0.073232
90 | feeder2_line111 | 3 | 99 | 2.5168e-08 | 3.8466e-07 | 2.5422e-08 | 3.8854e-07
90 | feeder2_line112 | 1 | 99 | 3.2679e-07 | 9.2383e-07 | 3.3009e-07 | 9.3317e-07
90 | feeder2_line112 | 2 | 99 | 0.040637 | 0.040652 | 0.041048 | 0.041063
90 | feeder2_line112 | 3 | 99 | 3.2704e-07 | 9.2436e-07 | 3.3034e-07 | 9.3369e-07
90 | feeder2_line113 | 1 | 99 | 0.12796 | 0.12796 | 0.12925 | 0.12925
90 | feeder2_line113 | 2 | 99 | 3.2693e-07 | 9.1103e-07 | 3.3024e-07 | 9.2023e-07
90 | feeder2_line113 | 3 | 99 | 3.2745e-07 | 9.1253e-07 | 3.3075e-07 | 9.2175e-07
90 | feeder2_line114 | 1 | 99 | 1.2626 | 1.2626 | 1.2754 | 1.2753
90 | feeder2_line114 | 2 | 99 | 2.5113e-08 | 4.3892e-07 | 2.5366e-08 | 4.4335e-07
90 | feeder2_line114 | 3 | 99 | 2.5142e-08 | 4.3955e-07 | 2.5396e-08 | 4.4399e-07
90 | feeder2_line115 | 1 | 99 | 2.5076e-08 | 5.6586e-07 | 2.5329e-08 | 5.7158e-07
90 | feeder2_line115 | 2 | 99 | 0.33249 | 0.33249 | 0.33585 | 0.33585
90 | feeder2_line115 | 3 | 99 | 2.5147e-08 | 5.661e-07 | 2.5401e-08 | 5.7182e-07
90 | feeder2_line116 | 1 | 354.6 | 0.19485 | 0.1946 | 0.054948 | 0.05488
90 | feeder2_line116 | 2 | 354.6 | 1.5656 | 1.5654 | 0.4415 | 0.44146
90 | feeder2_line116 | 3 | 354.6 | 3.1241 | 3.1239 | 0.88103 | 0.88098
90 | feeder2_line117 | 1 | 99 | 5.0288e-08 | 6.4772e-07 | 5.0796e-08 | 6.5426e-07
90 | feeder2_line117 | 2 | 99 | 1.5321 | 1.5321 | 1.5476 | 1.5476
90 | feeder2_line117 | 3 | 99 | 5.0423e-08 | 6.481e-07 | 5.0932e-08 | 6.5465e-07
90 | feeder2_line118 | 1 | 354.6 | 96.7177 | 96.7208 | 27.2752 | 27.276
90 | feeder2_line118 | 2 | 354.6 | 96.3723 | 96.3714 | 27.1778 | 27.1775
90 | feeder2_line118 | 3 | 354.6 | 97.9452 | 97.9427 | 27.6213 | 27.6206
90 | feeder2_line119 | 1 | 99 | 2.508e-08 | 6.089e-07 | 2.5333e-08 | 6.1506e-07
90 | feeder2_line119 | 2 | 99 | 2.5111e-08 | 6.0832e-07 | 2.5364e-08 | 6.1446e-07
90 | feeder2_line119 | 3 | 99 | 0.54661 | 0.5466 | 0.55213 | 0.55213
90 | feeder2_line120 | 1 | 354.6 | 0.19485 | 0.1946 | 0.054948 | 0.05488
90 | feeder2_line120 | 2 | 354.6 | 1.5656 | 1.5654 | 0.4415 | 0.44146
90 | feeder2_line120 | 3 | 354.6 | 2.686 | 2.6858 | 0.75746 | 0.75742
90 | feeder2_line121 | 1 | 99 | 3.2647e-07 | 9.429e-07 | 3.2977e-07 | 9.5242e-07
90 | feeder2_line121 | 2 | 99 | 0.043857 | 0.043857 | 0.0443 | 0.0443
90 | feeder2_line121 | 3 | 99 | 3.2668e-07 | 9.4321e-07 | 3.2998e-07 | 9.5274e-07
90 | feeder2_line122 | 1 | 354.6 | 0.19483 | 0.1946 | 0.054945 | 0.05488
90 | feeder2_line122 | 2 | 354.6 | 1.5376 | 1.5375 | 0.43363 | 0.4336
90 | feeder2_line122 | 3 | 354.6 | 2.6859 | 2.6858 | 0.75746 | 0.75742
90 | feeder2_line123 | 1 | 99 | 5.7771e-07 | 9.7706e-07 | 5.8355e-07 | 9.8693e-07
90 | feeder2_line123 | 2 | 99 | 5.7715e-07 | 9.7612e-07 | 5.8298e-07 | 9.8598e-07
90 | feeder2_line123 | 3 | 99 | 0.10807 | 0.10807 | 0.10916 | 0.10916
90 | feeder2_line124 | 1 | 354.6 | 0.19474 | 0.1946 | 0.054919 | 0.05488
90 | feeder2_line124 | 2 | 354.6 | 1.5377 | 1.5375 | 0.43364 | 0.4336
90 | feeder2_line124 | 3 | 354.6 | 2.6166 | 2.6164 | 0.7379 | 0.73786
90 | feeder2_line125 | 1 | 99 | 5.7771e-07 | 9.0828e-07 | 5.8354e-07 | 9.1745e-07
90 | feeder2_line125 | 2 | 99 | 5.7715e-07 | 9.074e-07 | 5.8298e-07 | 9.1657e-07
90 | feeder2_line125 | 3 | 99 | 0.15451 | 0.15449 | 0.15607 | 0.15605
90 | feeder2_line126 | 1 | 354.6 | 0.1949 | 0.1946 | 0.054964 | 0.05488
90 | feeder2_line126 | 2 | 354.6 | 1.5378 | 1.5375 | 0.43368 | 0.4336
90 | feeder2_line126 | 3 | 354.6 | 2.5239 | 2.5237 | 0.71177 | 0.71169
90 | feeder2_line127 | 1 | 99 | 5.7771e-07 | 1.0874e-06 | 5.8355e-07 | 1.0983e-06
90 | feeder2_line127 | 2 | 99 | 5.7715e-07 | 1.0863e-06 | 5.8298e-07 | 1.0973e-06
90 | feeder2_line127 | 3 | 99 | 1.061 | 1.061 | 1.0718 | 1.0718
90 | feeder2_line128 | 1 | 354.6 | 0.19482 | 0.1946 | 0.05494 | 0.05488
90 | feeder2_line128 | 2 | 354.6 | 1.5378 | 1.5375 | 0.43367 | 0.4336
90 | feeder2_line128 | 3 | 354.6 | 1.4634 | 1.4632 | 0.4127 | 0.41263
90 | feeder2_line129 | 1 | 99 | 5.5264e-07 | 8.8169e-07 | 5.5822e-07 | 8.906e-07
90 | feeder2_line129 | 2 | 99 | 1.5375 | 1.5375 | 1.5531 | 1.5531
90 | feeder2_line129 | 3 | 99 | 5.5271e-07 | 8.8194e-07 | 5.583e-07 | 8.9085e-07
90 | feeder2_line130 | 1 | 354.6 | 0.19483 | 0.1946 | 0.054945 | 0.05488
90 | feeder2_line130 | 2 | 354.6 | 0.00031005 | 4.6614e-06 | 8.7437e-05 | 1.3146e-06
90 | feeder2_line130 | 3 | 354.6 | 1.4635 | 1.4632 | 0.41271 | 0.41263
90 | feeder2_line131 | 1 | 99 | 5.7771e-07 | 9.7722e-07 | 5.8355e-07 | 9.8709e-07
90 | feeder2_line131 | 2 | 99 | 5.7714e-07 | 9.7627e-07 | 5.8297e-07 | 9.8613e-07
90 | feeder2_line131 | 3 | 99 | 1.3213 | 1.3213 | 1.3346 | 1.3347
90 | feeder2_line132 | 1 | 354.6 | 0.19467 | 0.1946 | 0.054898 | 0.05488
90 | feeder2_line132 | 2 | 354.6 | 0.0001263 | 2.9307e-06 | 3.5618e-05 | 8.2648e-07
90 | feeder2_line132 | 3 | 354.6 | 0.21263 | 0.21255 | 0.059962 | 0.059941
90 | feeder2_line133 | 1 | 99 | 0.19459 | 0.1946 | 0.19656 | 0.19657
90 | feeder2_line133 | 2 | 99 | 3.0113e-07 | 9.8407e-07 | 3.0417e-07 | 9.9401e-07
90 | feeder2_line133 | 3 | 99 | 3.0151e-07 | 9.8528e-07 | 3.0455e-07 | 9.9524e-07
90 | feeder2_line134 | 1 | 354.6 | 4.5963e-12 | 1.7962e-06 | 1.2962e-12 | 5.0655e-07
90 | feeder2_line134 | 2 | 354.6 | 7.4411e-12 | 1.7946e-06 | 2.0985e-12 | 5.0609e-07
90 | feeder2_line134 | 3 | 354.6 | 0.21255 | 0.21255 | 0.059941 | 0.059941
90 | feeder2_line135 | 1 | 99 | 1.4308 | 1.4308 | 1.4452 | 1.4452
90 | feeder2_line135 | 2 | 99 | 5.0412e-08 | 5.8983e-07 | 5.0922e-08 | 5.9579e-07
90 | feeder2_line135 | 3 | 99 | 5.0452e-08 | 5.9085e-07 | 5.0962e-08 | 5.9682e-07
90 | feeder2_line136 | 1 | 354.6 | 97.6972 | 97.7003 | 27.5514 | 27.5522
90 | feeder2_line136 | 2 | 354.6 | 96.3723 | 96.3714 | 27.1778 | 27.1775
90 | feeder2_line136 | 3 | 354.6 | 97.9452 | 97.9427 | 27.6213 | 27.6206
90 | feeder2_line137 | 1 | 99 | 0.085075 | 0.085087 | 0.085934 | 0.085946
90 | feeder2_line137 | 2 | 99 | 8.5605e-07 | 1.5888e-06 | 8.647e-07 | 1.6049e-06
90 | feeder2_line137 | 3 | 99 | 8.5755e-07 | 1.5916e-06 | 8.6622e-07 | 1.6077e-06
90 | feeder2_line138 | 1 | 354.6 | 97.7822 | 97.7853 | 27.5754 | 27.5762
90 | feeder2_line138 | 2 | 354.6 | 96.3724 | 96.3714 | 27.1778 | 27.1775
90 | feeder2_line138 | 3 | 354.6 | 97.9452 | 97.9427 | 27.6213 | 27.6206
90 | feeder2_line139 | 1 | 99 | 5.0342e-08 | 4.957e-07 | 5.0851e-08 | 5.007e-07
90 | feeder2_line139 | 2 | 99 | 5.0435e-08 | 4.9512e-07 | 5.0944e-08 | 5.0013e-07
90 | feeder2_line139 | 3 | 99 | 0.13649 | 0.13629 | 0.13787 | 0.13767
90 | feeder2_line140 | 1 | 354.6 | 97.7823 | 97.7853 | 27.5754 | 27.5762
90 | feeder2_line140 | 2 | 354.6 | 96.3725 | 96.3714 | 27.1778 | 27.1775
90 | feeder2_line140 | 3 | 354.6 | 98.0771 | 98.0743 | 27.6585 | 27.6577
90 | feeder2_line141 | 1 | 99 | 2.5476e-06 | 4.9042e-07 | 2.5734e-06 | 4.9537e-07
90 | feeder2_line141 | 2 | 99 | 1.2606 | 1.2606 | 1.2733 | 1.2733
90 | feeder2_line141 | 3 | 99 | 2.5483e-06 | 4.9069e-07 | 2.5741e-06 | 4.9565e-07
90 | feeder2_line142 | 1 | 354.6 | 97.7821 | 97.7853 | 27.5753 | 27.5762
90 | feeder2_line142 | 2 | 354.6 | 97.1687 | 97.1677 | 27.4023 | 27.4021
90 | feeder2_line142 | 3 | 354.6 | 98.0769 | 98.0743 | 27.6585 | 27.6577
90 | feeder2_line143 | 1 | 99 | 8.575e-07 | 1.7427e-06 | 8.6617e-07 | 1.7603e-06
90 | feeder2_line143 | 2 | 99 | 1.201 | 1.201 | 1.2131 | 1.2131
90 | feeder2_line143 | 3 | 99 | 8.5798e-07 | 1.7437e-06 | 8.6664e-07 | 1.7614e-06
90 | feeder2_line144 | 1 | 354.6 | 97.782 | 97.7853 | 27.5753 | 27.5762
90 | feeder2_line144 | 2 | 354.6 | 97.8997 | 97.899 | 27.6085 | 27.6083
90 | feeder2_line144 | 3 | 354.6 | 98.0768 | 98.0743 | 27.6584 | 27.6577
90 | feeder2_line145 | 1 | 99 | 2.5177e-08 | 4.887e-07 | 2.5432e-08 | 4.9363e-07
90 | feeder2_line145 | 2 | 99 | 0.25073 | 0.25073 | 0.25326 | 0.25326
90 | feeder2_line145 | 3 | 99 | 2.5247e-08 | 4.8898e-07 | 2.5502e-08 | 4.9392e-07
90 | feeder2_line146 | 1 | 354.6 | 97.7818 | 97.7853 | 27.5753 | 27.5762
90 | feeder2_line146 | 2 | 354.6 | 98.1503 | 98.1497 | 27.6792 | 27.679
90 | feeder2_line146 | 3 | 354.6 | 98.0766 | 98.0743 | 27.6584 | 27.6577
90 | feeder2_line147 | 1 | 99 | 1.1248 | 1.1248 | 1.1362 | 1.1362
90 | feeder2_line147 | 2 | 99 | 1.159e-06 | 2.2516e-06 | 1.1707e-06 | 2.2743e-06
90 | feeder2_line147 | 3 | 99 | 1.161e-06 | 2.2555e-06 | 1.1727e-06 | 2.2783e-06
90 | feeder2_line148 | 1 | 99 | 0.22049 | 0.22049 | 0.22271 | 0.22272
90 | feeder2_line148 | 2 | 99 | 6.0472e-07 | 1.5087e-06 | 6.1083e-07 | 1.524e-06
90 | feeder2_line148 | 3 | 99 | 6.0576e-07 | 1.5114e-06 | 6.1188e-07 | 1.5266e-06
90 | feeder2_line149 | 1 | 354.6 | 98.6958 | 98.6991 | 27.833 | 27.8339
90 | feeder2_line149 | 2 | 354.6 | 98.1505 | 98.1497 | 27.6792 | 27.679
90 | feeder2_line149 | 3 | 354.6 | 98.0768 | 98.0743 | 27.6584 | 27.6577
90 | feeder2_line150 | 1 | 354.6 | 98.6959 | 98.6991 | 27.833 | 27.8339
90 | feeder2_line150 | 2 | 354.6 | 99.0001 | 98.9992 | 27.9188 | 27.9185
90 | feeder2_line150 | 3 | 354.6 | 98.0769 | 98.0743 | 27.6585 | 27.6577
90 | feeder2_line151 | 1 | 99 | 9.8487e-06 | 1.7946e-06 | 9.9482e-06 | 1.8127e-06
90 | feeder2_line151 | 2 | 99 | 1.3159 | 1.3159 | 1.3292 | 1.3292
90 | feeder2_line151 | 3 | 99 | 9.851e-06 | 1.7956e-06 | 9.9505e-06 | 1.8137e-06
90 | feeder2_line152 | 1 | 354.6 | 1.2881e-11 | 1.1962e-06 | 3.6326e-12 | 3.3734e-07
90 | feeder2_line152 | 2 | 354.6 | 2.4171e-11 | 1.1949e-06 | 6.8165e-12 | 3.3696e-07
90 | feeder2_line152 | 3 | 354.6 | 1.1897 | 1.1897 | 0.33551 | 0.33551
90 | feeder2_line153 | 1 | 99 | 0.043568 | 0.04357 | 0.044008 | 0.04401
90 | feeder2_line153 | 2 | 99 | 5.0507e-08 | 5.9781e-07 | 5.1017e-08 | 6.0385e-07
90 | feeder2_line153 | 3 | 99 | 5.0552e-08 | 5.9884e-07 | 5.1062e-08 | 6.0489e-07
90 | feeder2_line154 | 1 | 99 | 5.8076e-07 | 8.9061e-07 | 5.8663e-07 | 8.9961e-07
90 | feeder2_line154 | 2 | 99 | 5.8007e-07 | 8.8957e-07 | 5.8593e-07 | 8.9855e-07
90 | feeder2_line154 | 3 | 99 | 0.040411 | 0.040388 | 0.040819 | 0.040796
90 | feeder2_line155 | 1 | 99 | 98.7394 | 98.7426 | 99.7368 | 99.74
90 | feeder2_line155 | 2 | 99 | 99 | 98.9992 | 100 | 99.9992
90 | feeder2_line155 | 3 | 99 | 98.8189 | 98.8164 | 99.8171 | 99.8145
90 | feeder2_line156 | 1 | 99 | 6.0568e-07 | 1.1718e-06 | 6.118e-07 | 1.1837e-06
90 | feeder2_line156 | 2 | 99 | 1.2639 | 1.2639 | 1.2767 | 1.2766
90 | feeder2_line156 | 3 | 99 | 6.0608e-07 | 1.1725e-06 | 6.122e-07 | 1.1843e-06
90 | feeder2_line157 | 1 | 99 | 2.5191e-08 | 2.544e-07 | 2.5445e-08 | 2.5697e-07
90 | feeder2_line157 | 2 | 99 | 0.089077 | 0.089076 | 0.089977 | 0.089976
90 | feeder2_line157 | 3 | 99 | 2.5263e-08 | 2.5454e-07 | 2.5518e-08 | 2.5712e-07
120 | feeder2_line1 | 1 | 354.6 | 80.9859 | 80.9878 | 22.8387 | 22.8392
120 | feeder2_line1 | 2 | 354.6 | 90.9067 | 90.9024 | 25.6364 | 25.6352
120 | feeder2_line1 | 3 | 354.6 | 87.7072 | 87.7121 | 24.7341 | 24.7355
120 | feeder2_line2 | 1 | 354.6 | 81.3073 | 81.309 | 22.9293 | 22.9298
120 | feeder2_line2 | 2 | 354.6 | 90.9069 | 90.9024 | 25.6365 | 25.6352
120 | feeder2_line2 | 3 | 354.6 | 87.7073 | 87.7121 | 24.7342 | 24.7355
120 | feeder2_line3 | 1 | 80.1 | 0.33959 | 0.33959 | 0.42396 | 0.42396
120 | feeder2_line3 | 2 | 80.1 | 5.723e-07 | 1.0576e-06 | 7.1448e-07 | 1.3203e-06
120 | feeder2_line3 | 3 | 80.1 | 5.7165e-07 | 1.0564e-06 | 7.1367e-07 | 1.3189e-06
120 | feeder2_line4 | 1 | 354.6 | 81.3075 | 81.309 | 22.9293 | 22.9298
120 | feeder2_line4 | 2 | 354.6 | 91.1772 | 91.1726 | 25.7127 | 25.7114
120 | feeder2_line4 | 3 | 354.6 | 87.7075 | 87.7121 | 24.7342 | 24.7355
120 | feeder2_line5 | 1 | 80.1 | 5.7154e-07 | 9.9729e-07 | 7.1353e-07 | 1.2451e-06
120 | feeder2_line5 | 2 | 80.1 | 0.27932 | 0.27932 | 0.34872 | 0.34872
120 | feeder2_line5 | 3 | 80.1 | 5.7169e-07 | 9.9755e-07 | 7.1372e-07 | 1.2454e-06
120 | feeder2_line6 | 1 | 80.1 | 5.7158e-07 | 1.1733e-06 | 7.1359e-07 | 1.4648e-06
120 | feeder2_line6 | 2 | 80.1 | 5.7244e-07 | 1.175e-06 | 7.1465e-07 | 1.4669e-06
120 | feeder2_line6 | 3 | 80.1 | 0.085422 | 0.085426 | 0.10664 | 0.10665
120 | feeder2_line7 | 1 | 354.6 | 81.3076 | 81.309 | 22.9294 | 22.9298
120 | feeder2_line7 | 2 | 354.6 | 91.1773 | 91.1726 | 25.7127 | 25.7114
120 | feeder2_line7 | 3 | 354.6 | 87.7881 | 87.7926 | 24.7569 | 24.7582
120 | feeder2_line8 | 1 | 80.1 | 0.072723 | 0.072723 | 0.09079 | 0.09079
120 | feeder2_line8 | 2 | 80.1 | 5.7268e-07 | 1.1335e-06 | 7.1496e-07 | 1.415e-06
120 | feeder2_line8 | 3 | 80.1 | 5.719e-07 | 1.1319e-06 | 7.1399e-07 | 1.4132e-06
120 | feeder2_line9 | 1 | 354.6 | 81.3778 | 81.3792 | 22.9492 | 22.9496
120 | feeder2_line9 | 2 | 354.6 | 91.1773 | 91.1726 | 25.7127 | 25.7114
120 | feeder2_line9 | 3 | 354.6 | 87.7881 | 87.7926 | 24.7569 | 24.7582
120 | feeder2_line10 | 1 | 80.1 | 8.4513e-07 | 1.4941e-06 | 1.0551e-06 | 1.8653e-06
120 | feeder2_line10 | 2 | 80.1 | 0.072518 | 0.072518 | 0.090535 | 0.090534
120 | feeder2_line10 | 3 | 80.1 | 8.4544e-07 | 1.4947e-06 | 1.0555e-06 | 1.866e-06
120 | feeder2_line11 | 1 | 354.6 | 81.3778 | 81.3792 | 22.9492 | 22.9496
120 | feeder2_line11 | 2 | 354.6 | 91.2484 | 91.2437 | 25.7328 | 25.7314
120 | feeder2_line11 | 3 | 354.6 | 87.7881 | 87.7926 | 24.7569 | 24.7582
120 | feeder2_line12 | 1 | 80.1 | 5.4684e-07 | 9.9119e-07 | 6.827e-07 | 1.2374e-06
120 | feeder2_line12 | 2 | 80.1 | 5.4801e-07 | 9.9296e-07 | 6.8416e-07 | 1.2397e-06
120 | feeder2_line12 | 3 | 80.1 | 0.061824 | 0.061825 | 0.077184 | 0.077185
120 | feeder2_line13 | 1 | 354.6 | 81.3778 | 81.3792 | 22.9492 | 22.9496
120 | feeder2_line13 | 2 | 354.6 | 91.2484 | 91.2437 | 25.7328 | 25.7314
120 | feeder2_line13 | 3 | 354.6 | 87.8464 | 87.8509 | 24.7734 | 24.7746
120 | feeder2_line14 | 1 | 80.1 | 1.1745 | 1.1744 | 1.4662 | 1.4662
120 | feeder2_line14 | 2 | 80.1 | 2.9885e-07 | 6.4759e-07 | 3.731e-07 | 8.0848e-07
120 | feeder2_line14 | 3 | 80.1 | 2.9847e-07 | 6.4664e-07 | 3.7263e-07 | 8.0729e-07
120 | feeder2_line15 | 1 | 354.6 | 81.9078 | 81.9092 | 23.0986 | 23.099
120 | feeder2_line15 | 2 | 354.6 | 91.2484 | 91.2437 | 25.7328 | 25.7314
120 | feeder2_line15 | 3 | 354.6 | 87.8464 | 87.8509 | 24.7734 | 24.7746
120 | feeder2_line16 | 1 | 80.1 | 5.7189e-07 | 1.0303e-06 | 7.1397e-07 | 1.2863e-06
120 | feeder2_line16 | 2 | 80.1 | 0.25458 | 0.25458 | 0.31783 | 0.31783
120 | feeder2_line16 | 3 | 80.1 | 5.7214e-07 | 1.0307e-06 | 7.1428e-07 | 1.2868e-06
120 | feeder2_line17 | 1 | 354.6 | 81.9078 | 81.9092 | 23.0987 | 23.099
120 | feeder2_line17 | 2 | 354.6 | 91.4936 | 91.4888 | 25.8019 | 25.8006
120 | feeder2_line17 | 3 | 354.6 | 87.8465 | 87.8509 | 24.7734 | 24.7746
120 | feeder2_line18 | 1 | 80.1 | 5.4724e-07 | 7.3793e-07 | 6.8319e-07 | 9.2126e-07
120 | feeder2_line18 | 2 | 80.1 | 5.4886e-07 | 7.3976e-07 | 6.8522e-07 | 9.2354e-07
120 | feeder2_line18 | 3 | 80.1 | 1.414 | 1.414 | 1.7653 | 1.7653
120 | feeder2_line19 | 1 | 354.6 | 81.9079 | 81.9092 | 23.0987 | 23.099
120 | feeder2_line19 | 2 | 354.6 | 91.4936 | 91.4888 | 25.8019 | 25.8006
120 | feeder2_line19 | 3 | 354.6 | 88.5096 | 88.514 | 24.9604 | 24.9617
120 | feeder2_line20 | 1 | 99 | 5.4735e-07 | 8.8493e-07 | 5.5287e-07 | 8.9387e-07
120 | feeder2_line20 | 2 | 99 | 5.4909e-07 | 8.8728e-07 | 5.5464e-07 | 8.9624e-07
120 | feeder2_line20 | 3 | 99 | 1.584 | 1.584 | 1.6 | 1.6
120 | feeder2_line21 | 1 | 354.6 | 81.908 | 81.9092 | 23.0987 | 23.099
120 | feeder2_line21 | 2 | 354.6 | 91.4937 | 91.4888 | 25.802 | 25.8006
120 | feeder2_line21 | 3 | 354.6 | 89.1332 | 89.1375 | 25.1363 | 25.1375
120 | feeder2_line22 | 1 | 99 | 5.7242e-07 | 1.0146e-06 | 5.782e-07 | 1.0248e-06
120 | feeder2_line22 | 2 | 99 | 0.093669 | 0.093668 | 0.094615 | 0.094614
120 | feeder2_line22 | 3 | 99 | 5.728e-07 | 1.0153e-06 | 5.7858e-07 | 1.0255e-06
120 | feeder2_line23 | 1 | 99 | 5.7242e-07 | 9.4975e-07 | 5.7821e-07 | 9.5934e-07
120 | feeder2_line23 | 2 | 99 | 5.7402e-07 | 9.5237e-07 | 5.7982e-07 | 9.6199e-07
120 | feeder2_line23 | 3 | 99 | 2.1975 | 2.1974 | 2.2197 | 2.2196
120 | feeder2_line24 | 1 | 354.6 | 81.908 | 81.9092 | 23.0987 | 23.099
120 | feeder2_line24 | 2 | 354.6 | 91.5854 | 91.5805 | 25.8278 | 25.8264
120 | feeder2_line24 | 3 | 354.6 | 89.7613 | 89.7656 | 25.3134 | 25.3146
120 | feeder2_line25 | 1 | 99 | 0.093998 | 0.093998 | 0.094947 | 0.094948
120 | feeder2_line25 | 2 | 99 | 4.9593e-08 | 6.9268e-07 | 5.0093e-08 | 6.9968e-07
120 | feeder2_line25 | 3 | 99 | 4.9912e-08 | 6.9116e-07 | 5.0417e-08 | 6.9814e-07
120 | feeder2_line26 | 1 | 99 | 0.2205 | 0.2205 | 0.22273 | 0.22273
120 | feeder2_line26 | 2 | 99 | 5.4946e-07 | 8.5819e-07 | 5.5501e-07 | 8.6686e-07
120 | feeder2_line26 | 3 | 99 | 5.4803e-07 | 8.563e-07 | 5.5356e-07 | 8.6495e-07
120 | feeder2_line27 | 1 | 354.6 | 82.2093 | 82.2104 | 23.1837 | 23.184
120 | feeder2_line27 | 2 | 354.6 | 91.5854 | 91.5805 | 25.8278 | 25.8264
120 | feeder2_line27 | 3 | 354.6 | 89.7613 | 89.7656 | 25.3134 | 25.3146
120 | feeder2_line28 | 1 | 99 | 2.5383e-06 | 7.1056e-07 | 2.564e-06 | 7.1774e-07
120 | feeder2_line28 | 2 | 99 | 1.9817 | 1.9817 | 2.0017 | 2.0017
120 | feeder2_line28 | 3 | 99 | 2.5419e-06 | 7.1119e-07 | 2.5675e-06 | 7.1838e-07
120 | feeder2_line29 | 1 | 354.6 | 82.2093 | 82.2104 | 23.1837 | 23.184
120 | feeder2_line29 | 2 | 354.6 | 92.3385 | 92.3335 | 26.0402 | 26.0388
120 | feeder2_line29 | 3 | 354.6 | 89.7614 | 89.7656 | 25.3134 | 25.3146
120 | feeder2_line30 | 1 | 266.4 | 11.3207 | 11.3204 | 4.2495 | 4.2494
120 | feeder2_line30 | 2 | 266.4 | 1.645 | 1.6451 | 0.61749 | 0.61755
120 | feeder2_line30 | 3 | 266.4 | 1.2137 | 1.2138 | 0.45559 | 0.45562
120 | feeder2_line31 | 1 | 354.6 | 92.9998 | 93.0005 | 26.2267 | 26.2269
120 | feeder2_line31 | 2 | 354.6 | 93.1786 | 93.1732 | 26.2771 | 26.2756
120 | feeder2_line31 | 3 | 354.6 | 90.4787 | 90.4825 | 25.5157 | 25.5168
120 | feeder2_line32 | 1 | 354.6 | 92.9998 | 93.0005 | 26.2267 | 26.2269
120 | feeder2_line32 | 2 | 354.6 | 93.4304 | 93.425 | 26.3481 | 26.3466
120 | feeder2_line32 | 3 | 354.6 | 90.4787 | 90.4825 | 25.5157 | 25.5168
120 | feeder2_line33 | 1 | 99 | 5.0189e-08 | 6.8615e-07 | 5.0696e-08 | 6.9308e-07
120 | feeder2_line33 | 2 | 99 | 0.25779 | 0.25778 | 0.26039 | 0.26039
120 | feeder2_line33 | 3 | 99 | 5.0001e-08 | 6.8691e-07 | 5.0506e-08 | 6.9384e-07
120 | feeder2_line34 | 1 | 354.6 | 92.9998 | 93.0005 | 26.2267 | 26.2269
120 | feeder2_line34 | 2 | 354.6 | 93.4304 | 93.425 | 26.3481 | 26.3466
120 | feeder2_line34 | 3 | 354.6 | 90.7386 | 90.7424 | 25.589 | 25.5901
120 | feeder2_line35 | 1 | 99 | 2.9926e-07 | 7.5997e-07 | 3.0228e-07 | 7.6765e-07
120 | feeder2_line35 | 2 | 99 | 3.0023e-07 | 7.6288e-07 | 3.0326e-07 | 7.7059e-07
120 | feeder2_line35 | 3 | 99 | 0.27531 | 0.27531 | 0.27809 | 0.27809
120 | feeder2_line36 | 1 | 354.6 | 93.0271 | 93.0279 | 26.2344 | 26.2346
120 | feeder2_line36 | 2 | 354.6 | 93.4303 | 93.425 | 26.3481 | 26.3466
120 | feeder2_line36 | 3 | 354.6 | 90.7386 | 90.7424 | 25.589 | 25.5901
120 | feeder2_line37 | 1 | 99 | 0.028145 | 0.028165 | 0.028429 | 0.02845
120 | feeder2_line37 | 2 | 99 | 3.0031e-07 | 8.4432e-07 | 3.0334e-07 | 8.5285e-07
120 | feeder2_line37 | 3 | 99 | 2.9959e-07 | 8.4197e-07 | 3.0262e-07 | 8.5047e-07
120 | feeder2_line38 | 1 | 99 | 3.2415e-07 | 7.7549e-07 | 3.2742e-07 | 7.8332e-07
120 | feeder2_line38 | 2 | 99 | 0.21253 | 0.21253 | 0.21468 | 0.21467
120 | feeder2_line38 | 3 | 99 | 3.2435e-07 | 7.7641e-07 | 3.2763e-07 | 7.8425e-07
120 | feeder2_line39 | 1 | 266.4 | 11.3207 | 11.3204 | 4.2495 | 4.2494
120 | feeder2_line39 | 2 | 266.4 | 1.5077 | 1.5079 | 0.56596 | 0.56604
120 | feeder2_line39 | 3 | 266.4 | 1.2137 | 1.2138 | 0.45559 | 0.45562
120 | feeder2_line40 | 1 | 354.6 | 93.1188 | 93.1195 | 26.2602 | 26.2604
120 | feeder2_line40 | 2 | 354.6 | 93.4304 | 93.425 | 26.3481 | 26.3466
120 | feeder2_line40 | 3 | 354.6 | 90.7386 | 90.7424 | 25.589 | 25.5901
120 | feeder2_line41 | 1 | 99 | 0.093879 | 0.09388 | 0.094827 | 0.094828
120 | feeder2_line41 | 2 | 99 | 4.963e-08 | 7.3789e-07 | 5.0132e-08 | 7.4534e-07
120 | feeder2_line41 | 3 | 99 | 5.0031e-08 | 7.3581e-07 | 5.0536e-08 | 7.4324e-07
120 | feeder2_line42 | 1 | 99 | 2.9903e-07 | 7.4844e-07 | 3.0205e-07 | 7.56e-07
120 | feeder2_line42 | 2 | 99 | 3.0002e-07 | 7.5134e-07 | 3.0305e-07 | 7.5893e-07
120 | feeder2_line42 | 3 | 99 | 0.18992 | 0.18992 | 0.19183 | 0.19183
120 | feeder2_line43 | 1 | 266.4 | 11.3206 | 11.3204 | 4.2495 | 4.2494
120 | feeder2_line43 | 2 | 266.4 | 1.5078 | 1.5079 | 0.566 | 0.56604
120 | feeder2_line43 | 3 | 266.4 | 1.0648 | 1.0648 | 0.39968 | 0.39972
120 | feeder2_line44 | 1 | 354.6 | 93.1188 | 93.1195 | 26.2603 | 26.2604
120 | feeder2_line44 | 2 | 354.6 | 93.4304 | 93.425 | 26.3481 | 26.3466
120 | feeder2_line44 | 3 | 354.6 | 91.4412 | 91.4449 | 25.7871 | 25.7882
120 | feeder2_line45 | 1 | 99 | 5.0239e-08 | 5.7973e-07 | 5.0746e-08 | 5.8558e-07
120 | feeder2_line45 | 2 | 99 | 4.9634e-08 | 5.8201e-07 | 5.0135e-08 | 5.8789e-07
120 | feeder2_line45 | 3 | 99 | 1.5851 | 1.5851 | 1.6011 | 1.6012
120 | feeder2_line46 | 1 | 99 | 5.7297e-07 | 1.3568e-06 | 5.7876e-07 | 1.3705e-06
120 | feeder2_line46 | 2 | 99 | 5.7523e-07 | 1.3621e-06 | 5.8104e-07 | 1.3758e-06
120 | feeder2_line46 | 3 | 99 | 0.95742 | 0.95745 | 0.9671 | 0.96712
120 | feeder2_line47 | 1 | 266.4 | 11.3206 | 11.3204 | 4.2495 | 4.2494
120 | feeder2_line47 | 2 | 266.4 | 1.508 | 1.5079 | 0.56607 | 0.56604
120 | feeder2_line47 | 3 | 266.4 | 0.17004 | 0.16978 | 0.06383 | 0.06373
120 | feeder2_line48 | 1 | 99 | 0.1365 | 0.1365 | 0.13787 | 0.13787
120 | feeder2_line48 | 2 | 99 | 4.9583e-08 | 7.3336e-07 | 5.0084e-08 | 7.4076e-07
120 | feeder2_line48 | 3 | 99 | 4.9972e-08 | 7.3148e-07 | 5.0477e-08 | 7.3887e-07
120 | feeder2_line49 | 1 | 266.4 | 11.1871 | 11.1869 | 4.1994 | 4.1993
120 | feeder2_line49 | 2 | 266.4 | 1.508 | 1.5079 | 0.56606 | 0.56604
120 | feeder2_line49 | 3 | 266.4 | 0.17003 | 0.16978 | 0.063824 | 0.06373
120 | feeder2_line50 | 1 | 99 | 5.7292e-07 | 1.2346e-06 | 5.787e-07 | 1.2471e-06
120 | feeder2_line50 | 2 | 99 | 0.084836 | 0.084814 | 0.085693 | 0.085671
120 | feeder2_line50 | 3 | 99 | 5.7375e-07 | 1.2364e-06 | 5.7955e-07 | 1.2489e-06
120 | feeder2_line51 | 1 | 99 | 10.5317 | 10.5317 | 10.638 | 10.638
120 | feeder2_line51 | 2 | 99 | 5.7522e-07 | 1.3457e-06 | 5.8103e-07 | 1.3593e-06
120 | feeder2_line51 | 3 | 99 | 5.7373e-07 | 1.3422e-06 | 5.7953e-07 | 1.3558e-06
120 | feeder2_line52 | 1 | 266.4 | 0.65535 | 0.65525 | 0.246 | 0.24597
120 | feeder2_line52 | 2 | 266.4 | 1.4615 | 1.4615 | 0.54861 | 0.54862
120 | feeder2_line52 | 3 | 266.4 | 0.16989 | 0.16978 | 0.063772 | 0.06373
120 | feeder2_line53 | 1 | 99 | 5.4782e-07 | 7.5352e-07 | 5.5336e-07 | 7.6113e-07
120 | feeder2_line53 | 2 | 99 | 1.4616 | 1.4615 | 1.4763 | 1.4763
120 | feeder2_line53 | 3 | 99 | 5.4877e-07 | 7.5461e-07 | 5.5431e-07 | 7.6223e-07
120 | feeder2_line54 | 1 | 266.4 | 0.65517 | 0.65525 | 0.24594 | 0.24597
120 | feeder2_line54 | 2 | 266.4 | 8.5767e-05 | 4.6405e-06 | 3.2195e-05 | 1.7419e-06
120 | feeder2_line54 | 3 | 266.4 | 0.1697 | 0.16978 | 0.0637 | 0.06373
120 | feeder2_line55 | 1 | 99 | 0.18096 | 0.18096 | 0.18279 | 0.18279
120 | feeder2_line55 | 2 | 99 | 4.9654e-08 | 7.3371e-07 | 5.0155e-08 | 7.4112e-07
120 | feeder2_line55 | 3 | 99 | 5.0068e-08 | 7.3153e-07 | 5.0574e-08 | 7.3892e-07
120 | feeder2_line56 | 1 | 354.6 | 93.293 | 93.2936 | 26.3094 | 26.3095
120 | feeder2_line56 | 2 | 354.6 | 93.4305 | 93.425 | 26.3481 | 26.3466
120 | feeder2_line56 | 3 | 354.6 | 91.4412 | 91.4449 | 25.7871 | 25.7882
120 | feeder2_line57 | 1 | 99 | 7.5271e-07 | 1.5435e-06 | 7.6031e-07 | 1.559e-06
120 | feeder2_line57 | 2 | 99 | 7.4373e-07 | 1.5496e-06 | 7.5124e-07 | 1.5653e-06
120 | feeder2_line57 | 3 | 99 | 0.16977 | 0.16978 | 0.17149 | 0.17149
120 | feeder2_line58 | 1 | 266.4 | 0.65523 | 0.65525 | 0.24596 | 0.24597
120 | feeder2_line58 | 2 | 266.4 | 1.9019e-05 | 2.6941e-06 | 7.1392e-06 | 1.0113e-06
120 | feeder2_line58 | 3 | 266.4 | 1.8971e-05 | 2.6876e-06 | 7.1211e-06 | 1.0089e-06
120 | feeder2_line59 | 1 | 99 | 5.0179e-08 | 5.3652e-07 | 5.0686e-08 | 5.4194e-07
120 | feeder2_line59 | 2 | 99 | 4.9583e-08 | 5.3867e-07 | 5.0083e-08 | 5.4411e-07
120 | feeder2_line59 | 3 | 99 | 0.10822 | 0.10822 | 0.10931 | 0.10932
120 | feeder2_line60 | 1 | 99 | 2.99e-07 | 8.1084e-07 | 3.0202e-07 | 8.1903e-07
120 | feeder2_line60 | 2 | 99 | 3.0001e-07 | 8.1409e-07 | 3.0304e-07 | 8.2231e-07
120 | feeder2_line60 | 3 | 99 | 0.06169 | 0.061691 | 0.062313 | 0.062315
120 | feeder2_line61 | 1 | 266.4 | 0.19844 | 0.19861 | 0.074489 | 0.074554
120 | feeder2_line61 | 2 | 266.4 | 0.6385 | 0.63865 | 0.23968 | 0.23973
120 | feeder2_line61 | 3 | 266.4 | 0.38488 | 0.38506 | 0.14447 | 0.14454
120 | feeder2_line62 | 1 | 354.6 | 93.4851 | 93.486 | 26.3635 | 26.3638
120 | feeder2_line62 | 2 | 354.6 | 94.0555 | 94.0502 | 26.5244 | 26.5229
120 | feeder2_line62 | 3 | 354.6 | 91.8098 | 91.8137 | 25.8911 | 25.8922
120 | feeder2_line63 | 1 | 99 | 0.3598 | 0.3598 | 0.36344 | 0.36344
120 | feeder2_line63 | 2 | 99 | 5.7524e-07 | 1.224e-06 | 5.8105e-07 | 1.2363e-06
120 | feeder2_line63 | 3 | 99 | 5.7375e-07 | 1.2208e-06 | 5.7955e-07 | 1.2332e-06
120 | feeder2_line64 | 1 | 99 | 0.29546 | 0.29546 | 0.29844 | 0.29844
120 | feeder2_line64 | 2 | 99 | 1.2884e-11 | 3.2242e-07 | 1.3014e-11 | 3.2568e-07
120 | feeder2_line64 | 3 | 99 | 4.3416e-12 | 3.2159e-07 | 4.3854e-12 | 3.2484e-07
120 | feeder2_line65 | 1 | 99 | 5.0343e-08 | 6.4235e-07 | 5.0851e-08 | 6.4884e-07
120 | feeder2_line65 | 2 | 99 | 0.27963 | 0.27962 | 0.28245 | 0.28245
120 | feeder2_line65 | 3 | 99 | 5.0117e-08 | 6.4304e-07 | 5.0623e-08 | 6.4954e-07
120 | feeder2_line66 | 1 | 354.6 | 93.485 | 93.486 | 26.3635 | 26.3638
120 | feeder2_line66 | 2 | 354.6 | 94.3289 | 94.3236 | 26.6015 | 26.6
120 | feeder2_line66 | 3 | 354.6 | 91.8097 | 91.8137 | 25.8911 | 25.8922
120 | feeder2_line67 | 1 | 99 | 2.5156e-08 | 3.63e-07 | 2.541e-08 | 3.6667e-07
120 | feeder2_line67 | 2 | 99 | 2.4828e-08 | 3.645e-07 | 2.5078e-08 | 3.6818e-07
120 | feeder2_line67 | 3 | 99 | 0.093653 | 0.093656 | 0.094599 | 0.094602
120 | feeder2_line68 | 1 | 266.4 | 0.19848 | 0.19861 | 0.074504 | 0.074554
120 | feeder2_line68 | 2 | 266.4 | 0.63854 | 0.63865 | 0.23969 | 0.23973
120 | feeder2_line68 | 3 | 266.4 | 0.29133 | 0.29147 | 0.10936 | 0.10941
120 | feeder2_line69 | 1 | 99 | 2.8461 | 2.846 | 2.8748 | 2.8748
120 | feeder2_line69 | 2 | 99 | 2.5626e-06 | 6.6983e-07 | 2.5885e-06 | 6.766e-07
120 | feeder2_line69 | 3 | 99 | 2.5504e-06 | 6.6767e-07 | 2.5762e-06 | 6.7442e-07
120 | feeder2_line70 | 1 | 354.6 | 94.5904 | 94.5913 | 26.6752 | 26.6755
120 | feeder2_line70 | 2 | 354.6 | 94.3288 | 94.3236 | 26.6015 | 26.6
120 | feeder2_line70 | 3 | 354.6 | 91.8097 | 91.8137 | 25.8911 | 25.8922
120 | feeder2_line71 | 1 | 99 | 5.0367e-08 | 7.1685e-07 | 5.0876e-08 | 7.2409e-07
120 | feeder2_line71 | 2 | 99 | 0.32468 | 0.32465 | 0.32796 | 0.32793
120 | feeder2_line71 | 3 | 99 | 5.0138e-08 | 7.1761e-07 | 5.0644e-08 | 7.2486e-07
120 | feeder2_line72 | 1 | 354.6 | 94.5905 | 94.5913 | 26.6753 | 26.6755
120 | feeder2_line72 | 2 | 354.6 | 94.6452 | 94.6399 | 26.6907 | 26.6892
120 | feeder2_line72 | 3 | 354.6 | 91.8098 | 91.8137 | 25.8911 | 25.8922
120 | feeder2_line73 | 1 | 99 | 5.994e-07 | 1.5368e-06 | 6.0546e-07 | 1.5523e-06
120 | feeder2_line73 | 2 | 99 | 0.25785 | 0.25785 | 0.26046 | 0.26046
120 | feeder2_line73 | 3 | 99 | 5.9992e-07 | 1.5384e-06 | 6.0598e-07 | 1.5539e-06
120 | feeder2_line74 | 1 | 99 | 5.0314e-08 | 4.5835e-07 | 5.0822e-08 | 4.6298e-07
120 | feeder2_line74 | 2 | 99 | 0.29157 | 0.29155 | 0.29451 | 0.2945
120 | feeder2_line74 | 3 | 99 | 5.0091e-08 | 4.5884e-07 | 5.0597e-08 | 4.6347e-07
120 | feeder2_line75 | 1 | 266.4 | 0.19858 | 0.19861 | 0.074541 | 0.074554
120 | feeder2_line75 | 2 | 266.4 | 0.089316 | 0.089347 | 0.033527 | 0.033539
120 | feeder2_line75 | 3 | 266.4 | 0.29143 | 0.29147 | 0.1094 | 0.10941
120 | feeder2_line76 | 1 | 99 | 0.19861 | 0.19861 | 0.20062 | 0.20062
120 | feeder2_line76 | 2 | 99 | 8.5258e-07 | 1.5918e-06 | 8.6119e-07 | 1.6079e-06
120 | feeder2_line76 | 3 | 99 | 8.4979e-07 | 1.5869e-06 | 8.5837e-07 | 1.603e-06
120 | feeder2_line77 | 1 | 99 | 2.5155e-08 | 5.7599e-07 | 2.5409e-08 | 5.818e-07
120 | feeder2_line77 | 2 | 99 | 2.4834e-08 | 5.7838e-07 | 2.5085e-08 | 5.8422e-07
120 | feeder2_line77 | 3 | 99 | 0.29147 | 0.29147 | 0.29441 | 0.29442
120 | feeder2_line78 | 1 | 266.4 | 7.5545e-12 | 9.5549e-07 | 2.8358e-12 | 3.5867e-07
120 | feeder2_line78 | 2 | 266.4 | 0.089349 | 0.089347 | 0.033539 | 0.033539
120 | feeder2_line78 | 3 | 266.4 | 7.5496e-12 | 9.5634e-07 | 2.8339e-12 | 3.5899e-07
120 | feeder2_line79 | 1 | 354.6 | 1.788 | 1.7878 | 0.50422 | 0.50416
120 | feeder2_line79 | 2 | 354.6 | 2.9119 | 2.9117 | 0.82117 | 0.82112
120 | feeder2_line79 | 3 | 354.6 | 9.1162 | 9.116 | 2.5708 | 2.5708
120 | feeder2_line80 | 1 | 354.6 | 95.698 | 95.6983 | 26.9876 | 26.9877
120 | feeder2_line80 | 2 | 354.6 | 96.3124 | 96.3065 | 27.1608 | 27.1592
120 | feeder2_line80 | 3 | 354.6 | 96.177 | 96.1806 | 27.1227 | 27.1237
120 | feeder2_line81 | 1 | 354.6 | 95.698 | 95.6983 | 26.9876 | 26.9877
120 | feeder2_line81 | 2 | 354.6 | 96.3123 | 96.3065 | 27.1608 | 27.1592
120 | feeder2_line81 | 3 | 354.6 | 96.7858 | 96.7895 | 27.2944 | 27.2954
120 | feeder2_line82 | 1 | 354.6 | 9.6621e-12 | 7.3569e-07 | 2.7248e-12 | 2.0747e-07
120 | feeder2_line82 | 2 | 354.6 | 7.455e-12 | 7.3865e-07 | 2.1024e-12 | 2.0831e-07
120 | feeder2_line82 | 3 | 354.6 | 1.1607 | 1.1607 | 0.32732 | 0.32732
120 | feeder2_line83 | 1 | 354.6 | 95.6981 | 95.6983 | 26.9876 | 26.9877
120 | feeder2_line83 | 2 | 354.6 | 96.428 | 96.4219 | 27.1935 | 27.1917
120 | feeder2_line83 | 3 | 354.6 | 96.786 | 96.7895 | 27.2944 | 27.2954
120 | feeder2_line84 | 1 | 354.6 | 2.3434e-11 | 1.3005e-06 | 6.6086e-12 | 3.6675e-07
120 | feeder2_line84 | 2 | 354.6 | 0.1156 | 0.11558 | 0.032601 | 0.032594
120 | feeder2_line84 | 3 | 354.6 | 3.6e-12 | 1.3017e-06 | 1.0152e-12 | 3.6708e-07
120 | feeder2_line85 | 1 | 99 | 0.21251 | 0.21251 | 0.21466 | 0.21466
120 | feeder2_line85 | 2 | 99 | 4.9735e-08 | 4.6619e-07 | 5.0237e-08 | 4.709e-07
120 | feeder2_line85 | 3 | 99 | 5.0191e-08 | 4.646e-07 | 5.0698e-08 | 4.6929e-07
120 | feeder2_line86 | 1 | 354.6 | 95.9061 | 95.9062 | 27.0463 | 27.0463
120 | feeder2_line86 | 2 | 354.6 | 96.4281 | 96.4219 | 27.1935 | 27.1917
120 | feeder2_line86 | 3 | 354.6 | 96.7861 | 96.7895 | 27.2944 | 27.2954
120 | feeder2_line87 | 1 | 354.6 | 95.9063 | 95.9062 | 27.0463 | 27.0463
120 | feeder2_line87 | 2 | 354.6 | 96.5408 | 96.5344 | 27.2253 | 27.2235
120 | feeder2_line87 | 3 | 354.6 | 97.0432 | 97.0464 | 27.3669 | 27.3678
120 | feeder2_line88 | 1 | 354.6 | 0.00011382 | 3.3709e-06 | 3.2098e-05 | 9.5062e-07
120 | feeder2_line88 | 2 | 354.6 | 0.11288 | 0.11269 | 0.031833 | 0.03178
120 | feeder2_line88 | 3 | 354.6 | 0.26256 | 0.26247 | 0.074043 | 0.074018
120 | feeder2_line89 | 1 | 354.6 | 95.904 | 95.9062 | 27.0457 | 27.0463
120 | feeder2_line89 | 2 | 354.6 | 96.8456 | 96.8415 | 27.3112 | 27.3101
120 | feeder2_line89 | 3 | 354.6 | 97.0409 | 97.0464 | 27.3663 | 27.3678
120 | feeder2_line90 | 1 | 354.6 | 0.00072459 | 2.0359e-06 | 0.00020434 | 5.7413e-07
120 | feeder2_line90 | 2 | 354.6 | 0.30898 | 0.30948 | 0.087135 | 0.087276
120 | feeder2_line90 | 3 | 354.6 | 0.00072568 | 2.0372e-06 | 0.00020465 | 5.745e-07
120 | feeder2_line91 | 1 | 354.6 | 95.904 | 95.9062 | 27.0457 | 27.0463
120 | feeder2_line91 | 2 | 354.6 | 96.8456 | 96.8415 | 27.3112 | 27.3101
120 | feeder2_line91 | 3 | 354.6 | 97.1016 | 97.1072 | 27.3834 | 27.385
120 | feeder2_line92 | 1 | 354.6 | 8.7796e-12 | 1.0268e-06 | 2.4759e-12 | 2.8957e-07
120 | feeder2_line92 | 2 | 354.6 | 1.6773e-11 | 1.031e-06 | 4.7302e-12 | 2.9074e-07
120 | feeder2_line92 | 3 | 354.6 | 0.061495 | 0.061497 | 0.017342 | 0.017343
120 | feeder2_line93 | 1 | 99 | 2.5232e-08 | 3.4267e-07 | 2.5487e-08 | 3.4613e-07
120 | feeder2_line93 | 2 | 99 | 0.11553 | 0.11551 | 0.1167 | 0.11668
120 | feeder2_line93 | 3 | 99 | 2.511e-08 | 3.4306e-07 | 2.5364e-08 | 3.4652e-07
120 | feeder2_line94 | 1 | 354.6 | 2.5236e-06 | 1.6687e-06 | 7.1167e-07 | 4.7058e-07
120 | feeder2_line94 | 2 | 354.6 | 0.19459 | 0.19457 | 0.054877 | 0.05487
120 | feeder2_line94 | 3 | 354.6 | 2.511e-06 | 1.6703e-06 | 7.0813e-07 | 4.7104e-07
120 | feeder2_line95 | 1 | 99 | 3.5697e-06 | 2.614e-06 | 3.6058e-06 | 2.6404e-06
120 | feeder2_line95 | 2 | 99 | 0.11277 | 0.11269 | 0.11391 | 0.11383
120 | feeder2_line95 | 3 | 99 | 3.5797e-06 | 2.6168e-06 | 3.6159e-06 | 2.6432e-06
120 | feeder2_line96 | 1 | 354.6 | 0.00012128 | 6.2301e-07 | 3.4203e-05 | 1.7569e-07
120 | feeder2_line96 | 2 | 354.6 | 0.00012192 | 6.2608e-07 | 3.4382e-05 | 1.7656e-07
120 | feeder2_line96 | 3 | 354.6 | 0.26254 | 0.26247 | 0.074038 | 0.074018
120 | feeder2_line97 | 1 | 354.6 | 96.0588 | 96.0609 | 27.0894 | 27.0899
120 | feeder2_line97 | 2 | 354.6 | 96.8458 | 96.8415 | 27.3113 | 27.3101
120 | feeder2_line97 | 3 | 354.6 | 97.1018 | 97.1072 | 27.3835 | 27.385
120 | feeder2_line98 | 1 | 354.6 | 0.15668 | 0.155 | 0.044184 | 0.043711
120 | feeder2_line98 | 2 | 354.6 | 0.0017206 | 6.2524e-07 | 0.00048522 | 1.7632e-07
120 | feeder2_line98 | 3 | 354.6 | 0.0017004 | 6.2412e-07 | 0.00047952 | 1.7601e-07
120 | feeder2_line99 | 1 | 99 | 2.5224e-08 | 4.4795e-07 | 2.5479e-08 | 4.5247e-07
120 | feeder2_line99 | 2 | 99 | 2.4872e-08 | 4.4997e-07 | 2.5123e-08 | 4.5452e-07
120 | feeder2_line99 | 3 | 99 | 0.26245 | 0.26247 | 0.2651 | 0.26512
120 | feeder2_line100 | 1 | 99 | 0.15497 | 0.155 | 0.15654 | 0.15657
120 | feeder2_line100 | 2 | 99 | 2.4894e-08 | 6.1803e-07 | 2.5145e-08 | 6.2428e-07
120 | feeder2_line100 | 3 | 99 | 2.5117e-08 | 6.1594e-07 | 2.537e-08 | 6.2216e-07
120 | feeder2_line101 | 1 | 354.6 | 0.19501 | 0.19462 | 0.054995 | 0.054883
120 | feeder2_line101 | 2 | 354.6 | 2.9119 | 2.9117 | 0.82117 | 0.82112
120 | feeder2_line101 | 3 | 354.6 | 9.1162 | 9.116 | 2.5708 | 2.5708
120 | feeder2_line102 | 1 | 99 | 1.6421 | 1.6421 | 1.6587 | 1.6587
120 | feeder2_line102 | 2 | 99 | 2.3554e-06 | 8.833e-07 | 2.3792e-06 | 8.9223e-07
120 | feeder2_line102 | 3 | 99 | 2.336e-06 | 8.8018e-07 | 2.3596e-06 | 8.8907e-07
120 | feeder2_line103 | 1 | 99 | 5.4981e-07 | 8.049e-07 | 5.5536e-07 | 8.1303e-07
120 | feeder2_line103 | 2 | 99 | 0.096156 | 0.096153 | 0.097127 | 0.097125
120 | feeder2_line103 | 3 | 99 | 5.5042e-07 | 8.056e-07 | 5.5598e-07 | 8.1373e-07
120 | feeder2_line104 | 1 | 354.6 | 0.19491 | 0.19462 | 0.054966 | 0.054883
120 | feeder2_line104 | 2 | 354.6 | 2.853 | 2.8528 | 0.80456 | 0.80452
120 | feeder2_line104 | 3 | 354.6 | 9.1162 | 9.116 | 2.5708 | 2.5708
120 | feeder2_line105 | 1 | 99 | 2.5474e-06 | 7.4061e-07 | 2.5732e-06 | 7.4809e-07
120 | feeder2_line105 | 2 | 99 | 2.5651e-06 | 7.4393e-07 | 2.591e-06 | 7.5144e-07
120 | feeder2_line105 | 3 | 99 | 1.4158 | 1.4158 | 1.4301 | 1.4301
120 | feeder2_line106 | 1 | 354.6 | 0.19485 | 0.19462 | 0.054951 | 0.054883
120 | feeder2_line106 | 2 | 354.6 | 2.8529 | 2.8528 | 0.80455 | 0.80452
120 | feeder2_line106 | 3 | 354.6 | 7.7112 | 7.7111 | 2.1746 | 2.1746
120 | feeder2_line107 | 1 | 99 | 3.2529e-07 | 9.0254e-07 | 3.2858e-07 | 9.1165e-07
120 | feeder2_line107 | 2 | 99 | 0.11568 | 0.11564 | 0.11684 | 0.11681
120 | feeder2_line107 | 3 | 99 | 3.2536e-07 | 9.0323e-07 | 3.2865e-07 | 9.1235e-07
120 | feeder2_line108 | 1 | 354.6 | 0.19484 | 0.19462 | 0.054948 | 0.054883
120 | feeder2_line108 | 2 | 354.6 | 2.7838 | 2.7837 | 0.78506 | 0.78503
120 | feeder2_line108 | 3 | 354.6 | 7.7112 | 7.7111 | 2.1746 | 2.1746
120 | feeder2_line109 | 1 | 354.6 | 96.6874 | 96.6883 | 27.2666 | 27.2669
120 | feeder2_line109 | 2 | 354.6 | 96.847 | 96.8415 | 27.3116 | 27.3101
120 | feeder2_line109 | 3 | 354.6 | 97.103 | 97.1072 | 27.3838 | 27.385
120 | feeder2_line110 | 1 | 99 | 1.1974 | 1.1968 | 1.2095 | 1.2089
120 | feeder2_line110 | 2 | 99 | 0.00081106 | 9.1496e-07 | 0.00081926 | 9.242e-07
120 | feeder2_line110 | 3 | 99 | 0.00080663 | 9.1178e-07 | 0.00081478 | 9.2099e-07
120 | feeder2_line111 | 1 | 99 | 2.5222e-08 | 3.8259e-07 | 2.5477e-08 | 3.8646e-07
120 | feeder2_line111 | 2 | 99 | 0.072423 | 0.072399 | 0.073154 | 0.07313
120 | feeder2_line111 | 3 | 99 | 2.5101e-08 | 3.83e-07 | 2.5355e-08 | 3.8687e-07
120 | feeder2_line112 | 1 | 99 | 3.2556e-07 | 9.1938e-07 | 3.2885e-07 | 9.2867e-07
120 | feeder2_line112 | 2 | 99 | 0.040564 | 0.040508 | 0.040973 | 0.040917
120 | feeder2_line112 | 3 | 99 | 3.2569e-07 | 9.2038e-07 | 3.2898e-07 | 9.2967e-07
120 | feeder2_line113 | 1 | 99 | 0.1285 | 0.1285 | 0.1298 | 0.1298
120 | feeder2_line113 | 2 | 99 | 3.2669e-07 | 9.1152e-07 | 3.2999e-07 | 9.2073e-07
120 | feeder2_line113 | 3 | 99 | 3.2603e-07 | 9.0843e-07 | 3.2932e-07 | 9.1761e-07
120 | feeder2_line114 | 1 | 99 | 0.096558 | 0.096558 | 0.097533 | 0.097534
120 | feeder2_line114 | 2 | 99 | 2.4854e-08 | 4.3923e-07 | 2.5106e-08 | 4.4367e-07
120 | feeder2_line114 | 3 | 99 | 2.5088e-08 | 4.3768e-07 | 2.5342e-08 | 4.421e-07
120 | feeder2_line115 | 1 | 99 | 2.5195e-08 | 5.6323e-07 | 2.5449e-08 | 5.6892e-07
120 | feeder2_line115 | 2 | 99 | 1.5032 | 1.5032 | 1.5183 | 1.5183
120 | feeder2_line115 | 3 | 99 | 2.5097e-08 | 5.6361e-07 | 2.535e-08 | 5.693e-07
120 | feeder2_line116 | 1 | 354.6 | 0.19485 | 0.19462 | 0.05495 | 0.054883
120 | feeder2_line116 | 2 | 354.6 | 1.2811 | 1.281 | 0.36129 | 0.36126
120 | feeder2_line116 | 3 | 354.6 | 7.7112 | 7.7111 | 2.1746 | 2.1746
120 | feeder2_line117 | 1 | 99 | 5.0536e-08 | 6.4436e-07 | 5.1046e-08 | 6.5086e-07
120 | feeder2_line117 | 2 | 99 | 0.96007 | 0.96007 | 0.96977 | 0.96976
120 | feeder2_line117 | 3 | 99 | 5.027e-08 | 6.4513e-07 | 5.0778e-08 | 6.5164e-07
120 | feeder2_line118 | 1 | 354.6 | 96.6874 | 96.6883 | 27.2666 | 27.2669
120 | feeder2_line118 | 2 | 354.6 | 97.3427 | 97.3371 | 27.4514 | 27.4498
120 | feeder2_line118 | 3 | 354.6 | 97.103 | 97.1072 | 27.3838 | 27.385
120 | feeder2_line119 | 1 | 99 | 2.5196e-08 | 6.0606e-07 | 2.5451e-08 | 6.1218e-07
120 | feeder2_line119 | 2 | 99 | 2.4836e-08 | 6.088e-07 | 2.5087e-08 | 6.1495e-07
120 | feeder2_line119 | 3 | 99 | 1.728 | 1.728 | 1.7455 | 1.7455
120 | feeder2_line120 | 1 | 354.6 | 0.19485 | 0.19462 | 0.05495 | 0.054883
120 | feeder2_line120 | 2 | 354.6 | 1.2811 | 1.281 | 0.36129 | 0.36126
120 | feeder2_line120 | 3 | 354.6 | 5.9968 | 5.9967 | 1.6911 | 1.6911
120 | feeder2_line121 | 1 | 99 | 3.2528e-07 | 9.3849e-07 | 3.2857e-07 | 9.4797e-07
120 | feeder2_line121 | 2 | 99 | 0.043741 | 0.043739 | 0.044182 | 0.044181
120 | feeder2_line121 | 3 | 99 | 3.253e-07 | 9.3897e-07 | 3.2858e-07 | 9.4846e-07
120 | feeder2_line122 | 1 | 354.6 | 0.19484 | 0.19462 | 0.054946 | 0.054883
120 | feeder2_line122 | 2 | 354.6 | 1.2525 | 1.2524 | 0.35321 | 0.35319
120 | feeder2_line122 | 3 | 354.6 | 5.9968 | 5.9967 | 1.6911 | 1.6911
120 | feeder2_line123 | 1 | 99 | 5.7499e-07 | 9.725e-07 | 5.8079e-07 | 9.8232e-07
120 | feeder2_line123 | 2 | 99 | 5.7765e-07 | 9.7694e-07 | 5.8349e-07 | 9.8681e-07
120 | feeder2_line123 | 3 | 99 | 1.9813 | 1.9812 | 2.0013 | 2.0013
120 | feeder2_line124 | 1 | 354.6 | 0.19475 | 0.19462 | 0.054921 | 0.054883
120 | feeder2_line124 | 2 | 354.6 | 1.2525 | 1.2524 | 0.35323 | 0.35319
120 | feeder2_line124 | 3 | 354.6 | 4.0231 | 4.023 | 1.1345 | 1.1345
120 | feeder2_line125 | 1 | 99 | 5.7499e-07 | 9.0403e-07 | 5.808e-07 | 9.1316e-07
120 | feeder2_line125 | 2 | 99 | 5.7766e-07 | 9.0817e-07 | 5.835e-07 | 9.1735e-07
120 | feeder2_line125 | 3 | 99 | 0.155 | 0.15501 | 0.15656 | 0.15657
120 | feeder2_line126 | 1 | 354.6 | 0.19491 | 0.19462 | 0.054965 | 0.054883
120 | feeder2_line126 | 2 | 354.6 | 1.2527 | 1.2524 | 0.35326 | 0.35319
120 | feeder2_line126 | 3 | 354.6 | 3.9399 | 3.9396 | 1.1111 | 1.111
120 | feeder2_line127 | 1 | 99 | 5.7499e-07 | 1.0823e-06 | 5.808e-07 | 1.0932e-06
120 | feeder2_line127 | 2 | 99 | 5.7765e-07 | 1.0872e-06 | 5.8349e-07 | 1.0982e-06
120 | feeder2_line127 | 3 | 99 | 2.4876 | 2.4876 | 2.5127 | 2.5127
120 | feeder2_line128 | 1 | 354.6 | 0.19482 | 0.19462 | 0.054942 | 0.054883
120 | feeder2_line128 | 2 | 354.6 | 1.2526 | 1.2524 | 0.35326 | 0.35319
120 | feeder2_line128 | 3 | 354.6 | 1.4617 | 1.4614 | 0.4122 | 0.41213
120 | feeder2_line129 | 1 | 99 | 5.4979e-07 | 8.7756e-07 | 5.5535e-07 | 8.8643e-07
120 | feeder2_line129 | 2 | 99 | 1.2524 | 1.2524 | 1.265 | 1.2651
120 | feeder2_line129 | 3 | 99 | 5.5014e-07 | 8.7794e-07 | 5.557e-07 | 8.8681e-07
120 | feeder2_line130 | 1 | 354.6 | 0.19484 | 0.19462 | 0.054946 | 0.054883
120 | feeder2_line130 | 2 | 354.6 | 0.00030987 | 4.6646e-06 | 8.7386e-05 | 1.3154e-06
120 | feeder2_line130 | 3 | 354.6 | 1.4617 | 1.4614 | 0.41221 | 0.41213
120 | feeder2_line131 | 1 | 99 | 5.7499e-07 | 9.7264e-07 | 5.808e-07 | 9.8246e-07
120 | feeder2_line131 | 2 | 99 | 5.7766e-07 | 9.771e-07 | 5.8349e-07 | 9.8697e-07
120 | feeder2_line131 | 3 | 99 | 1.3191 | 1.3191 | 1.3324 | 1.3324
120 | feeder2_line132 | 1 | 354.6 | 0.19467 | 0.19462 | 0.0549 | 0.054883
120 | feeder2_line132 | 2 | 354.6 | 0.00012657 | 2.9326e-06 | 3.5694e-05 | 8.2701e-07
120 | feeder2_line132 | 3 | 354.6 | 0.21259 | 0.21252 | 0.059953 | 0.059932
120 | feeder2_line133 | 1 | 99 | 0.1946 | 0.19462 | 0.19657 | 0.19658
120 | feeder2_line133 | 2 | 99 | 3.0124e-07 | 9.8491e-07 | 3.0429e-07 | 9.9485e-07
120 | feeder2_line133 | 3 | 99 | 3.0017e-07 | 9.8082e-07 | 3.032e-07 | 9.9073e-07
120 | feeder2_line134 | 1 | 354.6 | 5.882e-12 | 1.7883e-06 | 1.6588e-12 | 5.043e-07
120 | feeder2_line134 | 2 | 354.6 | 1.5702e-11 | 1.7956e-06 | 4.4281e-12 | 5.0638e-07
120 | feeder2_line134 | 3 | 354.6 | 0.21252 | 0.21252 | 0.059931 | 0.059932
120 | feeder2_line135 | 1 | 99 | 0.32426 | 0.32429 | 0.32753 | 0.32756
120 | feeder2_line135 | 2 | 99 | 4.9846e-08 | 5.901e-07 | 5.035e-08 | 5.9606e-07
120 | feeder2_line135 | 3 | 99 | 5.0296e-08 | 5.8809e-07 | 5.0804e-08 | 5.9403e-07
120 | feeder2_line136 | 1 | 354.6 | 97.0038 | 97.0048 | 27.3558 | 27.3561
120 | feeder2_line136 | 2 | 354.6 | 97.3426 | 97.3371 | 27.4514 | 27.4498
120 | feeder2_line136 | 3 | 354.6 | 97.103 | 97.1072 | 27.3838 | 27.385
120 | feeder2_line137 | 1 | 99 | 1.9808 | 1.9807 | 2.0008 | 2.0007
120 | feeder2_line137 | 2 | 99 | 8.5661e-07 | 1.5895e-06 | 8.6526e-07 | 1.6056e-06
120 | feeder2_line137 | 3 | 99 | 8.5347e-07 | 1.5841e-06 | 8.621e-07 | 1.6001e-06
120 | feeder2_line138 | 1 | 354.6 | 97.8212 | 97.8221 | 27.5864 | 27.5866
120 | feeder2_line138 | 2 | 354.6 | 97.3427 | 97.3371 | 27.4514 | 27.4498
120 | feeder2_line138 | 3 | 354.6 | 97.1031 | 97.1072 | 27.3838 | 27.385
120 | feeder2_line139 | 1 | 99 | 5.0587e-08 | 4.9302e-07 | 5.1098e-08 | 4.98e-07
120 | feeder2_line139 | 2 | 99 | 4.9862e-08 | 4.9533e-07 | 5.0365e-08 | 5.0034e-07
120 | feeder2_line139 | 3 | 99 | 2.2669 | 2.2671 | 2.2898 | 2.29
120 | feeder2_line140 | 1 | 354.6 | 97.8213 | 97.8221 | 27.5864 | 27.5866
120 | feeder2_line140 | 2 | 354.6 | 97.3428 | 97.3371 | 27.4514 | 27.4498
120 | feeder2_line140 | 3 | 354.6 | 98.0839 | 98.0882 | 27.6604 | 27.6617
120 | feeder2_line141 | 1 | 99 | 2.53e-06 | 4.8775e-07 | 2.5556e-06 | 4.9267e-07
120 | feeder2_line141 | 2 | 99 | 0.18985 | 0.18984 | 0.19177 | 0.19176
120 | feeder2_line141 | 3 | 99 | 2.5357e-06 | 4.8835e-07 | 2.5613e-06 | 4.9329e-07
120 | feeder2_line142 | 1 | 354.6 | 97.8211 | 97.8221 | 27.5863 | 27.5866
120 | feeder2_line142 | 2 | 354.6 | 97.53 | 97.5245 | 27.5042 | 27.5027
120 | feeder2_line142 | 3 | 354.6 | 98.0837 | 98.0882 | 27.6604 | 27.6617
120 | feeder2_line143 | 1 | 99 | 8.5268e-07 | 1.7332e-06 | 8.6129e-07 | 1.7507e-06
120 | feeder2_line143 | 2 | 99 | 0.1154 | 0.11536 | 0.11657 | 0.11652
120 | feeder2_line143 | 3 | 99 | 8.5385e-07 | 1.7354e-06 | 8.6247e-07 | 1.7529e-06
120 | feeder2_line144 | 1 | 354.6 | 97.8209 | 97.8221 | 27.5863 | 27.5866
120 | feeder2_line144 | 2 | 354.6 | 97.645 | 97.6397 | 27.5367 | 27.5352
120 | feeder2_line144 | 3 | 354.6 | 98.0835 | 98.0882 | 27.6603 | 27.6617
120 | feeder2_line145 | 1 | 99 | 2.53e-08 | 4.8603e-07 | 2.5556e-08 | 4.9094e-07
120 | feeder2_line145 | 2 | 99 | 1.1635 | 1.1634 | 1.1752 | 1.1752
120 | feeder2_line145 | 3 | 99 | 2.5163e-08 | 4.8663e-07 | 2.5417e-08 | 4.9155e-07
120 | feeder2_line146 | 1 | 354.6 | 97.8208 | 97.8221 | 27.5862 | 27.5866
120 | feeder2_line146 | 2 | 354.6 | 98.2931 | 98.2878 | 27.7194 | 27.7179
120 | feeder2_line146 | 3 | 354.6 | 98.0834 | 98.0882 | 27.6603 | 27.6617
120 | feeder2_line147 | 1 | 99 | 1.1226 | 1.1226 | 1.134 | 1.134
120 | feeder2_line147 | 2 | 99 | 1.1595e-06 | 2.2524e-06 | 1.1712e-06 | 2.2752e-06
120 | feeder2_line147 | 3 | 99 | 1.1554e-06 | 2.2447e-06 | 1.1671e-06 | 2.2673e-06
120 | feeder2_line148 | 1 | 99 | 0.22049 | 0.22049 | 0.22272 | 0.22272
120 | feeder2_line148 | 2 | 99 | 6.0467e-07 | 1.5093e-06 | 6.1077e-07 | 1.5245e-06
120 | feeder2_line148 | 3 | 99 | 6.0288e-07 | 1.5041e-06 | 6.0897e-07 | 1.5193e-06
120 | feeder2_line149 | 1 | 354.6 | 98.5685 | 98.5696 | 27.7971 | 27.7974
120 | feeder2_line149 | 2 | 354.6 | 98.2932 | 98.2878 | 27.7195 | 27.7179
120 | feeder2_line149 | 3 | 354.6 | 98.0836 | 98.0882 | 27.6603 | 27.6617
120 | feeder2_line150 | 1 | 354.6 | 98.5686 | 98.5696 | 27.7971 | 27.7974
120 | feeder2_line150 | 2 | 354.6 | 98.4776 | 98.4721 | 27.7715 | 27.7699
120 | feeder2_line150 | 3 | 354.6 | 98.0837 | 98.0882 | 27.6604 | 27.6617
120 | feeder2_line151 | 1 | 99 | 9.7772e-06 | 1.7846e-06 | 9.876e-06 | 1.8026e-06
120 | feeder2_line151 | 2 | 99 | 0.18469 | 0.18469 | 0.18656 | 0.18656
120 | feeder2_line151 | 3 | 99 | 9.797e-06 | 1.7868e-06 | 9.896e-06 | 1.8049e-06
120 | feeder2_line152 | 1 | 354.6 | 9.317e-12 | 1.1898e-06 | 2.6275e-12 | 3.3553e-07
120 | feeder2_line152 | 2 | 354.6 | 1.9593e-11 | 1.1948e-06 | 5.5255e-12 | 3.3695e-07
120 | feeder2_line152 | 3 | 354.6 | 1.1877 | 1.1877 | 0.33494 | 0.33493
120 | feeder2_line153 | 1 | 99 | 0.043887 | 0.043887 | 0.04433 | 0.04433
120 | feeder2_line153 | 2 | 99 | 4.9921e-08 | 5.9795e-07 | 5.0425e-08 | 6.0399e-07
120 | feeder2_line153 | 3 | 99 | 5.0371e-08 | 5.9588e-07 | 5.088e-08 | 6.019e-07
120 | feeder2_line154 | 1 | 99 | 5.7747e-07 | 8.8559e-07 | 5.833e-07 | 8.9454e-07
120 | feeder2_line154 | 2 | 99 | 5.8023e-07 | 8.8977e-07 | 5.8609e-07 | 8.9875e-07
120 | feeder2_line154 | 3 | 99 | 0.88442 | 0.88444 | 0.89335 | 0.89337
120 | feeder2_line155 | 1 | 99 | 98.6118 | 98.6128 | 99.6079 | 99.6089
120 | feeder2_line155 | 2 | 99 | 98.4775 | 98.4721 | 99.4722 | 99.4668
120 | feeder2_line155 | 3 | 99 | 99 | 99.0047 | 100 | 100.0047
120 | feeder2_line156 | 1 | 99 | 6.0256e-07 | 1.1653e-06 | 6.0865e-07 | 1.1771e-06
120 | feeder2_line156 | 2 | 99 | 0.095932 | 0.095928 | 0.096901 | 0.096897
120 | feeder2_line156 | 3 | 99 | 6.0315e-07 | 1.1668e-06 | 6.0925e-07 | 1.1786e-06
120 | feeder2_line157 | 1 | 99 | 2.5327e-08 | 2.5299e-07 | 2.5583e-08 | 2.5555e-07
120 | feeder2_line157 | 2 | 99 | 0.088925 | 0.088921 | 0.089823 | 0.089819
120 | feeder2_line157 | 3 | 99 | 2.5175e-08 | 2.533e-07 | 2.543e-08 | 2.5586e-07
150 | feeder2_line1 | 1 | 354.6 | 80.3731 | 80.3773 | 22.6658 | 22.667
150 | feeder2_line1 | 2 | 354.6 | 90.0831 | 90.0692 | 25.4042 | 25.4002
150 | feeder2_line1 | 3 | 354.6 | 88.9633 | 88.9791 | 25.0884 | 25.0928
150 | feeder2_line2 | 1 | 354.6 | 81.2041 | 81.2081 | 22.9002 | 22.9013
150 | feeder2_line2 | 2 | 354.6 | 90.0833 | 90.0692 | 25.4042 | 25.4002
150 | feeder2_line2 | 3 | 354.6 | 88.9635 | 88.9791 | 25.0884 | 25.0928
150 | feeder2_line3 | 1 | 80.1 | 1.432 | 1.432 | 1.7878 | 1.7878
150 | feeder2_line3 | 2 | 80.1 | 5.7252e-07 | 1.058e-06 | 7.1475e-07 | 1.3208e-06
150 | feeder2_line3 | 3 | 80.1 | 5.7242e-07 | 1.0578e-06 | 7.1464e-07 | 1.3206e-06
150 | feeder2_line4 | 1 | 354.6 | 81.2042 | 81.2081 | 22.9002 | 22.9013
150 | feeder2_line4 | 2 | 354.6 | 90.3595 | 90.3452 | 25.4821 | 25.4781
150 | feeder2_line4 | 3 | 354.6 | 88.9636 | 88.9791 | 25.0884 | 25.0928
150 | feeder2_line5 | 1 | 80.1 | 5.7211e-07 | 9.9829e-07 | 7.1425e-07 | 1.2463e-06
150 | feeder2_line5 | 2 | 80.1 | 0.27933 | 0.27933 | 0.34873 | 0.34872
150 | feeder2_line5 | 3 | 80.1 | 5.7248e-07 | 9.9892e-07 | 7.147e-07 | 1.2471e-06
150 | feeder2_line6 | 1 | 80.1 | 5.7218e-07 | 1.1745e-06 | 7.1433e-07 | 1.4663e-06
150 | feeder2_line6 | 2 | 80.1 | 5.7265e-07 | 1.1755e-06 | 7.1492e-07 | 1.4675e-06
150 | feeder2_line6 | 3 | 80.1 | 0.0853 | 0.085315 | 0.10649 | 0.10651
150 | feeder2_line7 | 1 | 354.6 | 81.2044 | 81.2081 | 22.9003 | 22.9013
150 | feeder2_line7 | 2 | 354.6 | 90.3596 | 90.3452 | 25.4821 | 25.4781
150 | feeder2_line7 | 3 | 354.6 | 89.0484 | 89.0638 | 25.1124 | 25.1167
150 | feeder2_line8 | 1 | 80.1 | 0.07263 | 0.07263 | 0.090674 | 0.090674
150 | feeder2_line8 | 2 | 80.1 | 5.729e-07 | 1.1339e-06 | 7.1523e-07 | 1.4156e-06
150 | feeder2_line8 | 3 | 80.1 | 5.7278e-07 | 1.1337e-06 | 7.1508e-07 | 1.4153e-06
150 | feeder2_line9 | 1 | 354.6 | 81.2767 | 81.2804 | 22.9207 | 22.9217
150 | feeder2_line9 | 2 | 354.6 | 90.3596 | 90.3452 | 25.4821 | 25.4781
150 | feeder2_line9 | 3 | 354.6 | 89.0485 | 89.0638 | 25.1124 | 25.1167
150 | feeder2_line10 | 1 | 80.1 | 8.461e-07 | 1.4959e-06 | 1.0563e-06 | 1.8675e-06
150 | feeder2_line10 | 2 | 80.1 | 0.072512 | 0.07251 | 0.090527 | 0.090524
150 | feeder2_line10 | 3 | 80.1 | 8.4676e-07 | 1.497e-06 | 1.0571e-06 | 1.8689e-06
150 | feeder2_line11 | 1 | 354.6 | 81.2767 | 81.2804 | 22.9207 | 22.9217
150 | feeder2_line11 | 2 | 354.6 | 90.4318 | 90.4174 | 25.5025 | 25.4984
150 | feeder2_line11 | 3 | 354.6 | 89.0485 | 89.0638 | 25.1124 | 25.1167
150 | feeder2_line12 | 1 | 80.1 | 5.4752e-07 | 9.9236e-07 | 6.8354e-07 | 1.2389e-06
150 | feeder2_line12 | 2 | 80.1 | 5.4817e-07 | 9.9334e-07 | 6.8436e-07 | 1.2401e-06
150 | feeder2_line12 | 3 | 80.1 | 0.81862 | 0.81864 | 1.022 | 1.022
150 | feeder2_line13 | 1 | 354.6 | 81.2767 | 81.2804 | 22.9207 | 22.9217
150 | feeder2_line13 | 2 | 354.6 | 90.4318 | 90.4174 | 25.5025 | 25.4984
150 | feeder2_line13 | 3 | 354.6 | 89.4275 | 89.4429 | 25.2193 | 25.2236
150 | feeder2_line14 | 1 | 80.1 | 0.27527 | 0.27527 | 0.34365 | 0.34365
150 | feeder2_line14 | 2 | 80.1 | 2.9899e-07 | 6.4784e-07 | 3.7328e-07 | 8.0879e-07
150 | feeder2_line14 | 3 | 80.1 | 2.9895e-07 | 6.4769e-07 | 3.7322e-07 | 8.086e-07
150 | feeder2_line15 | 1 | 354.6 | 81.5484 | 81.5521 | 22.9973 | 22.9983
150 | feeder2_line15 | 2 | 354.6 | 90.4318 | 90.4174 | 25.5025 | 25.4984
150 | feeder2_line15 | 3 | 354.6 | 89.4275 | 89.4429 | 25.2193 | 25.2236
150 | feeder2_line16 | 1 | 80.1 | 5.7262e-07 | 1.0316e-06 | 7.1488e-07 | 1.2879e-06
150 | feeder2_line16 | 2 | 80.1 | 0.25459 | 0.25458 | 0.31784 | 0.31783
150 | feeder2_line16 | 3 | 80.1 | 5.7311e-07 | 1.0325e-06 | 7.1549e-07 | 1.289e-06
150 | feeder2_line17 | 1 | 354.6 | 81.5484 | 81.5521 | 22.9973 | 22.9983
150 | feeder2_line17 | 2 | 354.6 | 90.6827 | 90.6683 | 25.5732 | 25.5692
150 | feeder2_line17 | 3 | 354.6 | 89.4275 | 89.4429 | 25.2193 | 25.2236
150 | feeder2_line18 | 1 | 80.1 | 5.4809e-07 | 7.3903e-07 | 6.8425e-07 | 9.2263e-07
150 | feeder2_line18 | 2 | 80.1 | 5.49e-07 | 7.4005e-07 | 6.8539e-07 | 9.2391e-07
150 | feeder2_line18 | 3 | 80.1 | 0.49186 | 0.49188 | 0.61405 | 0.61408
150 | feeder2_line19 | 1 | 354.6 | 81.5485 | 81.5521 | 22.9973 | 22.9983
150 | feeder2_line19 | 2 | 354.6 | 90.6827 | 90.6683 | 25.5732 | 25.5692
150 | feeder2_line19 | 3 | 354.6 | 89.9108 | 89.9261 | 25.3555 | 25.3599
150 | feeder2_line20 | 1 | 99 | 5.4825e-07 | 8.8631e-07 | 5.5379e-07 | 8.9527e-07
150 | feeder2_line20 | 2 | 99 | 5.4922e-07 | 8.8763e-07 | 5.5477e-07 | 8.966e-07
150 | feeder2_line20 | 3 | 99 | 0.35671 | 0.35673 | 0.36031 | 0.36034
150 | feeder2_line21 | 1 | 354.6 | 81.5486 | 81.5521 | 22.9973 | 22.9983
150 | feeder2_line21 | 2 | 354.6 | 90.6828 | 90.6683 | 25.5733 | 25.5692
150 | feeder2_line21 | 3 | 354.6 | 90.2626 | 90.2778 | 25.4548 | 25.4591
150 | feeder2_line22 | 1 | 99 | 5.7335e-07 | 1.0162e-06 | 5.7914e-07 | 1.0265e-06
150 | feeder2_line22 | 2 | 99 | 0.093677 | 0.093674 | 0.094624 | 0.09462
150 | feeder2_line22 | 3 | 99 | 5.7403e-07 | 1.0174e-06 | 5.7983e-07 | 1.0277e-06
150 | feeder2_line23 | 1 | 99 | 5.7335e-07 | 9.5129e-07 | 5.7914e-07 | 9.609e-07
150 | feeder2_line23 | 2 | 99 | 5.7424e-07 | 9.5275e-07 | 5.8004e-07 | 9.6237e-07
150 | feeder2_line23 | 3 | 99 | 2.1992 | 2.1992 | 2.2214 | 2.2214
150 | feeder2_line24 | 1 | 354.6 | 81.5486 | 81.5521 | 22.9974 | 22.9983
150 | feeder2_line24 | 2 | 354.6 | 90.776 | 90.7614 | 25.5995 | 25.5954
150 | feeder2_line24 | 3 | 354.6 | 91.2907 | 91.306 | 25.7447 | 25.749
150 | feeder2_line25 | 1 | 99 | 0.093847 | 0.093848 | 0.094795 | 0.094796
150 | feeder2_line25 | 2 | 99 | 4.9788e-08 | 6.9296e-07 | 5.0291e-08 | 6.9996e-07
150 | feeder2_line25 | 3 | 99 | 4.9935e-08 | 6.9272e-07 | 5.044e-08 | 6.9971e-07
150 | feeder2_line26 | 1 | 99 | 0.2205 | 0.2205 | 0.22272 | 0.22272
150 | feeder2_line26 | 2 | 99 | 5.4959e-07 | 8.5853e-07 | 5.5515e-07 | 8.6721e-07
150 | feeder2_line26 | 3 | 99 | 5.4931e-07 | 8.5823e-07 | 5.5486e-07 | 8.669e-07
150 | feeder2_line27 | 1 | 354.6 | 81.8599 | 81.8634 | 23.0851 | 23.0861
150 | feeder2_line27 | 2 | 354.6 | 90.776 | 90.7614 | 25.5996 | 25.5954
150 | feeder2_line27 | 3 | 354.6 | 91.2908 | 91.306 | 25.7447 | 25.749
150 | feeder2_line28 | 1 | 99 | 2.5436e-06 | 7.1187e-07 | 2.5693e-06 | 7.1906e-07
150 | feeder2_line28 | 2 | 99 | 0.76434 | 0.76432 | 0.77206 | 0.77205
150 | feeder2_line28 | 3 | 99 | 2.5486e-06 | 7.1291e-07 | 2.5744e-06 | 7.2011e-07
150 | feeder2_line29 | 1 | 354.6 | 81.8599 | 81.8634 | 23.0851 | 23.0861
150 | feeder2_line29 | 2 | 354.6 | 91.1875 | 91.1729 | 25.7156 | 25.7115
150 | feeder2_line29 | 3 | 354.6 | 91.2908 | 91.306 | 25.7447 | 25.749
150 | feeder2_line30 | 1 | 266.4 | 12.6918 | 12.6915 | 4.7642 | 4.7641
150 | feeder2_line30 | 2 | 266.4 | 1.3629 | 1.3631 | 0.51161 | 0.51166
150 | feeder2_line30 | 3 | 266.4 | 1.8244 | 1.8246 | 0.68484 | 0.68491
150 | feeder2_line31 | 1 | 354.6 | 94.0092 | 94.0122 | 26.5113 | 26.5122
150 | feeder2_line31 | 2 | 354.6 | 92.0244 | 92.0094 | 25.9516 | 25.9474
150 | feeder2_line31 | 3 | 354.6 | 92.4683 | 92.4832 | 26.0768 | 26.081
150 | feeder2_line32 | 1 | 354.6 | 94.0093 | 94.0122 | 26.5114 | 26.5122
150 | feeder2_line32 | 2 | 354.6 | 92.28 | 92.265 | 26.0237 | 26.0194
150 | feeder2_line32 | 3 | 354.6 | 92.4683 | 92.4832 | 26.0768 | 26.081
150 | feeder2_line33 | 1 | 99 | 5.0172e-08 | 6.8765e-07 | 5.0679e-08 | 6.9459e-07
150 | feeder2_line33 | 2 | 99 | 0.25778 | 0.25777 | 0.26038 | 0.26037
150 | feeder2_line33 | 3 | 99 | 5.0032e-08 | 6.888e-07 | 5.0538e-08 | 6.9575e-07
150 | feeder2_line34 | 1 | 354.6 | 94.0092 | 94.0122 | 26.5114 | 26.5122
150 | feeder2_line34 | 2 | 354.6 | 92.28 | 92.265 | 26.0237 | 26.0194
150 | feeder2_line34 | 3 | 354.6 | 92.7412 | 92.7561 | 26.1538 | 26.158
150 | feeder2_line35 | 1 | 99 | 2.999e-07 | 7.6167e-07 | 3.0293e-07 | 7.6937e-07
150 | feeder2_line35 | 2 | 99 | 3.0041e-07 | 7.632e-07 | 3.0344e-07 | 7.7091e-07
150 | feeder2_line35 | 3 | 99 | 0.27543 | 0.27544 | 0.27821 | 0.27822
150 | feeder2_line36 | 1 | 354.6 | 94.0372 | 94.0403 | 26.5192 | 26.5201
150 | feeder2_line36 | 2 | 354.6 | 92.28 | 92.265 | 26.0237 | 26.0194
150 | feeder2_line36 | 3 | 354.6 | 92.7412 | 92.7561 | 26.1537 | 26.158
150 | feeder2_line37 | 1 | 99 | 0.028068 | 0.028158 | 0.028351 | 0.028442
150 | feeder2_line37 | 2 | 99 | 3.0049e-07 | 8.4467e-07 | 3.0352e-07 | 8.532e-07
150 | feeder2_line37 | 3 | 99 | 3.0042e-07 | 8.4438e-07 | 3.0346e-07 | 8.5291e-07
150 | feeder2_line38 | 1 | 99 | 3.2473e-07 | 7.7707e-07 | 3.2801e-07 | 7.8491e-07
150 | feeder2_line38 | 2 | 99 | 0.21253 | 0.21252 | 0.21467 | 0.21467
150 | feeder2_line38 | 3 | 99 | 3.2513e-07 | 7.7846e-07 | 3.2842e-07 | 7.8633e-07
150 | feeder2_line39 | 1 | 266.4 | 12.6918 | 12.6915 | 4.7642 | 4.7641
150 | feeder2_line39 | 2 | 266.4 | 1.221 | 1.2212 | 0.45834 | 0.45842
150 | feeder2_line39 | 3 | 266.4 | 1.8244 | 1.8246 | 0.68485 | 0.68491
150 | feeder2_line40 | 1 | 354.6 | 94.1307 | 94.1338 | 26.5456 | 26.5465
150 | feeder2_line40 | 2 | 354.6 | 92.28 | 92.265 | 26.0237 | 26.0194
150 | feeder2_line40 | 3 | 354.6 | 92.7412 | 92.7561 | 26.1538 | 26.158
150 | feeder2_line41 | 1 | 99 | 0.093666 | 0.093668 | 0.094612 | 0.094614
150 | feeder2_line41 | 2 | 99 | 4.9903e-08 | 7.3818e-07 | 5.0407e-08 | 7.4564e-07
150 | feeder2_line41 | 3 | 99 | 5.0068e-08 | 7.3794e-07 | 5.0573e-08 | 7.4539e-07
150 | feeder2_line42 | 1 | 99 | 2.9961e-07 | 7.4994e-07 | 3.0263e-07 | 7.5752e-07
150 | feeder2_line42 | 2 | 99 | 3.0019e-07 | 7.5166e-07 | 3.0322e-07 | 7.5925e-07
150 | feeder2_line42 | 3 | 99 | 0.1899 | 0.1899 | 0.19182 | 0.19182
150 | feeder2_line43 | 1 | 266.4 | 12.6918 | 12.6915 | 4.7642 | 4.7641
150 | feeder2_line43 | 2 | 266.4 | 1.2211 | 1.2212 | 0.45838 | 0.45842
150 | feeder2_line43 | 3 | 266.4 | 1.6902 | 1.6904 | 0.63447 | 0.63452
150 | feeder2_line44 | 1 | 354.6 | 94.1307 | 94.1338 | 26.5456 | 26.5465
150 | feeder2_line44 | 2 | 354.6 | 92.2801 | 92.265 | 26.0237 | 26.0194
150 | feeder2_line44 | 3 | 354.6 | 93.0954 | 93.1103 | 26.2536 | 26.2578
150 | feeder2_line45 | 1 | 99 | 5.021e-08 | 5.811e-07 | 5.0717e-08 | 5.8697e-07
150 | feeder2_line45 | 2 | 99 | 4.9909e-08 | 5.8225e-07 | 5.0413e-08 | 5.8813e-07
150 | feeder2_line45 | 3 | 99 | 0.35701 | 0.35705 | 0.36062 | 0.36066
150 | feeder2_line46 | 1 | 99 | 5.7413e-07 | 1.3595e-06 | 5.7993e-07 | 1.3732e-06
150 | feeder2_line46 | 2 | 99 | 5.7547e-07 | 1.3626e-06 | 5.8129e-07 | 1.3764e-06
150 | feeder2_line46 | 3 | 99 | 0.16252 | 0.16255 | 0.16416 | 0.16419
150 | feeder2_line47 | 1 | 266.4 | 12.6918 | 12.6915 | 4.7642 | 4.7641
150 | feeder2_line47 | 2 | 266.4 | 1.2213 | 1.2212 | 0.45844 | 0.45842
150 | feeder2_line47 | 3 | 266.4 | 1.5834 | 1.5833 | 0.59436 | 0.59434
150 | feeder2_line48 | 1 | 99 | 1.1996 | 1.1996 | 1.2117 | 1.2117
150 | feeder2_line48 | 2 | 99 | 4.9823e-08 | 7.3367e-07 | 5.0326e-08 | 7.4108e-07
150 | feeder2_line48 | 3 | 99 | 4.9993e-08 | 7.3342e-07 | 5.0498e-08 | 7.4082e-07
150 | feeder2_line49 | 1 | 266.4 | 11.8139 | 11.8137 | 4.4347 | 4.4346
150 | feeder2_line49 | 2 | 266.4 | 1.2213 | 1.2212 | 0.45844 | 0.45842
150 | feeder2_line49 | 3 | 266.4 | 1.5834 | 1.5833 | 0.59435 | 0.59434
150 | feeder2_line50 | 1 | 99 | 5.7407e-07 | 1.2371e-06 | 5.7987e-07 | 1.2496e-06
150 | feeder2_line50 | 2 | 99 | 0.084854 | 0.084791 | 0.085711 | 0.085648
150 | feeder2_line50 | 3 | 99 | 5.7527e-07 | 1.2397e-06 | 5.8108e-07 | 1.2522e-06
150 | feeder2_line51 | 1 | 99 | 10.556 | 10.556 | 10.6626 | 10.6626
150 | feeder2_line51 | 2 | 99 | 5.7545e-07 | 1.3462e-06 | 5.8126e-07 | 1.3598e-06
150 | feeder2_line51 | 3 | 99 | 5.7525e-07 | 1.3458e-06 | 5.8106e-07 | 1.3594e-06
150 | feeder2_line52 | 1 | 266.4 | 1.4767 | 1.4767 | 0.55433 | 0.55433
150 | feeder2_line52 | 2 | 266.4 | 1.1738 | 1.1739 | 0.44063 | 0.44067
150 | feeder2_line52 | 3 | 266.4 | 1.5833 | 1.5833 | 0.59433 | 0.59434
150 | feeder2_line53 | 1 | 99 | 5.4898e-07 | 7.5502e-07 | 5.5452e-07 | 7.6265e-07
150 | feeder2_line53 | 2 | 99 | 1.1739 | 1.1739 | 1.1858 | 1.1858
150 | feeder2_line53 | 3 | 99 | 5.5027e-07 | 7.566e-07 | 5.5583e-07 | 7.6424e-07
150 | feeder2_line54 | 1 | 266.4 | 1.4767 | 1.4767 | 0.55431 | 0.55433
150 | feeder2_line54 | 2 | 266.4 | 8.5825e-05 | 4.6427e-06 | 3.2217e-05 | 1.7428e-06
150 | feeder2_line54 | 3 | 266.4 | 1.5833 | 1.5833 | 0.59432 | 0.59434
150 | feeder2_line55 | 1 | 99 | 0.1811 | 0.18111 | 0.18293 | 0.18294
150 | feeder2_line55 | 2 | 99 | 4.9949e-08 | 7.3402e-07 | 5.0454e-08 | 7.4143e-07
150 | feeder2_line55 | 3 | 99 | 5.0113e-08 | 7.3377e-07 | 5.0619e-08 | 7.4118e-07
150 | feeder2_line56 | 1 | 354.6 | 94.3105 | 94.3135 | 26.5963 | 26.5972
150 | feeder2_line56 | 2 | 354.6 | 92.2801 | 92.265 | 26.0237 | 26.0194
150 | feeder2_line56 | 3 | 354.6 | 93.0955 | 93.1103 | 26.2537 | 26.2578
150 | feeder2_line57 | 1 | 99 | 7.526e-07 | 1.5466e-06 | 7.602e-07 | 1.5622e-06
150 | feeder2_line57 | 2 | 99 | 7.4724e-07 | 1.5503e-06 | 7.5479e-07 | 1.5659e-06
150 | feeder2_line57 | 3 | 99 | 1.5834 | 1.5833 | 1.5993 | 1.5993
150 | feeder2_line58 | 1 | 266.4 | 1.4767 | 1.4767 | 0.55433 | 0.55433
150 | feeder2_line58 | 2 | 266.4 | 1.9022e-05 | 2.6954e-06 | 7.1403e-06 | 1.0118e-06
150 | feeder2_line58 | 3 | 266.4 | 1.902e-05 | 2.6947e-06 | 7.1395e-06 | 1.0115e-06
150 | feeder2_line59 | 1 | 99 | 5.0169e-08 | 5.3759e-07 | 5.0676e-08 | 5.4302e-07
150 | feeder2_line59 | 2 | 99 | 4.9814e-08 | 5.3889e-07 | 5.0318e-08 | 5.4433e-07
150 | feeder2_line59 | 3 | 99 | 0.76455 | 0.76452 | 0.77228 | 0.77224
150 | feeder2_line60 | 1 | 99 | 2.9958e-07 | 8.1246e-07 | 3.026e-07 | 8.2067e-07
150 | feeder2_line60 | 2 | 99 | 3.0019e-07 | 8.1443e-07 | 3.0322e-07 | 8.2265e-07
150 | feeder2_line60 | 3 | 99 | 0.81967 | 0.81969 | 0.82795 | 0.82797
150 | feeder2_line61 | 1 | 266.4 | 0.19842 | 0.19859 | 0.074482 | 0.074548
150 | feeder2_line61 | 2 | 266.4 | 2.6214 | 2.6216 | 0.98402 | 0.98408
150 | feeder2_line61 | 3 | 266.4 | 1.0449 | 1.0451 | 0.39221 | 0.39231
150 | feeder2_line62 | 1 | 354.6 | 94.5079 | 94.5111 | 26.652 | 26.6529
150 | feeder2_line62 | 2 | 354.6 | 93.9083 | 93.8933 | 26.4829 | 26.4787
150 | feeder2_line62 | 3 | 354.6 | 93.8321 | 93.8473 | 26.4614 | 26.4657
150 | feeder2_line63 | 1 | 99 | 0.35996 | 0.35996 | 0.3636 | 0.3636
150 | feeder2_line63 | 2 | 99 | 5.7548e-07 | 1.2245e-06 | 5.8129e-07 | 1.2369e-06
150 | feeder2_line63 | 3 | 99 | 5.7527e-07 | 1.2241e-06 | 5.8108e-07 | 1.2364e-06
150 | feeder2_line64 | 1 | 99 | 1.1972 | 1.1972 | 1.2093 | 1.2093
150 | feeder2_line64 | 2 | 99 | 5.897e-12 | 3.2255e-07 | 5.9565e-12 | 3.2581e-07
150 | feeder2_line64 | 3 | 99 | 7.4991e-12 | 3.2245e-07 | 7.5749e-12 | 3.257e-07
150 | feeder2_line65 | 1 | 99 | 5.0296e-08 | 6.4417e-07 | 5.0804e-08 | 6.5067e-07
150 | feeder2_line65 | 2 | 99 | 0.27961 | 0.2796 | 0.28244 | 0.28242
150 | feeder2_line65 | 3 | 99 | 5.0171e-08 | 6.4516e-07 | 5.0678e-08 | 6.5167e-07
150 | feeder2_line66 | 1 | 354.6 | 94.5078 | 94.5111 | 26.652 | 26.6529
150 | feeder2_line66 | 2 | 354.6 | 94.1863 | 94.1714 | 26.5613 | 26.5571
150 | feeder2_line66 | 3 | 354.6 | 93.8321 | 93.8473 | 26.4614 | 26.4657
150 | feeder2_line67 | 1 | 99 | 2.5131e-08 | 3.6398e-07 | 2.5385e-08 | 3.6765e-07
150 | feeder2_line67 | 2 | 99 | 2.4982e-08 | 3.6465e-07 | 2.5234e-08 | 3.6833e-07
150 | feeder2_line67 | 3 | 99 | 0.093389 | 0.093398 | 0.094333 | 0.094341
150 | feeder2_line68 | 1 | 266.4 | 0.19846 | 0.19859 | 0.074497 | 0.074548
150 | feeder2_line68 | 2 | 266.4 | 2.6215 | 2.6216 | 0.98404 | 0.98408
150 | feeder2_line68 | 3 | 266.4 | 0.97639 | 0.97658 | 0.36651 | 0.36658
150 | feeder2_line69 | 1 | 99 | 0.21382 | 0.2139 | 0.21598 | 0.21606
150 | feeder2_line69 | 2 | 99 | 2.5618e-06 | 6.7013e-07 | 2.5877e-06 | 6.769e-07
150 | feeder2_line69 | 3 | 99 | 2.5596e-06 | 6.6991e-07 | 2.5855e-06 | 6.7667e-07
150 | feeder2_line70 | 1 | 354.6 | 94.7204 | 94.7238 | 26.7119 | 26.7129
150 | feeder2_line70 | 2 | 354.6 | 94.1862 | 94.1714 | 26.5613 | 26.5571
150 | feeder2_line70 | 3 | 354.6 | 93.832 | 93.8473 | 26.4614 | 26.4657
150 | feeder2_line71 | 1 | 99 | 5.0317e-08 | 7.1894e-07 | 5.0825e-08 | 7.262e-07
150 | feeder2_line71 | 2 | 99 | 0.32463 | 0.32455 | 0.32791 | 0.32782
150 | feeder2_line71 | 3 | 99 | 5.0195e-08 | 7.2004e-07 | 5.0702e-08 | 7.2731e-07
150 | feeder2_line72 | 1 | 354.6 | 94.7205 | 94.7238 | 26.7119 | 26.7129
150 | feeder2_line72 | 2 | 354.6 | 94.5085 | 94.4935 | 26.6521 | 26.6479
150 | feeder2_line72 | 3 | 354.6 | 93.8321 | 93.8473 | 26.4614 | 26.4657
150 | feeder2_line73 | 1 | 99 | 6.0094e-07 | 1.5409e-06 | 6.0701e-07 | 1.5565e-06
150 | feeder2_line73 | 2 | 99 | 0.25784 | 0.25783 | 0.26044 | 0.26043
150 | feeder2_line73 | 3 | 99 | 6.0176e-07 | 1.5432e-06 | 6.0784e-07 | 1.5588e-06
150 | feeder2_line74 | 1 | 99 | 5.0261e-08 | 4.5959e-07 | 5.0769e-08 | 4.6423e-07
150 | feeder2_line74 | 2 | 99 | 0.97667 | 0.97666 | 0.98654 | 0.98652
150 | feeder2_line74 | 3 | 99 | 5.0144e-08 | 4.6028e-07 | 5.065e-08 | 4.6493e-07
150 | feeder2_line75 | 1 | 266.4 | 0.19856 | 0.19859 | 0.074534 | 0.074548
150 | feeder2_line75 | 2 | 266.4 | 1.4809 | 1.481 | 0.55591 | 0.55593
150 | feeder2_line75 | 3 | 266.4 | 0.97648 | 0.97658 | 0.36655 | 0.36659
150 | feeder2_line76 | 1 | 99 | 0.19859 | 0.19859 | 0.2006 | 0.2006
150 | feeder2_line76 | 2 | 99 | 8.5283e-07 | 1.5924e-06 | 8.6144e-07 | 1.6085e-06
150 | feeder2_line76 | 3 | 99 | 8.5249e-07 | 1.5919e-06 | 8.611e-07 | 1.608e-06
150 | feeder2_line77 | 1 | 99 | 2.5129e-08 | 5.7755e-07 | 2.5383e-08 | 5.8338e-07
150 | feeder2_line77 | 2 | 99 | 2.4986e-08 | 5.786e-07 | 2.5238e-08 | 5.8445e-07
150 | feeder2_line77 | 3 | 99 | 0.97652 | 0.97658 | 0.98639 | 0.98645
150 | feeder2_line78 | 1 | 266.4 | 5.2139e-12 | 9.5798e-07 | 1.9572e-12 | 3.596e-07
150 | feeder2_line78 | 2 | 266.4 | 1.481 | 1.481 | 0.55592 | 0.55593
150 | feeder2_line78 | 3 | 266.4 | 1.4759e-11 | 9.5928e-07 | 5.5402e-12 | 3.6009e-07
150 | feeder2_line79 | 1 | 354.6 | 0.64369 | 0.64337 | 0.18153 | 0.18143
150 | feeder2_line79 | 2 | 354.6 | 0.7666 | 0.76604 | 0.21619 | 0.21603
150 | feeder2_line79 | 3 | 354.6 | 3.413 | 3.4129 | 0.96249 | 0.96246
150 | feeder2_line80 | 1 | 354.6 | 95.3619 | 95.3648 | 26.8928 | 26.8936
150 | feeder2_line80 | 2 | 354.6 | 95.2734 | 95.2577 | 26.8678 | 26.8634
150 | feeder2_line80 | 3 | 354.6 | 96.6407 | 96.6555 | 27.2534 | 27.2576
150 | feeder2_line81 | 1 | 354.6 | 95.3618 | 95.3648 | 26.8928 | 26.8936
150 | feeder2_line81 | 2 | 354.6 | 95.2733 | 95.2577 | 26.8678 | 26.8634
150 | feeder2_line81 | 3 | 354.6 | 96.8901 | 96.905 | 27.3238 | 27.328
150 | feeder2_line82 | 1 | 354.6 | 9.1541e-12 | 7.3793e-07 | 2.5815e-12 | 2.081e-07
150 | feeder2_line82 | 2 | 354.6 | 1.5889e-11 | 7.3915e-07 | 4.4807e-12 | 2.0845e-07
150 | feeder2_line82 | 3 | 354.6 | 0.2506 | 0.25061 | 0.070671 | 0.070674
150 | feeder2_line83 | 1 | 354.6 | 95.362 | 95.3648 | 26.8928 | 26.8936
150 | feeder2_line83 | 2 | 354.6 | 95.8206 | 95.8047 | 27.0222 | 27.0177
150 | feeder2_line83 | 3 | 354.6 | 96.8903 | 96.905 | 27.3238 | 27.328
150 | feeder2_line84 | 1 | 354.6 | 9.9642e-12 | 1.3044e-06 | 2.81e-12 | 3.6784e-07
150 | feeder2_line84 | 2 | 354.6 | 0.98365 | 0.98357 | 0.2774 | 0.27738
150 | feeder2_line84 | 3 | 354.6 | 5.6344e-12 | 1.3063e-06 | 1.5889e-12 | 3.6838e-07
150 | feeder2_line85 | 1 | 99 | 0.21254 | 0.21254 | 0.21469 | 0.21469
150 | feeder2_line85 | 2 | 99 | 5.0092e-08 | 4.6641e-07 | 5.0598e-08 | 4.7112e-07
150 | feeder2_line85 | 3 | 99 | 5.0253e-08 | 4.6627e-07 | 5.076e-08 | 4.7098e-07
150 | feeder2_line86 | 1 | 354.6 | 95.5736 | 95.5763 | 26.9525 | 26.9533
150 | feeder2_line86 | 2 | 354.6 | 95.8207 | 95.8047 | 27.0222 | 27.0177
150 | feeder2_line86 | 3 | 354.6 | 96.8904 | 96.905 | 27.3239 | 27.328
150 | feeder2_line87 | 1 | 354.6 | 95.5738 | 95.5763 | 26.9526 | 26.9533
150 | feeder2_line87 | 2 | 354.6 | 96.4395 | 96.4231 | 27.1967 | 27.1921
150 | feeder2_line87 | 3 | 354.6 | 97.1521 | 97.1665 | 27.3977 | 27.4017
150 | feeder2_line88 | 1 | 354.6 | 0.00011428 | 3.3817e-06 | 3.2226e-05 | 9.5365e-07
150 | feeder2_line88 | 2 | 354.6 | 1.1328 | 1.1326 | 0.31947 | 0.31941
150 | feeder2_line88 | 3 | 354.6 | 0.26271 | 0.26265 | 0.074085 | 0.07407
150 | feeder2_line89 | 1 | 354.6 | 95.5715 | 95.5763 | 26.9519 | 26.9533
150 | feeder2_line89 | 2 | 354.6 | 97.1935 | 97.1793 | 27.4093 | 27.4053
150 | feeder2_line89 | 3 | 354.6 | 97.1498 | 97.1665 | 27.397 | 27.4017
150 | feeder2_line90 | 1 | 354.6 | 0.00072735 | 2.0409e-06 | 0.00020512 | 5.7555e-07
150 | feeder2_line90 | 2 | 354.6 | 1.1162 | 1.1161 | 0.31477 | 0.31474
150 | feeder2_line90 | 3 | 354.6 | 0.0007289 | 2.045e-06 | 0.00020555 | 5.767e-07
150 | feeder2_line91 | 1 | 354.6 | 95.5714 | 95.5763 | 26.9519 | 26.9533
150 | feeder2_line91 | 2 | 354.6 | 97.1934 | 97.1793 | 27.4093 | 27.4053
150 | feeder2_line91 | 3 | 354.6 | 97.5854 | 97.6022 | 27.5198 | 27.5246
150 | feeder2_line92 | 1 | 354.6 | 9.4552e-12 | 1.03e-06 | 2.6664e-12 | 2.9046e-07
150 | feeder2_line92 | 2 | 354.6 | 1.0539e-11 | 1.0317e-06 | 2.9721e-12 | 2.9096e-07
150 | feeder2_line92 | 3 | 354.6 | 0.82109 | 0.8211 | 0.23155 | 0.23156
150 | feeder2_line93 | 1 | 99 | 2.5211e-08 | 3.4378e-07 | 2.5465e-08 | 3.4725e-07
150 | feeder2_line93 | 2 | 99 | 0.98385 | 0.98377 | 0.99378 | 0.9937
150 | feeder2_line93 | 3 | 99 | 2.5144e-08 | 3.4432e-07 | 2.5398e-08 | 3.478e-07
150 | feeder2_line94 | 1 | 354.6 | 2.521e-06 | 1.6739e-06 | 7.1095e-07 | 4.7204e-07
150 | feeder2_line94 | 2 | 354.6 | 0.19459 | 0.19452 | 0.054877 | 0.054857
150 | feeder2_line94 | 3 | 354.6 | 2.5143e-06 | 1.6763e-06 | 7.0906e-07 | 4.7274e-07
150 | feeder2_line95 | 1 | 99 | 3.5835e-06 | 2.6222e-06 | 3.6197e-06 | 2.6487e-06
150 | feeder2_line95 | 2 | 99 | 1.1328 | 1.1326 | 1.1443 | 1.1441
150 | feeder2_line95 | 3 | 99 | 3.5919e-06 | 2.6263e-06 | 3.6281e-06 | 2.6528e-06
150 | feeder2_line96 | 1 | 354.6 | 0.00012168 | 6.2509e-07 | 3.4314e-05 | 1.7628e-07
150 | feeder2_line96 | 2 | 354.6 | 0.00012195 | 6.2635e-07 | 3.439e-05 | 1.7664e-07
150 | feeder2_line96 | 3 | 354.6 | 0.26269 | 0.26265 | 0.07408 | 0.07407
150 | feeder2_line97 | 1 | 354.6 | 96.3243 | 96.3289 | 27.1642 | 27.1655
150 | feeder2_line97 | 2 | 354.6 | 97.1936 | 97.1793 | 27.4094 | 27.4053
150 | feeder2_line97 | 3 | 354.6 | 97.5856 | 97.6022 | 27.5199 | 27.5246
150 | feeder2_line98 | 1 | 354.6 | 1.3575 | 1.3566 | 0.38282 | 0.38257
150 | feeder2_line98 | 2 | 354.6 | 0.0017175 | 6.2642e-07 | 0.00048435 | 1.7666e-07
150 | feeder2_line98 | 3 | 354.6 | 0.0017113 | 6.2505e-07 | 0.00048261 | 1.7627e-07
150 | feeder2_line99 | 1 | 99 | 2.5193e-08 | 4.4937e-07 | 2.5448e-08 | 4.5391e-07
150 | feeder2_line99 | 2 | 99 | 2.5047e-08 | 4.502e-07 | 2.53e-08 | 4.5475e-07
150 | feeder2_line99 | 3 | 99 | 0.2626 | 0.26265 | 0.26525 | 0.26531
150 | feeder2_line100 | 1 | 99 | 1.3566 | 1.3566 | 1.3703 | 1.3703
150 | feeder2_line100 | 2 | 99 | 2.5071e-08 | 6.184e-07 | 2.5324e-08 | 6.2465e-07
150 | feeder2_line100 | 3 | 99 | 2.515e-08 | 6.1822e-07 | 2.5404e-08 | 6.2447e-07
150 | feeder2_line101 | 1 | 354.6 | 0.19501 | 0.19465 | 0.054994 | 0.054892
150 | feeder2_line101 | 2 | 354.6 | 0.76659 | 0.76604 | 0.21618 | 0.21603
150 | feeder2_line101 | 3 | 354.6 | 3.413 | 3.4129 | 0.96249 | 0.96246
150 | feeder2_line102 | 1 | 99 | 0.44868 | 0.44873 | 0.45321 | 0.45326
150 | feeder2_line102 | 2 | 99 | 2.3528e-06 | 8.8373e-07 | 2.3766e-06 | 8.9266e-07
150 | feeder2_line102 | 3 | 99 | 2.3476e-06 | 8.8335e-07 | 2.3713e-06 | 8.9228e-07
150 | feeder2_line103 | 1 | 99 | 5.5159e-07 | 8.0735e-07 | 5.5716e-07 | 8.1551e-07
150 | feeder2_line103 | 2 | 99 | 0.096185 | 0.096177 | 0.097156 | 0.097148
150 | feeder2_line103 | 3 | 99 | 5.5249e-07 | 8.0853e-07 | 5.5807e-07 | 8.167e-07
150 | feeder2_line104 | 1 | 354.6 | 0.19491 | 0.19465 | 0.054965 | 0.054892
150 | feeder2_line104 | 2 | 354.6 | 0.67085 | 0.67041 | 0.18918 | 0.18906
150 | feeder2_line104 | 3 | 354.6 | 3.4129 | 3.4129 | 0.96247 | 0.96246
150 | feeder2_line105 | 1 | 99 | 2.5566e-06 | 7.4287e-07 | 2.5824e-06 | 7.5037e-07
150 | feeder2_line105 | 2 | 99 | 2.5641e-06 | 7.4428e-07 | 2.59e-06 | 7.518e-07
150 | feeder2_line105 | 3 | 99 | 0.49328 | 0.49333 | 0.49827 | 0.49832
150 | feeder2_line106 | 1 | 354.6 | 0.19485 | 0.19465 | 0.05495 | 0.054892
150 | feeder2_line106 | 2 | 354.6 | 0.67079 | 0.67041 | 0.18917 | 0.18906
150 | feeder2_line106 | 3 | 354.6 | 2.9842 | 2.9841 | 0.84156 | 0.84154
150 | feeder2_line107 | 1 | 99 | 3.2614e-07 | 9.053e-07 | 3.2944e-07 | 9.1444e-07
150 | feeder2_line107 | 2 | 99 | 0.11572 | 0.11562 | 0.11689 | 0.11679
150 | feeder2_line107 | 3 | 99 | 3.2647e-07 | 9.0657e-07 | 3.2976e-07 | 9.1573e-07
150 | feeder2_line108 | 1 | 354.6 | 0.19484 | 0.19465 | 0.054947 | 0.054892
150 | feeder2_line108 | 2 | 354.6 | 0.55581 | 0.55553 | 0.15674 | 0.15666
150 | feeder2_line108 | 3 | 354.6 | 2.9842 | 2.9841 | 0.84156 | 0.84154
150 | feeder2_line109 | 1 | 354.6 | 97.8314 | 97.8347 | 27.5892 | 27.5901
150 | feeder2_line109 | 2 | 354.6 | 97.1948 | 97.1793 | 27.4097 | 27.4053
150 | feeder2_line109 | 3 | 354.6 | 97.5868 | 97.6022 | 27.5202 | 27.5246
150 | feeder2_line110 | 1 | 99 | 2.7699 | 2.7694 | 2.7979 | 2.7974
150 | feeder2_line110 | 2 | 99 | 0.00081068 | 9.153e-07 | 0.00081887 | 9.2454e-07
150 | feeder2_line110 | 3 | 99 | 0.00080998 | 9.1518e-07 | 0.00081816 | 9.2442e-07
150 | feeder2_line111 | 1 | 99 | 2.5197e-08 | 3.838e-07 | 2.5452e-08 | 3.8768e-07
150 | feeder2_line111 | 2 | 99 | 0.072438 | 0.07237 | 0.07317 | 0.073101
150 | feeder2_line111 | 3 | 99 | 2.5134e-08 | 3.8439e-07 | 2.5388e-08 | 3.8828e-07
150 | feeder2_line112 | 1 | 99 | 3.2642e-07 | 9.2227e-07 | 3.2972e-07 | 9.3159e-07
150 | feeder2_line112 | 2 | 99 | 1.1 | 1.0999 | 1.1112 | 1.111
150 | feeder2_line112 | 3 | 99 | 3.2679e-07 | 9.2372e-07 | 3.3009e-07 | 9.3305e-07
150 | feeder2_line113 | 1 | 99 | 2.7174 | 2.7174 | 2.7448 | 2.7448
150 | feeder2_line113 | 2 | 99 | 3.2714e-07 | 9.121e-07 | 3.3045e-07 | 9.2132e-07
150 | feeder2_line113 | 3 | 99 | 3.2716e-07 | 9.1184e-07 | 3.3047e-07 | 9.2105e-07
150 | feeder2_line114 | 1 | 99 | 0.096355 | 0.096357 | 0.097328 | 0.09733
150 | feeder2_line114 | 2 | 99 | 2.5028e-08 | 4.3944e-07 | 2.5281e-08 | 4.4388e-07
150 | feeder2_line114 | 3 | 99 | 2.5114e-08 | 4.3926e-07 | 2.5368e-08 | 4.4369e-07
150 | feeder2_line115 | 1 | 99 | 2.5176e-08 | 5.6495e-07 | 2.543e-08 | 5.7066e-07
150 | feeder2_line115 | 2 | 99 | 0.33269 | 0.33268 | 0.33605 | 0.33604
150 | feeder2_line115 | 3 | 99 | 2.5116e-08 | 5.6573e-07 | 2.537e-08 | 5.7144e-07
150 | feeder2_line116 | 1 | 354.6 | 0.19485 | 0.19465 | 0.054949 | 0.054892
150 | feeder2_line116 | 2 | 354.6 | 0.22315 | 0.22289 | 0.062931 | 0.062856
150 | feeder2_line116 | 3 | 354.6 | 2.9842 | 2.9841 | 0.84156 | 0.84154
150 | feeder2_line117 | 1 | 99 | 5.0486e-08 | 6.4653e-07 | 5.0996e-08 | 6.5306e-07
150 | feeder2_line117 | 2 | 99 | 0.16235 | 0.16224 | 0.16399 | 0.16388
150 | feeder2_line117 | 3 | 99 | 5.0346e-08 | 6.4759e-07 | 5.0855e-08 | 6.5413e-07
150 | feeder2_line118 | 1 | 354.6 | 97.8314 | 97.8347 | 27.5892 | 27.5901
150 | feeder2_line118 | 2 | 354.6 | 97.3567 | 97.3411 | 27.4554 | 27.451
150 | feeder2_line118 | 3 | 354.6 | 97.5868 | 97.6022 | 27.5202 | 27.5246
150 | feeder2_line119 | 1 | 99 | 2.5173e-08 | 6.0791e-07 | 2.5427e-08 | 6.1405e-07
150 | feeder2_line119 | 2 | 99 | 2.5021e-08 | 6.0908e-07 | 2.5274e-08 | 6.1523e-07
150 | feeder2_line119 | 3 | 99 | 0.54651 | 0.54653 | 0.55203 | 0.55205
150 | feeder2_line120 | 1 | 354.6 | 0.19485 | 0.19465 | 0.054949 | 0.054892
150 | feeder2_line120 | 2 | 354.6 | 0.22316 | 0.22289 | 0.062932 | 0.062856
150 | feeder2_line120 | 3 | 354.6 | 2.5392 | 2.5391 | 0.71607 | 0.71604
150 | feeder2_line121 | 1 | 99 | 3.2614e-07 | 9.4137e-07 | 3.2943e-07 | 9.5087e-07
150 | feeder2_line121 | 2 | 99 | 0.043768 | 0.043763 | 0.04421 | 0.044205
150 | feeder2_line121 | 3 | 99 | 3.2644e-07 | 9.426e-07 | 3.2974e-07 | 9.5212e-07
150 | feeder2_line122 | 1 | 354.6 | 0.19484 | 0.19465 | 0.054945 | 0.054892
150 | feeder2_line122 | 2 | 354.6 | 0.17938 | 0.17913 | 0.050586 | 0.050515
150 | feeder2_line122 | 3 | 354.6 | 2.5392 | 2.5391 | 0.71606 | 0.71604
150 | feeder2_line123 | 1 | 99 | 5.7676e-07 | 9.7547e-07 | 5.8258e-07 | 9.8532e-07
150 | feeder2_line123 | 2 | 99 | 5.779e-07 | 9.7738e-07 | 5.8374e-07 | 9.8725e-07
150 | feeder2_line123 | 3 | 99 | 0.76488 | 0.76486 | 0.77261 | 0.77258
150 | feeder2_line124 | 1 | 354.6 | 0.19474 | 0.19465 | 0.05492 | 0.054892
150 | feeder2_line124 | 2 | 354.6 | 0.17929 | 0.17913 | 0.05056 | 0.050515
150 | feeder2_line124 | 3 | 354.6 | 1.7885 | 1.7885 | 0.50438 | 0.50436
150 | feeder2_line125 | 1 | 99 | 5.7676e-07 | 9.068e-07 | 5.8258e-07 | 9.1596e-07
150 | feeder2_line125 | 2 | 99 | 5.779e-07 | 9.0857e-07 | 5.8374e-07 | 9.1775e-07
150 | feeder2_line125 | 3 | 99 | 1.3567 | 1.3567 | 1.3704 | 1.3704
150 | feeder2_line126 | 1 | 354.6 | 0.1949 | 0.19465 | 0.054964 | 0.054892
150 | feeder2_line126 | 2 | 354.6 | 0.17944 | 0.17913 | 0.050605 | 0.050515
150 | feeder2_line126 | 3 | 354.6 | 0.58795 | 0.58767 | 0.16581 | 0.16573
150 | feeder2_line127 | 1 | 99 | 5.7676e-07 | 1.0856e-06 | 5.8258e-07 | 1.0966e-06
150 | feeder2_line127 | 2 | 99 | 5.779e-07 | 1.0877e-06 | 5.8374e-07 | 1.0987e-06
150 | feeder2_line127 | 3 | 99 | 0.21255 | 0.21256 | 0.21469 | 0.21471
150 | feeder2_line128 | 1 | 354.6 | 0.19482 | 0.19465 | 0.054941 | 0.054892
150 | feeder2_line128 | 2 | 354.6 | 0.17936 | 0.17913 | 0.050581 | 0.050515
150 | feeder2_line128 | 3 | 354.6 | 0.37533 | 0.37512 | 0.10585 | 0.10579
150 | feeder2_line129 | 1 | 99 | 5.5158e-07 | 8.8025e-07 | 5.5715e-07 | 8.8914e-07
150 | feeder2_line129 | 2 | 99 | 0.17914 | 0.17912 | 0.18095 | 0.18093
150 | feeder2_line129 | 3 | 99 | 5.5238e-07 | 8.8139e-07 | 5.5796e-07 | 8.9029e-07
150 | feeder2_line130 | 1 | 354.6 | 0.19484 | 0.19465 | 0.054945 | 0.054892
150 | feeder2_line130 | 2 | 354.6 | 0.00031019 | 4.6671e-06 | 8.7476e-05 | 1.3162e-06
150 | feeder2_line130 | 3 | 354.6 | 0.37535 | 0.37512 | 0.10585 | 0.10579
150 | feeder2_line131 | 1 | 99 | 5.7676e-07 | 9.7562e-07 | 5.8258e-07 | 9.8547e-07
150 | feeder2_line131 | 2 | 99 | 5.7791e-07 | 9.7753e-07 | 5.8375e-07 | 9.8741e-07
150 | feeder2_line131 | 3 | 99 | 0.1626 | 0.16261 | 0.16424 | 0.16425
150 | feeder2_line132 | 1 | 354.6 | 0.19467 | 0.19465 | 0.054899 | 0.054892
150 | feeder2_line132 | 2 | 354.6 | 0.00012653 | 2.9341e-06 | 3.5682e-05 | 8.2745e-07
150 | feeder2_line132 | 3 | 354.6 | 0.21262 | 0.21256 | 0.059961 | 0.059943
150 | feeder2_line133 | 1 | 99 | 0.1946 | 0.19465 | 0.19656 | 0.19661
150 | feeder2_line133 | 2 | 99 | 3.0146e-07 | 9.8534e-07 | 3.0451e-07 | 9.9529e-07
150 | feeder2_line133 | 3 | 99 | 3.0131e-07 | 9.8468e-07 | 3.0436e-07 | 9.9462e-07
150 | feeder2_line134 | 1 | 354.6 | 2.7736e-12 | 1.7936e-06 | 7.8219e-13 | 5.058e-07
150 | feeder2_line134 | 2 | 354.6 | 7.8235e-12 | 1.7967e-06 | 2.2063e-12 | 5.0669e-07
150 | feeder2_line134 | 3 | 354.6 | 0.21255 | 0.21256 | 0.05994 | 0.059943
150 | feeder2_line135 | 1 | 99 | 0.3247 | 0.32479 | 0.32798 | 0.32807
150 | feeder2_line135 | 2 | 99 | 5.0212e-08 | 5.9054e-07 | 5.0719e-08 | 5.965e-07
150 | feeder2_line135 | 3 | 99 | 5.0378e-08 | 5.9036e-07 | 5.0887e-08 | 5.9632e-07
150 | feeder2_line136 | 1 | 354.6 | 98.1549 | 98.1583 | 27.6805 | 27.6814
150 | feeder2_line136 | 2 | 354.6 | 97.3567 | 97.3411 | 27.4553 | 27.451
150 | feeder2_line136 | 3 | 354.6 | 97.5868 | 97.6022 | 27.5202 | 27.5246
150 | feeder2_line137 | 1 | 99 | 0.8334 | 0.83341 | 0.84182 | 0.84182
150 | feeder2_line137 | 2 | 99 | 8.5715e-07 | 1.5907e-06 | 8.6581e-07 | 1.6068e-06
150 | feeder2_line137 | 3 | 99 | 8.5683e-07 | 1.5902e-06 | 8.6548e-07 | 1.6063e-06
150 | feeder2_line138 | 1 | 354.6 | 98.6293 | 98.6326 | 27.8142 | 27.8152
150 | feeder2_line138 | 2 | 354.6 | 97.3567 | 97.3411 | 27.4554 | 27.451
150 | feeder2_line138 | 3 | 354.6 | 97.5868 | 97.6022 | 27.5203 | 27.5246
150 | feeder2_line139 | 1 | 99 | 5.054e-08 | 4.9477e-07 | 5.105e-08 | 4.9976e-07
150 | feeder2_line139 | 2 | 99 | 5.0232e-08 | 4.9571e-07 | 5.0739e-08 | 5.0071e-07
150 | feeder2_line139 | 3 | 99 | 0.97794 | 0.97873 | 0.98781 | 0.98862
150 | feeder2_line140 | 1 | 354.6 | 98.6294 | 98.6326 | 27.8143 | 27.8152
150 | feeder2_line140 | 2 | 354.6 | 97.3568 | 97.3411 | 27.4554 | 27.451
150 | feeder2_line140 | 3 | 354.6 | 98.1709 | 98.1871 | 27.685 | 27.6896
150 | feeder2_line141 | 1 | 99 | 2.5407e-06 | 4.8948e-07 | 2.5664e-06 | 4.9443e-07
150 | feeder2_line141 | 2 | 99 | 0.18985 | 0.18984 | 0.19177 | 0.19175
150 | feeder2_line141 | 3 | 99 | 2.5463e-06 | 4.9027e-07 | 2.5721e-06 | 4.9522e-07
150 | feeder2_line142 | 1 | 354.6 | 98.6292 | 98.6326 | 27.8142 | 27.8152
150 | feeder2_line142 | 2 | 354.6 | 97.5461 | 97.5305 | 27.5088 | 27.5044
150 | feeder2_line142 | 3 | 354.6 | 98.1707 | 98.1871 | 27.6849 | 27.6896
150 | feeder2_line143 | 1 | 99 | 8.558e-07 | 1.7394e-06 | 8.6444e-07 | 1.757e-06
150 | feeder2_line143 | 2 | 99 | 0.11542 | 0.11529 | 0.11659 | 0.11646
150 | feeder2_line143 | 3 | 99 | 8.5723e-07 | 1.7422e-06 | 8.6589e-07 | 1.7598e-06
150 | feeder2_line144 | 1 | 354.6 | 98.629 | 98.6326 | 27.8142 | 27.8152
150 | feeder2_line144 | 2 | 354.6 | 97.6612 | 97.6457 | 27.5412 | 27.5368
150 | feeder2_line144 | 3 | 354.6 | 98.1706 | 98.1871 | 27.6849 | 27.6896
150 | feeder2_line145 | 1 | 99 | 2.5277e-08 | 4.8777e-07 | 2.5533e-08 | 4.9269e-07
150 | feeder2_line145 | 2 | 99 | 0.25083 | 0.25081 | 0.25336 | 0.25335
150 | feeder2_line145 | 3 | 99 | 2.5207e-08 | 4.8855e-07 | 2.5462e-08 | 4.9348e-07
150 | feeder2_line146 | 1 | 354.6 | 98.6289 | 98.6326 | 27.8141 | 27.8152
150 | feeder2_line146 | 2 | 354.6 | 97.9111 | 97.8957 | 27.6117 | 27.6074
150 | feeder2_line146 | 3 | 354.6 | 98.1704 | 98.1871 | 27.6848 | 27.6896
150 | feeder2_line147 | 1 | 99 | 0.10747 | 0.10747 | 0.10855 | 0.10856
150 | feeder2_line147 | 2 | 99 | 1.1604e-06 | 2.2542e-06 | 1.1721e-06 | 2.277e-06
150 | feeder2_line147 | 3 | 99 | 1.16e-06 | 2.2535e-06 | 1.1717e-06 | 2.2763e-06
150 | feeder2_line148 | 1 | 99 | 0.22049 | 0.22049 | 0.22271 | 0.22272
150 | feeder2_line148 | 2 | 99 | 6.0531e-07 | 1.5105e-06 | 6.1142e-07 | 1.5258e-06
150 | feeder2_line148 | 3 | 99 | 6.052e-07 | 1.51e-06 | 6.1132e-07 | 1.5253e-06
150 | feeder2_line149 | 1 | 354.6 | 98.9564 | 98.9599 | 27.9065 | 27.9075
150 | feeder2_line149 | 2 | 354.6 | 97.9113 | 97.8957 | 27.6118 | 27.6074
150 | feeder2_line149 | 3 | 354.6 | 98.1706 | 98.1871 | 27.6849 | 27.6896
150 | feeder2_line150 | 1 | 354.6 | 98.9565 | 98.9599 | 27.9065 | 27.9075
150 | feeder2_line150 | 2 | 354.6 | 98.7979 | 98.7822 | 27.8618 | 27.8574
150 | feeder2_line150 | 3 | 354.6 | 98.1707 | 98.1871 | 27.6849 | 27.6896
150 | feeder2_line151 | 1 | 99 | 9.8201e-06 | 1.7911e-06 | 9.9193e-06 | 1.8092e-06
150 | feeder2_line151 | 2 | 99 | 1.532 | 1.532 | 1.5474 | 1.5475
150 | feeder2_line151 | 3 | 99 | 9.8414e-06 | 1.7939e-06 | 9.9408e-06 | 1.8121e-06
150 | feeder2_line152 | 1 | 354.6 | 1.114e-11 | 1.1941e-06 | 3.1415e-12 | 3.3674e-07
150 | feeder2_line152 | 2 | 354.6 | 1.8463e-11 | 1.1961e-06 | 5.2067e-12 | 3.373e-07
150 | feeder2_line152 | 3 | 354.6 | 0.076283 | 0.076294 | 0.021512 | 0.021515
150 | feeder2_line153 | 1 | 99 | 0.043692 | 0.043694 | 0.044134 | 0.044135
150 | feeder2_line153 | 2 | 99 | 5.0305e-08 | 5.9847e-07 | 5.0813e-08 | 6.0452e-07
150 | feeder2_line153 | 3 | 99 | 5.047e-08 | 5.9828e-07 | 5.098e-08 | 6.0432e-07
150 | feeder2_line154 | 1 | 99 | 5.7962e-07 | 8.8888e-07 | 5.8548e-07 | 8.9786e-07
150 | feeder2_line154 | 2 | 99 | 5.8073e-07 | 8.9055e-07 | 5.866e-07 | 8.9954e-07
150 | feeder2_line154 | 3 | 99 | 1.2464 | 1.2465 | 1.259 | 1.2591
150 | feeder2_line155 | 1 | 99 | 99 | 99.0036 | 100 | 100.0036
150 | feeder2_line155 | 2 | 99 | 98.7978 | 98.7822 | 99.7957 | 99.78
150 | feeder2_line155 | 3 | 99 | 98.8851 | 98.9018 | 99.884 | 99.9008
150 | feeder2_line156 | 1 | 99 | 6.0466e-07 | 1.1696e-06 | 6.1076e-07 | 1.1814e-06
150 | feeder2_line156 | 2 | 99 | 0.095943 | 0.095932 | 0.096912 | 0.096901
150 | feeder2_line156 | 3 | 99 | 6.0551e-07 | 1.1714e-06 | 6.1162e-07 | 1.1833e-06
150 | feeder2_line157 | 1 | 99 | 2.5282e-08 | 2.5391e-07 | 2.5537e-08 | 2.5648e-07
150 | feeder2_line157 | 2 | 99 | 1.4841 | 1.4841 | 1.4991 | 1.4991
150 | feeder2_line157 | 3 | 99 | 2.5223e-08 | 2.5431e-07 | 2.5478e-08 | 2.5688e-07
180 | feeder2_line1 | 1 | 354.6 | 79.7503 | 79.7559 | 22.4902 | 22.4918
180 | feeder2_line1 | 2 | 354.6 | 87.4456 | 87.4293 | 24.6603 | 24.6558
180 | feeder2_line1 | 3 | 354.6 | 90.1055 | 90.118 | 25.4105 | 25.414
180 | feeder2_line2 | 1 | 354.6 | 80.6504 | 80.6559 | 22.7441 | 22.7456
180 | feeder2_line2 | 2 | 354.6 | 87.4457 | 87.4293 | 24.6604 | 24.6558
180 | feeder2_line2 | 3 | 354.6 | 90.1057 | 90.118 | 25.4105 | 25.414
180 | feeder2_line3 | 1 | 80.1 | 1.5729 | 1.5729 | 1.9637 | 1.9637
180 | feeder2_line3 | 2 | 80.1 | 5.722e-07 | 1.0574e-06 | 7.1436e-07 | 1.3201e-06
180 | feeder2_line3 | 3 | 80.1 | 5.7257e-07 | 1.0581e-06 | 7.1482e-07 | 1.321e-06
180 | feeder2_line4 | 1 | 354.6 | 80.6506 | 80.6559 | 22.7441 | 22.7456
180 | feeder2_line4 | 2 | 354.6 | 88.2249 | 88.2084 | 24.8801 | 24.8755
180 | feeder2_line4 | 3 | 354.6 | 90.1058 | 90.118 | 25.4106 | 25.414
180 | feeder2_line5 | 1 | 80.1 | 5.7225e-07 | 9.9853e-07 | 7.1442e-07 | 1.2466e-06
180 | feeder2_line5 | 2 | 80.1 | 1.5293 | 1.5294 | 1.9093 | 1.9093
180 | feeder2_line5 | 3 | 80.1 | 5.7262e-07 | 9.9918e-07 | 7.1489e-07 | 1.2474e-06
180 | feeder2_line6 | 1 | 80.1 | 5.7232e-07 | 1.1748e-06 | 7.1451e-07 | 1.4667e-06
180 | feeder2_line6 | 2 | 80.1 | 5.7232e-07 | 1.1748e-06 | 7.1451e-07 | 1.4666e-06
180 | feeder2_line6 | 3 | 80.1 | 0.085275 | 0.085281 | 0.10646 | 0.10647
180 | feeder2_line7 | 1 | 354.6 | 80.6507 | 80.6559 | 22.7441 | 22.7456
180 | feeder2_line7 | 2 | 354.6 | 88.225 | 88.2084 | 24.8802 | 24.8755
180 | feeder2_line7 | 3 | 354.6 | 90.191 | 90.203 | 25.4346 | 25.438
180 | feeder2_line8 | 1 | 80.1 | 0.072595 | 0.072595 | 0.09063 | 0.090631
180 | feeder2_line8 | 2 | 80.1 | 5.7253e-07 | 1.1332e-06 | 7.1478e-07 | 1.4147e-06
180 | feeder2_line8 | 3 | 80.1 | 5.7294e-07 | 1.134e-06 | 7.1529e-07 | 1.4157e-06
180 | feeder2_line9 | 1 | 354.6 | 80.723 | 80.7282 | 22.7645 | 22.766
180 | feeder2_line9 | 2 | 354.6 | 88.2251 | 88.2084 | 24.8802 | 24.8755
180 | feeder2_line9 | 3 | 354.6 | 90.1911 | 90.203 | 25.4346 | 25.438
180 | feeder2_line10 | 1 | 80.1 | 8.4636e-07 | 1.4963e-06 | 1.0566e-06 | 1.868e-06
180 | feeder2_line10 | 2 | 80.1 | 0.072579 | 0.072577 | 0.090611 | 0.090608
180 | feeder2_line10 | 3 | 80.1 | 8.4701e-07 | 1.4974e-06 | 1.0574e-06 | 1.8694e-06
180 | feeder2_line11 | 1 | 354.6 | 80.723 | 80.7282 | 22.7645 | 22.766
180 | feeder2_line11 | 2 | 354.6 | 88.297 | 88.2803 | 24.9004 | 24.8957
180 | feeder2_line11 | 3 | 354.6 | 90.191 | 90.203 | 25.4346 | 25.438
180 | feeder2_line12 | 1 | 80.1 | 5.4771e-07 | 9.9265e-07 | 6.8379e-07 | 1.2393e-06
180 | feeder2_line12 | 2 | 80.1 | 5.4776e-07 | 9.9269e-07 | 6.8385e-07 | 1.2393e-06
180 | feeder2_line12 | 3 | 80.1 | 0.81871 | 0.81873 | 1.0221 | 1.0221
180 | feeder2_line13 | 1 | 354.6 | 80.723 | 80.7282 | 22.7645 | 22.766
180 | feeder2_line13 | 2 | 354.6 | 88.297 | 88.2803 | 24.9004 | 24.8957
180 | feeder2_line13 | 3 | 354.6 | 90.6046 | 90.6167 | 25.5512 | 25.5546
180 | feeder2_line14 | 1 | 80.1 | 0.27529 | 0.27529 | 0.34368 | 0.34368
180 | feeder2_line14 | 2 | 80.1 | 2.9881e-07 | 6.474e-07 | 3.7305e-07 | 8.0824e-07
180 | feeder2_line14 | 3 | 80.1 | 2.9903e-07 | 6.4789e-07 | 3.7333e-07 | 8.0885e-07
180 | feeder2_line15 | 1 | 354.6 | 80.9952 | 81.0003 | 22.8413 | 22.8427
180 | feeder2_line15 | 2 | 354.6 | 88.297 | 88.2803 | 24.9004 | 24.8957
180 | feeder2_line15 | 3 | 354.6 | 90.6047 | 90.6167 | 25.5512 | 25.5546
180 | feeder2_line16 | 1 | 80.1 | 5.7281e-07 | 1.032e-06 | 7.1512e-07 | 1.2883e-06
180 | feeder2_line16 | 2 | 80.1 | 0.25448 | 0.25447 | 0.3177 | 0.3177
180 | feeder2_line16 | 3 | 80.1 | 5.733e-07 | 1.0328e-06 | 7.1572e-07 | 1.2894e-06
180 | feeder2_line17 | 1 | 354.6 | 80.9952 | 81.0003 | 22.8413 | 22.8427
180 | feeder2_line17 | 2 | 354.6 | 88.5457 | 88.5289 | 24.9706 | 24.9659
180 | feeder2_line17 | 3 | 354.6 | 90.6047 | 90.6167 | 25.5512 | 25.5546
180 | feeder2_line18 | 1 | 80.1 | 5.4836e-07 | 7.3933e-07 | 6.8459e-07 | 9.23e-07
180 | feeder2_line18 | 2 | 80.1 | 5.4847e-07 | 7.3942e-07 | 6.8473e-07 | 9.2313e-07
180 | feeder2_line18 | 3 | 80.1 | 0.49196 | 0.49197 | 0.61418 | 0.61419
180 | feeder2_line19 | 1 | 354.6 | 80.9952 | 81.0003 | 22.8413 | 22.8427
180 | feeder2_line19 | 2 | 354.6 | 88.5457 | 88.5289 | 24.9706 | 24.9659
180 | feeder2_line19 | 3 | 354.6 | 91.0919 | 91.1038 | 25.6886 | 25.692
180 | feeder2_line20 | 1 | 99 | 5.4853e-07 | 8.8669e-07 | 5.5407e-07 | 8.9564e-07
180 | feeder2_line20 | 2 | 99 | 5.4866e-07 | 8.8683e-07 | 5.542e-07 | 8.9579e-07
180 | feeder2_line20 | 3 | 99 | 0.35675 | 0.35676 | 0.36035 | 0.36036
180 | feeder2_line21 | 1 | 354.6 | 80.9954 | 81.0003 | 22.8413 | 22.8427
180 | feeder2_line21 | 2 | 354.6 | 88.5458 | 88.5289 | 24.9706 | 24.9659
180 | feeder2_line21 | 3 | 354.6 | 91.4462 | 91.458 | 25.7885 | 25.7919
180 | feeder2_line22 | 1 | 99 | 5.7361e-07 | 1.0167e-06 | 5.794e-07 | 1.027e-06
180 | feeder2_line22 | 2 | 99 | 0.09378 | 0.093776 | 0.094727 | 0.094723
180 | feeder2_line22 | 3 | 99 | 5.7427e-07 | 1.0179e-06 | 5.8007e-07 | 1.0281e-06
180 | feeder2_line23 | 1 | 99 | 5.7361e-07 | 9.517e-07 | 5.794e-07 | 9.6132e-07
180 | feeder2_line23 | 2 | 99 | 5.7371e-07 | 9.5187e-07 | 5.795e-07 | 9.6149e-07
180 | feeder2_line23 | 3 | 99 | 0.84084 | 0.84085 | 0.84934 | 0.84934
180 | feeder2_line24 | 1 | 354.6 | 80.9954 | 81.0003 | 22.8413 | 22.8427
180 | feeder2_line24 | 2 | 354.6 | 88.6386 | 88.6216 | 24.9968 | 24.992
180 | feeder2_line24 | 3 | 354.6 | 91.9328 | 91.9446 | 25.9258 | 25.9291
180 | feeder2_line25 | 1 | 99 | 0.093785 | 0.093787 | 0.094733 | 0.094734
180 | feeder2_line25 | 2 | 99 | 4.9884e-08 | 6.9229e-07 | 5.0388e-08 | 6.9928e-07
180 | feeder2_line25 | 3 | 99 | 4.9924e-08 | 6.9301e-07 | 5.0429e-08 | 7.0001e-07
180 | feeder2_line26 | 1 | 99 | 0.22049 | 0.2205 | 0.22272 | 0.22272
180 | feeder2_line26 | 2 | 99 | 5.4898e-07 | 8.577e-07 | 5.5453e-07 | 8.6636e-07
180 | feeder2_line26 | 3 | 99 | 5.4956e-07 | 8.586e-07 | 5.5511e-07 | 8.6727e-07
180 | feeder2_line27 | 1 | 354.6 | 81.307 | 81.3119 | 22.9292 | 22.9306
180 | feeder2_line27 | 2 | 354.6 | 88.6386 | 88.6216 | 24.9968 | 24.992
180 | feeder2_line27 | 3 | 354.6 | 91.9328 | 91.9446 | 25.9258 | 25.9291
180 | feeder2_line28 | 1 | 99 | 2.5458e-06 | 7.1224e-07 | 2.5715e-06 | 7.1943e-07
180 | feeder2_line28 | 2 | 99 | 0.10851 | 0.1085 | 0.1096 | 0.1096
180 | feeder2_line28 | 3 | 99 | 2.55e-06 | 7.1323e-07 | 2.5757e-06 | 7.2043e-07
180 | feeder2_line29 | 1 | 354.6 | 81.307 | 81.3119 | 22.9292 | 22.9306
180 | feeder2_line29 | 2 | 354.6 | 88.747 | 88.73 | 25.0274 | 25.0226
180 | feeder2_line29 | 3 | 354.6 | 91.9328 | 91.9446 | 25.9258 | 25.9291
180 | feeder2_line30 | 1 | 266.4 | 12.0451 | 12.0448 | 4.5214 | 4.5213
180 | feeder2_line30 | 2 | 266.4 | 1.3625 | 1.3626 | 0.51146 | 0.5115
180 | feeder2_line30 | 3 | 266.4 | 3.2337 | 3.2339 | 1.2138 | 1.2139
180 | feeder2_line31 | 1 | 354.6 | 93.0405 | 93.045 | 26.2382 | 26.2394
180 | feeder2_line31 | 2 | 354.6 | 89.5316 | 89.5141 | 25.2486 | 25.2437
180 | feeder2_line31 | 3 | 354.6 | 93.8404 | 93.852 | 26.4637 | 26.467
180 | feeder2_line32 | 1 | 354.6 | 93.0405 | 93.045 | 26.2382 | 26.2394
180 | feeder2_line32 | 2 | 354.6 | 89.7852 | 89.7677 | 25.3201 | 25.3152
180 | feeder2_line32 | 3 | 354.6 | 93.8405 | 93.852 | 26.4638 | 26.467
180 | feeder2_line33 | 1 | 99 | 5.0052e-08 | 6.8806e-07 | 5.0557e-08 | 6.9501e-07
180 | feeder2_line33 | 2 | 99 | 0.25772 | 0.25771 | 0.26032 | 0.26031
180 | feeder2_line33 | 3 | 99 | 5.0021e-08 | 6.8914e-07 | 5.0526e-08 | 6.961e-07
180 | feeder2_line34 | 1 | 354.6 | 93.0405 | 93.045 | 26.2382 | 26.2394
180 | feeder2_line34 | 2 | 354.6 | 89.7852 | 89.7677 | 25.3201 | 25.3152
180 | feeder2_line34 | 3 | 354.6 | 94.1148 | 94.1263 | 26.5411 | 26.5444
180 | feeder2_line35 | 1 | 99 | 3.0005e-07 | 7.6215e-07 | 3.0308e-07 | 7.6985e-07
180 | feeder2_line35 | 2 | 99 | 3.0007e-07 | 7.6222e-07 | 3.031e-07 | 7.6992e-07
180 | feeder2_line35 | 3 | 99 | 0.27545 | 0.27546 | 0.27824 | 0.27824
180 | feeder2_line36 | 1 | 354.6 | 93.6267 | 93.6313 | 26.4035 | 26.4048
180 | feeder2_line36 | 2 | 354.6 | 89.7851 | 89.7677 | 25.3201 | 25.3152
180 | feeder2_line36 | 3 | 354.6 | 94.1148 | 94.1263 | 26.5411 | 26.5444
180 | feeder2_line37 | 1 | 99 | 1.2352 | 1.2349 | 1.2477 | 1.2474
180 | feeder2_line37 | 2 | 99 | 3.0014e-07 | 8.4355e-07 | 3.0317e-07 | 8.5207e-07
180 | feeder2_line37 | 3 | 99 | 3.0057e-07 | 8.4482e-07 | 3.0361e-07 | 8.5336e-07
180 | feeder2_line38 | 1 | 99 | 3.2482e-07 | 7.7752e-07 | 3.281e-07 | 7.8538e-07
180 | feeder2_line38 | 2 | 99 | 0.21252 | 0.21251 | 0.21466 | 0.21465
180 | feeder2_line38 | 3 | 99 | 3.2526e-07 | 7.7882e-07 | 3.2854e-07 | 7.8669e-07
180 | feeder2_line39 | 1 | 266.4 | 12.0451 | 12.0448 | 4.5214 | 4.5213
180 | feeder2_line39 | 2 | 266.4 | 1.2204 | 1.2206 | 0.45812 | 0.4582
180 | feeder2_line39 | 3 | 266.4 | 3.2337 | 3.2339 | 1.2138 | 1.2139
180 | feeder2_line40 | 1 | 354.6 | 93.7202 | 93.7248 | 26.4298 | 26.4311
180 | feeder2_line40 | 2 | 354.6 | 89.7852 | 89.7677 | 25.3201 | 25.3152
180 | feeder2_line40 | 3 | 354.6 | 94.1148 | 94.1263 | 26.5411 | 26.5444
180 | feeder2_line41 | 1 | 99 | 0.093578 | 0.093581 | 0.094523 | 0.094526
180 | feeder2_line41 | 2 | 99 | 5.0038e-08 | 7.372e-07 | 5.0543e-08 | 7.4465e-07
180 | feeder2_line41 | 3 | 99 | 5.0055e-08 | 7.3833e-07 | 5.0561e-08 | 7.4579e-07
180 | feeder2_line42 | 1 | 99 | 2.9976e-07 | 7.5039e-07 | 3.0278e-07 | 7.5797e-07
180 | feeder2_line42 | 2 | 99 | 2.9988e-07 | 7.5078e-07 | 3.0291e-07 | 7.5837e-07
180 | feeder2_line42 | 3 | 99 | 0.18989 | 0.1899 | 0.19181 | 0.19182
180 | feeder2_line43 | 1 | 266.4 | 12.045 | 12.0448 | 4.5214 | 4.5213
180 | feeder2_line43 | 2 | 266.4 | 1.2205 | 1.2206 | 0.45816 | 0.4582
180 | feeder2_line43 | 3 | 266.4 | 3.113 | 3.1131 | 1.1685 | 1.1686
180 | feeder2_line44 | 1 | 354.6 | 93.7202 | 93.7248 | 26.4298 | 26.4311
180 | feeder2_line44 | 2 | 354.6 | 89.7852 | 89.7677 | 25.3201 | 25.3152
180 | feeder2_line44 | 3 | 354.6 | 94.4708 | 94.4823 | 26.6415 | 26.6447
180 | feeder2_line45 | 1 | 99 | 5.0078e-08 | 5.8149e-07 | 5.0584e-08 | 5.8736e-07
180 | feeder2_line45 | 2 | 99 | 5.0051e-08 | 5.8145e-07 | 5.0556e-08 | 5.8732e-07
180 | feeder2_line45 | 3 | 99 | 0.35707 | 0.35709 | 0.36067 | 0.36069
180 | feeder2_line46 | 1 | 99 | 5.7448e-07 | 1.3603e-06 | 5.8028e-07 | 1.3741e-06
180 | feeder2_line46 | 2 | 99 | 5.7479e-07 | 1.361e-06 | 5.8059e-07 | 1.3748e-06
180 | feeder2_line46 | 3 | 99 | 1.5296 | 1.5296 | 1.5451 | 1.5451
180 | feeder2_line47 | 1 | 266.4 | 12.045 | 12.0448 | 4.5214 | 4.5213
180 | feeder2_line47 | 2 | 266.4 | 1.2207 | 1.2206 | 0.45822 | 0.4582
180 | feeder2_line47 | 3 | 266.4 | 1.5836 | 1.5835 | 0.59444 | 0.59442
180 | feeder2_line48 | 1 | 99 | 1.1999 | 1.1999 | 1.212 | 1.212
180 | feeder2_line48 | 2 | 99 | 4.9935e-08 | 7.3281e-07 | 5.0439e-08 | 7.4022e-07
180 | feeder2_line48 | 3 | 99 | 4.9987e-08 | 7.3374e-07 | 5.0491e-08 | 7.4115e-07
180 | feeder2_line49 | 1 | 266.4 | 11.223 | 11.2228 | 4.2128 | 4.2128
180 | feeder2_line49 | 2 | 266.4 | 1.2207 | 1.2206 | 0.45822 | 0.4582
180 | feeder2_line49 | 3 | 266.4 | 1.5836 | 1.5835 | 0.59443 | 0.59442
180 | feeder2_line50 | 1 | 99 | 5.7442e-07 | 1.2378e-06 | 5.8022e-07 | 1.2503e-06
180 | feeder2_line50 | 2 | 99 | 0.084985 | 0.084918 | 0.085843 | 0.085776
180 | feeder2_line50 | 3 | 99 | 5.7552e-07 | 1.2402e-06 | 5.8134e-07 | 1.2527e-06
180 | feeder2_line51 | 1 | 99 | 10.5669 | 10.5669 | 10.6736 | 10.6736
180 | feeder2_line51 | 2 | 99 | 5.7477e-07 | 1.3447e-06 | 5.8058e-07 | 1.3583e-06
180 | feeder2_line51 | 3 | 99 | 5.755e-07 | 1.3464e-06 | 5.8132e-07 | 1.36e-06
180 | feeder2_line52 | 1 | 266.4 | 0.65604 | 0.65595 | 0.24626 | 0.24623
180 | feeder2_line52 | 2 | 266.4 | 1.1731 | 1.1732 | 0.44036 | 0.4404
180 | feeder2_line52 | 3 | 266.4 | 1.5835 | 1.5835 | 0.5944 | 0.59442
180 | feeder2_line53 | 1 | 99 | 5.4939e-07 | 7.5548e-07 | 5.5494e-07 | 7.6311e-07
180 | feeder2_line53 | 2 | 99 | 1.1732 | 1.1732 | 1.185 | 1.1851
180 | feeder2_line53 | 3 | 99 | 5.5053e-07 | 7.5693e-07 | 5.5609e-07 | 7.6458e-07
180 | feeder2_line54 | 1 | 266.4 | 0.65586 | 0.65595 | 0.24619 | 0.24623
180 | feeder2_line54 | 2 | 266.4 | 8.5739e-05 | 4.6375e-06 | 3.2184e-05 | 1.7408e-06
180 | feeder2_line54 | 3 | 266.4 | 1.5835 | 1.5835 | 0.5944 | 0.59442
180 | feeder2_line55 | 1 | 99 | 1.1873 | 1.1873 | 1.1993 | 1.1993
180 | feeder2_line55 | 2 | 99 | 5.0097e-08 | 7.3295e-07 | 5.0603e-08 | 7.4035e-07
180 | feeder2_line55 | 3 | 99 | 5.0098e-08 | 7.342e-07 | 5.0604e-08 | 7.4161e-07
180 | feeder2_line56 | 1 | 354.6 | 94.404 | 94.4084 | 26.6227 | 26.6239
180 | feeder2_line56 | 2 | 354.6 | 89.7853 | 89.7677 | 25.3202 | 25.3152
180 | feeder2_line56 | 3 | 354.6 | 94.4708 | 94.4823 | 26.6415 | 26.6447
180 | feeder2_line57 | 1 | 99 | 7.5086e-07 | 1.5475e-06 | 7.5845e-07 | 1.5631e-06
180 | feeder2_line57 | 2 | 99 | 7.4896e-07 | 1.5485e-06 | 7.5653e-07 | 1.5641e-06
180 | feeder2_line57 | 3 | 99 | 1.5836 | 1.5835 | 1.5995 | 1.5995
180 | feeder2_line58 | 1 | 266.4 | 0.65592 | 0.65595 | 0.24622 | 0.24623
180 | feeder2_line58 | 2 | 266.4 | 1.8997e-05 | 2.6924e-06 | 7.131e-06 | 1.0107e-06
180 | feeder2_line58 | 3 | 266.4 | 1.9025e-05 | 2.6958e-06 | 7.1414e-06 | 1.0119e-06
180 | feeder2_line59 | 1 | 99 | 5.0059e-08 | 5.3791e-07 | 5.0565e-08 | 5.4334e-07
180 | feeder2_line59 | 2 | 99 | 4.993e-08 | 5.3827e-07 | 5.0434e-08 | 5.437e-07
180 | feeder2_line59 | 3 | 99 | 0.76462 | 0.76459 | 0.77235 | 0.77231
180 | feeder2_line60 | 1 | 99 | 2.9972e-07 | 8.1295e-07 | 3.0275e-07 | 8.2116e-07
180 | feeder2_line60 | 2 | 99 | 2.9988e-07 | 8.1348e-07 | 3.0291e-07 | 8.217e-07
180 | feeder2_line60 | 3 | 99 | 0.8198 | 0.81982 | 0.82808 | 0.8281
180 | feeder2_line61 | 1 | 266.4 | 1.5493 | 1.5495 | 0.58157 | 0.58163
180 | feeder2_line61 | 2 | 266.4 | 1.996 | 1.9961 | 0.74925 | 0.74929
180 | feeder2_line61 | 3 | 266.4 | 1.8136 | 1.8137 | 0.68077 | 0.68083
180 | feeder2_line62 | 1 | 354.6 | 95.289 | 95.2936 | 26.8723 | 26.8736
180 | feeder2_line62 | 2 | 354.6 | 91.0498 | 91.0324 | 25.6768 | 25.6719
180 | feeder2_line62 | 3 | 354.6 | 95.6295 | 95.6412 | 26.9683 | 26.9716
180 | feeder2_line63 | 1 | 99 | 0.36004 | 0.36004 | 0.36367 | 0.36368
180 | feeder2_line63 | 2 | 99 | 5.748e-07 | 1.2231e-06 | 5.8061e-07 | 1.2354e-06
180 | feeder2_line63 | 3 | 99 | 5.7552e-07 | 1.2246e-06 | 5.8133e-07 | 1.237e-06
180 | feeder2_line64 | 1 | 99 | 0.29591 | 0.29591 | 0.2989 | 0.2989
180 | feeder2_line64 | 2 | 99 | 7.7226e-12 | 3.2217e-07 | 7.8006e-12 | 3.2543e-07
180 | feeder2_line64 | 3 | 99 | 3.7857e-12 | 3.2258e-07 | 3.8239e-12 | 3.2584e-07
180 | feeder2_line65 | 1 | 99 | 5.0126e-08 | 6.4472e-07 | 5.0632e-08 | 6.5123e-07
180 | feeder2_line65 | 2 | 99 | 1.5322 | 1.5322 | 1.5476 | 1.5477
180 | feeder2_line65 | 3 | 99 | 5.0164e-08 | 6.4556e-07 | 5.0671e-08 | 6.5208e-07
180 | feeder2_line66 | 1 | 354.6 | 95.289 | 95.2936 | 26.8722 | 26.8736
180 | feeder2_line66 | 2 | 354.6 | 91.8936 | 91.8763 | 25.9147 | 25.9098
180 | feeder2_line66 | 3 | 354.6 | 95.6294 | 95.6412 | 26.9683 | 26.9716
180 | feeder2_line67 | 1 | 99 | 2.5058e-08 | 3.6425e-07 | 2.5311e-08 | 3.6793e-07
180 | feeder2_line67 | 2 | 99 | 2.5067e-08 | 3.641e-07 | 2.532e-08 | 3.6777e-07
180 | feeder2_line67 | 3 | 99 | 0.093334 | 0.093341 | 0.094277 | 0.094284
180 | feeder2_line68 | 1 | 266.4 | 1.5494 | 1.5495 | 0.58159 | 0.58163
180 | feeder2_line68 | 2 | 266.4 | 1.9961 | 1.9961 | 0.74927 | 0.74929
180 | feeder2_line68 | 3 | 266.4 | 1.7537 | 1.7538 | 0.65831 | 0.65835
180 | feeder2_line69 | 1 | 99 | 0.21378 | 0.21386 | 0.21593 | 0.21602
180 | feeder2_line69 | 2 | 99 | 2.5559e-06 | 6.6903e-07 | 2.5817e-06 | 6.7579e-07
180 | feeder2_line69 | 3 | 99 | 2.5615e-06 | 6.7033e-07 | 2.5874e-06 | 6.771e-07
180 | feeder2_line70 | 1 | 354.6 | 95.5021 | 95.507 | 26.9324 | 26.9337
180 | feeder2_line70 | 2 | 354.6 | 91.8935 | 91.8763 | 25.9147 | 25.9098
180 | feeder2_line70 | 3 | 354.6 | 95.6293 | 95.6412 | 26.9682 | 26.9716
180 | feeder2_line71 | 1 | 99 | 5.014e-08 | 7.196e-07 | 5.0646e-08 | 7.2687e-07
180 | feeder2_line71 | 2 | 99 | 1.4283 | 1.4282 | 1.4427 | 1.4426
180 | feeder2_line71 | 3 | 99 | 5.0189e-08 | 7.205e-07 | 5.0696e-08 | 7.2778e-07
180 | feeder2_line72 | 1 | 354.6 | 95.5022 | 95.507 | 26.9324 | 26.9337
180 | feeder2_line72 | 2 | 354.6 | 92.7363 | 92.7188 | 26.1524 | 26.1474
180 | feeder2_line72 | 3 | 354.6 | 95.6294 | 95.6412 | 26.9683 | 26.9716
180 | feeder2_line73 | 1 | 99 | 6.0131e-07 | 1.5421e-06 | 6.0738e-07 | 1.5577e-06
180 | feeder2_line73 | 2 | 99 | 0.25777 | 0.25775 | 0.26037 | 0.26036
180 | feeder2_line73 | 3 | 99 | 6.021e-07 | 1.5442e-06 | 6.0818e-07 | 1.5598e-06
180 | feeder2_line74 | 1 | 99 | 5.0109e-08 | 4.5993e-07 | 5.0615e-08 | 4.6458e-07
180 | feeder2_line74 | 2 | 99 | 1.7528 | 1.7528 | 1.7705 | 1.7705
180 | feeder2_line74 | 3 | 99 | 5.0131e-08 | 4.6056e-07 | 5.0637e-08 | 4.6521e-07
180 | feeder2_line75 | 1 | 266.4 | 1.5494 | 1.5495 | 0.58162 | 0.58163
180 | feeder2_line75 | 2 | 266.4 | 0.089513 | 0.089537 | 0.033601 | 0.03361
180 | feeder2_line75 | 3 | 266.4 | 1.7538 | 1.7538 | 0.65834 | 0.65835
180 | feeder2_line76 | 1 | 99 | 1.5495 | 1.5495 | 1.5651 | 1.5651
180 | feeder2_line76 | 2 | 99 | 8.5146e-07 | 1.59e-06 | 8.6006e-07 | 1.6061e-06
180 | feeder2_line76 | 3 | 99 | 8.53e-07 | 1.5929e-06 | 8.6162e-07 | 1.609e-06
180 | feeder2_line77 | 1 | 99 | 2.5054e-08 | 5.7798e-07 | 2.5307e-08 | 5.8382e-07
180 | feeder2_line77 | 2 | 99 | 2.5069e-08 | 5.7773e-07 | 2.5322e-08 | 5.8356e-07
180 | feeder2_line77 | 3 | 99 | 1.7539 | 1.7538 | 1.7716 | 1.7716
180 | feeder2_line78 | 1 | 266.4 | 8.6261e-12 | 9.5855e-07 | 3.238e-12 | 3.5981e-07
180 | feeder2_line78 | 2 | 266.4 | 0.089545 | 0.089537 | 0.033613 | 0.03361
180 | feeder2_line78 | 3 | 266.4 | 8.3438e-12 | 9.5983e-07 | 3.1321e-12 | 3.603e-07
180 | feeder2_line79 | 1 | 354.6 | 1.6527 | 1.6525 | 0.46609 | 0.46602
180 | feeder2_line79 | 2 | 354.6 | 4.1022 | 4.1019 | 1.1568 | 1.1568
180 | feeder2_line79 | 3 | 354.6 | 1.8877 | 1.8873 | 0.53234 | 0.53224
180 | feeder2_line80 | 1 | 354.6 | 96.7435 | 96.7477 | 27.2824 | 27.2836
180 | feeder2_line80 | 2 | 354.6 | 95.1502 | 95.1321 | 26.8331 | 26.828
180 | feeder2_line80 | 3 | 354.6 | 97.515 | 97.5263 | 27.5 | 27.5032
180 | feeder2_line81 | 1 | 354.6 | 96.7434 | 96.7477 | 27.2824 | 27.2836
180 | feeder2_line81 | 2 | 354.6 | 95.1502 | 95.1321 | 26.8331 | 26.828
180 | feeder2_line81 | 3 | 354.6 | 97.765 | 97.7764 | 27.5705 | 27.5737
180 | feeder2_line82 | 1 | 354.6 | 3.0721e-11 | 7.3856e-07 | 8.6636e-12 | 2.0828e-07
180 | feeder2_line82 | 2 | 354.6 | 3.6173e-11 | 7.3793e-07 | 1.0201e-11 | 2.081e-07
180 | feeder2_line82 | 3 | 354.6 | 0.25064 | 0.25065 | 0.070681 | 0.070684
180 | feeder2_line83 | 1 | 354.6 | 96.7436 | 96.7477 | 27.2825 | 27.2836
180 | feeder2_line83 | 2 | 354.6 | 95.2661 | 95.2478 | 26.8658 | 26.8606
180 | feeder2_line83 | 3 | 354.6 | 97.7652 | 97.7764 | 27.5706 | 27.5737
180 | feeder2_line84 | 1 | 354.6 | 1.6921e-11 | 1.3056e-06 | 4.7718e-12 | 3.6819e-07
180 | feeder2_line84 | 2 | 354.6 | 0.11586 | 0.11579 | 0.032674 | 0.032654
180 | feeder2_line84 | 3 | 354.6 | 1.786e-11 | 1.3071e-06 | 5.0367e-12 | 3.6862e-07
180 | feeder2_line85 | 1 | 99 | 0.21255 | 0.21255 | 0.2147 | 0.2147
180 | feeder2_line85 | 2 | 99 | 5.0281e-08 | 4.6561e-07 | 5.0789e-08 | 4.7031e-07
180 | feeder2_line85 | 3 | 99 | 5.0254e-08 | 4.6658e-07 | 5.0762e-08 | 4.713e-07
180 | feeder2_line86 | 1 | 354.6 | 96.956 | 96.96 | 27.3424 | 27.3435
180 | feeder2_line86 | 2 | 354.6 | 95.2663 | 95.2478 | 26.8658 | 26.8606
180 | feeder2_line86 | 3 | 354.6 | 97.7653 | 97.7764 | 27.5706 | 27.5737
180 | feeder2_line87 | 1 | 354.6 | 96.9562 | 96.96 | 27.3424 | 27.3435
180 | feeder2_line87 | 2 | 354.6 | 95.9879 | 95.9691 | 27.0694 | 27.064
180 | feeder2_line87 | 3 | 354.6 | 98.0277 | 98.0386 | 27.6446 | 27.6477
180 | feeder2_line88 | 1 | 354.6 | 0.0001147 | 3.3851e-06 | 3.2345e-05 | 9.5461e-07
180 | feeder2_line88 | 2 | 354.6 | 1.347 | 1.3468 | 0.37987 | 0.37981
180 | feeder2_line88 | 3 | 354.6 | 0.26274 | 0.26265 | 0.074093 | 0.07407
180 | feeder2_line89 | 1 | 354.6 | 96.9539 | 96.96 | 27.3418 | 27.3435
180 | feeder2_line89 | 2 | 354.6 | 96.2953 | 96.2786 | 27.156 | 27.1513
180 | feeder2_line89 | 3 | 354.6 | 98.0254 | 98.0386 | 27.6439 | 27.6477
180 | feeder2_line90 | 1 | 354.6 | 0.00072877 | 2.0439e-06 | 0.00020552 | 5.764e-07
180 | feeder2_line90 | 2 | 354.6 | 0.30924 | 0.30964 | 0.087208 | 0.08732
180 | feeder2_line90 | 3 | 354.6 | 0.00072968 | 2.0468e-06 | 0.00020578 | 5.7722e-07
180 | feeder2_line91 | 1 | 354.6 | 96.9538 | 96.96 | 27.3417 | 27.3435
180 | feeder2_line91 | 2 | 354.6 | 96.2952 | 96.2786 | 27.156 | 27.1513
180 | feeder2_line91 | 3 | 354.6 | 98.4827 | 98.4961 | 27.7729 | 27.7767
180 | feeder2_line92 | 1 | 354.6 | 1.0943e-12 | 1.031e-06 | 3.0859e-13 | 2.9075e-07
180 | feeder2_line92 | 2 | 354.6 | 9.752e-12 | 1.03e-06 | 2.7501e-12 | 2.9048e-07
180 | feeder2_line92 | 3 | 354.6 | 0.82129 | 0.82131 | 0.23161 | 0.23162
180 | feeder2_line93 | 1 | 99 | 2.5114e-08 | 3.4416e-07 | 2.5367e-08 | 3.4763e-07
180 | feeder2_line93 | 2 | 99 | 0.11579 | 0.11572 | 0.11696 | 0.11688
180 | feeder2_line93 | 3 | 99 | 2.5148e-08 | 3.4455e-07 | 2.5402e-08 | 3.4803e-07
180 | feeder2_line94 | 1 | 354.6 | 2.5112e-06 | 1.6755e-06 | 7.0817e-07 | 4.725e-07
180 | feeder2_line94 | 2 | 354.6 | 0.19459 | 0.19452 | 0.054877 | 0.054856
180 | feeder2_line94 | 3 | 354.6 | 2.5147e-06 | 1.6775e-06 | 7.0916e-07 | 4.7306e-07
180 | feeder2_line95 | 1 | 99 | 3.5896e-06 | 2.625e-06 | 3.6259e-06 | 2.6515e-06
180 | feeder2_line95 | 2 | 99 | 1.347 | 1.3468 | 1.3606 | 1.3604
180 | feeder2_line95 | 3 | 99 | 3.593e-06 | 2.6281e-06 | 3.6293e-06 | 2.6546e-06
180 | feeder2_line96 | 1 | 354.6 | 0.00012183 | 6.2579e-07 | 3.4356e-05 | 1.7648e-07
180 | feeder2_line96 | 2 | 354.6 | 0.0001217 | 6.2527e-07 | 3.4321e-05 | 1.7633e-07
180 | feeder2_line96 | 3 | 354.6 | 0.26272 | 0.26265 | 0.074088 | 0.07407
180 | feeder2_line97 | 1 | 354.6 | 97.1076 | 97.1137 | 27.3851 | 27.3868
180 | feeder2_line97 | 2 | 354.6 | 96.2954 | 96.2786 | 27.1561 | 27.1513
180 | feeder2_line97 | 3 | 354.6 | 98.4829 | 98.4961 | 27.773 | 27.7767
180 | feeder2_line98 | 1 | 354.6 | 0.15611 | 0.15449 | 0.044024 | 0.043567
180 | feeder2_line98 | 2 | 354.6 | 0.00171 | 6.2709e-07 | 0.00048223 | 1.7684e-07
180 | feeder2_line98 | 3 | 354.6 | 0.0017161 | 6.2962e-07 | 0.00048395 | 1.7756e-07
180 | feeder2_line99 | 1 | 99 | 2.5101e-08 | 4.4984e-07 | 2.5354e-08 | 4.5439e-07
180 | feeder2_line99 | 2 | 99 | 2.5144e-08 | 4.4942e-07 | 2.5398e-08 | 4.5396e-07
180 | feeder2_line99 | 3 | 99 | 0.26263 | 0.26265 | 0.26528 | 0.26531
180 | feeder2_line100 | 1 | 99 | 0.1544 | 0.15449 | 0.15596 | 0.15605
180 | feeder2_line100 | 2 | 99 | 2.5166e-08 | 6.1731e-07 | 2.542e-08 | 6.2355e-07
180 | feeder2_line100 | 3 | 99 | 2.5155e-08 | 6.1864e-07 | 2.5409e-08 | 6.2489e-07
180 | feeder2_line101 | 1 | 354.6 | 0.19501 | 0.19465 | 0.054993 | 0.054893
180 | feeder2_line101 | 2 | 354.6 | 4.1022 | 4.1019 | 1.1568 | 1.1568
180 | feeder2_line101 | 3 | 354.6 | 1.8877 | 1.8873 | 0.53233 | 0.53224
180 | feeder2_line102 | 1 | 99 | 1.5041 | 1.5041 | 1.5193 | 1.5193
180 | feeder2_line102 | 2 | 99 | 2.3449e-06 | 8.8214e-07 | 2.3686e-06 | 8.9105e-07
180 | feeder2_line102 | 3 | 99 | 2.3515e-06 | 8.8396e-07 | 2.3753e-06 | 8.9289e-07
180 | feeder2_line103 | 1 | 99 | 5.5228e-07 | 8.0817e-07 | 5.5786e-07 | 8.1633e-07
180 | feeder2_line103 | 2 | 99 | 1.2618 | 1.2618 | 1.2746 | 1.2746
180 | feeder2_line103 | 3 | 99 | 5.529e-07 | 8.0909e-07 | 5.5848e-07 | 8.1726e-07
180 | feeder2_line104 | 1 | 354.6 | 0.1949 | 0.19465 | 0.054965 | 0.054893
180 | feeder2_line104 | 2 | 354.6 | 2.848 | 2.8477 | 0.80315 | 0.80308
180 | feeder2_line104 | 3 | 354.6 | 1.8875 | 1.8873 | 0.5323 | 0.53224
180 | feeder2_line105 | 1 | 99 | 2.5608e-06 | 7.4363e-07 | 2.5867e-06 | 7.5114e-07
180 | feeder2_line105 | 2 | 99 | 2.5574e-06 | 7.4292e-07 | 2.5833e-06 | 7.5042e-07
180 | feeder2_line105 | 3 | 99 | 0.49346 | 0.49348 | 0.49844 | 0.49847
180 | feeder2_line106 | 1 | 354.6 | 0.19485 | 0.19465 | 0.054949 | 0.054893
180 | feeder2_line106 | 2 | 354.6 | 2.8479 | 2.8477 | 0.80314 | 0.80308
180 | feeder2_line106 | 3 | 354.6 | 1.3944 | 1.3942 | 0.39323 | 0.39318
180 | feeder2_line107 | 1 | 99 | 3.2629e-07 | 9.0623e-07 | 3.2959e-07 | 9.1538e-07
180 | feeder2_line107 | 2 | 99 | 1.0563 | 1.0563 | 1.067 | 1.067
180 | feeder2_line107 | 3 | 99 | 3.2667e-07 | 9.0722e-07 | 3.2997e-07 | 9.1638e-07
180 | feeder2_line108 | 1 | 354.6 | 0.19484 | 0.19465 | 0.054946 | 0.054892
180 | feeder2_line108 | 2 | 354.6 | 1.8001 | 1.7999 | 0.50764 | 0.5076
180 | feeder2_line108 | 3 | 354.6 | 1.3944 | 1.3942 | 0.39323 | 0.39318
180 | feeder2_line109 | 1 | 354.6 | 97.344 | 97.3489 | 27.4518 | 27.4531
180 | feeder2_line109 | 2 | 354.6 | 96.2966 | 96.2786 | 27.1564 | 27.1513
180 | feeder2_line109 | 3 | 354.6 | 98.4841 | 98.4961 | 27.7733 | 27.7767
180 | feeder2_line110 | 1 | 99 | 0.23625 | 0.23545 | 0.23864 | 0.23783
180 | feeder2_line110 | 2 | 99 | 0.00080846 | 9.1343e-07 | 0.00081663 | 9.2266e-07
180 | feeder2_line110 | 3 | 99 | 0.0008106 | 9.1582e-07 | 0.00081879 | 9.2507e-07
180 | feeder2_line111 | 1 | 99 | 2.5097e-08 | 3.842e-07 | 2.535e-08 | 3.8808e-07
180 | feeder2_line111 | 2 | 99 | 0.072517 | 0.072447 | 0.073249 | 0.073179
180 | feeder2_line111 | 3 | 99 | 2.5135e-08 | 3.8465e-07 | 2.5389e-08 | 3.8854e-07
180 | feeder2_line112 | 1 | 99 | 3.2658e-07 | 9.2326e-07 | 3.2988e-07 | 9.3258e-07
180 | feeder2_line112 | 2 | 99 | 1.3147 | 1.3146 | 1.328 | 1.3279
180 | feeder2_line112 | 3 | 99 | 3.2699e-07 | 9.2434e-07 | 3.3029e-07 | 9.3368e-07
180 | feeder2_line113 | 1 | 99 | 0.12801 | 0.12802 | 0.12931 | 0.12931
180 | feeder2_line113 | 2 | 99 | 3.2677e-07 | 9.1049e-07 | 3.3007e-07 | 9.1968e-07
180 | feeder2_line113 | 3 | 99 | 3.2738e-07 | 9.1248e-07 | 3.3069e-07 | 9.2169e-07
180 | feeder2_line114 | 1 | 99 | 1.2624 | 1.2623 | 1.2751 | 1.2751
180 | feeder2_line114 | 2 | 99 | 2.512e-08 | 4.3865e-07 | 2.5374e-08 | 4.4308e-07
180 | feeder2_line114 | 3 | 99 | 2.5112e-08 | 4.3956e-07 | 2.5365e-08 | 4.44e-07
180 | feeder2_line115 | 1 | 99 | 2.507e-08 | 5.6554e-07 | 2.5323e-08 | 5.7125e-07
180 | feeder2_line115 | 2 | 99 | 0.33241 | 0.3324 | 0.33577 | 0.33576
180 | feeder2_line115 | 3 | 99 | 2.5114e-08 | 5.6614e-07 | 2.5368e-08 | 5.7186e-07
180 | feeder2_line116 | 1 | 354.6 | 0.19485 | 0.19465 | 0.054948 | 0.054892
180 | feeder2_line116 | 2 | 354.6 | 1.5652 | 1.5651 | 0.4414 | 0.44136
180 | feeder2_line116 | 3 | 354.6 | 1.3944 | 1.3942 | 0.39323 | 0.39318
180 | feeder2_line117 | 1 | 99 | 5.0281e-08 | 6.473e-07 | 5.0789e-08 | 6.5384e-07
180 | feeder2_line117 | 2 | 99 | 1.5318 | 1.5317 | 1.5473 | 1.5472
180 | feeder2_line117 | 3 | 99 | 5.0359e-08 | 6.4805e-07 | 5.0867e-08 | 6.5459e-07
180 | feeder2_line118 | 1 | 354.6 | 97.344 | 97.3489 | 27.4518 | 27.4531
180 | feeder2_line118 | 2 | 354.6 | 97.1516 | 97.1336 | 27.3975 | 27.3924
180 | feeder2_line118 | 3 | 354.6 | 98.4842 | 98.4961 | 27.7733 | 27.7767
180 | feeder2_line119 | 1 | 99 | 2.5067e-08 | 6.0855e-07 | 2.5321e-08 | 6.147e-07
180 | feeder2_line119 | 2 | 99 | 2.5127e-08 | 6.0792e-07 | 2.538e-08 | 6.1406e-07
180 | feeder2_line119 | 3 | 99 | 0.54666 | 0.54668 | 0.55219 | 0.5522
180 | feeder2_line120 | 1 | 354.6 | 0.19485 | 0.19465 | 0.054949 | 0.054892
180 | feeder2_line120 | 2 | 354.6 | 1.5652 | 1.5651 | 0.4414 | 0.44136
180 | feeder2_line120 | 3 | 354.6 | 0.84838 | 0.84818 | 0.23925 | 0.23919
180 | feeder2_line121 | 1 | 99 | 3.2629e-07 | 9.4237e-07 | 3.2959e-07 | 9.5189e-07
180 | feeder2_line121 | 2 | 99 | 0.043894 | 0.043889 | 0.044338 | 0.044333
180 | feeder2_line121 | 3 | 99 | 3.2666e-07 | 9.4332e-07 | 3.2996e-07 | 9.5285e-07
180 | feeder2_line122 | 1 | 354.6 | 0.19483 | 0.19465 | 0.054945 | 0.054892
180 | feeder2_line122 | 2 | 354.6 | 1.5372 | 1.5371 | 0.43351 | 0.43349
180 | feeder2_line122 | 3 | 354.6 | 0.84837 | 0.84818 | 0.23925 | 0.23919
180 | feeder2_line123 | 1 | 99 | 5.7739e-07 | 9.7652e-07 | 5.8322e-07 | 9.8639e-07
180 | feeder2_line123 | 2 | 99 | 5.7676e-07 | 9.7547e-07 | 5.8259e-07 | 9.8533e-07
180 | feeder2_line123 | 3 | 99 | 0.10804 | 0.10805 | 0.10913 | 0.10914
180 | feeder2_line124 | 1 | 354.6 | 0.19474 | 0.19465 | 0.054919 | 0.054892
180 | feeder2_line124 | 2 | 354.6 | 1.5373 | 1.5371 | 0.43352 | 0.43349
180 | feeder2_line124 | 3 | 354.6 | 0.74081 | 0.74071 | 0.20891 | 0.20889
180 | feeder2_line125 | 1 | 99 | 5.7739e-07 | 9.0778e-07 | 5.8322e-07 | 9.1695e-07
180 | feeder2_line125 | 2 | 99 | 5.7676e-07 | 9.068e-07 | 5.8259e-07 | 9.1596e-07
180 | feeder2_line125 | 3 | 99 | 0.15447 | 0.15448 | 0.15603 | 0.15605
180 | feeder2_line126 | 1 | 354.6 | 0.1949 | 0.19465 | 0.054964 | 0.054892
180 | feeder2_line126 | 2 | 354.6 | 1.5374 | 1.5371 | 0.43356 | 0.43349
180 | feeder2_line126 | 3 | 354.6 | 0.58799 | 0.58771 | 0.16582 | 0.16574
180 | feeder2_line127 | 1 | 99 | 5.7739e-07 | 1.0868e-06 | 5.8322e-07 | 1.0977e-06
180 | feeder2_line127 | 2 | 99 | 5.7676e-07 | 1.0856e-06 | 5.8258e-07 | 1.0965e-06
180 | feeder2_line127 | 3 | 99 | 0.21255 | 0.21256 | 0.2147 | 0.21471
180 | feeder2_line128 | 1 | 354.6 | 0.19482 | 0.19465 | 0.05494 | 0.054892
180 | feeder2_line128 | 2 | 354.6 | 1.5374 | 1.5371 | 0.43355 | 0.43349
180 | feeder2_line128 | 3 | 354.6 | 0.37537 | 0.37516 | 0.10586 | 0.1058
180 | feeder2_line129 | 1 | 99 | 5.5233e-07 | 8.8121e-07 | 5.5791e-07 | 8.9011e-07
180 | feeder2_line129 | 2 | 99 | 1.5371 | 1.5371 | 1.5526 | 1.5527
180 | feeder2_line129 | 3 | 99 | 5.5284e-07 | 8.8207e-07 | 5.5842e-07 | 8.9098e-07
180 | feeder2_line130 | 1 | 354.6 | 0.19483 | 0.19465 | 0.054945 | 0.054892
180 | feeder2_line130 | 2 | 354.6 | 0.00030983 | 4.6583e-06 | 8.7375e-05 | 1.3137e-06
180 | feeder2_line130 | 3 | 354.6 | 0.37539 | 0.37516 | 0.10586 | 0.1058
180 | feeder2_line131 | 1 | 99 | 5.7739e-07 | 9.7668e-07 | 5.8322e-07 | 9.8655e-07
180 | feeder2_line131 | 2 | 99 | 5.7675e-07 | 9.7561e-07 | 5.8258e-07 | 9.8546e-07
180 | feeder2_line131 | 3 | 99 | 0.16263 | 0.16263 | 0.16427 | 0.16428
180 | feeder2_line132 | 1 | 354.6 | 0.19467 | 0.19465 | 0.054898 | 0.054892
180 | feeder2_line132 | 2 | 354.6 | 0.0001262 | 2.9289e-06 | 3.5588e-05 | 8.2597e-07
180 | feeder2_line132 | 3 | 354.6 | 0.21263 | 0.21256 | 0.059963 | 0.059945
180 | feeder2_line133 | 1 | 99 | 0.19459 | 0.19465 | 0.19656 | 0.19661
180 | feeder2_line133 | 2 | 99 | 3.0094e-07 | 9.8339e-07 | 3.0398e-07 | 9.9333e-07
180 | feeder2_line133 | 3 | 99 | 3.0153e-07 | 9.8544e-07 | 3.0458e-07 | 9.9539e-07
180 | feeder2_line134 | 1 | 354.6 | 4.3671e-12 | 1.7953e-06 | 1.2316e-12 | 5.0628e-07
180 | feeder2_line134 | 2 | 354.6 | 1.4171e-11 | 1.7934e-06 | 3.9964e-12 | 5.0576e-07
180 | feeder2_line134 | 3 | 354.6 | 0.21255 | 0.21256 | 0.059942 | 0.059945
180 | feeder2_line135 | 1 | 99 | 1.4305 | 1.4305 | 1.4449 | 1.4449
180 | feeder2_line135 | 2 | 99 | 5.0426e-08 | 5.8946e-07 | 5.0935e-08 | 5.9542e-07
180 | feeder2_line135 | 3 | 99 | 5.0386e-08 | 5.908e-07 | 5.0895e-08 | 5.9677e-07
180 | feeder2_line136 | 1 | 354.6 | 98.2787 | 98.2836 | 27.7154 | 27.7168
180 | feeder2_line136 | 2 | 354.6 | 97.1516 | 97.1336 | 27.3975 | 27.3924
180 | feeder2_line136 | 3 | 354.6 | 98.4841 | 98.4961 | 27.7733 | 27.7767
180 | feeder2_line137 | 1 | 99 | 0.085125 | 0.085213 | 0.085985 | 0.086074
180 | feeder2_line137 | 2 | 99 | 8.5551e-07 | 1.5878e-06 | 8.6415e-07 | 1.6039e-06
180 | feeder2_line137 | 3 | 99 | 8.5748e-07 | 1.5914e-06 | 8.6614e-07 | 1.6075e-06
180 | feeder2_line138 | 1 | 354.6 | 98.3639 | 98.3689 | 27.7394 | 27.7408
180 | feeder2_line138 | 2 | 354.6 | 97.1517 | 97.1336 | 27.3975 | 27.3924
180 | feeder2_line138 | 3 | 354.6 | 98.4842 | 98.4961 | 27.7733 | 27.7767
180 | feeder2_line139 | 1 | 99 | 5.032e-08 | 4.9535e-07 | 5.0828e-08 | 5.0036e-07
180 | feeder2_line139 | 2 | 99 | 5.0439e-08 | 4.9481e-07 | 5.0948e-08 | 4.998e-07
180 | feeder2_line139 | 3 | 99 | 0.13649 | 0.13701 | 0.13787 | 0.13839
180 | feeder2_line140 | 1 | 354.6 | 98.364 | 98.3689 | 27.7394 | 27.7408
180 | feeder2_line140 | 2 | 354.6 | 97.1518 | 97.1336 | 27.3976 | 27.3924
180 | feeder2_line140 | 3 | 354.6 | 98.6174 | 98.6299 | 27.8109 | 27.8144
180 | feeder2_line141 | 1 | 99 | 2.5457e-06 | 4.9007e-07 | 2.5714e-06 | 4.9502e-07
180 | feeder2_line141 | 2 | 99 | 0.18987 | 0.18985 | 0.19178 | 0.19176
180 | feeder2_line141 | 3 | 99 | 2.5485e-06 | 4.9064e-07 | 2.5742e-06 | 4.9559e-07
180 | feeder2_line142 | 1 | 354.6 | 98.3638 | 98.3689 | 27.7394 | 27.7408
180 | feeder2_line142 | 2 | 354.6 | 97.3411 | 97.3231 | 27.451 | 27.4459
180 | feeder2_line142 | 3 | 354.6 | 98.6173 | 98.6299 | 27.8108 | 27.8144
180 | feeder2_line143 | 1 | 99 | 8.5691e-07 | 1.7415e-06 | 8.6557e-07 | 1.7591e-06
180 | feeder2_line143 | 2 | 99 | 1.0573 | 1.0572 | 1.068 | 1.0679
180 | feeder2_line143 | 3 | 99 | 8.5789e-07 | 1.7435e-06 | 8.6656e-07 | 1.7612e-06
180 | feeder2_line144 | 1 | 354.6 | 98.3636 | 98.3689 | 27.7393 | 27.7408
180 | feeder2_line144 | 2 | 354.6 | 97.9523 | 97.9343 | 27.6233 | 27.6182
180 | feeder2_line144 | 3 | 354.6 | 98.6171 | 98.6299 | 27.8108 | 27.8144
180 | feeder2_line145 | 1 | 99 | 2.5169e-08 | 4.8837e-07 | 2.5423e-08 | 4.933e-07
180 | feeder2_line145 | 2 | 99 | 0.25069 | 0.25068 | 0.25323 | 0.25321
180 | feeder2_line145 | 3 | 99 | 2.5213e-08 | 4.8892e-07 | 2.5468e-08 | 4.9386e-07
180 | feeder2_line146 | 1 | 354.6 | 98.3635 | 98.3689 | 27.7393 | 27.7408
180 | feeder2_line146 | 2 | 354.6 | 98.2023 | 98.1844 | 27.6938 | 27.6888
180 | feeder2_line146 | 3 | 354.6 | 98.6169 | 98.6299 | 27.8108 | 27.8144
180 | feeder2_line147 | 1 | 99 | 0.10731 | 0.10732 | 0.1084 | 0.1084
180 | feeder2_line147 | 2 | 99 | 1.1582e-06 | 2.2501e-06 | 1.1699e-06 | 2.2729e-06
180 | feeder2_line147 | 3 | 99 | 1.1609e-06 | 2.2553e-06 | 1.1726e-06 | 2.278e-06
180 | feeder2_line148 | 1 | 99 | 0.22049 | 0.22049 | 0.22271 | 0.22272
180 | feeder2_line148 | 2 | 99 | 6.0435e-07 | 1.5078e-06 | 6.1046e-07 | 1.523e-06
180 | feeder2_line148 | 3 | 99 | 6.0565e-07 | 1.5112e-06 | 6.1177e-07 | 1.5265e-06
180 | feeder2_line149 | 1 | 354.6 | 98.6909 | 98.696 | 27.8316 | 27.8331
180 | feeder2_line149 | 2 | 354.6 | 98.2025 | 98.1844 | 27.6939 | 27.6888
180 | feeder2_line149 | 3 | 354.6 | 98.6171 | 98.6299 | 27.8108 | 27.8144
180 | feeder2_line150 | 1 | 354.6 | 98.691 | 98.696 | 27.8316 | 27.8331
180 | feeder2_line150 | 2 | 354.6 | 99.0001 | 98.9819 | 27.9188 | 27.9137
180 | feeder2_line150 | 3 | 354.6 | 98.6172 | 98.6299 | 27.8108 | 27.8144
180 | feeder2_line151 | 1 | 99 | 9.8407e-06 | 1.7933e-06 | 9.9401e-06 | 1.8114e-06
180 | feeder2_line151 | 2 | 99 | 1.3157 | 1.3157 | 1.329 | 1.329
180 | feeder2_line151 | 3 | 99 | 9.8519e-06 | 1.7954e-06 | 9.9514e-06 | 1.8135e-06
180 | feeder2_line152 | 1 | 354.6 | 1.1097e-11 | 1.1954e-06 | 3.1294e-12 | 3.371e-07
180 | feeder2_line152 | 2 | 354.6 | 1.099e-11 | 1.1941e-06 | 3.0991e-12 | 3.3674e-07
180 | feeder2_line152 | 3 | 354.6 | 0.076222 | 0.076231 | 0.021495 | 0.021498
180 | feeder2_line153 | 1 | 99 | 0.043603 | 0.043605 | 0.044043 | 0.044045
180 | feeder2_line153 | 2 | 99 | 5.0513e-08 | 5.9739e-07 | 5.1024e-08 | 6.0343e-07
180 | feeder2_line153 | 3 | 99 | 5.0481e-08 | 5.9875e-07 | 5.099e-08 | 6.048e-07
180 | feeder2_line154 | 1 | 99 | 5.8034e-07 | 8.8996e-07 | 5.862e-07 | 8.9895e-07
180 | feeder2_line154 | 2 | 99 | 5.7967e-07 | 8.8895e-07 | 5.8553e-07 | 8.9793e-07
180 | feeder2_line154 | 3 | 99 | 0.040409 | 0.040424 | 0.040818 | 0.040832
180 | feeder2_line155 | 1 | 99 | 98.7344 | 98.7396 | 99.7318 | 99.737
180 | feeder2_line155 | 2 | 99 | 99 | 98.9819 | 100 | 99.9817
180 | feeder2_line155 | 3 | 99 | 98.7337 | 98.7465 | 99.7311 | 99.744
180 | feeder2_line156 | 1 | 99 | 6.0526e-07 | 1.171e-06 | 6.1137e-07 | 1.1828e-06
180 | feeder2_line156 | 2 | 99 | 1.2636 | 1.2636 | 1.2763 | 1.2763
180 | feeder2_line156 | 3 | 99 | 6.0597e-07 | 1.1723e-06 | 6.1209e-07 | 1.1842e-06
180 | feeder2_line157 | 1 | 99 | 2.5194e-08 | 2.5422e-07 | 2.5449e-08 | 2.5679e-07
180 | feeder2_line157 | 2 | 99 | 0.089134 | 0.089121 | 0.090034 | 0.090021
180 | feeder2_line157 | 3 | 99 | 2.5228e-08 | 2.5451e-07 | 2.5483e-08 | 2.5708e-07
210 | feeder2_line1 | 1 | 354.6 | 77.759 | 77.7683 | 21.9287 | 21.9313
210 | feeder2_line1 | 2 | 354.6 | 84.1167 | 84.1256 | 23.7216 | 23.7241
210 | feeder2_line1 | 3 | 354.6 | 83.8827 | 83.869 | 23.6556 | 23.6517
210 | feeder2_line2 | 1 | 354.6 | 78.7349 | 78.744 | 22.2039 | 22.2064
210 | feeder2_line2 | 2 | 354.6 | 84.1169 | 84.1256 | 23.7216 | 23.7241
210 | feeder2_line2 | 3 | 354.6 | 83.8828 | 83.869 | 23.6556 | 23.6517
210 | feeder2_line3 | 1 | 80.1 | 1.5026 | 1.5026 | 1.8759 | 1.8759
210 | feeder2_line3 | 2 | 80.1 | 5.7247e-07 | 1.0579e-06 | 7.1469e-07 | 1.3207e-06
210 | feeder2_line3 | 3 | 80.1 | 5.7232e-07 | 1.0576e-06 | 7.145e-07 | 1.3204e-06
210 | feeder2_line4 | 1 | 354.6 | 78.735 | 78.744 | 22.2039 | 22.2064
210 | feeder2_line4 | 2 | 354.6 | 84.9709 | 84.9795 | 23.9625 | 23.9649
210 | feeder2_line4 | 3 | 354.6 | 83.883 | 83.869 | 23.6557 | 23.6517
210 | feeder2_line5 | 1 | 80.1 | 5.7241e-07 | 9.9881e-07 | 7.1462e-07 | 1.247e-06
210 | feeder2_line5 | 2 | 80.1 | 1.5296 | 1.5296 | 1.9096 | 1.9096
210 | feeder2_line5 | 3 | 80.1 | 5.7237e-07 | 9.9873e-07 | 7.1456e-07 | 1.2469e-06
210 | feeder2_line6 | 1 | 80.1 | 5.7249e-07 | 1.1751e-06 | 7.1472e-07 | 1.4671e-06
210 | feeder2_line6 | 2 | 80.1 | 5.7259e-07 | 1.1753e-06 | 7.1485e-07 | 1.4673e-06
210 | feeder2_line6 | 3 | 80.1 | 2.1192 | 2.1192 | 2.6458 | 2.6458
210 | feeder2_line7 | 1 | 354.6 | 78.7352 | 78.744 | 22.2039 | 22.2064
210 | feeder2_line7 | 2 | 354.6 | 84.971 | 84.9795 | 23.9625 | 23.9649
210 | feeder2_line7 | 3 | 354.6 | 84.8625 | 84.8483 | 23.9319 | 23.9279
210 | feeder2_line8 | 1 | 80.1 | 0.072571 | 0.072573 | 0.090601 | 0.090602
210 | feeder2_line8 | 2 | 80.1 | 5.7284e-07 | 1.1338e-06 | 7.1515e-07 | 1.4154e-06
210 | feeder2_line8 | 3 | 80.1 | 5.7265e-07 | 1.1334e-06 | 7.1491e-07 | 1.415e-06
210 | feeder2_line9 | 1 | 354.6 | 78.8078 | 78.8166 | 22.2244 | 22.2269
210 | feeder2_line9 | 2 | 354.6 | 84.9711 | 84.9795 | 23.9625 | 23.9649
210 | feeder2_line9 | 3 | 354.6 | 84.8625 | 84.8483 | 23.9319 | 23.9279
210 | feeder2_line10 | 1 | 80.1 | 8.4662e-07 | 1.4967e-06 | 1.057e-06 | 1.8686e-06
210 | feeder2_line10 | 2 | 80.1 | 0.072522 | 0.072523 | 0.09054 | 0.090541
210 | feeder2_line10 | 3 | 80.1 | 8.4654e-07 | 1.4966e-06 | 1.0569e-06 | 1.8684e-06
210 | feeder2_line11 | 1 | 354.6 | 78.8078 | 78.8166 | 22.2244 | 22.2269
210 | feeder2_line11 | 2 | 354.6 | 85.0433 | 85.0518 | 23.9829 | 23.9853
210 | feeder2_line11 | 3 | 354.6 | 84.8625 | 84.8483 | 23.9319 | 23.9279
210 | feeder2_line12 | 1 | 80.1 | 5.4788e-07 | 9.9296e-07 | 6.84e-07 | 1.2396e-06
210 | feeder2_line12 | 2 | 80.1 | 5.481e-07 | 9.9324e-07 | 6.8427e-07 | 1.24e-06
210 | feeder2_line12 | 3 | 80.1 | 0.061766 | 0.061764 | 0.077111 | 0.077108
210 | feeder2_line13 | 1 | 354.6 | 78.8077 | 78.8166 | 22.2244 | 22.2269
210 | feeder2_line13 | 2 | 354.6 | 85.0433 | 85.0518 | 23.9829 | 23.9853
210 | feeder2_line13 | 3 | 354.6 | 84.9241 | 84.9099 | 23.9493 | 23.9453
210 | feeder2_line14 | 1 | 80.1 | 1.5992 | 1.5991 | 1.9965 | 1.9964
210 | feeder2_line14 | 2 | 80.1 | 2.9896e-07 | 6.4776e-07 | 3.7323e-07 | 8.0869e-07
210 | feeder2_line14 | 3 | 80.1 | 2.9889e-07 | 6.4752e-07 | 3.7314e-07 | 8.0839e-07
210 | feeder2_line15 | 1 | 354.6 | 79.8092 | 79.8181 | 22.5068 | 22.5093
210 | feeder2_line15 | 2 | 354.6 | 85.0433 | 85.0518 | 23.9829 | 23.9853
210 | feeder2_line15 | 3 | 354.6 | 84.9241 | 84.9099 | 23.9493 | 23.9453
210 | feeder2_line16 | 1 | 80.1 | 5.7299e-07 | 1.0323e-06 | 7.1535e-07 | 1.2887e-06
210 | feeder2_line16 | 2 | 80.1 | 0.25457 | 0.25457 | 0.31782 | 0.31781
210 | feeder2_line16 | 3 | 80.1 | 5.7295e-07 | 1.0322e-06 | 7.153e-07 | 1.2887e-06
210 | feeder2_line17 | 1 | 354.6 | 79.8093 | 79.8181 | 22.5068 | 22.5093
210 | feeder2_line17 | 2 | 354.6 | 85.2948 | 85.3032 | 24.0538 | 24.0562
210 | feeder2_line17 | 3 | 354.6 | 84.9241 | 84.9099 | 23.9493 | 23.9453
210 | feeder2_line18 | 1 | 80.1 | 5.4857e-07 | 7.3961e-07 | 6.8486e-07 | 9.2335e-07
210 | feeder2_line18 | 2 | 80.1 | 5.4891e-07 | 7.3994e-07 | 6.8528e-07 | 9.2377e-07
210 | feeder2_line18 | 3 | 80.1 | 1.4146 | 1.4145 | 1.766 | 1.7659
210 | feeder2_line19 | 1 | 354.6 | 79.8093 | 79.8181 | 22.5068 | 22.5093
210 | feeder2_line19 | 2 | 354.6 | 85.2948 | 85.3032 | 24.0538 | 24.0562
210 | feeder2_line19 | 3 | 354.6 | 85.8908 | 85.8765 | 24.2219 | 24.2179
210 | feeder2_line20 | 1 | 99 | 5.4877e-07 | 8.8705e-07 | 5.5431e-07 | 8.9601e-07
210 | feeder2_line20 | 2 | 99 | 5.4913e-07 | 8.8748e-07 | 5.5467e-07 | 8.9644e-07
210 | feeder2_line20 | 3 | 99 | 1.5846 | 1.5846 | 1.6006 | 1.6006
210 | feeder2_line21 | 1 | 354.6 | 79.8094 | 79.8181 | 22.5069 | 22.5093
210 | feeder2_line21 | 2 | 354.6 | 85.295 | 85.3032 | 24.0539 | 24.0562
210 | feeder2_line21 | 3 | 354.6 | 86.8704 | 86.8559 | 24.4981 | 24.4941
210 | feeder2_line22 | 1 | 99 | 5.7385e-07 | 1.0171e-06 | 5.7965e-07 | 1.0274e-06
210 | feeder2_line22 | 2 | 99 | 0.093693 | 0.093696 | 0.094639 | 0.094642
210 | feeder2_line22 | 3 | 99 | 5.738e-07 | 1.017e-06 | 5.796e-07 | 1.0273e-06
210 | feeder2_line23 | 1 | 99 | 5.7385e-07 | 9.5211e-07 | 5.7965e-07 | 9.6173e-07
210 | feeder2_line23 | 2 | 99 | 5.7414e-07 | 9.5259e-07 | 5.7994e-07 | 9.6221e-07
210 | feeder2_line23 | 3 | 99 | 0.12721 | 0.12721 | 0.1285 | 0.12849
210 | feeder2_line24 | 1 | 354.6 | 79.8094 | 79.8181 | 22.5069 | 22.5093
210 | feeder2_line24 | 2 | 354.6 | 85.3883 | 85.3965 | 24.0802 | 24.0825
210 | feeder2_line24 | 3 | 354.6 | 86.9973 | 86.9828 | 24.5339 | 24.5298
210 | feeder2_line25 | 1 | 99 | 0.093748 | 0.093751 | 0.094695 | 0.094698
210 | feeder2_line25 | 2 | 99 | 4.9788e-08 | 6.9283e-07 | 5.029e-08 | 6.9983e-07
210 | feeder2_line25 | 3 | 99 | 5.0025e-08 | 6.9242e-07 | 5.053e-08 | 6.9941e-07
210 | feeder2_line26 | 1 | 99 | 0.22049 | 0.2205 | 0.22272 | 0.22272
210 | feeder2_line26 | 2 | 99 | 5.4948e-07 | 8.5838e-07 | 5.5503e-07 | 8.6705e-07
210 | feeder2_line26 | 3 | 99 | 5.4901e-07 | 8.5786e-07 | 5.5456e-07 | 8.6653e-07
210 | feeder2_line27 | 1 | 354.6 | 80.1235 | 80.1322 | 22.5955 | 22.5979
210 | feeder2_line27 | 2 | 354.6 | 85.3883 | 85.3965 | 24.0802 | 24.0825
210 | feeder2_line27 | 3 | 354.6 | 86.9973 | 86.9828 | 24.5339 | 24.5298
210 | feeder2_line28 | 1 | 99 | 2.5471e-06 | 7.1259e-07 | 2.5728e-06 | 7.1979e-07
210 | feeder2_line28 | 2 | 99 | 1.2644 | 1.2644 | 1.2772 | 1.2772
210 | feeder2_line28 | 3 | 99 | 2.5466e-06 | 7.1256e-07 | 2.5723e-06 | 7.1976e-07
210 | feeder2_line29 | 1 | 354.6 | 80.1235 | 80.1322 | 22.5955 | 22.5979
210 | feeder2_line29 | 2 | 354.6 | 86.0312 | 86.0393 | 24.2615 | 24.2638
210 | feeder2_line29 | 3 | 354.6 | 86.9974 | 86.9828 | 24.5339 | 24.5298
210 | feeder2_line30 | 1 | 266.4 | 11.3631 | 11.3628 | 4.2654 | 4.2653
210 | feeder2_line30 | 2 | 266.4 | 3.5637 | 3.564 | 1.3377 | 1.3378
210 | feeder2_line30 | 3 | 266.4 | 3.3735 | 3.3737 | 1.2663 | 1.2664
210 | feeder2_line31 | 1 | 354.6 | 91.4658 | 91.4743 | 25.7941 | 25.7965
210 | feeder2_line31 | 2 | 354.6 | 87.9245 | 87.9322 | 24.7954 | 24.7976
210 | feeder2_line31 | 3 | 354.6 | 88.9986 | 88.9836 | 25.0983 | 25.0941
210 | feeder2_line32 | 1 | 354.6 | 91.4659 | 91.4743 | 25.7941 | 25.7965
210 | feeder2_line32 | 2 | 354.6 | 88.1813 | 88.189 | 24.8678 | 24.87
210 | feeder2_line32 | 3 | 354.6 | 88.9986 | 88.9836 | 25.0983 | 25.0941
210 | feeder2_line33 | 1 | 99 | 5.0077e-08 | 6.8844e-07 | 5.0583e-08 | 6.954e-07
210 | feeder2_line33 | 2 | 99 | 0.25777 | 0.25777 | 0.26037 | 0.26038
210 | feeder2_line33 | 3 | 99 | 5.0153e-08 | 6.884e-07 | 5.066e-08 | 6.9535e-07
210 | feeder2_line34 | 1 | 354.6 | 91.4659 | 91.4743 | 25.7941 | 25.7965
210 | feeder2_line34 | 2 | 354.6 | 88.1813 | 88.189 | 24.8678 | 24.87
210 | feeder2_line34 | 3 | 354.6 | 89.2731 | 89.2581 | 25.1757 | 25.1715
210 | feeder2_line35 | 1 | 99 | 3.0022e-07 | 7.6257e-07 | 3.0325e-07 | 7.7028e-07
210 | feeder2_line35 | 2 | 99 | 3.0034e-07 | 7.6303e-07 | 3.0338e-07 | 7.7074e-07
210 | feeder2_line35 | 3 | 99 | 0.27539 | 0.27538 | 0.27817 | 0.27816
210 | feeder2_line36 | 1 | 354.6 | 92.7875 | 92.7962 | 26.1668 | 26.1693
210 | feeder2_line36 | 2 | 354.6 | 88.1812 | 88.189 | 24.8678 | 24.87
210 | feeder2_line36 | 3 | 354.6 | 89.2731 | 89.2581 | 25.1757 | 25.1715
210 | feeder2_line37 | 1 | 99 | 2.4572 | 2.4575 | 2.482 | 2.4823
210 | feeder2_line37 | 2 | 99 | 3.0042e-07 | 8.4449e-07 | 3.0346e-07 | 8.5302e-07
210 | feeder2_line37 | 3 | 99 | 3.0028e-07 | 8.4388e-07 | 3.0331e-07 | 8.5241e-07
210 | feeder2_line38 | 1 | 99 | 3.2498e-07 | 7.7796e-07 | 3.2827e-07 | 7.8582e-07
210 | feeder2_line38 | 2 | 99 | 1.4155 | 1.4155 | 1.4298 | 1.4298
210 | feeder2_line38 | 3 | 99 | 3.2505e-07 | 7.7801e-07 | 3.2834e-07 | 7.8587e-07
210 | feeder2_line39 | 1 | 266.4 | 11.3631 | 11.3628 | 4.2654 | 4.2653
210 | feeder2_line39 | 2 | 266.4 | 2.1505 | 2.1508 | 0.80723 | 0.80734
210 | feeder2_line39 | 3 | 266.4 | 3.3736 | 3.3737 | 1.2664 | 1.2664
210 | feeder2_line40 | 1 | 354.6 | 92.8811 | 92.8897 | 26.1932 | 26.1956
210 | feeder2_line40 | 2 | 354.6 | 88.1813 | 88.189 | 24.8678 | 24.87
210 | feeder2_line40 | 3 | 354.6 | 89.2731 | 89.2581 | 25.1757 | 25.1715
210 | feeder2_line41 | 1 | 99 | 0.093536 | 0.09354 | 0.094481 | 0.094485
210 | feeder2_line41 | 2 | 99 | 4.9895e-08 | 7.3803e-07 | 5.0399e-08 | 7.4549e-07
210 | feeder2_line41 | 3 | 99 | 5.0194e-08 | 7.375e-07 | 5.0701e-08 | 7.4495e-07
210 | feeder2_line42 | 1 | 99 | 2.9992e-07 | 7.5082e-07 | 3.0295e-07 | 7.584e-07
210 | feeder2_line42 | 2 | 99 | 3.0012e-07 | 7.5149e-07 | 3.0316e-07 | 7.5908e-07
210 | feeder2_line42 | 3 | 99 | 1.2578 | 1.2578 | 1.2705 | 1.2705
210 | feeder2_line43 | 1 | 266.4 | 11.363 | 11.3628 | 4.2654 | 4.2653
210 | feeder2_line43 | 2 | 266.4 | 2.1506 | 2.1508 | 0.80727 | 0.80734
210 | feeder2_line43 | 3 | 266.4 | 2.1159 | 2.1159 | 0.79424 | 0.79426
210 | feeder2_line44 | 1 | 354.6 | 92.8811 | 92.8897 | 26.1932 | 26.1956
210 | feeder2_line44 | 2 | 354.6 | 88.1813 | 88.189 | 24.8678 | 24.87
210 | feeder2_line44 | 3 | 354.6 | 90.3099 | 90.2947 | 25.4681 | 25.4638
210 | feeder2_line45 | 1 | 99 | 5.0106e-08 | 5.8183e-07 | 5.0612e-08 | 5.877e-07
210 | feeder2_line45 | 2 | 99 | 4.9908e-08 | 5.8212e-07 | 5.0412e-08 | 5.88e-07
210 | feeder2_line45 | 3 | 99 | 1.586 | 1.586 | 1.602 | 1.602
210 | feeder2_line46 | 1 | 99 | 5.7481e-07 | 1.3611e-06 | 5.8062e-07 | 1.3748e-06
210 | feeder2_line46 | 2 | 99 | 5.7534e-07 | 1.3623e-06 | 5.8115e-07 | 1.3761e-06
210 | feeder2_line46 | 3 | 99 | 1.3143 | 1.3143 | 1.3276 | 1.3276
210 | feeder2_line47 | 1 | 266.4 | 11.363 | 11.3628 | 4.2654 | 4.2653
210 | feeder2_line47 | 2 | 266.4 | 2.1508 | 2.1508 | 0.80734 | 0.80734
210 | feeder2_line47 | 3 | 266.4 | 0.80372 | 0.80363 | 0.3017 | 0.30166
210 | feeder2_line48 | 1 | 99 | 0.13621 | 0.13621 | 0.13758 | 0.13759
210 | feeder2_line48 | 2 | 99 | 4.9818e-08 | 7.335e-07 | 5.0321e-08 | 7.4091e-07
210 | feeder2_line48 | 3 | 99 | 5.012e-08 | 7.3297e-07 | 5.0626e-08 | 7.4037e-07
210 | feeder2_line49 | 1 | 266.4 | 11.2298 | 11.2296 | 4.2154 | 4.2153
210 | feeder2_line49 | 2 | 266.4 | 2.1507 | 2.1508 | 0.80733 | 0.80734
210 | feeder2_line49 | 3 | 266.4 | 0.8037 | 0.80363 | 0.30169 | 0.30166
210 | feeder2_line50 | 1 | 99 | 5.7474e-07 | 1.2386e-06 | 5.8055e-07 | 1.2511e-06
210 | feeder2_line50 | 2 | 99 | 2.1238 | 2.1238 | 2.1452 | 2.1452
210 | feeder2_line50 | 3 | 99 | 5.7492e-07 | 1.2389e-06 | 5.8073e-07 | 1.2514e-06
210 | feeder2_line51 | 1 | 99 | 10.5735 | 10.5735 | 10.6803 | 10.6803
210 | feeder2_line51 | 2 | 99 | 5.7532e-07 | 1.3459e-06 | 5.8113e-07 | 1.3595e-06
210 | feeder2_line51 | 3 | 99 | 5.749e-07 | 1.345e-06 | 5.8071e-07 | 1.3586e-06
210 | feeder2_line52 | 1 | 266.4 | 0.65617 | 0.65608 | 0.24631 | 0.24628
210 | feeder2_line52 | 2 | 266.4 | 0.048849 | 0.048747 | 0.018337 | 0.018298
210 | feeder2_line52 | 3 | 266.4 | 0.80362 | 0.80363 | 0.30166 | 0.30166
210 | feeder2_line53 | 1 | 99 | 5.4972e-07 | 7.5592e-07 | 5.5527e-07 | 7.6356e-07
210 | feeder2_line53 | 2 | 99 | 0.048745 | 0.048746 | 0.049237 | 0.049239
210 | feeder2_line53 | 3 | 99 | 5.4986e-07 | 7.5614e-07 | 5.5541e-07 | 7.6378e-07
210 | feeder2_line54 | 1 | 266.4 | 0.65599 | 0.65608 | 0.24624 | 0.24628
210 | feeder2_line54 | 2 | 266.4 | 8.5798e-05 | 4.6417e-06 | 3.2206e-05 | 1.7424e-06
210 | feeder2_line54 | 3 | 266.4 | 0.80359 | 0.80363 | 0.30165 | 0.30166
210 | feeder2_line55 | 1 | 99 | 0.18119 | 0.1812 | 0.18302 | 0.18303
210 | feeder2_line55 | 2 | 99 | 4.9943e-08 | 7.3387e-07 | 5.0447e-08 | 7.4128e-07
210 | feeder2_line55 | 3 | 99 | 5.025e-08 | 7.3333e-07 | 5.0757e-08 | 7.4074e-07
210 | feeder2_line56 | 1 | 354.6 | 93.0623 | 93.0709 | 26.2443 | 26.2467
210 | feeder2_line56 | 2 | 354.6 | 88.1814 | 88.189 | 24.8678 | 24.87
210 | feeder2_line56 | 3 | 354.6 | 90.3099 | 90.2947 | 25.4681 | 25.4638
210 | feeder2_line57 | 1 | 99 | 7.5102e-07 | 1.5484e-06 | 7.5861e-07 | 1.564e-06
210 | feeder2_line57 | 2 | 99 | 7.4721e-07 | 1.55e-06 | 7.5476e-07 | 1.5656e-06
210 | feeder2_line57 | 3 | 99 | 0.80366 | 0.80363 | 0.81178 | 0.81175
210 | feeder2_line58 | 1 | 266.4 | 0.65605 | 0.65608 | 0.24627 | 0.24628
210 | feeder2_line58 | 2 | 266.4 | 1.9021e-05 | 2.6948e-06 | 7.14e-06 | 1.0116e-06
210 | feeder2_line58 | 3 | 266.4 | 1.9002e-05 | 2.6931e-06 | 7.133e-06 | 1.0109e-06
210 | feeder2_line59 | 1 | 99 | 5.0078e-08 | 5.3823e-07 | 5.0583e-08 | 5.4367e-07
210 | feeder2_line59 | 2 | 99 | 4.9819e-08 | 5.3877e-07 | 5.0322e-08 | 5.4421e-07
210 | feeder2_line59 | 3 | 99 | 0.76441 | 0.76438 | 0.77213 | 0.7721
210 | feeder2_line60 | 1 | 99 | 2.9989e-07 | 8.1343e-07 | 3.0292e-07 | 8.2165e-07
210 | feeder2_line60 | 2 | 99 | 3.0013e-07 | 8.1425e-07 | 3.0316e-07 | 8.2248e-07
210 | feeder2_line60 | 3 | 99 | 0.061607 | 0.061604 | 0.06223 | 0.062226
210 | feeder2_line61 | 1 | 266.4 | 0.19841 | 0.19859 | 0.074478 | 0.074546
210 | feeder2_line61 | 2 | 266.4 | 0.63851 | 0.63874 | 0.23968 | 0.23977
210 | feeder2_line61 | 3 | 266.4 | 0.38475 | 0.38487 | 0.14443 | 0.14447
210 | feeder2_line62 | 1 | 354.6 | 93.2606 | 93.2695 | 26.3002 | 26.3027
210 | feeder2_line62 | 2 | 354.6 | 88.818 | 88.8259 | 25.0474 | 25.0496
210 | feeder2_line62 | 3 | 354.6 | 90.6943 | 90.6793 | 25.5765 | 25.5723
210 | feeder2_line63 | 1 | 99 | 0.36008 | 0.36009 | 0.36372 | 0.36373
210 | feeder2_line63 | 2 | 99 | 5.7534e-07 | 1.2242e-06 | 5.8116e-07 | 1.2366e-06
210 | feeder2_line63 | 3 | 99 | 5.7492e-07 | 1.2233e-06 | 5.8072e-07 | 1.2357e-06
210 | feeder2_line64 | 1 | 99 | 0.296 | 0.296 | 0.29899 | 0.29899
210 | feeder2_line64 | 2 | 99 | 6.1699e-12 | 3.2248e-07 | 6.2322e-12 | 3.2574e-07
210 | feeder2_line64 | 3 | 99 | 9.3952e-12 | 3.2225e-07 | 9.4901e-12 | 3.255e-07
210 | feeder2_line65 | 1 | 99 | 5.0172e-08 | 6.4511e-07 | 5.0678e-08 | 6.5163e-07
210 | feeder2_line65 | 2 | 99 | 1.533 | 1.533 | 1.5485 | 1.5485
210 | feeder2_line65 | 3 | 99 | 5.0324e-08 | 6.4475e-07 | 5.0832e-08 | 6.5126e-07
210 | feeder2_line66 | 1 | 354.6 | 93.2606 | 93.2695 | 26.3002 | 26.3027
210 | feeder2_line66 | 2 | 354.6 | 89.7545 | 89.7625 | 25.3115 | 25.3137
210 | feeder2_line66 | 3 | 354.6 | 90.6943 | 90.6793 | 25.5765 | 25.5723
210 | feeder2_line67 | 1 | 99 | 2.5074e-08 | 3.6447e-07 | 2.5327e-08 | 3.6815e-07
210 | feeder2_line67 | 2 | 99 | 2.4982e-08 | 3.6457e-07 | 2.5235e-08 | 3.6825e-07
210 | feeder2_line67 | 3 | 99 | 0.093475 | 0.093467 | 0.094419 | 0.094412
210 | feeder2_line68 | 1 | 266.4 | 0.19845 | 0.19859 | 0.074493 | 0.074545
210 | feeder2_line68 | 2 | 266.4 | 0.63855 | 0.63874 | 0.2397 | 0.23977
210 | feeder2_line68 | 3 | 266.4 | 0.29138 | 0.29147 | 0.10938 | 0.10941
210 | feeder2_line69 | 1 | 99 | 1.561 | 1.5611 | 1.5768 | 1.5769
210 | feeder2_line69 | 2 | 99 | 2.5611e-06 | 6.6998e-07 | 2.587e-06 | 6.7675e-07
210 | feeder2_line69 | 3 | 99 | 2.5568e-06 | 6.6947e-07 | 2.5826e-06 | 6.7623e-07
210 | feeder2_line70 | 1 | 354.6 | 94.2573 | 94.2663 | 26.5813 | 26.5838
210 | feeder2_line70 | 2 | 354.6 | 89.7545 | 89.7625 | 25.3115 | 25.3137
210 | feeder2_line70 | 3 | 354.6 | 90.6942 | 90.6793 | 25.5765 | 25.5723
210 | feeder2_line71 | 1 | 99 | 5.019e-08 | 7.2003e-07 | 5.0697e-08 | 7.2731e-07
210 | feeder2_line71 | 2 | 99 | 1.4292 | 1.4292 | 1.4436 | 1.4436
210 | feeder2_line71 | 3 | 99 | 5.0353e-08 | 7.1957e-07 | 5.0861e-08 | 7.2684e-07
210 | feeder2_line72 | 1 | 354.6 | 94.2574 | 94.2663 | 26.5813 | 26.5838
210 | feeder2_line72 | 2 | 354.6 | 90.6802 | 90.6882 | 25.5725 | 25.5748
210 | feeder2_line72 | 3 | 354.6 | 90.6943 | 90.6793 | 25.5765 | 25.5723
210 | feeder2_line73 | 1 | 99 | 6.0168e-07 | 1.543e-06 | 6.0776e-07 | 1.5586e-06
210 | feeder2_line73 | 2 | 99 | 0.25783 | 0.25784 | 0.26044 | 0.26044
210 | feeder2_line73 | 3 | 99 | 6.0148e-07 | 1.5423e-06 | 6.0756e-07 | 1.5579e-06
210 | feeder2_line74 | 1 | 99 | 5.0155e-08 | 4.6022e-07 | 5.0661e-08 | 4.6487e-07
210 | feeder2_line74 | 2 | 99 | 0.29155 | 0.2916 | 0.2945 | 0.29455
210 | feeder2_line74 | 3 | 99 | 5.0286e-08 | 4.6001e-07 | 5.0794e-08 | 4.6465e-07
210 | feeder2_line75 | 1 | 266.4 | 0.19855 | 0.19859 | 0.074531 | 0.074545
210 | feeder2_line75 | 2 | 266.4 | 0.089366 | 0.089403 | 0.033546 | 0.03356
210 | feeder2_line75 | 3 | 266.4 | 0.29148 | 0.29147 | 0.10942 | 0.10941
210 | feeder2_line76 | 1 | 99 | 0.19858 | 0.19859 | 0.20059 | 0.20059
210 | feeder2_line76 | 2 | 99 | 8.5267e-07 | 1.5922e-06 | 8.6128e-07 | 1.6082e-06
210 | feeder2_line76 | 3 | 99 | 8.5194e-07 | 1.591e-06 | 8.6054e-07 | 1.6071e-06
210 | feeder2_line77 | 1 | 99 | 2.5075e-08 | 5.7834e-07 | 2.5328e-08 | 5.8418e-07
210 | feeder2_line77 | 2 | 99 | 2.4985e-08 | 5.785e-07 | 2.5237e-08 | 5.8434e-07
210 | feeder2_line77 | 3 | 99 | 0.29152 | 0.29147 | 0.29446 | 0.29441
210 | feeder2_line78 | 1 | 266.4 | 6.4749e-12 | 9.5918e-07 | 2.4305e-12 | 3.6005e-07
210 | feeder2_line78 | 2 | 266.4 | 0.089399 | 0.089403 | 0.033558 | 0.03356
210 | feeder2_line78 | 3 | 266.4 | 7.7289e-12 | 9.5882e-07 | 2.9012e-12 | 3.5992e-07
210 | feeder2_line79 | 1 | 354.6 | 0.64377 | 0.64335 | 0.18155 | 0.18143
210 | feeder2_line79 | 2 | 354.6 | 3.3338 | 3.3336 | 0.94015 | 0.94009
210 | feeder2_line79 | 3 | 354.6 | 7.5668 | 7.5664 | 2.1339 | 2.1338
210 | feeder2_line80 | 1 | 354.6 | 94.9011 | 94.9095 | 26.7629 | 26.7652
210 | feeder2_line80 | 2 | 354.6 | 92.9138 | 92.9212 | 26.2024 | 26.2045
210 | feeder2_line80 | 3 | 354.6 | 95.975 | 95.9593 | 27.0657 | 27.0613
210 | feeder2_line81 | 1 | 354.6 | 94.9011 | 94.9095 | 26.7628 | 26.7652
210 | feeder2_line81 | 2 | 354.6 | 92.9138 | 92.9212 | 26.2024 | 26.2045
210 | feeder2_line81 | 3 | 354.6 | 96.2255 | 96.2098 | 27.1364 | 27.1319
210 | feeder2_line82 | 1 | 354.6 | 3.5477e-11 | 7.3902e-07 | 1.0005e-11 | 2.0841e-07
210 | feeder2_line82 | 2 | 354.6 | 9.7455e-12 | 7.3897e-07 | 2.7483e-12 | 2.0839e-07
210 | feeder2_line82 | 3 | 354.6 | 0.25053 | 0.25052 | 0.070653 | 0.070649
210 | feeder2_line83 | 1 | 354.6 | 94.9012 | 94.9095 | 26.7629 | 26.7652
210 | feeder2_line83 | 2 | 354.6 | 93.7104 | 93.7177 | 26.4271 | 26.4291
210 | feeder2_line83 | 3 | 354.6 | 96.2257 | 96.2098 | 27.1364 | 27.1319
210 | feeder2_line84 | 1 | 354.6 | 7.2258e-12 | 1.3064e-06 | 2.0377e-12 | 3.6843e-07
210 | feeder2_line84 | 2 | 354.6 | 1.342 | 1.342 | 0.37846 | 0.37846
210 | feeder2_line84 | 3 | 354.6 | 8.684e-12 | 1.3056e-06 | 2.449e-12 | 3.6818e-07
210 | feeder2_line85 | 1 | 99 | 1.4173 | 1.4173 | 1.4316 | 1.4316
210 | feeder2_line85 | 2 | 99 | 5.0088e-08 | 4.6633e-07 | 5.0594e-08 | 4.7104e-07
210 | feeder2_line85 | 3 | 99 | 5.0424e-08 | 4.6597e-07 | 5.0933e-08 | 4.7067e-07
210 | feeder2_line86 | 1 | 354.6 | 95.8317 | 95.8399 | 27.0253 | 27.0276
210 | feeder2_line86 | 2 | 354.6 | 93.7106 | 93.7177 | 26.4271 | 26.4291
210 | feeder2_line86 | 3 | 354.6 | 96.2258 | 96.2098 | 27.1364 | 27.1319
210 | feeder2_line87 | 1 | 354.6 | 95.8319 | 95.8399 | 27.0253 | 27.0276
210 | feeder2_line87 | 2 | 354.6 | 94.3617 | 94.3688 | 26.6107 | 26.6128
210 | feeder2_line87 | 3 | 354.6 | 97.2115 | 97.1953 | 27.4144 | 27.4098
210 | feeder2_line88 | 1 | 354.6 | 0.00011513 | 3.3873e-06 | 3.2468e-05 | 9.5524e-07
210 | feeder2_line88 | 2 | 354.6 | 1.0589 | 1.059 | 0.29862 | 0.29864
210 | feeder2_line88 | 3 | 354.6 | 1.4515 | 1.4514 | 0.40934 | 0.40931
210 | feeder2_line89 | 1 | 354.6 | 95.8296 | 95.8399 | 27.0247 | 27.0276
210 | feeder2_line89 | 2 | 354.6 | 95.3724 | 95.3819 | 26.8958 | 26.8985
210 | feeder2_line89 | 3 | 354.6 | 97.2092 | 97.1953 | 27.4138 | 27.4098
210 | feeder2_line90 | 1 | 354.6 | 0.00072938 | 2.0442e-06 | 0.00020569 | 5.7648e-07
210 | feeder2_line90 | 2 | 354.6 | 1.468 | 1.4681 | 0.41399 | 0.414
210 | feeder2_line90 | 3 | 354.6 | 0.00072795 | 2.0435e-06 | 0.00020529 | 5.763e-07
210 | feeder2_line91 | 1 | 354.6 | 95.8295 | 95.8399 | 27.0247 | 27.0276
210 | feeder2_line91 | 2 | 354.6 | 95.3723 | 95.3819 | 26.8958 | 26.8985
210 | feeder2_line91 | 3 | 354.6 | 97.2703 | 97.2565 | 27.431 | 27.4271
210 | feeder2_line92 | 1 | 354.6 | 6.2033e-12 | 1.0317e-06 | 1.7494e-12 | 2.9095e-07
210 | feeder2_line92 | 2 | 354.6 | 1.8605e-11 | 1.0316e-06 | 5.2468e-12 | 2.9091e-07
210 | feeder2_line92 | 3 | 354.6 | 0.061373 | 0.061366 | 0.017308 | 0.017306
210 | feeder2_line93 | 1 | 99 | 2.5142e-08 | 3.4439e-07 | 2.5396e-08 | 3.4787e-07
210 | feeder2_line93 | 2 | 99 | 1.3424 | 1.3424 | 1.3559 | 1.3559
210 | feeder2_line93 | 3 | 99 | 2.5234e-08 | 3.4411e-07 | 2.5489e-08 | 3.4759e-07
210 | feeder2_line94 | 1 | 354.6 | 2.514e-06 | 1.6767e-06 | 7.0898e-07 | 4.7283e-07
210 | feeder2_line94 | 2 | 354.6 | 0.19459 | 0.19466 | 0.054877 | 0.054895
210 | feeder2_line94 | 3 | 354.6 | 2.5234e-06 | 1.6755e-06 | 7.1161e-07 | 4.7251e-07
210 | feeder2_line95 | 1 | 99 | 3.5904e-06 | 2.6267e-06 | 3.6267e-06 | 2.6532e-06
210 | feeder2_line95 | 2 | 99 | 1.0589 | 1.059 | 1.0696 | 1.0697
210 | feeder2_line95 | 3 | 99 | 3.5877e-06 | 2.6246e-06 | 3.6239e-06 | 2.6511e-06
210 | feeder2_line96 | 1 | 354.6 | 0.00012191 | 6.2623e-07 | 3.4381e-05 | 1.766e-07
210 | feeder2_line96 | 2 | 354.6 | 0.00012191 | 6.263e-07 | 3.438e-05 | 1.7662e-07
210 | feeder2_line96 | 3 | 354.6 | 1.4515 | 1.4514 | 0.40932 | 0.40931
210 | feeder2_line97 | 1 | 354.6 | 95.9817 | 95.9919 | 27.0676 | 27.0705
210 | feeder2_line97 | 2 | 354.6 | 95.3725 | 95.3819 | 26.8958 | 26.8985
210 | feeder2_line97 | 3 | 354.6 | 97.2705 | 97.2565 | 27.431 | 27.4271
210 | feeder2_line98 | 1 | 354.6 | 0.15605 | 0.15433 | 0.044008 | 0.043521
210 | feeder2_line98 | 2 | 354.6 | 0.0017142 | 6.2211e-07 | 0.00048343 | 1.7544e-07
210 | feeder2_line98 | 3 | 354.6 | 0.0017096 | 6.2688e-07 | 0.00048211 | 1.7679e-07
210 | feeder2_line99 | 1 | 99 | 2.5127e-08 | 4.5014e-07 | 2.538e-08 | 4.5469e-07
210 | feeder2_line99 | 2 | 99 | 2.5061e-08 | 4.5012e-07 | 2.5315e-08 | 4.5467e-07
210 | feeder2_line99 | 3 | 99 | 1.4515 | 1.4514 | 1.4661 | 1.4661
210 | feeder2_line100 | 1 | 99 | 0.15434 | 0.15433 | 0.1559 | 0.15589
210 | feeder2_line100 | 2 | 99 | 2.5071e-08 | 6.183e-07 | 2.5324e-08 | 6.2455e-07
210 | feeder2_line100 | 3 | 99 | 2.5242e-08 | 6.1786e-07 | 2.5497e-08 | 6.241e-07
210 | feeder2_line101 | 1 | 354.6 | 0.19501 | 0.1946 | 0.054993 | 0.054878
210 | feeder2_line101 | 2 | 354.6 | 3.3338 | 3.3336 | 0.94014 | 0.94009
210 | feeder2_line101 | 3 | 354.6 | 7.5668 | 7.5664 | 2.1339 | 2.1338
210 | feeder2_line102 | 1 | 99 | 0.44876 | 0.44876 | 0.45329 | 0.4533
210 | feeder2_line102 | 2 | 99 | 2.3507e-06 | 8.8353e-07 | 2.3744e-06 | 8.9245e-07
210 | feeder2_line102 | 3 | 99 | 2.3445e-06 | 8.827e-07 | 2.3682e-06 | 8.9162e-07
210 | feeder2_line103 | 1 | 99 | 5.5259e-07 | 8.0865e-07 | 5.5817e-07 | 8.1682e-07
210 | feeder2_line103 | 2 | 99 | 0.096198 | 0.096203 | 0.09717 | 0.097175
210 | feeder2_line103 | 3 | 99 | 5.5196e-07 | 8.0791e-07 | 5.5753e-07 | 8.1607e-07
210 | feeder2_line104 | 1 | 354.6 | 0.1949 | 0.1946 | 0.054965 | 0.054878
210 | feeder2_line104 | 2 | 354.6 | 3.277 | 3.2768 | 0.92413 | 0.92408
210 | feeder2_line104 | 3 | 354.6 | 7.5667 | 7.5664 | 2.1339 | 2.1338
210 | feeder2_line105 | 1 | 99 | 2.5621e-06 | 7.4407e-07 | 2.588e-06 | 7.5158e-07
210 | feeder2_line105 | 2 | 99 | 2.5634e-06 | 7.4411e-07 | 2.5893e-06 | 7.5162e-07
210 | feeder2_line105 | 3 | 99 | 1.4168 | 1.4167 | 1.4311 | 1.431
210 | feeder2_line106 | 1 | 354.6 | 0.19485 | 0.1946 | 0.054949 | 0.054878
210 | feeder2_line106 | 2 | 354.6 | 3.2769 | 3.2768 | 0.92412 | 0.92408
210 | feeder2_line106 | 3 | 354.6 | 6.1551 | 6.1549 | 1.7358 | 1.7357
210 | feeder2_line107 | 1 | 99 | 3.265e-07 | 9.0676e-07 | 3.298e-07 | 9.1592e-07
210 | feeder2_line107 | 2 | 99 | 2.2063 | 2.2063 | 2.2285 | 2.2285
210 | feeder2_line107 | 3 | 99 | 3.2636e-07 | 9.0584e-07 | 3.2966e-07 | 9.1499e-07
210 | feeder2_line108 | 1 | 354.6 | 0.19484 | 0.1946 | 0.054946 | 0.054878
210 | feeder2_line108 | 2 | 354.6 | 1.1238 | 1.1236 | 0.31692 | 0.31686
210 | feeder2_line108 | 3 | 354.6 | 6.1551 | 6.1549 | 1.7358 | 1.7357
210 | feeder2_line109 | 1 | 354.6 | 96.2163 | 96.2253 | 27.1338 | 27.1363
210 | feeder2_line109 | 2 | 354.6 | 95.3737 | 95.3819 | 26.8961 | 26.8985
210 | feeder2_line109 | 3 | 354.6 | 97.2717 | 97.2565 | 27.4314 | 27.4271
210 | feeder2_line110 | 1 | 99 | 0.23615 | 0.23536 | 0.23854 | 0.23774
210 | feeder2_line110 | 2 | 99 | 0.0008105 | 9.1444e-07 | 0.00081869 | 9.2368e-07
210 | feeder2_line110 | 3 | 99 | 0.00080894 | 9.1478e-07 | 0.00081711 | 9.2402e-07
210 | feeder2_line111 | 1 | 99 | 2.5128e-08 | 3.8445e-07 | 2.5382e-08 | 3.8834e-07
210 | feeder2_line111 | 2 | 99 | 1.0353 | 1.0353 | 1.0458 | 1.0458
210 | feeder2_line111 | 3 | 99 | 2.5222e-08 | 3.8415e-07 | 2.5477e-08 | 3.8803e-07
210 | feeder2_line112 | 1 | 99 | 3.2682e-07 | 9.2386e-07 | 3.3012e-07 | 9.3319e-07
210 | feeder2_line112 | 2 | 99 | 0.040587 | 0.040744 | 0.040997 | 0.041156
210 | feeder2_line112 | 3 | 99 | 3.2673e-07 | 9.2313e-07 | 3.3003e-07 | 9.3245e-07
210 | feeder2_line113 | 1 | 99 | 0.12796 | 0.12797 | 0.12926 | 0.12926
210 | feeder2_line113 | 2 | 99 | 3.271e-07 | 9.1197e-07 | 3.3041e-07 | 9.2118e-07
210 | feeder2_line113 | 3 | 99 | 3.2715e-07 | 9.1133e-07 | 3.3045e-07 | 9.2054e-07
210 | feeder2_line114 | 1 | 99 | 0.096231 | 0.096236 | 0.097203 | 0.097208
210 | feeder2_line114 | 2 | 99 | 2.5023e-08 | 4.3934e-07 | 2.5275e-08 | 4.4378e-07
210 | feeder2_line114 | 3 | 99 | 2.5201e-08 | 4.3893e-07 | 2.5456e-08 | 4.4336e-07
210 | feeder2_line115 | 1 | 99 | 2.5109e-08 | 5.6586e-07 | 2.5363e-08 | 5.7158e-07
210 | feeder2_line115 | 2 | 99 | 0.33267 | 0.33268 | 0.33603 | 0.33604
210 | feeder2_line115 | 3 | 99 | 2.5208e-08 | 5.6525e-07 | 2.5462e-08 | 5.7096e-07
210 | feeder2_line116 | 1 | 354.6 | 0.19485 | 0.1946 | 0.054948 | 0.054878
210 | feeder2_line116 | 2 | 354.6 | 0.85925 | 0.85907 | 0.24232 | 0.24226
210 | feeder2_line116 | 3 | 354.6 | 6.1552 | 6.1549 | 1.7358 | 1.7357
210 | feeder2_line117 | 1 | 99 | 5.0344e-08 | 6.4776e-07 | 5.0852e-08 | 6.543e-07
210 | feeder2_line117 | 2 | 99 | 1.3177 | 1.3178 | 1.331 | 1.3311
210 | feeder2_line117 | 3 | 99 | 5.0535e-08 | 6.4725e-07 | 5.1046e-08 | 6.5379e-07
210 | feeder2_line118 | 1 | 354.6 | 96.2163 | 96.2253 | 27.1338 | 27.1363
210 | feeder2_line118 | 2 | 354.6 | 96.2123 | 96.2205 | 27.1326 | 27.1349
210 | feeder2_line118 | 3 | 354.6 | 97.2717 | 97.2565 | 27.4314 | 27.4271
210 | feeder2_line119 | 1 | 99 | 2.5104e-08 | 6.0888e-07 | 2.5358e-08 | 6.1503e-07
210 | feeder2_line119 | 2 | 99 | 2.5008e-08 | 6.0894e-07 | 2.5261e-08 | 6.1509e-07
210 | feeder2_line119 | 3 | 99 | 1.7291 | 1.7291 | 1.7466 | 1.7466
210 | feeder2_line120 | 1 | 354.6 | 0.19485 | 0.1946 | 0.054949 | 0.054878
210 | feeder2_line120 | 2 | 354.6 | 0.85925 | 0.85907 | 0.24231 | 0.24226
210 | feeder2_line120 | 3 | 354.6 | 4.432 | 4.4318 | 1.2499 | 1.2498
210 | feeder2_line121 | 1 | 99 | 3.265e-07 | 9.4287e-07 | 3.2979e-07 | 9.5239e-07
210 | feeder2_line121 | 2 | 99 | 0.7433 | 0.74328 | 0.7508 | 0.75079
210 | feeder2_line121 | 3 | 99 | 3.2631e-07 | 9.4174e-07 | 3.2961e-07 | 9.5125e-07
210 | feeder2_line122 | 1 | 354.6 | 0.19483 | 0.1946 | 0.054945 | 0.054878
210 | feeder2_line122 | 2 | 354.6 | 0.17938 | 0.17915 | 0.050587 | 0.050521
210 | feeder2_line122 | 3 | 354.6 | 4.432 | 4.4318 | 1.2499 | 1.2498
210 | feeder2_line123 | 1 | 99 | 5.7769e-07 | 9.7703e-07 | 5.8352e-07 | 9.869e-07
210 | feeder2_line123 | 2 | 99 | 5.7778e-07 | 9.7718e-07 | 5.8362e-07 | 9.8705e-07
210 | feeder2_line123 | 3 | 99 | 1.2653 | 1.2653 | 1.2781 | 1.2781
210 | feeder2_line124 | 1 | 354.6 | 0.19474 | 0.1946 | 0.054919 | 0.054878
210 | feeder2_line124 | 2 | 354.6 | 0.17929 | 0.17915 | 0.050561 | 0.050521
210 | feeder2_line124 | 3 | 354.6 | 3.1734 | 3.1732 | 0.89492 | 0.89486
210 | feeder2_line125 | 1 | 99 | 5.7768e-07 | 9.0825e-07 | 5.8352e-07 | 9.1742e-07
210 | feeder2_line125 | 2 | 99 | 5.7779e-07 | 9.0839e-07 | 5.8362e-07 | 9.1757e-07
210 | feeder2_line125 | 3 | 99 | 0.15473 | 0.15466 | 0.15629 | 0.15622
210 | feeder2_line126 | 1 | 354.6 | 0.1949 | 0.1946 | 0.054964 | 0.054878
210 | feeder2_line126 | 2 | 354.6 | 0.17945 | 0.17915 | 0.050606 | 0.050521
210 | feeder2_line126 | 3 | 354.6 | 3.0854 | 3.0851 | 0.87009 | 0.87002
210 | feeder2_line127 | 1 | 99 | 5.7768e-07 | 1.0873e-06 | 5.8352e-07 | 1.0983e-06
210 | feeder2_line127 | 2 | 99 | 5.7778e-07 | 1.0875e-06 | 5.8362e-07 | 1.0985e-06
210 | feeder2_line127 | 3 | 99 | 1.5589 | 1.5589 | 1.5746 | 1.5747
210 | feeder2_line128 | 1 | 354.6 | 0.19482 | 0.1946 | 0.05494 | 0.054878
210 | feeder2_line128 | 2 | 354.6 | 0.17937 | 0.17915 | 0.050582 | 0.050521
210 | feeder2_line128 | 3 | 354.6 | 1.5296 | 1.5294 | 0.43137 | 0.4313
210 | feeder2_line129 | 1 | 99 | 5.5258e-07 | 8.8166e-07 | 5.5816e-07 | 8.9056e-07
210 | feeder2_line129 | 2 | 99 | 0.17914 | 0.17915 | 0.18095 | 0.18096
210 | feeder2_line129 | 3 | 99 | 5.5174e-07 | 8.8055e-07 | 5.5731e-07 | 8.8944e-07
210 | feeder2_line130 | 1 | 354.6 | 0.19483 | 0.1946 | 0.054945 | 0.054878
210 | feeder2_line130 | 2 | 354.6 | 0.00031035 | 4.6662e-06 | 8.7521e-05 | 1.3159e-06
210 | feeder2_line130 | 3 | 354.6 | 1.5297 | 1.5294 | 0.43138 | 0.4313
210 | feeder2_line131 | 1 | 99 | 5.7768e-07 | 9.7717e-07 | 5.8352e-07 | 9.8704e-07
210 | feeder2_line131 | 2 | 99 | 5.7779e-07 | 9.7735e-07 | 5.8363e-07 | 9.8722e-07
210 | feeder2_line131 | 3 | 99 | 0.16254 | 0.16254 | 0.16419 | 0.16418
210 | feeder2_line132 | 1 | 354.6 | 0.19467 | 0.1946 | 0.054898 | 0.054878
210 | feeder2_line132 | 2 | 354.6 | 0.00012651 | 2.9338e-06 | 3.5678e-05 | 8.2735e-07
210 | feeder2_line132 | 3 | 354.6 | 1.4163 | 1.4161 | 0.3994 | 0.39936
210 | feeder2_line133 | 1 | 99 | 0.19459 | 0.1946 | 0.19656 | 0.19656
210 | feeder2_line133 | 2 | 99 | 3.014e-07 | 9.8515e-07 | 3.0444e-07 | 9.951e-07
210 | feeder2_line133 | 3 | 99 | 3.0108e-07 | 9.8373e-07 | 3.0412e-07 | 9.9367e-07
210 | feeder2_line134 | 1 | 354.6 | 7.9626e-12 | 1.7962e-06 | 2.2455e-12 | 5.0654e-07
210 | feeder2_line134 | 2 | 354.6 | 2.4083e-12 | 1.7964e-06 | 6.7915e-13 | 5.0659e-07
210 | feeder2_line134 | 3 | 354.6 | 1.4161 | 1.4161 | 0.39936 | 0.39936
210 | feeder2_line135 | 1 | 99 | 1.4307 | 1.4308 | 1.4452 | 1.4452
210 | feeder2_line135 | 2 | 99 | 5.0237e-08 | 5.9048e-07 | 5.0745e-08 | 5.9644e-07
210 | feeder2_line135 | 3 | 99 | 5.0565e-08 | 5.9009e-07 | 5.1076e-08 | 5.9605e-07
210 | feeder2_line136 | 1 | 354.6 | 97.2303 | 97.2394 | 27.4197 | 27.4223
210 | feeder2_line136 | 2 | 354.6 | 96.2123 | 96.2205 | 27.1326 | 27.1349
210 | feeder2_line136 | 3 | 354.6 | 97.2717 | 97.2565 | 27.4314 | 27.4271
210 | feeder2_line137 | 1 | 99 | 1.1935 | 1.1935 | 1.2055 | 1.2056
210 | feeder2_line137 | 2 | 99 | 8.5706e-07 | 1.5906e-06 | 8.6572e-07 | 1.6066e-06
210 | feeder2_line137 | 3 | 99 | 8.5639e-07 | 1.5895e-06 | 8.6504e-07 | 1.6056e-06
210 | feeder2_line138 | 1 | 354.6 | 97.9732 | 97.9823 | 27.6292 | 27.6318
210 | feeder2_line138 | 2 | 354.6 | 96.2124 | 96.2205 | 27.1326 | 27.1349
210 | feeder2_line138 | 3 | 354.6 | 97.2717 | 97.2565 | 27.4314 | 27.4271
210 | feeder2_line139 | 1 | 99 | 5.0399e-08 | 4.9573e-07 | 5.0908e-08 | 5.0074e-07
210 | feeder2_line139 | 2 | 99 | 5.0252e-08 | 4.9566e-07 | 5.076e-08 | 5.0067e-07
210 | feeder2_line139 | 3 | 99 | 2.6291 | 2.6287 | 2.6557 | 2.6553
210 | feeder2_line140 | 1 | 354.6 | 97.9733 | 97.9823 | 27.6293 | 27.6318
210 | feeder2_line140 | 2 | 354.6 | 96.2125 | 96.2205 | 27.1327 | 27.1349
210 | feeder2_line140 | 3 | 354.6 | 98.884 | 98.8676 | 27.8861 | 27.8814
210 | feeder2_line141 | 1 | 99 | 2.5475e-06 | 4.9045e-07 | 2.5732e-06 | 4.9541e-07
210 | feeder2_line141 | 2 | 99 | 1.2613 | 1.2613 | 1.274 | 1.274
210 | feeder2_line141 | 3 | 99 | 2.5438e-06 | 4.9006e-07 | 2.5695e-06 | 4.9501e-07
210 | feeder2_line142 | 1 | 354.6 | 97.9731 | 97.9823 | 27.6292 | 27.6318
210 | feeder2_line142 | 2 | 354.6 | 97.0485 | 97.0567 | 27.3685 | 27.3708
210 | feeder2_line142 | 3 | 354.6 | 98.8838 | 98.8676 | 27.886 | 27.8814
210 | feeder2_line143 | 1 | 99 | 8.5755e-07 | 1.7429e-06 | 8.6622e-07 | 1.7605e-06
210 | feeder2_line143 | 2 | 99 | 2.2092 | 2.2092 | 2.2315 | 2.2315
210 | feeder2_line143 | 3 | 99 | 8.5683e-07 | 1.7415e-06 | 8.6549e-07 | 1.7591e-06
210 | feeder2_line144 | 1 | 354.6 | 97.973 | 97.9823 | 27.6291 | 27.6318
210 | feeder2_line144 | 2 | 354.6 | 98.3995 | 98.4078 | 27.7494 | 27.7518
210 | feeder2_line144 | 3 | 354.6 | 98.8836 | 98.8676 | 27.886 | 27.8814
210 | feeder2_line145 | 1 | 99 | 2.5204e-08 | 4.8874e-07 | 2.5459e-08 | 4.9368e-07
210 | feeder2_line145 | 2 | 99 | 0.25082 | 0.25083 | 0.25336 | 0.25336
210 | feeder2_line145 | 3 | 99 | 2.5303e-08 | 4.8835e-07 | 2.5558e-08 | 4.9329e-07
210 | feeder2_line146 | 1 | 354.6 | 97.9728 | 97.9823 | 27.6291 | 27.6318
210 | feeder2_line146 | 2 | 354.6 | 98.65 | 98.6585 | 27.8201 | 27.8225
210 | feeder2_line146 | 3 | 354.6 | 98.8835 | 98.8676 | 27.8859 | 27.8814
210 | feeder2_line147 | 1 | 99 | 0.10726 | 0.10727 | 0.10835 | 0.10835
210 | feeder2_line147 | 2 | 99 | 1.1603e-06 | 2.2541e-06 | 1.172e-06 | 2.2769e-06
210 | feeder2_line147 | 3 | 99 | 1.1595e-06 | 2.2527e-06 | 1.1713e-06 | 2.2754e-06
210 | feeder2_line148 | 1 | 99 | 0.22049 | 0.2205 | 0.22271 | 0.22272
210 | feeder2_line148 | 2 | 99 | 6.0529e-07 | 1.5104e-06 | 6.114e-07 | 1.5257e-06
210 | feeder2_line148 | 3 | 99 | 6.0508e-07 | 1.5095e-06 | 6.1119e-07 | 1.5247e-06
210 | feeder2_line149 | 1 | 354.6 | 98.299 | 98.3083 | 27.7211 | 27.7237
210 | feeder2_line149 | 2 | 354.6 | 98.6502 | 98.6585 | 27.8201 | 27.8225
210 | feeder2_line149 | 3 | 354.6 | 98.8836 | 98.8676 | 27.886 | 27.8814
210 | feeder2_line150 | 1 | 354.6 | 98.2991 | 98.3083 | 27.7211 | 27.7237
210 | feeder2_line150 | 2 | 354.6 | 98.8333 | 98.8415 | 27.8718 | 27.8741
210 | feeder2_line150 | 3 | 354.6 | 98.8837 | 98.8676 | 27.886 | 27.8814
210 | feeder2_line151 | 1 | 99 | 9.849e-06 | 1.7948e-06 | 9.9485e-06 | 1.8129e-06
210 | feeder2_line151 | 2 | 99 | 0.18473 | 0.18475 | 0.18659 | 0.18662
210 | feeder2_line151 | 3 | 99 | 9.8318e-06 | 1.7934e-06 | 9.9311e-06 | 1.8115e-06
210 | feeder2_line152 | 1 | 354.6 | 8.0354e-12 | 1.1964e-06 | 2.266e-12 | 3.3738e-07
210 | feeder2_line152 | 2 | 354.6 | 2.171e-11 | 1.1961e-06 | 6.1225e-12 | 3.3731e-07
210 | feeder2_line152 | 3 | 354.6 | 0.076343 | 0.076331 | 0.021529 | 0.021526
210 | feeder2_line153 | 1 | 99 | 0.74449 | 0.74448 | 0.75201 | 0.752
210 | feeder2_line153 | 2 | 99 | 5.0336e-08 | 5.9849e-07 | 5.0845e-08 | 6.0453e-07
210 | feeder2_line153 | 3 | 99 | 5.0661e-08 | 5.9812e-07 | 5.1173e-08 | 6.0416e-07
210 | feeder2_line154 | 1 | 99 | 5.8082e-07 | 8.9071e-07 | 5.8669e-07 | 8.9971e-07
210 | feeder2_line154 | 2 | 99 | 5.8075e-07 | 8.9058e-07 | 5.8661e-07 | 8.9958e-07
210 | feeder2_line154 | 3 | 99 | 0.040465 | 0.040381 | 0.040873 | 0.040789
210 | feeder2_line155 | 1 | 99 | 98.7585 | 98.7678 | 99.756 | 99.7655
210 | feeder2_line155 | 2 | 99 | 98.8332 | 98.8415 | 99.8315 | 99.8399
210 | feeder2_line155 | 3 | 99 | 99 | 98.9839 | 100 | 99.9837
210 | feeder2_line156 | 1 | 99 | 6.0577e-07 | 1.172e-06 | 6.1189e-07 | 1.1838e-06
210 | feeder2_line156 | 2 | 99 | 0.095947 | 0.095954 | 0.096916 | 0.096923
210 | feeder2_line156 | 3 | 99 | 6.0542e-07 | 1.1711e-06 | 6.1153e-07 | 1.1829e-06
210 | feeder2_line157 | 1 | 99 | 2.5229e-08 | 2.5444e-07 | 2.5484e-08 | 2.5701e-07
210 | feeder2_line157 | 2 | 99 | 0.088945 | 0.088952 | 0.089843 | 0.08985
210 | feeder2_line157 | 3 | 99 | 2.532e-08 | 2.5423e-07 | 2.5575e-08 | 2.568e-07
240 | feeder2_line1 | 1 | 354.6 | 99.9954 | 99.9851 | 28.1995 | 28.1966
240 | feeder2_line1 | 2 | 354.6 | 106.6789 | 106.6659 | 30.0843 | 30.0806
240 | feeder2_line1 | 3 | 354.6 | 106.7124 | 106.7071 | 30.0938 | 30.0923
240 | feeder2_line2 | 1 | 354.6 | 99.9466 | 99.9362 | 28.1857 | 28.1828
240 | feeder2_line2 | 2 | 354.6 | 106.679 | 106.6659 | 30.0843 | 30.0806
240 | feeder2_line2 | 3 | 354.6 | 106.7125 | 106.7072 | 30.0938 | 30.0923
240 | feeder2_line3 | 1 | 80.1 | 0.33896 | 0.33894 | 0.42317 | 0.42315
240 | feeder2_line3 | 2 | 80.1 | 5.6735e-07 | 1.0484e-06 | 7.083e-07 | 1.3089e-06
240 | feeder2_line3 | 3 | 80.1 | 5.6718e-07 | 1.0481e-06 | 7.0809e-07 | 1.3085e-06
240 | feeder2_line4 | 1 | 354.6 | 99.9465 | 99.9362 | 28.1857 | 28.1828
240 | feeder2_line4 | 2 | 354.6 | 106.6553 | 106.6422 | 30.0776 | 30.0739
240 | feeder2_line4 | 3 | 354.6 | 106.7125 | 106.7072 | 30.0938 | 30.0923
240 | feeder2_line5 | 1 | 80.1 | 5.6723e-07 | 9.8977e-07 | 7.0815e-07 | 1.2357e-06
240 | feeder2_line5 | 2 | 80.1 | 0.27903 | 0.27903 | 0.34835 | 0.34836
240 | feeder2_line5 | 3 | 80.1 | 5.6713e-07 | 9.8959e-07 | 7.0802e-07 | 1.2354e-06
240 | feeder2_line6 | 1 | 80.1 | 5.6714e-07 | 1.1642e-06 | 7.0804e-07 | 1.4534e-06
240 | feeder2_line6 | 2 | 80.1 | 5.672e-07 | 1.1643e-06 | 7.0812e-07 | 1.4535e-06
240 | feeder2_line6 | 3 | 80.1 | 2.3265 | 2.3265 | 2.9045 | 2.9045
240 | feeder2_line7 | 1 | 354.6 | 99.9465 | 99.9362 | 28.1857 | 28.1828
240 | feeder2_line7 | 2 | 354.6 | 106.6553 | 106.6422 | 30.0776 | 30.0739
240 | feeder2_line7 | 3 | 354.6 | 104.7174 | 104.712 | 29.5311 | 29.5296
240 | feeder2_line8 | 1 | 80.1 | 0.073328 | 0.073328 | 0.091545 | 0.091546
240 | feeder2_line8 | 2 | 80.1 | 5.6697e-07 | 1.1222e-06 | 7.0783e-07 | 1.401e-06
240 | feeder2_line8 | 3 | 80.1 | 5.6677e-07 | 1.1218e-06 | 7.0758e-07 | 1.4005e-06
240 | feeder2_line9 | 1 | 354.6 | 99.941 | 99.9308 | 28.1841 | 28.1813
240 | feeder2_line9 | 2 | 354.6 | 106.6551 | 106.6422 | 30.0776 | 30.0739
240 | feeder2_line9 | 3 | 354.6 | 104.7173 | 104.712 | 29.5311 | 29.5296
240 | feeder2_line10 | 1 | 80.1 | 8.3793e-07 | 1.4814e-06 | 1.0461e-06 | 1.8494e-06
240 | feeder2_line10 | 2 | 80.1 | 0.073296 | 0.073298 | 0.091506 | 0.091508
240 | feeder2_line10 | 3 | 80.1 | 8.3777e-07 | 1.4811e-06 | 1.0459e-06 | 1.8491e-06
240 | feeder2_line11 | 1 | 354.6 | 99.9411 | 99.9308 | 28.1842 | 28.1813
240 | feeder2_line11 | 2 | 354.6 | 106.6536 | 106.6405 | 30.0772 | 30.0735
240 | feeder2_line11 | 3 | 354.6 | 104.7174 | 104.712 | 29.5311 | 29.5296
240 | feeder2_line12 | 1 | 80.1 | 5.4208e-07 | 9.8243e-07 | 6.7675e-07 | 1.2265e-06
240 | feeder2_line12 | 2 | 80.1 | 5.4224e-07 | 9.8261e-07 | 6.7695e-07 | 1.2267e-06
240 | feeder2_line12 | 3 | 80.1 | 0.9585 | 0.95852 | 1.1966 | 1.1967
240 | feeder2_line13 | 1 | 354.6 | 99.9412 | 99.9308 | 28.1842 | 28.1813
240 | feeder2_line13 | 2 | 354.6 | 106.6537 | 106.6405 | 30.0772 | 30.0735
240 | feeder2_line13 | 3 | 354.6 | 103.9131 | 103.9075 | 29.3043 | 29.3027
240 | feeder2_line14 | 1 | 80.1 | 0.2749 | 0.2749 | 0.3432 | 0.3432
240 | feeder2_line14 | 2 | 80.1 | 2.9568e-07 | 6.4065e-07 | 3.6913e-07 | 7.9981e-07
240 | feeder2_line14 | 3 | 80.1 | 2.956e-07 | 6.4041e-07 | 3.6904e-07 | 7.9951e-07
240 | feeder2_line15 | 1 | 354.6 | 99.904 | 99.8935 | 28.1737 | 28.1708
240 | feeder2_line15 | 2 | 354.6 | 106.6537 | 106.6405 | 30.0772 | 30.0735
240 | feeder2_line15 | 3 | 354.6 | 103.913 | 103.9075 | 29.3043 | 29.3027
240 | feeder2_line16 | 1 | 80.1 | 5.6649e-07 | 1.0206e-06 | 7.0723e-07 | 1.2741e-06
240 | feeder2_line16 | 2 | 80.1 | 0.25336 | 0.25336 | 0.31631 | 0.31631
240 | feeder2_line16 | 3 | 80.1 | 5.6639e-07 | 1.0204e-06 | 7.0711e-07 | 1.2739e-06
240 | feeder2_line17 | 1 | 354.6 | 99.904 | 99.8935 | 28.1737 | 28.1708
240 | feeder2_line17 | 2 | 354.6 | 106.6286 | 106.6154 | 30.0701 | 30.0664
240 | feeder2_line17 | 3 | 354.6 | 103.9131 | 103.9075 | 29.3043 | 29.3027
240 | feeder2_line18 | 1 | 80.1 | 5.4122e-07 | 7.2969e-07 | 6.7568e-07 | 9.1097e-07
240 | feeder2_line18 | 2 | 80.1 | 5.4145e-07 | 7.299e-07 | 6.7597e-07 | 9.1124e-07
240 | feeder2_line18 | 3 | 80.1 | 0.48891 | 0.4889 | 0.61038 | 0.61036
240 | feeder2_line19 | 1 | 354.6 | 99.904 | 99.8935 | 28.1737 | 28.1708
240 | feeder2_line19 | 2 | 354.6 | 106.6286 | 106.6154 | 30.0701 | 30.0664
240 | feeder2_line19 | 3 | 354.6 | 103.868 | 103.8624 | 29.2916 | 29.29
240 | feeder2_line20 | 1 | 99 | 5.4098e-07 | 8.7447e-07 | 5.4645e-07 | 8.833e-07
240 | feeder2_line20 | 2 | 99 | 5.4124e-07 | 8.7476e-07 | 5.4671e-07 | 8.8359e-07
240 | feeder2_line20 | 3 | 99 | 0.3555 | 0.35548 | 0.35909 | 0.35907
240 | feeder2_line21 | 1 | 354.6 | 99.904 | 99.8935 | 28.1737 | 28.1708
240 | feeder2_line21 | 2 | 354.6 | 106.6286 | 106.6154 | 30.0701 | 30.0664
240 | feeder2_line21 | 3 | 354.6 | 103.8439 | 103.8383 | 29.2848 | 29.2832
240 | feeder2_line22 | 1 | 99 | 5.6544e-07 | 1.0022e-06 | 5.7115e-07 | 1.0123e-06
240 | feeder2_line22 | 2 | 99 | 0.094847 | 0.094849 | 0.095805 | 0.095807
240 | feeder2_line22 | 3 | 99 | 5.6537e-07 | 1.0021e-06 | 5.7108e-07 | 1.0122e-06
240 | feeder2_line23 | 1 | 99 | 5.6544e-07 | 9.3815e-07 | 5.7115e-07 | 9.4763e-07
240 | feeder2_line23 | 2 | 99 | 5.6564e-07 | 9.3847e-07 | 5.7135e-07 | 9.4795e-07
240 | feeder2_line23 | 3 | 99 | 0.12827 | 0.12828 | 0.12957 | 0.12957
240 | feeder2_line24 | 1 | 354.6 | 99.904 | 99.8935 | 28.1737 | 28.1708
240 | feeder2_line24 | 2 | 354.6 | 106.6257 | 106.6125 | 30.0693 | 30.0656
240 | feeder2_line24 | 3 | 354.6 | 103.8588 | 103.8531 | 29.289 | 29.2874
240 | feeder2_line25 | 1 | 99 | 0.094948 | 0.094948 | 0.095907 | 0.095907
240 | feeder2_line25 | 2 | 99 | 4.9035e-08 | 6.82e-07 | 4.953e-08 | 6.8889e-07
240 | feeder2_line25 | 3 | 99 | 4.924e-08 | 6.8168e-07 | 4.9737e-08 | 6.8856e-07
240 | feeder2_line26 | 1 | 99 | 0.22053 | 0.22053 | 0.22276 | 0.22276
240 | feeder2_line26 | 2 | 99 | 5.4088e-07 | 8.4495e-07 | 5.4634e-07 | 8.5349e-07
240 | feeder2_line26 | 3 | 99 | 5.405e-07 | 8.4456e-07 | 5.4596e-07 | 8.5309e-07
240 | feeder2_line27 | 1 | 354.6 | 99.869 | 99.8585 | 28.1639 | 28.1609
240 | feeder2_line27 | 2 | 354.6 | 106.6257 | 106.6125 | 30.0693 | 30.0656
240 | feeder2_line27 | 3 | 354.6 | 103.8588 | 103.8531 | 29.289 | 29.2874
240 | feeder2_line28 | 1 | 99 | 2.5043e-06 | 7.0059e-07 | 2.5296e-06 | 7.0766e-07
240 | feeder2_line28 | 2 | 99 | 1.9706 | 1.9706 | 1.9905 | 1.9905
240 | feeder2_line28 | 3 | 99 | 2.5037e-06 | 7.0054e-07 | 2.529e-06 | 7.0762e-07
240 | feeder2_line29 | 1 | 354.6 | 99.869 | 99.8585 | 28.1639 | 28.1609
240 | feeder2_line29 | 2 | 354.6 | 104.9716 | 104.9583 | 29.6028 | 29.5991
240 | feeder2_line29 | 3 | 354.6 | 103.8588 | 103.8531 | 29.289 | 29.2874
240 | feeder2_line30 | 1 | 266.4 | 11.77 | 11.7697 | 4.4182 | 4.4181
240 | feeder2_line30 | 2 | 266.4 | 2.4829 | 2.4831 | 0.93202 | 0.93211
240 | feeder2_line30 | 3 | 266.4 | 2.4499 | 2.4502 | 0.91965 | 0.91973
240 | feeder2_line31 | 1 | 354.6 | 98.0119 | 97.9995 | 27.6401 | 27.6366
240 | feeder2_line31 | 2 | 354.6 | 103.0047 | 102.9907 | 29.0481 | 29.0442
240 | feeder2_line31 | 3 | 354.6 | 102.0338 | 102.0274 | 28.7743 | 28.7725
240 | feeder2_line32 | 1 | 354.6 | 98.0119 | 97.9995 | 27.6401 | 27.6366
240 | feeder2_line32 | 2 | 354.6 | 102.9926 | 102.9786 | 29.0447 | 29.0408
240 | feeder2_line32 | 3 | 354.6 | 102.0337 | 102.0274 | 28.7743 | 28.7725
240 | feeder2_line33 | 1 | 99 | 4.9075e-08 | 6.7486e-07 | 4.9571e-08 | 6.8168e-07
240 | feeder2_line33 | 2 | 99 | 0.25715 | 0.25715 | 0.25975 | 0.25975
240 | feeder2_line33 | 3 | 99 | 4.9149e-08 | 6.748e-07 | 4.9646e-08 | 6.8162e-07
240 | feeder2_line34 | 1 | 354.6 | 98.0119 | 97.9995 | 27.6401 | 27.6366
240 | feeder2_line34 | 2 | 354.6 | 102.9926 | 102.9786 | 29.0447 | 29.0408
240 | feeder2_line34 | 3 | 354.6 | 102.0193 | 102.013 | 28.7703 | 28.7685
240 | feeder2_line35 | 1 | 99 | 2.9415e-07 | 7.4716e-07 | 2.9712e-07 | 7.547e-07
240 | feeder2_line35 | 2 | 99 | 2.9424e-07 | 7.475e-07 | 2.9721e-07 | 7.5505e-07
240 | feeder2_line35 | 3 | 99 | 0.27464 | 0.27465 | 0.27742 | 0.27742
240 | feeder2_line36 | 1 | 354.6 | 97.0091 | 96.9963 | 27.3573 | 27.3537
240 | feeder2_line36 | 2 | 354.6 | 102.9926 | 102.9786 | 29.0447 | 29.0408
240 | feeder2_line36 | 3 | 354.6 | 102.0194 | 102.013 | 28.7703 | 28.7685
240 | feeder2_line37 | 1 | 99 | 1.2258 | 1.2261 | 1.2382 | 1.2385
240 | feeder2_line37 | 2 | 99 | 2.9416e-07 | 8.2686e-07 | 2.9713e-07 | 8.3522e-07
240 | feeder2_line37 | 3 | 99 | 2.9405e-07 | 8.2636e-07 | 2.9702e-07 | 8.3471e-07
240 | feeder2_line38 | 1 | 99 | 3.1887e-07 | 7.6333e-07 | 3.2209e-07 | 7.7104e-07
240 | feeder2_line38 | 2 | 99 | 0.21242 | 0.21242 | 0.21457 | 0.21457
240 | feeder2_line38 | 3 | 99 | 3.1893e-07 | 7.6339e-07 | 3.2216e-07 | 7.7111e-07
240 | feeder2_line39 | 1 | 266.4 | 11.77 | 11.7697 | 4.4182 | 4.4181
240 | feeder2_line39 | 2 | 266.4 | 2.351 | 2.3512 | 0.88249 | 0.8826
240 | feeder2_line39 | 3 | 266.4 | 2.45 | 2.4502 | 0.91965 | 0.91973
240 | feeder2_line40 | 1 | 354.6 | 97.0137 | 97.001 | 27.3586 | 27.355
240 | feeder2_line40 | 2 | 354.6 | 102.9926 | 102.9786 | 29.0447 | 29.0408
240 | feeder2_line40 | 3 | 354.6 | 102.0193 | 102.013 | 28.7702 | 28.7685
240 | feeder2_line41 | 1 | 99 | 0.09517 | 0.09517 | 0.096131 | 0.096131
240 | feeder2_line41 | 2 | 99 | 4.8867e-08 | 7.2242e-07 | 4.9361e-08 | 7.2972e-07
240 | feeder2_line41 | 3 | 99 | 4.9126e-08 | 7.2198e-07 | 4.9623e-08 | 7.2927e-07
240 | feeder2_line42 | 1 | 99 | 2.9428e-07 | 7.3669e-07 | 2.9725e-07 | 7.4413e-07
240 | feeder2_line42 | 2 | 99 | 2.9445e-07 | 7.3726e-07 | 2.9742e-07 | 7.4471e-07
240 | feeder2_line42 | 3 | 99 | 0.19004 | 0.19004 | 0.19196 | 0.19196
240 | feeder2_line43 | 1 | 266.4 | 11.7699 | 11.7697 | 4.4181 | 4.4181
240 | feeder2_line43 | 2 | 266.4 | 2.3511 | 2.3512 | 0.88253 | 0.8826
240 | feeder2_line43 | 3 | 266.4 | 2.322 | 2.3222 | 0.87162 | 0.87168
240 | feeder2_line44 | 1 | 354.6 | 97.0137 | 97.001 | 27.3586 | 27.355
240 | feeder2_line44 | 2 | 354.6 | 102.9926 | 102.9786 | 29.0447 | 29.0408
240 | feeder2_line44 | 3 | 354.6 | 102.0053 | 101.9989 | 28.7663 | 28.7645
240 | feeder2_line45 | 1 | 99 | 4.9026e-08 | 5.6941e-07 | 4.9521e-08 | 5.7516e-07
240 | feeder2_line45 | 2 | 99 | 4.8856e-08 | 5.6962e-07 | 4.935e-08 | 5.7537e-07
240 | feeder2_line45 | 3 | 99 | 0.35518 | 0.35516 | 0.35877 | 0.35874
240 | feeder2_line46 | 1 | 99 | 5.64e-07 | 1.3355e-06 | 5.6969e-07 | 1.349e-06
240 | feeder2_line46 | 2 | 99 | 5.6444e-07 | 1.3365e-06 | 5.7014e-07 | 1.35e-06
240 | feeder2_line46 | 3 | 99 | 1.3074 | 1.3074 | 1.3206 | 1.3207
240 | feeder2_line47 | 1 | 266.4 | 11.77 | 11.7697 | 4.4182 | 4.4181
240 | feeder2_line47 | 2 | 266.4 | 2.3512 | 2.3512 | 0.88259 | 0.8826
240 | feeder2_line47 | 3 | 266.4 | 1.0154 | 1.0154 | 0.38115 | 0.38114
240 | feeder2_line48 | 1 | 99 | 0.13759 | 0.13758 | 0.13898 | 0.13897
240 | feeder2_line48 | 2 | 99 | 4.8898e-08 | 7.1961e-07 | 4.9392e-08 | 7.2688e-07
240 | feeder2_line48 | 3 | 99 | 4.916e-08 | 7.1921e-07 | 4.9656e-08 | 7.2647e-07
240 | feeder2_line49 | 1 | 266.4 | 11.6378 | 11.6376 | 4.3685 | 4.3685
240 | feeder2_line49 | 2 | 266.4 | 2.3512 | 2.3512 | 0.88259 | 0.8826
240 | feeder2_line49 | 3 | 266.4 | 1.0154 | 1.0154 | 0.38115 | 0.38114
240 | feeder2_line50 | 1 | 99 | 5.6393e-07 | 1.2152e-06 | 5.6962e-07 | 1.2275e-06
240 | feeder2_line50 | 2 | 99 | 2.3235 | 2.3235 | 2.347 | 2.347
240 | feeder2_line50 | 3 | 99 | 5.6413e-07 | 1.2157e-06 | 5.6982e-07 | 1.2279e-06
240 | feeder2_line51 | 1 | 99 | 10.3771 | 10.3771 | 10.482 | 10.4819
240 | feeder2_line51 | 2 | 99 | 5.6442e-07 | 1.3204e-06 | 5.7012e-07 | 1.3338e-06
240 | feeder2_line51 | 3 | 99 | 5.641e-07 | 1.3197e-06 | 5.698e-07 | 1.3331e-06
240 | feeder2_line52 | 1 | 266.4 | 1.4719 | 1.4719 | 0.55252 | 0.55252
240 | feeder2_line52 | 2 | 266.4 | 0.049625 | 0.049523 | 0.018628 | 0.01859
240 | feeder2_line52 | 3 | 266.4 | 1.0153 | 1.0154 | 0.38112 | 0.38114
240 | feeder2_line53 | 1 | 99 | 5.3938e-07 | 7.417e-07 | 5.4482e-07 | 7.4919e-07
240 | feeder2_line53 | 2 | 99 | 0.049522 | 0.049523 | 0.050022 | 0.050023
240 | feeder2_line53 | 3 | 99 | 5.3954e-07 | 7.4194e-07 | 5.4499e-07 | 7.4944e-07
240 | feeder2_line54 | 1 | 266.4 | 1.4718 | 1.4719 | 0.55249 | 0.55252
240 | feeder2_line54 | 2 | 266.4 | 8.4176e-05 | 4.5537e-06 | 3.1597e-05 | 1.7094e-06
240 | feeder2_line54 | 3 | 266.4 | 1.0153 | 1.0154 | 0.38111 | 0.38114
240 | feeder2_line55 | 1 | 99 | 0.18011 | 0.18011 | 0.18193 | 0.18193
240 | feeder2_line55 | 2 | 99 | 4.8826e-08 | 7.1713e-07 | 4.9319e-08 | 7.2438e-07
240 | feeder2_line55 | 3 | 99 | 4.9098e-08 | 7.1666e-07 | 4.9594e-08 | 7.239e-07
240 | feeder2_line56 | 1 | 354.6 | 97.0121 | 96.9993 | 27.3582 | 27.3546
240 | feeder2_line56 | 2 | 354.6 | 102.9926 | 102.9786 | 29.0447 | 29.0408
240 | feeder2_line56 | 3 | 354.6 | 102.0053 | 101.9989 | 28.7663 | 28.7645
240 | feeder2_line57 | 1 | 99 | 7.3681e-07 | 1.5192e-06 | 7.4425e-07 | 1.5345e-06
240 | feeder2_line57 | 2 | 99 | 7.3342e-07 | 1.5205e-06 | 7.4083e-07 | 1.5359e-06
240 | feeder2_line57 | 3 | 99 | 1.0153 | 1.0154 | 1.0256 | 1.0256
240 | feeder2_line58 | 1 | 266.4 | 1.4719 | 1.4719 | 0.55252 | 0.55252
240 | feeder2_line58 | 2 | 266.4 | 1.866e-05 | 2.6438e-06 | 7.0044e-06 | 9.9241e-07
240 | feeder2_line58 | 3 | 266.4 | 1.8646e-05 | 2.6426e-06 | 6.9991e-06 | 9.9195e-07
240 | feeder2_line59 | 1 | 99 | 4.912e-08 | 5.2809e-07 | 4.9616e-08 | 5.3342e-07
240 | feeder2_line59 | 2 | 99 | 4.8897e-08 | 5.2856e-07 | 4.9391e-08 | 5.339e-07
240 | feeder2_line59 | 3 | 99 | 0.10955 | 0.10955 | 0.11065 | 0.11066
240 | feeder2_line60 | 1 | 99 | 2.9425e-07 | 7.9811e-07 | 2.9722e-07 | 8.0617e-07
240 | feeder2_line60 | 2 | 99 | 2.9444e-07 | 7.9882e-07 | 2.9742e-07 | 8.0689e-07
240 | feeder2_line60 | 3 | 99 | 0.95724 | 0.95726 | 0.96691 | 0.96693
240 | feeder2_line61 | 1 | 266.4 | 0.19857 | 0.19874 | 0.074538 | 0.074601
240 | feeder2_line61 | 2 | 266.4 | 0.63905 | 0.63918 | 0.23988 | 0.23993
240 | feeder2_line61 | 3 | 266.4 | 0.38614 | 0.38629 | 0.14495 | 0.14501
240 | feeder2_line62 | 1 | 354.6 | 97.0159 | 97.003 | 27.3592 | 27.3556
240 | feeder2_line62 | 2 | 354.6 | 102.9729 | 102.9587 | 29.0392 | 29.0352
240 | feeder2_line62 | 3 | 354.6 | 101.9991 | 101.9926 | 28.7645 | 28.7627
240 | feeder2_line63 | 1 | 99 | 0.35878 | 0.35878 | 0.36241 | 0.36241
240 | feeder2_line63 | 2 | 99 | 5.6444e-07 | 1.201e-06 | 5.7014e-07 | 1.2131e-06
240 | feeder2_line63 | 3 | 99 | 5.6412e-07 | 1.2004e-06 | 5.6982e-07 | 1.2125e-06
240 | feeder2_line64 | 1 | 99 | 1.1913 | 1.1913 | 1.2033 | 1.2033
240 | feeder2_line64 | 2 | 99 | 6.2251e-12 | 3.1636e-07 | 6.288e-12 | 3.1956e-07
240 | feeder2_line64 | 3 | 99 | 1.6008e-12 | 3.162e-07 | 1.617e-12 | 3.1939e-07
240 | feeder2_line65 | 1 | 99 | 4.8916e-08 | 6.2906e-07 | 4.941e-08 | 6.3541e-07
240 | feeder2_line65 | 2 | 99 | 0.27879 | 0.27879 | 0.28161 | 0.28161
240 | feeder2_line65 | 3 | 99 | 4.9061e-08 | 6.2866e-07 | 4.9557e-08 | 6.3501e-07
240 | feeder2_line66 | 1 | 354.6 | 97.0159 | 97.003 | 27.3592 | 27.3556
240 | feeder2_line66 | 2 | 354.6 | 102.9635 | 102.9492 | 29.0365 | 29.0325
240 | feeder2_line66 | 3 | 354.6 | 101.9991 | 101.9926 | 28.7645 | 28.7627
240 | feeder2_line67 | 1 | 99 | 2.4469e-08 | 3.558e-07 | 2.4717e-08 | 3.594e-07
240 | feeder2_line67 | 2 | 99 | 2.4405e-08 | 3.5587e-07 | 2.4652e-08 | 3.5946e-07
240 | feeder2_line67 | 3 | 99 | 0.095334 | 0.095337 | 0.096297 | 0.0963
240 | feeder2_line68 | 1 | 266.4 | 0.19861 | 0.19874 | 0.074553 | 0.074601
240 | feeder2_line68 | 2 | 266.4 | 0.63909 | 0.63918 | 0.2399 | 0.23993
240 | feeder2_line68 | 3 | 266.4 | 0.29091 | 0.29103 | 0.1092 | 0.10925
240 | feeder2_line69 | 1 | 99 | 1.5506 | 1.5506 | 1.5662 | 1.5663
240 | feeder2_line69 | 2 | 99 | 2.4959e-06 | 6.5294e-07 | 2.5211e-06 | 6.5954e-07
240 | feeder2_line69 | 3 | 99 | 2.4918e-06 | 6.5246e-07 | 2.517e-06 | 6.5905e-07
240 | feeder2_line70 | 1 | 354.6 | 95.8575 | 95.8444 | 27.0326 | 27.0289
240 | feeder2_line70 | 2 | 354.6 | 102.9636 | 102.9492 | 29.0365 | 29.0325
240 | feeder2_line70 | 3 | 354.6 | 101.9992 | 101.9926 | 28.7646 | 28.7627
240 | feeder2_line71 | 1 | 99 | 4.889e-08 | 7.0151e-07 | 4.9384e-08 | 7.086e-07
240 | feeder2_line71 | 2 | 99 | 0.32185 | 0.32177 | 0.3251 | 0.32503
240 | feeder2_line71 | 3 | 99 | 4.9047e-08 | 7.01e-07 | 4.9543e-08 | 7.0808e-07
240 | feeder2_line72 | 1 | 354.6 | 95.8575 | 95.8444 | 27.0326 | 27.0289
240 | feeder2_line72 | 2 | 354.6 | 102.9478 | 102.9334 | 29.0321 | 29.028
240 | feeder2_line72 | 3 | 354.6 | 101.9992 | 101.9926 | 28.7646 | 28.7627
240 | feeder2_line73 | 1 | 99 | 5.8738e-07 | 1.5064e-06 | 5.9331e-07 | 1.5216e-06
240 | feeder2_line73 | 2 | 99 | 0.25709 | 0.25709 | 0.25969 | 0.25969
240 | feeder2_line73 | 3 | 99 | 5.8714e-07 | 1.5056e-06 | 5.9307e-07 | 1.5208e-06
240 | feeder2_line74 | 1 | 99 | 4.8952e-08 | 4.4928e-07 | 4.9446e-08 | 4.5382e-07
240 | feeder2_line74 | 2 | 99 | 0.29107 | 0.29103 | 0.29401 | 0.29397
240 | feeder2_line74 | 3 | 99 | 4.9079e-08 | 4.4905e-07 | 4.9575e-08 | 4.5358e-07
240 | feeder2_line75 | 1 | 266.4 | 0.19871 | 0.19874 | 0.074589 | 0.074601
240 | feeder2_line75 | 2 | 266.4 | 0.091141 | 0.091175 | 0.034212 | 0.034225
240 | feeder2_line75 | 3 | 266.4 | 0.29101 | 0.29103 | 0.10924 | 0.10925
240 | feeder2_line76 | 1 | 99 | 0.19874 | 0.19874 | 0.20075 | 0.20074
240 | feeder2_line76 | 2 | 99 | 8.323e-07 | 1.5541e-06 | 8.4071e-07 | 1.5698e-06
240 | feeder2_line76 | 3 | 99 | 8.3163e-07 | 1.5531e-06 | 8.4003e-07 | 1.5688e-06
240 | feeder2_line77 | 1 | 99 | 2.4474e-08 | 5.646e-07 | 2.4721e-08 | 5.703e-07
240 | feeder2_line77 | 2 | 99 | 2.4401e-08 | 5.6469e-07 | 2.4648e-08 | 5.704e-07
240 | feeder2_line77 | 3 | 99 | 0.29104 | 0.29103 | 0.29398 | 0.29397
240 | feeder2_line78 | 1 | 266.4 | 6.9501e-12 | 9.3635e-07 | 2.6089e-12 | 3.5148e-07
240 | feeder2_line78 | 2 | 266.4 | 0.091173 | 0.091175 | 0.034224 | 0.034225
240 | feeder2_line78 | 3 | 266.4 | 3.4174e-12 | 9.3597e-07 | 1.2828e-12 | 3.5134e-07
240 | feeder2_line79 | 1 | 354.6 | 1.2524 | 1.252 | 0.35318 | 0.35309
240 | feeder2_line79 | 2 | 354.6 | 4.7142 | 4.7141 | 1.3294 | 1.3294
240 | feeder2_line79 | 3 | 354.6 | 5.5995 | 5.5993 | 1.5791 | 1.579
240 | feeder2_line80 | 1 | 354.6 | 95.2568 | 95.2434 | 26.8632 | 26.8594
240 | feeder2_line80 | 2 | 354.6 | 99.4148 | 99.4 | 28.0358 | 28.0316
240 | feeder2_line80 | 3 | 354.6 | 98.421 | 98.4141 | 27.7555 | 27.7536
240 | feeder2_line81 | 1 | 354.6 | 95.2567 | 95.2434 | 26.8631 | 26.8594
240 | feeder2_line81 | 2 | 354.6 | 99.4147 | 99.4 | 28.0357 | 28.0316
240 | feeder2_line81 | 3 | 354.6 | 98.4239 | 98.4171 | 27.7563 | 27.7544
240 | feeder2_line82 | 1 | 354.6 | 1.1307e-11 | 7.1889e-07 | 3.1886e-12 | 2.0273e-07
240 | feeder2_line82 | 2 | 354.6 | 2.0483e-11 | 7.1873e-07 | 5.7764e-12 | 2.0269e-07
240 | feeder2_line82 | 3 | 354.6 | 0.24922 | 0.24922 | 0.070281 | 0.070282
240 | feeder2_line83 | 1 | 354.6 | 95.2567 | 95.2434 | 26.8632 | 26.8594
240 | feeder2_line83 | 2 | 354.6 | 99.4318 | 99.417 | 28.0406 | 28.0364
240 | feeder2_line83 | 3 | 354.6 | 98.4239 | 98.4171 | 27.7563 | 27.7544
240 | feeder2_line84 | 1 | 354.6 | 2.2391e-11 | 1.2702e-06 | 6.3145e-12 | 3.582e-07
240 | feeder2_line84 | 2 | 354.6 | 0.11811 | 0.11804 | 0.033307 | 0.033287
240 | feeder2_line84 | 3 | 354.6 | 1.2355e-11 | 1.2691e-06 | 3.4843e-12 | 3.5791e-07
240 | feeder2_line85 | 1 | 99 | 0.2124 | 0.2124 | 0.21455 | 0.21454
240 | feeder2_line85 | 2 | 99 | 4.869e-08 | 4.5324e-07 | 4.9182e-08 | 4.5782e-07
240 | feeder2_line85 | 3 | 99 | 4.9011e-08 | 4.5286e-07 | 4.9506e-08 | 4.5743e-07
240 | feeder2_line86 | 1 | 354.6 | 95.2659 | 95.2526 | 26.8657 | 26.862
240 | feeder2_line86 | 2 | 354.6 | 99.4318 | 99.417 | 28.0405 | 28.0364
240 | feeder2_line86 | 3 | 354.6 | 98.4239 | 98.4171 | 27.7563 | 27.7544
240 | feeder2_line87 | 1 | 354.6 | 95.2658 | 95.2526 | 26.8657 | 26.862
240 | feeder2_line87 | 2 | 354.6 | 96.5987 | 96.5836 | 27.2416 | 27.2373
240 | feeder2_line87 | 3 | 354.6 | 96.5925 | 96.5857 | 27.2398 | 27.2379
240 | feeder2_line88 | 1 | 354.6 | 0.00011188 | 3.2907e-06 | 3.1551e-05 | 9.2799e-07
240 | feeder2_line88 | 2 | 354.6 | 3.5366 | 3.5367 | 0.99736 | 0.99738
240 | feeder2_line88 | 3 | 354.6 | 2.4296 | 2.4296 | 0.68517 | 0.68517
240 | feeder2_line89 | 1 | 354.6 | 95.2655 | 95.2526 | 26.8656 | 26.862
240 | feeder2_line89 | 2 | 354.6 | 96.6263 | 96.6114 | 27.2494 | 27.2452
240 | feeder2_line89 | 3 | 354.6 | 96.5921 | 96.5857 | 27.2397 | 27.2379
240 | feeder2_line90 | 1 | 354.6 | 0.00070802 | 1.986e-06 | 0.00019967 | 5.6006e-07
240 | feeder2_line90 | 2 | 354.6 | 0.31168 | 0.31209 | 0.087898 | 0.088011
240 | feeder2_line90 | 3 | 354.6 | 0.00070642 | 1.984e-06 | 0.00019921 | 5.595e-07
240 | feeder2_line91 | 1 | 354.6 | 95.2657 | 95.2526 | 26.8657 | 26.862
240 | feeder2_line91 | 2 | 354.6 | 96.6265 | 96.6114 | 27.2494 | 27.2452
240 | feeder2_line91 | 3 | 354.6 | 95.8598 | 95.8532 | 27.0332 | 27.0314
240 | feeder2_line92 | 1 | 354.6 | 9.6218e-12 | 1.0014e-06 | 2.7134e-12 | 2.824e-07
240 | feeder2_line92 | 2 | 354.6 | 2.7497e-11 | 1.0011e-06 | 7.7543e-12 | 2.8232e-07
240 | feeder2_line92 | 3 | 354.6 | 0.95567 | 0.95569 | 0.26951 | 0.26951
240 | feeder2_line93 | 1 | 99 | 2.4395e-08 | 3.3428e-07 | 2.4641e-08 | 3.3766e-07
240 | feeder2_line93 | 2 | 99 | 0.11817 | 0.1181 | 0.11936 | 0.11929
240 | feeder2_line93 | 3 | 99 | 2.4492e-08 | 3.3394e-07 | 2.474e-08 | 3.3731e-07
240 | feeder2_line94 | 1 | 354.6 | 2.4396e-06 | 1.6274e-06 | 6.8799e-07 | 4.5895e-07
240 | feeder2_line94 | 2 | 354.6 | 0.19466 | 0.1946 | 0.054896 | 0.05488
240 | feeder2_line94 | 3 | 354.6 | 2.4492e-06 | 1.626e-06 | 6.9069e-07 | 4.5855e-07
240 | feeder2_line95 | 1 | 99 | 3.4882e-06 | 2.5518e-06 | 3.5234e-06 | 2.5775e-06
240 | feeder2_line95 | 2 | 99 | 3.5366 | 3.5367 | 3.5723 | 3.5724
240 | feeder2_line95 | 3 | 99 | 3.4845e-06 | 2.5493e-06 | 3.5197e-06 | 2.575e-06
240 | feeder2_line96 | 1 | 354.6 | 0.00011844 | 6.082e-07 | 3.3401e-05 | 1.7152e-07
240 | feeder2_line96 | 2 | 354.6 | 0.00011842 | 6.0842e-07 | 3.3395e-05 | 1.7158e-07
240 | feeder2_line96 | 3 | 354.6 | 2.4296 | 2.4296 | 0.68516 | 0.68517
240 | feeder2_line97 | 1 | 354.6 | 95.2963 | 95.2829 | 26.8743 | 26.8705
240 | feeder2_line97 | 2 | 354.6 | 96.6267 | 96.6114 | 27.2495 | 27.2452
240 | feeder2_line97 | 3 | 354.6 | 95.8601 | 95.8532 | 27.0333 | 27.0314
240 | feeder2_line98 | 1 | 354.6 | 0.15905 | 0.1573 | 0.044854 | 0.04436
240 | feeder2_line98 | 2 | 354.6 | 0.0016626 | 6.0822e-07 | 0.00046887 | 1.7152e-07
240 | feeder2_line98 | 3 | 354.6 | 0.0016581 | 6.0546e-07 | 0.00046759 | 1.7075e-07
240 | feeder2_line99 | 1 | 99 | 2.4407e-08 | 4.373e-07 | 2.4653e-08 | 4.4172e-07
240 | feeder2_line99 | 2 | 99 | 2.4341e-08 | 4.3722e-07 | 2.4587e-08 | 4.4164e-07
240 | feeder2_line99 | 3 | 99 | 2.4296 | 2.4296 | 2.4541 | 2.4541
240 | feeder2_line100 | 1 | 99 | 0.15739 | 0.1573 | 0.15898 | 0.15889
240 | feeder2_line100 | 2 | 99 | 2.4326e-08 | 5.9974e-07 | 2.4572e-08 | 6.058e-07
240 | feeder2_line100 | 3 | 99 | 2.4486e-08 | 5.9925e-07 | 2.4733e-08 | 6.053e-07
240 | feeder2_line101 | 1 | 354.6 | 0.19506 | 0.19461 | 0.055009 | 0.054882
240 | feeder2_line101 | 2 | 354.6 | 4.7142 | 4.7141 | 1.3294 | 1.3294
240 | feeder2_line101 | 3 | 354.6 | 5.5994 | 5.5993 | 1.5791 | 1.579
240 | feeder2_line102 | 1 | 99 | 1.0896 | 1.0896 | 1.1006 | 1.1006
240 | feeder2_line102 | 2 | 99 | 2.2868e-06 | 8.5961e-07 | 2.3099e-06 | 8.6829e-07
240 | feeder2_line102 | 3 | 99 | 2.2813e-06 | 8.5886e-07 | 2.3044e-06 | 8.6753e-07
240 | feeder2_line103 | 1 | 99 | 5.3774e-07 | 7.8691e-07 | 5.4317e-07 | 7.9486e-07
240 | feeder2_line103 | 2 | 99 | 0.097734 | 0.097736 | 0.098721 | 0.098723
240 | feeder2_line103 | 3 | 99 | 5.3705e-07 | 7.8609e-07 | 5.4248e-07 | 7.9403e-07
240 | feeder2_line104 | 1 | 354.6 | 0.19496 | 0.19461 | 0.054981 | 0.054882
240 | feeder2_line104 | 2 | 354.6 | 4.6596 | 4.6596 | 1.314 | 1.314
240 | feeder2_line104 | 3 | 354.6 | 5.5994 | 5.5993 | 1.5791 | 1.579
240 | feeder2_line105 | 1 | 99 | 2.4934e-06 | 7.2406e-07 | 2.5186e-06 | 7.3137e-07
240 | feeder2_line105 | 2 | 99 | 2.4938e-06 | 7.2395e-07 | 2.519e-06 | 7.3126e-07
240 | feeder2_line105 | 3 | 99 | 0.48731 | 0.48728 | 0.49223 | 0.4922
240 | feeder2_line106 | 1 | 354.6 | 0.19491 | 0.19461 | 0.054966 | 0.054882
240 | feeder2_line106 | 2 | 354.6 | 4.6596 | 4.6596 | 1.314 | 1.314
240 | feeder2_line106 | 3 | 354.6 | 5.2241 | 5.224 | 1.4732 | 1.4732
240 | feeder2_line107 | 1 | 99 | 3.1771e-07 | 8.8238e-07 | 3.2092e-07 | 8.9129e-07
240 | feeder2_line107 | 2 | 99 | 1.1924 | 1.1925 | 1.2045 | 1.2045
240 | feeder2_line107 | 3 | 99 | 3.1755e-07 | 8.8138e-07 | 3.2075e-07 | 8.9029e-07
240 | feeder2_line108 | 1 | 354.6 | 0.1949 | 0.19461 | 0.054963 | 0.054882
240 | feeder2_line108 | 2 | 354.6 | 3.468 | 3.4679 | 0.97801 | 0.97799
240 | feeder2_line108 | 3 | 354.6 | 5.2241 | 5.224 | 1.4732 | 1.4732
240 | feeder2_line109 | 1 | 354.6 | 95.3336 | 95.3202 | 26.8848 | 26.8811
240 | feeder2_line109 | 2 | 354.6 | 96.6266 | 96.6114 | 27.2495 | 27.2452
240 | feeder2_line109 | 3 | 354.6 | 95.86 | 95.8532 | 27.0333 | 27.0314
240 | feeder2_line110 | 1 | 99 | 0.24113 | 0.24035 | 0.24357 | 0.24277
240 | feeder2_line110 | 2 | 99 | 0.00078559 | 8.8623e-07 | 0.00079352 | 8.9518e-07
240 | feeder2_line110 | 3 | 99 | 0.00078397 | 8.866e-07 | 0.00079189 | 8.9556e-07
240 | feeder2_line111 | 1 | 99 | 2.4398e-08 | 3.7349e-07 | 2.4644e-08 | 3.7726e-07
240 | feeder2_line111 | 2 | 99 | 2.4481 | 2.4481 | 2.4728 | 2.4729
240 | feeder2_line111 | 3 | 99 | 2.4502e-08 | 3.7312e-07 | 2.475e-08 | 3.7689e-07
240 | feeder2_line112 | 1 | 99 | 3.1748e-07 | 8.975e-07 | 3.2068e-07 | 9.0657e-07
240 | feeder2_line112 | 2 | 99 | 1.0885 | 1.0886 | 1.0995 | 1.0996
240 | feeder2_line112 | 3 | 99 | 3.1736e-07 | 8.9663e-07 | 3.2056e-07 | 9.0569e-07
240 | feeder2_line113 | 1 | 99 | 0.13057 | 0.13057 | 0.13189 | 0.13188
240 | feeder2_line113 | 2 | 99 | 3.1706e-07 | 8.8395e-07 | 3.2026e-07 | 8.9288e-07
240 | feeder2_line113 | 3 | 99 | 3.1706e-07 | 8.8323e-07 | 3.2026e-07 | 8.9215e-07
240 | feeder2_line114 | 1 | 99 | 0.097751 | 0.09775 | 0.098738 | 0.098737
240 | feeder2_line114 | 2 | 99 | 2.4348e-08 | 4.2745e-07 | 2.4594e-08 | 4.3177e-07
240 | feeder2_line114 | 3 | 99 | 2.4518e-08 | 4.2708e-07 | 2.4766e-08 | 4.3139e-07
240 | feeder2_line115 | 1 | 99 | 2.4413e-08 | 5.5066e-07 | 2.4659e-08 | 5.5622e-07
240 | feeder2_line115 | 2 | 99 | 1.4919 | 1.4919 | 1.507 | 1.507
240 | feeder2_line115 | 3 | 99 | 2.4524e-08 | 5.4999e-07 | 2.4771e-08 | 5.5555e-07
240 | feeder2_line116 | 1 | 354.6 | 0.1949 | 0.19461 | 0.054965 | 0.054882
240 | feeder2_line116 | 2 | 354.6 | 1.9793 | 1.9792 | 0.55819 | 0.55816
240 | feeder2_line116 | 3 | 354.6 | 5.2241 | 5.224 | 1.4732 | 1.4732
240 | feeder2_line117 | 1 | 99 | 4.8741e-08 | 6.273e-07 | 4.9233e-08 | 6.3363e-07
240 | feeder2_line117 | 2 | 99 | 1.3058 | 1.3058 | 1.319 | 1.319
240 | feeder2_line117 | 3 | 99 | 4.8937e-08 | 6.2666e-07 | 4.9432e-08 | 6.3299e-07
240 | feeder2_line118 | 1 | 354.6 | 95.3336 | 95.3202 | 26.8848 | 26.8811
240 | feeder2_line118 | 2 | 354.6 | 95.6607 | 95.6453 | 26.9771 | 26.9727
240 | feeder2_line118 | 3 | 354.6 | 95.86 | 95.8532 | 27.0333 | 27.0314
240 | feeder2_line119 | 1 | 99 | 2.4413e-08 | 5.9253e-07 | 2.466e-08 | 5.9852e-07
240 | feeder2_line119 | 2 | 99 | 2.4349e-08 | 5.9242e-07 | 2.4595e-08 | 5.984e-07
240 | feeder2_line119 | 3 | 99 | 0.54153 | 0.54153 | 0.547 | 0.547
240 | feeder2_line120 | 1 | 354.6 | 0.19491 | 0.19461 | 0.054965 | 0.054882
240 | feeder2_line120 | 2 | 354.6 | 1.9793 | 1.9792 | 0.55819 | 0.55816
240 | feeder2_line120 | 3 | 354.6 | 4.8336 | 4.8335 | 1.3631 | 1.3631
240 | feeder2_line121 | 1 | 99 | 3.1771e-07 | 9.1755e-07 | 3.2092e-07 | 9.2682e-07
240 | feeder2_line121 | 2 | 99 | 0.73697 | 0.73697 | 0.74442 | 0.74441
240 | feeder2_line121 | 3 | 99 | 3.175e-07 | 9.1632e-07 | 3.2071e-07 | 9.2557e-07
240 | feeder2_line122 | 1 | 354.6 | 0.19489 | 0.19461 | 0.054961 | 0.054882
240 | feeder2_line122 | 2 | 354.6 | 1.2435 | 1.2435 | 0.35069 | 0.35067
240 | feeder2_line122 | 3 | 354.6 | 4.8336 | 4.8335 | 1.3631 | 1.3631
240 | feeder2_line123 | 1 | 99 | 5.6219e-07 | 9.508e-07 | 5.6786e-07 | 9.6041e-07
240 | feeder2_line123 | 2 | 99 | 5.6208e-07 | 9.5062e-07 | 5.6775e-07 | 9.6023e-07
240 | feeder2_line123 | 3 | 99 | 1.9662 | 1.9662 | 1.9861 | 1.9861
240 | feeder2_line124 | 1 | 354.6 | 0.1948 | 0.19461 | 0.054936 | 0.054882
240 | feeder2_line124 | 2 | 354.6 | 1.2436 | 1.2435 | 0.3507 | 0.35067
240 | feeder2_line124 | 3 | 354.6 | 2.8838 | 2.8836 | 0.81325 | 0.81321
240 | feeder2_line125 | 1 | 99 | 5.6218e-07 | 8.8387e-07 | 5.6786e-07 | 8.9279e-07
240 | feeder2_line125 | 2 | 99 | 5.6208e-07 | 8.8371e-07 | 5.6776e-07 | 8.9263e-07
240 | feeder2_line125 | 3 | 99 | 0.15749 | 0.15745 | 0.15908 | 0.15904
240 | feeder2_line126 | 1 | 354.6 | 0.19496 | 0.19461 | 0.05498 | 0.054882
240 | feeder2_line126 | 2 | 354.6 | 1.2437 | 1.2435 | 0.35073 | 0.35067
240 | feeder2_line126 | 3 | 354.6 | 2.7901 | 2.7898 | 0.78683 | 0.78675
240 | feeder2_line127 | 1 | 99 | 5.6218e-07 | 1.0581e-06 | 5.6786e-07 | 1.0688e-06
240 | feeder2_line127 | 2 | 99 | 5.6208e-07 | 1.0579e-06 | 5.6776e-07 | 1.0686e-06
240 | feeder2_line127 | 3 | 99 | 0.21239 | 0.2124 | 0.21454 | 0.21454
240 | feeder2_line128 | 1 | 354.6 | 0.19488 | 0.19461 | 0.054957 | 0.054882
240 | feeder2_line128 | 2 | 354.6 | 1.2437 | 1.2435 | 0.35073 | 0.35067
240 | feeder2_line128 | 3 | 354.6 | 2.6477 | 2.6474 | 0.74666 | 0.74658
240 | feeder2_line129 | 1 | 99 | 5.3777e-07 | 8.5799e-07 | 5.432e-07 | 8.6666e-07
240 | feeder2_line129 | 2 | 99 | 1.2434 | 1.2435 | 1.256 | 1.256
240 | feeder2_line129 | 3 | 99 | 5.3684e-07 | 8.5677e-07 | 5.4226e-07 | 8.6542e-07
240 | feeder2_line130 | 1 | 354.6 | 0.19489 | 0.19461 | 0.054961 | 0.054882
240 | feeder2_line130 | 2 | 354.6 | 0.00030195 | 4.5394e-06 | 8.5151e-05 | 1.2802e-06
240 | feeder2_line130 | 3 | 354.6 | 2.6477 | 2.6474 | 0.74667 | 0.74658
240 | feeder2_line131 | 1 | 99 | 5.6218e-07 | 9.5095e-07 | 5.6786e-07 | 9.6056e-07
240 | feeder2_line131 | 2 | 99 | 5.6208e-07 | 9.5078e-07 | 5.6776e-07 | 9.6039e-07
240 | feeder2_line131 | 3 | 99 | 2.5149 | 2.5148 | 2.5403 | 2.5402
240 | feeder2_line132 | 1 | 354.6 | 0.19473 | 0.19461 | 0.054916 | 0.054882
240 | feeder2_line132 | 2 | 354.6 | 0.00012307 | 2.8539e-06 | 3.4706e-05 | 8.0483e-07
240 | feeder2_line132 | 3 | 354.6 | 0.21247 | 0.2124 | 0.059917 | 0.059898
240 | feeder2_line133 | 1 | 99 | 0.19466 | 0.19461 | 0.19662 | 0.19658
240 | feeder2_line133 | 2 | 99 | 2.9322e-07 | 9.5838e-07 | 2.9618e-07 | 9.6806e-07
240 | feeder2_line133 | 3 | 99 | 2.9294e-07 | 9.5716e-07 | 2.959e-07 | 9.6683e-07
240 | feeder2_line134 | 1 | 354.6 | 1.4056e-11 | 1.748e-06 | 3.9639e-12 | 4.9294e-07
240 | feeder2_line134 | 2 | 354.6 | 9.5742e-12 | 1.7476e-06 | 2.7e-12 | 4.9283e-07
240 | feeder2_line134 | 3 | 354.6 | 0.21239 | 0.2124 | 0.059897 | 0.059898
240 | feeder2_line135 | 1 | 99 | 0.3215 | 0.32142 | 0.32475 | 0.32466
240 | feeder2_line135 | 2 | 99 | 4.8593e-08 | 5.7112e-07 | 4.9083e-08 | 5.7689e-07
240 | feeder2_line135 | 3 | 99 | 4.8913e-08 | 5.7066e-07 | 4.9408e-08 | 5.7643e-07
240 | feeder2_line136 | 1 | 354.6 | 95.342 | 95.3286 | 26.8872 | 26.8834
240 | feeder2_line136 | 2 | 354.6 | 95.6607 | 95.6453 | 26.9771 | 26.9727
240 | feeder2_line136 | 3 | 354.6 | 95.86 | 95.8532 | 27.0333 | 27.0314
240 | feeder2_line137 | 1 | 99 | 0.0874 | 0.087315 | 0.088283 | 0.088197
240 | feeder2_line137 | 2 | 99 | 8.2872e-07 | 1.538e-06 | 8.3709e-07 | 1.5535e-06
240 | feeder2_line137 | 3 | 99 | 8.2795e-07 | 1.5368e-06 | 8.3631e-07 | 1.5523e-06
240 | feeder2_line138 | 1 | 354.6 | 95.3512 | 95.3376 | 26.8898 | 26.886
240 | feeder2_line138 | 2 | 354.6 | 95.6607 | 95.6453 | 26.9771 | 26.9727
240 | feeder2_line138 | 3 | 354.6 | 95.86 | 95.8532 | 27.0333 | 27.0314
240 | feeder2_line139 | 1 | 99 | 4.8707e-08 | 4.7923e-07 | 4.9199e-08 | 4.8407e-07
240 | feeder2_line139 | 2 | 99 | 4.8582e-08 | 4.7912e-07 | 4.9072e-08 | 4.8396e-07
240 | feeder2_line139 | 3 | 99 | 0.13821 | 0.13814 | 0.1396 | 0.13954
240 | feeder2_line140 | 1 | 354.6 | 95.3511 | 95.3376 | 26.8898 | 26.886
240 | feeder2_line140 | 2 | 354.6 | 95.6607 | 95.6453 | 26.9771 | 26.9727
240 | feeder2_line140 | 3 | 354.6 | 95.9034 | 95.8958 | 27.0455 | 27.0434
240 | feeder2_line141 | 1 | 99 | 2.4618e-06 | 4.7395e-07 | 2.4867e-06 | 4.7874e-07
240 | feeder2_line141 | 2 | 99 | 0.19009 | 0.19009 | 0.19201 | 0.19201
240 | feeder2_line141 | 3 | 99 | 2.4575e-06 | 4.7346e-07 | 2.4823e-06 | 4.7824e-07
240 | feeder2_line142 | 1 | 354.6 | 95.3512 | 95.3376 | 26.8898 | 26.886
240 | feeder2_line142 | 2 | 354.6 | 95.671 | 95.6555 | 26.98 | 26.9756
240 | feeder2_line142 | 3 | 354.6 | 95.9035 | 95.8958 | 27.0455 | 27.0434
240 | feeder2_line143 | 1 | 99 | 8.2858e-07 | 1.684e-06 | 8.3695e-07 | 1.701e-06
240 | feeder2_line143 | 2 | 99 | 1.1916 | 1.1917 | 1.2037 | 1.2037
240 | feeder2_line143 | 3 | 99 | 8.2766e-07 | 1.6822e-06 | 8.3602e-07 | 1.6992e-06
240 | feeder2_line144 | 1 | 354.6 | 95.3511 | 95.3376 | 26.8898 | 26.886
240 | feeder2_line144 | 2 | 354.6 | 94.7891 | 94.7736 | 26.7313 | 26.7269
240 | feeder2_line144 | 3 | 354.6 | 95.9034 | 95.8958 | 27.0455 | 27.0434
240 | feeder2_line145 | 1 | 99 | 2.4343e-08 | 4.7215e-07 | 2.4589e-08 | 4.7692e-07
240 | feeder2_line145 | 2 | 99 | 0.24917 | 0.24917 | 0.25169 | 0.25169
240 | feeder2_line145 | 3 | 99 | 2.4444e-08 | 4.7166e-07 | 2.4691e-08 | 4.7642e-07
240 | feeder2_line146 | 1 | 354.6 | 95.3511 | 95.3376 | 26.8898 | 26.886
240 | feeder2_line146 | 2 | 354.6 | 94.8008 | 94.7853 | 26.7346 | 26.7302
240 | feeder2_line146 | 3 | 354.6 | 95.9034 | 95.8958 | 27.0455 | 27.0434
240 | feeder2_line147 | 1 | 99 | 0.10995 | 0.10994 | 0.11106 | 0.11105
240 | feeder2_line147 | 2 | 99 | 1.1206e-06 | 2.177e-06 | 1.1319e-06 | 2.199e-06
240 | feeder2_line147 | 3 | 99 | 1.1197e-06 | 2.1753e-06 | 1.131e-06 | 2.1972e-06
240 | feeder2_line148 | 1 | 99 | 0.22056 | 0.22056 | 0.22279 | 0.22279
240 | feeder2_line148 | 2 | 99 | 5.8458e-07 | 1.4588e-06 | 5.9049e-07 | 1.4735e-06
240 | feeder2_line148 | 3 | 99 | 5.8428e-07 | 1.4576e-06 | 5.9018e-07 | 1.4723e-06
240 | feeder2_line149 | 1 | 354.6 | 95.3833 | 95.3697 | 26.8989 | 26.895
240 | feeder2_line149 | 2 | 354.6 | 94.8009 | 94.7853 | 26.7346 | 26.7302
240 | feeder2_line149 | 3 | 354.6 | 95.9035 | 95.8958 | 27.0455 | 27.0434
240 | feeder2_line150 | 1 | 354.6 | 95.3833 | 95.3697 | 26.8989 | 26.895
240 | feeder2_line150 | 2 | 354.6 | 94.83 | 94.8144 | 26.7428 | 26.7384
240 | feeder2_line150 | 3 | 354.6 | 95.9035 | 95.8958 | 27.0455 | 27.0434
240 | feeder2_line151 | 1 | 99 | 9.5045e-06 | 1.7319e-06 | 9.6005e-06 | 1.7494e-06
240 | feeder2_line151 | 2 | 99 | 0.18934 | 0.18935 | 0.19125 | 0.19126
240 | feeder2_line151 | 3 | 99 | 9.4844e-06 | 1.7301e-06 | 9.5802e-06 | 1.7476e-06
240 | feeder2_line152 | 1 | 354.6 | 1.2737e-11 | 1.1535e-06 | 3.592e-12 | 3.253e-07
240 | feeder2_line152 | 2 | 354.6 | 1.5008e-11 | 1.1532e-06 | 4.2323e-12 | 3.2521e-07
240 | feeder2_line152 | 3 | 354.6 | 1.1763 | 1.1762 | 0.33171 | 0.33171
240 | feeder2_line153 | 1 | 99 | 0.73615 | 0.73615 | 0.74358 | 0.74358
240 | feeder2_line153 | 2 | 99 | 4.8529e-08 | 5.7702e-07 | 4.902e-08 | 5.8285e-07
240 | feeder2_line153 | 3 | 99 | 4.8849e-08 | 5.7655e-07 | 4.9343e-08 | 5.8237e-07
240 | feeder2_line154 | 1 | 99 | 5.6003e-07 | 8.5882e-07 | 5.6569e-07 | 8.675e-07
240 | feeder2_line154 | 2 | 99 | 5.5992e-07 | 8.5864e-07 | 5.6557e-07 | 8.6731e-07
240 | feeder2_line154 | 3 | 99 | 0.041642 | 0.041594 | 0.042062 | 0.042014
240 | feeder2_line155 | 1 | 99 | 94.8228 | 94.8092 | 95.7806 | 95.7668
240 | feeder2_line155 | 2 | 99 | 94.8301 | 94.8144 | 95.7879 | 95.7721
240 | feeder2_line155 | 3 | 99 | 95.0174 | 95.0097 | 95.9771 | 95.9694
240 | feeder2_line156 | 1 | 99 | 5.8455e-07 | 1.1309e-06 | 5.9046e-07 | 1.1423e-06
240 | feeder2_line156 | 2 | 99 | 0.097939 | 0.097941 | 0.098928 | 0.09893
240 | feeder2_line156 | 3 | 99 | 5.8406e-07 | 1.1297e-06 | 5.8996e-07 | 1.1411e-06
240 | feeder2_line157 | 1 | 99 | 2.4334e-08 | 2.4552e-07 | 2.458e-08 | 2.48e-07
240 | feeder2_line157 | 2 | 99 | 0.091559 | 0.091562 | 0.092484 | 0.092487
240 | feeder2_line157 | 3 | 99 | 2.4433e-08 | 2.4526e-07 | 2.468e-08 | 2.4774e-07
270 | feeder2_line1 | 1 | 354.6 | 102.677 | 102.6778 | 28.9557 | 28.956
270 | feeder2_line1 | 2 | 354.6 | 104.2235 | 104.2133 | 29.3919 | 29.389
270 | feeder2_line1 | 3 | 354.6 | 95.7887 | 95.8048 | 27.0132 | 27.0177
270 | feeder2_line2 | 1 | 354.6 | 101.6098 | 101.6105 | 28.6548 | 28.655
270 | feeder2_line2 | 2 | 354.6 | 104.2236 | 104.2133 | 29.3919 | 29.389
270 | feeder2_line2 | 3 | 354.6 | 95.7888 | 95.8048 | 27.0132 | 27.0177
270 | feeder2_line3 | 1 | 80.1 | 1.4292 | 1.4292 | 1.7842 | 1.7842
270 | feeder2_line3 | 2 | 80.1 | 5.6746e-07 | 1.0487e-06 | 7.0844e-07 | 1.3092e-06
270 | feeder2_line3 | 3 | 80.1 | 5.6805e-07 | 1.0498e-06 | 7.0918e-07 | 1.3106e-06
270 | feeder2_line4 | 1 | 354.6 | 101.6097 | 101.6105 | 28.6547 | 28.655
270 | feeder2_line4 | 2 | 354.6 | 104.2298 | 104.2195 | 29.3936 | 29.3907
270 | feeder2_line4 | 3 | 354.6 | 95.7887 | 95.8048 | 27.0132 | 27.0177
270 | feeder2_line5 | 1 | 80.1 | 5.6732e-07 | 9.8992e-07 | 7.0826e-07 | 1.2359e-06
270 | feeder2_line5 | 2 | 80.1 | 0.27903 | 0.27903 | 0.34835 | 0.34835
270 | feeder2_line5 | 3 | 80.1 | 5.6802e-07 | 9.9115e-07 | 7.0914e-07 | 1.2374e-06
270 | feeder2_line6 | 1 | 80.1 | 5.6723e-07 | 1.1643e-06 | 7.0816e-07 | 1.4536e-06
270 | feeder2_line6 | 2 | 80.1 | 5.6733e-07 | 1.1645e-06 | 7.0828e-07 | 1.4539e-06
270 | feeder2_line6 | 3 | 80.1 | 0.90056 | 0.90054 | 1.1243 | 1.1243
270 | feeder2_line7 | 1 | 354.6 | 101.6097 | 101.6105 | 28.6547 | 28.655
270 | feeder2_line7 | 2 | 354.6 | 104.2298 | 104.2195 | 29.3936 | 29.3907
270 | feeder2_line7 | 3 | 354.6 | 95.1332 | 95.1494 | 26.8283 | 26.8329
270 | feeder2_line8 | 1 | 80.1 | 0.073324 | 0.073322 | 0.09154 | 0.091538
270 | feeder2_line8 | 2 | 80.1 | 5.671e-07 | 1.1224e-06 | 7.0799e-07 | 1.4013e-06
270 | feeder2_line8 | 3 | 80.1 | 5.678e-07 | 1.1238e-06 | 7.0886e-07 | 1.403e-06
270 | feeder2_line9 | 1 | 354.6 | 101.61 | 101.6108 | 28.6548 | 28.6551
270 | feeder2_line9 | 2 | 354.6 | 104.2297 | 104.2195 | 29.3936 | 29.3907
270 | feeder2_line9 | 3 | 354.6 | 95.1332 | 95.1494 | 26.8283 | 26.8329
270 | feeder2_line10 | 1 | 80.1 | 8.3809e-07 | 1.4817e-06 | 1.0463e-06 | 1.8498e-06
270 | feeder2_line10 | 2 | 80.1 | 0.073302 | 0.073303 | 0.091514 | 0.091514
270 | feeder2_line10 | 3 | 80.1 | 8.3934e-07 | 1.4838e-06 | 1.0479e-06 | 1.8524e-06
270 | feeder2_line11 | 1 | 354.6 | 101.6101 | 101.6108 | 28.6548 | 28.6551
270 | feeder2_line11 | 2 | 354.6 | 104.236 | 104.2258 | 29.3954 | 29.3925
270 | feeder2_line11 | 3 | 354.6 | 95.1333 | 95.1494 | 26.8283 | 26.8329
270 | feeder2_line12 | 1 | 80.1 | 5.4217e-07 | 9.8264e-07 | 6.7687e-07 | 1.2268e-06
270 | feeder2_line12 | 2 | 80.1 | 5.4231e-07 | 9.8285e-07 | 6.7705e-07 | 1.227e-06
270 | feeder2_line12 | 3 | 80.1 | 0.06214 | 0.062141 | 0.077578 | 0.07758
270 | feeder2_line13 | 1 | 354.6 | 101.6102 | 101.6108 | 28.6549 | 28.6551
270 | feeder2_line13 | 2 | 354.6 | 104.2361 | 104.2258 | 29.3954 | 29.3925
270 | feeder2_line13 | 3 | 354.6 | 95.1422 | 95.1582 | 26.8308 | 26.8354
270 | feeder2_line14 | 1 | 80.1 | 0.27491 | 0.2749 | 0.3432 | 0.3432
270 | feeder2_line14 | 2 | 80.1 | 2.9578e-07 | 6.408e-07 | 3.6926e-07 | 8.0001e-07
270 | feeder2_line14 | 3 | 80.1 | 2.9614e-07 | 6.4166e-07 | 3.6972e-07 | 8.0107e-07
270 | feeder2_line15 | 1 | 354.6 | 101.5946 | 101.5953 | 28.6505 | 28.6507
270 | feeder2_line15 | 2 | 354.6 | 104.2361 | 104.2258 | 29.3954 | 29.3925
270 | feeder2_line15 | 3 | 354.6 | 95.1422 | 95.1582 | 26.8308 | 26.8354
270 | feeder2_line16 | 1 | 80.1 | 5.6663e-07 | 1.0208e-06 | 7.074e-07 | 1.2744e-06
270 | feeder2_line16 | 2 | 80.1 | 0.25335 | 0.25335 | 0.3163 | 0.31629
270 | feeder2_line16 | 3 | 80.1 | 5.6756e-07 | 1.0225e-06 | 7.0856e-07 | 1.2765e-06
270 | feeder2_line17 | 1 | 354.6 | 101.5947 | 101.5953 | 28.6505 | 28.6507
270 | feeder2_line17 | 2 | 354.6 | 104.2381 | 104.2277 | 29.396 | 29.393
270 | feeder2_line17 | 3 | 354.6 | 95.1422 | 95.1582 | 26.8309 | 26.8354
270 | feeder2_line18 | 1 | 80.1 | 5.4136e-07 | 7.2992e-07 | 6.7586e-07 | 9.1126e-07
270 | feeder2_line18 | 2 | 80.1 | 5.4155e-07 | 7.3014e-07 | 6.7609e-07 | 9.1153e-07
270 | feeder2_line18 | 3 | 80.1 | 0.48954 | 0.48958 | 0.61117 | 0.61122
270 | feeder2_line19 | 1 | 354.6 | 101.5947 | 101.5953 | 28.6505 | 28.6507
270 | feeder2_line19 | 2 | 354.6 | 104.2381 | 104.2277 | 29.396 | 29.393
270 | feeder2_line19 | 3 | 354.6 | 95.1742 | 95.1903 | 26.8399 | 26.8444
270 | feeder2_line20 | 1 | 99 | 5.4114e-07 | 8.7478e-07 | 5.4661e-07 | 8.8361e-07
270 | feeder2_line20 | 2 | 99 | 5.4134e-07 | 8.7506e-07 | 5.4681e-07 | 8.8389e-07
270 | feeder2_line20 | 3 | 99 | 0.35576 | 0.35581 | 0.35935 | 0.3594
270 | feeder2_line21 | 1 | 354.6 | 101.5947 | 101.5953 | 28.6505 | 28.6507
270 | feeder2_line21 | 2 | 354.6 | 104.2381 | 104.2277 | 29.396 | 29.393
270 | feeder2_line21 | 3 | 354.6 | 95.2062 | 95.2224 | 26.8489 | 26.8535
270 | feeder2_line22 | 1 | 99 | 5.6565e-07 | 1.0026e-06 | 5.7136e-07 | 1.0127e-06
270 | feeder2_line22 | 2 | 99 | 0.094859 | 0.09486 | 0.095817 | 0.095818
270 | feeder2_line22 | 3 | 99 | 5.6689e-07 | 1.0048e-06 | 5.7262e-07 | 1.0149e-06
270 | feeder2_line23 | 1 | 99 | 5.6565e-07 | 9.385e-07 | 5.7136e-07 | 9.4798e-07
270 | feeder2_line23 | 2 | 99 | 5.6584e-07 | 9.3881e-07 | 5.7155e-07 | 9.483e-07
270 | feeder2_line23 | 3 | 99 | 0.12803 | 0.12803 | 0.12932 | 0.12933
270 | feeder2_line24 | 1 | 354.6 | 101.5947 | 101.5953 | 28.6505 | 28.6507
270 | feeder2_line24 | 2 | 354.6 | 104.2454 | 104.235 | 29.398 | 29.3951
270 | feeder2_line24 | 3 | 354.6 | 95.2409 | 95.257 | 26.8587 | 26.8632
270 | feeder2_line25 | 1 | 99 | 0.094932 | 0.094929 | 0.095891 | 0.095888
270 | feeder2_line25 | 2 | 99 | 4.9227e-08 | 6.8226e-07 | 4.9725e-08 | 6.8915e-07
270 | feeder2_line25 | 3 | 99 | 4.9139e-08 | 6.8361e-07 | 4.9635e-08 | 6.9052e-07
270 | feeder2_line26 | 1 | 99 | 0.22053 | 0.22053 | 0.22276 | 0.22275
270 | feeder2_line26 | 2 | 99 | 5.4099e-07 | 8.4527e-07 | 5.4645e-07 | 8.5381e-07
270 | feeder2_line26 | 3 | 99 | 5.4216e-07 | 8.4695e-07 | 5.4764e-07 | 8.5551e-07
270 | feeder2_line27 | 1 | 354.6 | 101.5849 | 101.5855 | 28.6478 | 28.6479
270 | feeder2_line27 | 2 | 354.6 | 104.2454 | 104.235 | 29.398 | 29.3951
270 | feeder2_line27 | 3 | 354.6 | 95.2409 | 95.257 | 26.8587 | 26.8632
270 | feeder2_line28 | 1 | 99 | 2.5049e-06 | 7.0091e-07 | 2.5302e-06 | 7.0799e-07
270 | feeder2_line28 | 2 | 99 | 0.76224 | 0.76222 | 0.76994 | 0.76992
270 | feeder2_line28 | 3 | 99 | 2.5132e-06 | 7.0271e-07 | 2.5386e-06 | 7.0981e-07
270 | feeder2_line29 | 1 | 354.6 | 101.5849 | 101.5855 | 28.6478 | 28.6479
270 | feeder2_line29 | 2 | 354.6 | 103.6942 | 103.6838 | 29.2426 | 29.2396
270 | feeder2_line29 | 3 | 354.6 | 95.2409 | 95.257 | 26.8587 | 26.8632
270 | feeder2_line30 | 1 | 266.4 | 12.5749 | 12.5745 | 4.7203 | 4.7202
270 | feeder2_line30 | 2 | 266.4 | 2.4812 | 2.4814 | 0.93138 | 0.93144
270 | feeder2_line30 | 3 | 266.4 | 0.52391 | 0.52362 | 0.19666 | 0.19656
270 | feeder2_line31 | 1 | 354.6 | 99.722 | 99.7216 | 28.1224 | 28.1223
270 | feeder2_line31 | 2 | 354.6 | 101.896 | 101.8849 | 28.7355 | 28.7324
270 | feeder2_line31 | 3 | 354.6 | 95.3166 | 95.3321 | 26.88 | 26.8844
270 | feeder2_line32 | 1 | 354.6 | 99.7219 | 99.7216 | 28.1224 | 28.1223
270 | feeder2_line32 | 2 | 354.6 | 101.9107 | 101.8996 | 28.7396 | 28.7365
270 | feeder2_line32 | 3 | 354.6 | 95.3165 | 95.3321 | 26.88 | 26.8844
270 | feeder2_line33 | 1 | 99 | 4.918e-08 | 6.7525e-07 | 4.9677e-08 | 6.8207e-07
270 | feeder2_line33 | 2 | 99 | 0.25714 | 0.25714 | 0.25974 | 0.25974
270 | feeder2_line33 | 3 | 99 | 4.9018e-08 | 6.7724e-07 | 4.9513e-08 | 6.8408e-07
270 | feeder2_line34 | 1 | 354.6 | 99.7219 | 99.7216 | 28.1224 | 28.1223
270 | feeder2_line34 | 2 | 354.6 | 101.9107 | 101.8996 | 28.7396 | 28.7365
270 | feeder2_line34 | 3 | 354.6 | 95.3426 | 95.3582 | 26.8874 | 26.8918
270 | feeder2_line35 | 1 | 99 | 2.9435e-07 | 7.4762e-07 | 2.9732e-07 | 7.5518e-07
270 | feeder2_line35 | 2 | 99 | 2.9444e-07 | 7.4787e-07 | 2.9741e-07 | 7.5543e-07
270 | feeder2_line35 | 3 | 99 | 0.27481 | 0.27482 | 0.27759 | 0.27759
270 | feeder2_line36 | 1 | 354.6 | 99.7251 | 99.725 | 28.1233 | 28.1232
270 | feeder2_line36 | 2 | 354.6 | 101.9107 | 101.8996 | 28.7396 | 28.7365
270 | feeder2_line36 | 3 | 354.6 | 95.3426 | 95.3582 | 26.8874 | 26.8918
270 | feeder2_line37 | 1 | 99 | 0.028604 | 0.028322 | 0.028893 | 0.028608
270 | feeder2_line37 | 2 | 99 | 2.9436e-07 | 8.2728e-07 | 2.9734e-07 | 8.3563e-07
270 | feeder2_line37 | 3 | 99 | 2.9509e-07 | 8.2949e-07 | 2.9807e-07 | 8.3787e-07
270 | feeder2_line38 | 1 | 99 | 3.1909e-07 | 7.6374e-07 | 3.2231e-07 | 7.7145e-07
270 | feeder2_line38 | 2 | 99 | 0.21242 | 0.21242 | 0.21456 | 0.21456
270 | feeder2_line38 | 3 | 99 | 3.1983e-07 | 7.6605e-07 | 3.2306e-07 | 7.7379e-07
270 | feeder2_line39 | 1 | 266.4 | 12.5749 | 12.5745 | 4.7203 | 4.7202
270 | feeder2_line39 | 2 | 266.4 | 2.3492 | 2.3493 | 0.88181 | 0.88189
270 | feeder2_line39 | 3 | 266.4 | 0.52392 | 0.52362 | 0.19667 | 0.19656
270 | feeder2_line40 | 1 | 354.6 | 99.7373 | 99.7372 | 28.1267 | 28.1267
270 | feeder2_line40 | 2 | 354.6 | 101.9107 | 101.8996 | 28.7396 | 28.7365
270 | feeder2_line40 | 3 | 354.6 | 95.3426 | 95.3582 | 26.8874 | 26.8918
270 | feeder2_line41 | 1 | 99 | 0.095137 | 0.095132 | 0.096098 | 0.096093
270 | feeder2_line41 | 2 | 99 | 4.9139e-08 | 7.2279e-07 | 4.9635e-08 | 7.3009e-07
270 | feeder2_line41 | 3 | 99 | 4.8989e-08 | 7.2475e-07 | 4.9484e-08 | 7.3207e-07
270 | feeder2_line42 | 1 | 99 | 2.9445e-07 | 7.3708e-07 | 2.9742e-07 | 7.4453e-07
270 | feeder2_line42 | 2 | 99 | 2.9463e-07 | 7.3758e-07 | 2.976e-07 | 7.4503e-07
270 | feeder2_line42 | 3 | 99 | 0.19 | 0.19001 | 0.19192 | 0.19193
270 | feeder2_line43 | 1 | 266.4 | 12.5748 | 12.5745 | 4.7203 | 4.7202
270 | feeder2_line43 | 2 | 266.4 | 2.3492 | 2.3493 | 0.88185 | 0.88189
270 | feeder2_line43 | 3 | 266.4 | 0.33395 | 0.33375 | 0.12536 | 0.12528
270 | feeder2_line44 | 1 | 354.6 | 99.7373 | 99.7372 | 28.1267 | 28.1267
270 | feeder2_line44 | 2 | 354.6 | 101.9107 | 101.8996 | 28.7396 | 28.7365
270 | feeder2_line44 | 3 | 354.6 | 95.3809 | 95.3966 | 26.8982 | 26.9026
270 | feeder2_line45 | 1 | 99 | 4.9129e-08 | 5.6979e-07 | 4.9625e-08 | 5.7554e-07
270 | feeder2_line45 | 2 | 99 | 4.9136e-08 | 5.6992e-07 | 4.9633e-08 | 5.7567e-07
270 | feeder2_line45 | 3 | 99 | 0.35557 | 0.35565 | 0.35916 | 0.35925
270 | feeder2_line46 | 1 | 99 | 5.6429e-07 | 1.3362e-06 | 5.6999e-07 | 1.3497e-06
270 | feeder2_line46 | 2 | 99 | 5.6468e-07 | 1.3371e-06 | 5.7038e-07 | 1.3506e-06
270 | feeder2_line46 | 3 | 99 | 0.16288 | 0.16294 | 0.16452 | 0.16458
270 | feeder2_line47 | 1 | 266.4 | 12.5749 | 12.5745 | 4.7203 | 4.7202
270 | feeder2_line47 | 2 | 266.4 | 2.3494 | 2.3493 | 0.88192 | 0.88189
270 | feeder2_line47 | 3 | 266.4 | 0.17158 | 0.17132 | 0.064407 | 0.06431
270 | feeder2_line48 | 1 | 99 | 2.2608 | 2.2609 | 2.2836 | 2.2837
270 | feeder2_line48 | 2 | 99 | 4.9148e-08 | 7.1992e-07 | 4.9645e-08 | 7.2719e-07
270 | feeder2_line48 | 3 | 99 | 4.9025e-08 | 7.2173e-07 | 4.952e-08 | 7.2902e-07
270 | feeder2_line49 | 1 | 266.4 | 11.0327 | 11.0324 | 4.1414 | 4.1413
270 | feeder2_line49 | 2 | 266.4 | 2.3494 | 2.3493 | 0.88191 | 0.88189
270 | feeder2_line49 | 3 | 266.4 | 0.17156 | 0.17132 | 0.0644 | 0.06431
270 | feeder2_line50 | 1 | 99 | 5.6423e-07 | 1.2159e-06 | 5.6993e-07 | 1.2282e-06
270 | feeder2_line50 | 2 | 99 | 0.89928 | 0.89926 | 0.90837 | 0.90834
270 | feeder2_line50 | 3 | 99 | 5.6612e-07 | 1.2199e-06 | 5.7184e-07 | 1.2323e-06
270 | feeder2_line51 | 1 | 99 | 10.3802 | 10.3801 | 10.485 | 10.485
270 | feeder2_line51 | 2 | 99 | 5.6465e-07 | 1.321e-06 | 5.7035e-07 | 1.3343e-06
270 | feeder2_line51 | 3 | 99 | 5.661e-07 | 1.3244e-06 | 5.7182e-07 | 1.3377e-06
270 | feeder2_line52 | 1 | 266.4 | 0.6524 | 0.65229 | 0.24489 | 0.24485
270 | feeder2_line52 | 2 | 266.4 | 1.4509 | 1.451 | 0.54464 | 0.54465
270 | feeder2_line52 | 3 | 266.4 | 0.17143 | 0.17132 | 0.064349 | 0.06431
270 | feeder2_line53 | 1 | 99 | 5.3962e-07 | 7.4208e-07 | 5.4507e-07 | 7.4958e-07
270 | feeder2_line53 | 2 | 99 | 1.451 | 1.451 | 1.4656 | 1.4656
270 | feeder2_line53 | 3 | 99 | 5.416e-07 | 7.4455e-07 | 5.4707e-07 | 7.5207e-07
270 | feeder2_line54 | 1 | 266.4 | 0.65222 | 0.65229 | 0.24483 | 0.24485
270 | feeder2_line54 | 2 | 266.4 | 8.4244e-05 | 4.5559e-06 | 3.1623e-05 | 1.7102e-06
270 | feeder2_line54 | 3 | 266.4 | 0.17124 | 0.17132 | 0.064278 | 0.06431
270 | feeder2_line55 | 1 | 99 | 0.18013 | 0.18013 | 0.18195 | 0.18195
270 | feeder2_line55 | 2 | 99 | 4.9118e-08 | 7.1753e-07 | 4.9614e-08 | 7.2477e-07
270 | feeder2_line55 | 3 | 99 | 4.895e-08 | 7.1961e-07 | 4.9445e-08 | 7.2688e-07
270 | feeder2_line56 | 1 | 354.6 | 99.7502 | 99.75 | 28.1303 | 28.1303
270 | feeder2_line56 | 2 | 354.6 | 101.9107 | 101.8996 | 28.7396 | 28.7365
270 | feeder2_line56 | 3 | 354.6 | 95.3809 | 95.3966 | 26.8982 | 26.9026
270 | feeder2_line57 | 1 | 99 | 7.3828e-07 | 1.52e-06 | 7.4574e-07 | 1.5354e-06
270 | feeder2_line57 | 2 | 99 | 7.3721e-07 | 1.5212e-06 | 7.4465e-07 | 1.5366e-06
270 | feeder2_line57 | 3 | 99 | 0.17131 | 0.17132 | 0.17304 | 0.17305
270 | feeder2_line58 | 1 | 266.4 | 0.65229 | 0.65229 | 0.24485 | 0.24485
270 | feeder2_line58 | 2 | 266.4 | 1.8658e-05 | 2.6451e-06 | 7.0037e-06 | 9.9291e-07
270 | feeder2_line58 | 3 | 266.4 | 1.8717e-05 | 2.6516e-06 | 7.0257e-06 | 9.9535e-07
270 | feeder2_line59 | 1 | 99 | 4.922e-08 | 5.2838e-07 | 4.9717e-08 | 5.3372e-07
270 | feeder2_line59 | 2 | 99 | 4.9148e-08 | 5.2879e-07 | 4.9644e-08 | 5.3413e-07
270 | feeder2_line59 | 3 | 99 | 0.1092 | 0.1092 | 0.1103 | 0.1103
270 | feeder2_line60 | 1 | 99 | 2.9442e-07 | 7.9853e-07 | 2.9739e-07 | 8.066e-07
270 | feeder2_line60 | 2 | 99 | 2.9462e-07 | 7.9917e-07 | 2.976e-07 | 8.0724e-07
270 | feeder2_line60 | 3 | 99 | 0.062251 | 0.062254 | 0.06288 | 0.062883
270 | feeder2_line61 | 1 | 266.4 | 0.19857 | 0.19873 | 0.074537 | 0.074597
270 | feeder2_line61 | 2 | 266.4 | 1.853 | 1.8532 | 0.69556 | 0.69563
270 | feeder2_line61 | 3 | 266.4 | 0.38581 | 0.38605 | 0.14482 | 0.14491
270 | feeder2_line62 | 1 | 354.6 | 99.7699 | 99.7697 | 28.1359 | 28.1358
270 | feeder2_line62 | 2 | 354.6 | 100.8429 | 100.8317 | 28.4385 | 28.4353
270 | feeder2_line62 | 3 | 354.6 | 95.4314 | 95.4471 | 26.9124 | 26.9168
270 | feeder2_line63 | 1 | 99 | 0.35881 | 0.3588 | 0.36243 | 0.36242
270 | feeder2_line63 | 2 | 99 | 5.6468e-07 | 1.2015e-06 | 5.7038e-07 | 1.2137e-06
270 | feeder2_line63 | 3 | 99 | 5.6612e-07 | 1.2046e-06 | 5.7183e-07 | 1.2167e-06
270 | feeder2_line64 | 1 | 99 | 0.29351 | 0.2935 | 0.29647 | 0.29647
270 | feeder2_line64 | 2 | 99 | 2.2609e-12 | 3.1651e-07 | 2.2837e-12 | 3.197e-07
270 | feeder2_line64 | 3 | 99 | 5.2964e-12 | 3.1731e-07 | 5.3499e-12 | 3.2051e-07
270 | feeder2_line65 | 1 | 99 | 4.9038e-08 | 6.2956e-07 | 4.9534e-08 | 6.3592e-07
270 | feeder2_line65 | 2 | 99 | 0.27878 | 0.27878 | 0.2816 | 0.2816
270 | feeder2_line65 | 3 | 99 | 4.8898e-08 | 6.3148e-07 | 4.9392e-08 | 6.3786e-07
270 | feeder2_line66 | 1 | 354.6 | 99.7699 | 99.7697 | 28.1359 | 28.1358
270 | feeder2_line66 | 2 | 354.6 | 100.8649 | 100.8537 | 28.4447 | 28.4415
270 | feeder2_line66 | 3 | 354.6 | 95.4314 | 95.4471 | 26.9124 | 26.9168
270 | feeder2_line67 | 1 | 99 | 2.4533e-08 | 3.5608e-07 | 2.4781e-08 | 3.5967e-07
270 | feeder2_line67 | 2 | 99 | 2.4554e-08 | 3.5608e-07 | 2.4802e-08 | 3.5968e-07
270 | feeder2_line67 | 3 | 99 | 0.09491 | 0.094917 | 0.095869 | 0.095876
270 | feeder2_line68 | 1 | 266.4 | 0.1986 | 0.19873 | 0.074551 | 0.074597
270 | feeder2_line68 | 2 | 266.4 | 1.853 | 1.8532 | 0.69558 | 0.69563
270 | feeder2_line68 | 3 | 266.4 | 0.29101 | 0.2912 | 0.10924 | 0.10931
270 | feeder2_line69 | 1 | 99 | 2.8279 | 2.8279 | 2.8565 | 2.8564
270 | feeder2_line69 | 2 | 99 | 2.4955e-06 | 6.5337e-07 | 2.5207e-06 | 6.5997e-07
270 | feeder2_line69 | 3 | 99 | 2.5058e-06 | 6.5544e-07 | 2.5311e-06 | 6.6206e-07
270 | feeder2_line70 | 1 | 354.6 | 97.7181 | 97.7178 | 27.5573 | 27.5572
270 | feeder2_line70 | 2 | 354.6 | 100.865 | 100.8537 | 28.4447 | 28.4415
270 | feeder2_line70 | 3 | 354.6 | 95.4315 | 95.4471 | 26.9124 | 26.9168
270 | feeder2_line71 | 1 | 99 | 4.9023e-08 | 7.021e-07 | 4.9518e-08 | 7.0919e-07
270 | feeder2_line71 | 2 | 99 | 0.32182 | 0.32175 | 0.32507 | 0.325
270 | feeder2_line71 | 3 | 99 | 4.8881e-08 | 7.0424e-07 | 4.9374e-08 | 7.1136e-07
270 | feeder2_line72 | 1 | 354.6 | 97.7181 | 97.7178 | 27.5573 | 27.5572
270 | feeder2_line72 | 2 | 354.6 | 100.8855 | 100.8742 | 28.4505 | 28.4473
270 | feeder2_line72 | 3 | 354.6 | 95.4315 | 95.4471 | 26.9124 | 26.9168
270 | feeder2_line73 | 1 | 99 | 5.8787e-07 | 1.5075e-06 | 5.9381e-07 | 1.5227e-06
270 | feeder2_line73 | 2 | 99 | 0.25708 | 0.25708 | 0.25968 | 0.25968
270 | feeder2_line73 | 3 | 99 | 5.8949e-07 | 1.512e-06 | 5.9545e-07 | 1.5273e-06
270 | feeder2_line74 | 1 | 99 | 4.9064e-08 | 4.4962e-07 | 4.956e-08 | 4.5416e-07
270 | feeder2_line74 | 2 | 99 | 0.29107 | 0.29103 | 0.29401 | 0.29397
270 | feeder2_line74 | 3 | 99 | 4.8925e-08 | 4.5097e-07 | 4.9419e-08 | 4.5553e-07
270 | feeder2_line75 | 1 | 266.4 | 0.1987 | 0.19873 | 0.074588 | 0.074597
270 | feeder2_line75 | 2 | 266.4 | 1.4697 | 1.4697 | 0.55168 | 0.55169
270 | feeder2_line75 | 3 | 266.4 | 0.29111 | 0.2912 | 0.10928 | 0.10931
270 | feeder2_line76 | 1 | 99 | 0.19873 | 0.19873 | 0.20074 | 0.20073
270 | feeder2_line76 | 2 | 99 | 8.3268e-07 | 1.555e-06 | 8.4109e-07 | 1.5707e-06
270 | feeder2_line76 | 3 | 99 | 8.3531e-07 | 1.5597e-06 | 8.4375e-07 | 1.5755e-06
270 | feeder2_line77 | 1 | 99 | 2.4533e-08 | 5.6502e-07 | 2.4781e-08 | 5.7073e-07
270 | feeder2_line77 | 2 | 99 | 2.4553e-08 | 5.65e-07 | 2.4801e-08 | 5.7071e-07
270 | feeder2_line77 | 3 | 99 | 0.29114 | 0.2912 | 0.29408 | 0.29414
270 | feeder2_line78 | 1 | 266.4 | 2.191e-12 | 9.3715e-07 | 8.2246e-13 | 3.5178e-07
270 | feeder2_line78 | 2 | 266.4 | 1.4697 | 1.4697 | 0.55169 | 0.55169
270 | feeder2_line78 | 3 | 266.4 | 8.0135e-12 | 9.3976e-07 | 3.0081e-12 | 3.5276e-07
270 | feeder2_line79 | 1 | 354.6 | 1.3169 | 1.3165 | 0.37138 | 0.37128
270 | feeder2_line79 | 2 | 354.6 | 2.6909 | 2.6907 | 0.75885 | 0.75881
270 | feeder2_line79 | 3 | 354.6 | 2.3495 | 2.3493 | 0.66258 | 0.66254
270 | feeder2_line80 | 1 | 354.6 | 97.1648 | 97.1643 | 27.4012 | 27.4011
270 | feeder2_line80 | 2 | 354.6 | 99.2937 | 99.282 | 28.0016 | 27.9983
270 | feeder2_line80 | 3 | 354.6 | 95.176 | 95.1918 | 26.8404 | 26.8448
270 | feeder2_line81 | 1 | 354.6 | 97.1646 | 97.1643 | 27.4012 | 27.4011
270 | feeder2_line81 | 2 | 354.6 | 99.2936 | 99.282 | 28.0016 | 27.9983
270 | feeder2_line81 | 3 | 354.6 | 94.4812 | 94.4973 | 26.6445 | 26.649
270 | feeder2_line82 | 1 | 354.6 | 2.8895e-11 | 7.1957e-07 | 8.1485e-12 | 2.0292e-07
270 | feeder2_line82 | 2 | 354.6 | 3.3409e-11 | 7.1941e-07 | 9.4217e-12 | 2.0288e-07
270 | feeder2_line82 | 3 | 354.6 | 1.1553 | 1.1552 | 0.32579 | 0.32578
270 | feeder2_line83 | 1 | 354.6 | 97.1647 | 97.1643 | 27.4012 | 27.4011
270 | feeder2_line83 | 2 | 354.6 | 98.6259 | 98.6142 | 27.8133 | 27.81
270 | feeder2_line83 | 3 | 354.6 | 94.4813 | 94.4973 | 26.6445 | 26.649
270 | feeder2_line84 | 1 | 354.6 | 1.4363e-11 | 1.2714e-06 | 4.0503e-12 | 3.5855e-07
270 | feeder2_line84 | 2 | 354.6 | 0.97799 | 0.97796 | 0.2758 | 0.27579
270 | feeder2_line84 | 3 | 354.6 | 1.1526e-11 | 1.2751e-06 | 3.2505e-12 | 3.5959e-07
270 | feeder2_line85 | 1 | 99 | 0.2124 | 0.21239 | 0.21455 | 0.21454
270 | feeder2_line85 | 2 | 99 | 4.9061e-08 | 4.5358e-07 | 4.9556e-08 | 4.5816e-07
270 | feeder2_line85 | 3 | 99 | 4.8835e-08 | 4.5511e-07 | 4.9328e-08 | 4.5971e-07
270 | feeder2_line86 | 1 | 354.6 | 97.193 | 97.1926 | 27.4092 | 27.4091
270 | feeder2_line86 | 2 | 354.6 | 98.6258 | 98.6142 | 27.8133 | 27.81
270 | feeder2_line86 | 3 | 354.6 | 94.4813 | 94.4973 | 26.6445 | 26.649
270 | feeder2_line87 | 1 | 354.6 | 97.193 | 97.1926 | 27.4092 | 27.4091
270 | feeder2_line87 | 2 | 354.6 | 98.653 | 98.6412 | 27.8209 | 27.8176
270 | feeder2_line87 | 3 | 354.6 | 94.5223 | 94.5384 | 26.656 | 26.6606
270 | feeder2_line88 | 1 | 354.6 | 0.00011115 | 3.2938e-06 | 3.1346e-05 | 9.2888e-07
270 | feeder2_line88 | 2 | 354.6 | 0.11478 | 0.11445 | 0.03237 | 0.032276
270 | feeder2_line88 | 3 | 354.6 | 0.26185 | 0.26186 | 0.073843 | 0.073845
270 | feeder2_line89 | 1 | 354.6 | 97.1925 | 97.1926 | 27.409 | 27.4091
270 | feeder2_line89 | 2 | 354.6 | 97.384 | 97.3727 | 27.4631 | 27.4599
270 | feeder2_line89 | 3 | 354.6 | 94.5217 | 94.5384 | 26.6559 | 26.6606
270 | feeder2_line90 | 1 | 354.6 | 0.00070818 | 1.9855e-06 | 0.00019971 | 5.5992e-07
270 | feeder2_line90 | 2 | 354.6 | 1.9487 | 1.9487 | 0.54956 | 0.54954
270 | feeder2_line90 | 3 | 354.6 | 0.00071139 | 1.9942e-06 | 0.00020062 | 5.6239e-07
270 | feeder2_line91 | 1 | 354.6 | 97.1926 | 97.1926 | 27.4091 | 27.4091
270 | feeder2_line91 | 2 | 354.6 | 97.3842 | 97.3727 | 27.4631 | 27.4599
270 | feeder2_line91 | 3 | 354.6 | 94.5355 | 94.552 | 26.6598 | 26.6644
270 | feeder2_line92 | 1 | 354.6 | 1.1808e-11 | 1.0024e-06 | 3.3298e-12 | 2.827e-07
270 | feeder2_line92 | 2 | 354.6 | 3.0155e-11 | 1.0021e-06 | 8.5039e-12 | 2.826e-07
270 | feeder2_line92 | 3 | 354.6 | 0.062425 | 0.062431 | 0.017604 | 0.017606
270 | feeder2_line93 | 1 | 99 | 2.4464e-08 | 3.3462e-07 | 2.4711e-08 | 3.38e-07
270 | feeder2_line93 | 2 | 99 | 0.97787 | 0.97784 | 0.98775 | 0.98772
270 | feeder2_line93 | 3 | 99 | 2.4404e-08 | 3.3566e-07 | 2.465e-08 | 3.3905e-07
270 | feeder2_line94 | 1 | 354.6 | 2.4468e-06 | 1.6292e-06 | 6.9001e-07 | 4.5944e-07
270 | feeder2_line94 | 2 | 354.6 | 0.97165 | 0.97166 | 0.27401 | 0.27402
270 | feeder2_line94 | 3 | 354.6 | 2.4403e-06 | 1.634e-06 | 6.8818e-07 | 4.608e-07
270 | feeder2_line95 | 1 | 99 | 3.4931e-06 | 2.5543e-06 | 3.5284e-06 | 2.5801e-06
270 | feeder2_line95 | 2 | 99 | 0.11468 | 0.11445 | 0.11584 | 0.11561
270 | feeder2_line95 | 3 | 99 | 3.5041e-06 | 2.5621e-06 | 3.5395e-06 | 2.588e-06
270 | feeder2_line96 | 1 | 354.6 | 0.00011853 | 6.0891e-07 | 3.3426e-05 | 1.7172e-07
270 | feeder2_line96 | 2 | 354.6 | 0.00011849 | 6.0869e-07 | 3.3415e-05 | 1.7166e-07
270 | feeder2_line96 | 3 | 354.6 | 0.26183 | 0.26186 | 0.073838 | 0.073845
270 | feeder2_line97 | 1 | 354.6 | 97.2372 | 97.2369 | 27.4216 | 27.4216
270 | feeder2_line97 | 2 | 354.6 | 97.3845 | 97.3727 | 27.4632 | 27.4599
270 | feeder2_line97 | 3 | 354.6 | 94.5358 | 94.552 | 26.6598 | 26.6644
270 | feeder2_line98 | 1 | 354.6 | 0.15897 | 0.15732 | 0.044831 | 0.044365
270 | feeder2_line98 | 2 | 354.6 | 0.0016636 | 6.0414e-07 | 0.00046915 | 1.7037e-07
270 | feeder2_line98 | 3 | 354.6 | 0.0016729 | 6.1189e-07 | 0.00047177 | 1.7256e-07
270 | feeder2_line99 | 1 | 99 | 2.4478e-08 | 4.3773e-07 | 2.4725e-08 | 4.4215e-07
270 | feeder2_line99 | 2 | 99 | 2.4533e-08 | 4.3757e-07 | 2.478e-08 | 4.4199e-07
270 | feeder2_line99 | 3 | 99 | 0.26174 | 0.26186 | 0.26439 | 0.2645
270 | feeder2_line100 | 1 | 99 | 0.15731 | 0.15732 | 0.1589 | 0.15891
270 | feeder2_line100 | 2 | 99 | 2.4514e-08 | 6.0025e-07 | 2.4762e-08 | 6.0632e-07
270 | feeder2_line100 | 3 | 99 | 2.4396e-08 | 6.0236e-07 | 2.4643e-08 | 6.0845e-07
270 | feeder2_line101 | 1 | 354.6 | 0.97213 | 0.97191 | 0.27415 | 0.27409
270 | feeder2_line101 | 2 | 354.6 | 2.6909 | 2.6907 | 0.75885 | 0.75881
270 | feeder2_line101 | 3 | 354.6 | 2.3495 | 2.3493 | 0.66257 | 0.66254
270 | feeder2_line102 | 1 | 99 | 0.44795 | 0.44794 | 0.45248 | 0.45246
270 | feeder2_line102 | 2 | 99 | 2.2869e-06 | 8.6023e-07 | 2.31e-06 | 8.6892e-07
270 | feeder2_line102 | 3 | 99 | 2.2977e-06 | 8.6306e-07 | 2.3209e-06 | 8.7177e-07
270 | feeder2_line103 | 1 | 99 | 5.3817e-07 | 7.876e-07 | 5.436e-07 | 7.9556e-07
270 | feeder2_line103 | 2 | 99 | 0.09775 | 0.09775 | 0.098738 | 0.098737
270 | feeder2_line103 | 3 | 99 | 5.3992e-07 | 7.8995e-07 | 5.4537e-07 | 7.9793e-07
270 | feeder2_line104 | 1 | 354.6 | 0.97212 | 0.97191 | 0.27414 | 0.27409
270 | feeder2_line104 | 2 | 354.6 | 2.6285 | 2.6283 | 0.74124 | 0.74121
270 | feeder2_line104 | 3 | 354.6 | 2.3494 | 2.3493 | 0.66255 | 0.66254
270 | feeder2_line105 | 1 | 99 | 2.4949e-06 | 7.247e-07 | 2.5201e-06 | 7.3202e-07
270 | feeder2_line105 | 2 | 99 | 2.4935e-06 | 7.2448e-07 | 2.5187e-06 | 7.318e-07
270 | feeder2_line105 | 3 | 99 | 0.48859 | 0.48868 | 0.49352 | 0.49362
270 | feeder2_line106 | 1 | 354.6 | 0.97209 | 0.97191 | 0.27414 | 0.27409
270 | feeder2_line106 | 2 | 354.6 | 2.6284 | 2.6283 | 0.74124 | 0.74121
270 | feeder2_line106 | 3 | 354.6 | 1.8754 | 1.8753 | 0.52887 | 0.52884
270 | feeder2_line107 | 1 | 99 | 3.1807e-07 | 8.8316e-07 | 3.2128e-07 | 8.9208e-07
270 | feeder2_line107 | 2 | 99 | 0.9799 | 0.97993 | 0.9898 | 0.98983
270 | feeder2_line107 | 3 | 99 | 3.1881e-07 | 8.8576e-07 | 3.2203e-07 | 8.9471e-07
270 | feeder2_line108 | 1 | 354.6 | 0.9721 | 0.97191 | 0.27414 | 0.27409
270 | feeder2_line108 | 2 | 354.6 | 1.6574 | 1.6573 | 0.46741 | 0.46737
270 | feeder2_line108 | 3 | 354.6 | 1.8754 | 1.8753 | 0.52887 | 0.52884
270 | feeder2_line109 | 1 | 354.6 | 97.2958 | 97.2956 | 27.4382 | 27.4381
270 | feeder2_line109 | 2 | 354.6 | 97.3845 | 97.3727 | 27.4632 | 27.4599
270 | feeder2_line109 | 3 | 354.6 | 94.5358 | 94.552 | 26.6599 | 26.6644
270 | feeder2_line110 | 1 | 99 | 0.241 | 0.2402 | 0.24344 | 0.24263
270 | feeder2_line110 | 2 | 99 | 0.00078534 | 8.8758e-07 | 0.00079328 | 8.9655e-07
270 | feeder2_line110 | 3 | 99 | 0.00078928 | 8.9107e-07 | 0.00079726 | 9.0007e-07
270 | feeder2_line111 | 1 | 99 | 2.4476e-08 | 3.7386e-07 | 2.4723e-08 | 3.7763e-07
270 | feeder2_line111 | 2 | 99 | 0.073355 | 0.073287 | 0.074096 | 0.074027
270 | feeder2_line111 | 3 | 99 | 2.4412e-08 | 3.7501e-07 | 2.4658e-08 | 3.7879e-07
270 | feeder2_line112 | 1 | 99 | 3.1788e-07 | 8.984e-07 | 3.2109e-07 | 9.0747e-07
270 | feeder2_line112 | 2 | 99 | 0.041534 | 0.041383 | 0.041953 | 0.041801
270 | feeder2_line112 | 3 | 99 | 3.1864e-07 | 9.0116e-07 | 3.2186e-07 | 9.1026e-07
270 | feeder2_line113 | 1 | 99 | 0.1305 | 0.13049 | 0.13182 | 0.13181
270 | feeder2_line113 | 2 | 99 | 3.1758e-07 | 8.8472e-07 | 3.2079e-07 | 8.9366e-07
270 | feeder2_line113 | 3 | 99 | 3.1841e-07 | 8.8788e-07 | 3.2163e-07 | 8.9685e-07
270 | feeder2_line114 | 1 | 99 | 0.097716 | 0.09771 | 0.098703 | 0.098697
270 | feeder2_line114 | 2 | 99 | 2.4531e-08 | 4.2776e-07 | 2.4779e-08 | 4.3209e-07
270 | feeder2_line114 | 3 | 99 | 2.4429e-08 | 4.2916e-07 | 2.4676e-08 | 4.335e-07
270 | feeder2_line115 | 1 | 99 | 2.449e-08 | 5.5113e-07 | 2.4738e-08 | 5.567e-07
270 | feeder2_line115 | 2 | 99 | 0.32997 | 0.32997 | 0.3333 | 0.3333
270 | feeder2_line115 | 3 | 99 | 2.4431e-08 | 5.5275e-07 | 2.4677e-08 | 5.5833e-07
270 | feeder2_line116 | 1 | 354.6 | 0.97211 | 0.97191 | 0.27414 | 0.27409
270 | feeder2_line116 | 2 | 354.6 | 1.4168 | 1.4167 | 0.39956 | 0.39953
270 | feeder2_line116 | 3 | 354.6 | 1.8754 | 1.8753 | 0.52887 | 0.52884
270 | feeder2_line117 | 1 | 99 | 4.8895e-08 | 6.2802e-07 | 4.9388e-08 | 6.3436e-07
270 | feeder2_line117 | 2 | 99 | 0.16311 | 0.16302 | 0.16476 | 0.16467
270 | feeder2_line117 | 3 | 99 | 4.8757e-08 | 6.3002e-07 | 4.925e-08 | 6.3638e-07
270 | feeder2_line118 | 1 | 354.6 | 97.2958 | 97.2956 | 27.4382 | 27.4381
270 | feeder2_line118 | 2 | 354.6 | 97.4062 | 97.3943 | 27.4693 | 27.466
270 | feeder2_line118 | 3 | 354.6 | 94.5358 | 94.552 | 26.6599 | 26.6644
270 | feeder2_line119 | 1 | 99 | 2.4488e-08 | 5.9304e-07 | 2.4736e-08 | 5.9903e-07
270 | feeder2_line119 | 2 | 99 | 2.4534e-08 | 5.9283e-07 | 2.4781e-08 | 5.9882e-07
270 | feeder2_line119 | 3 | 99 | 0.54262 | 0.54263 | 0.5481 | 0.54812
270 | feeder2_line120 | 1 | 354.6 | 0.97211 | 0.97191 | 0.27414 | 0.27409
270 | feeder2_line120 | 2 | 354.6 | 1.4168 | 1.4167 | 0.39955 | 0.39953
270 | feeder2_line120 | 3 | 354.6 | 1.3626 | 1.3625 | 0.38428 | 0.38424
270 | feeder2_line121 | 1 | 99 | 3.1805e-07 | 9.1834e-07 | 3.2127e-07 | 9.2761e-07
270 | feeder2_line121 | 2 | 99 | 1.3059 | 1.3059 | 1.3191 | 1.3191
270 | feeder2_line121 | 3 | 99 | 3.188e-07 | 9.21e-07 | 3.2202e-07 | 9.3031e-07
270 | feeder2_line122 | 1 | 354.6 | 0.97208 | 0.97192 | 0.27413 | 0.27409
270 | feeder2_line122 | 2 | 354.6 | 0.18026 | 0.18003 | 0.050836 | 0.050769
270 | feeder2_line122 | 3 | 354.6 | 1.3626 | 1.3625 | 0.38427 | 0.38424
270 | feeder2_line123 | 1 | 99 | 5.6266e-07 | 9.5161e-07 | 5.6834e-07 | 9.6123e-07
270 | feeder2_line123 | 2 | 99 | 5.6245e-07 | 9.5127e-07 | 5.6813e-07 | 9.6088e-07
270 | feeder2_line123 | 3 | 99 | 0.76215 | 0.76212 | 0.76985 | 0.76982
270 | feeder2_line124 | 1 | 354.6 | 0.97211 | 0.97192 | 0.27414 | 0.27409
270 | feeder2_line124 | 2 | 354.6 | 0.18017 | 0.18003 | 0.05081 | 0.050769
270 | feeder2_line124 | 3 | 354.6 | 0.74212 | 0.7421 | 0.20928 | 0.20928
270 | feeder2_line125 | 1 | 99 | 5.6266e-07 | 8.8462e-07 | 5.6834e-07 | 8.9355e-07
270 | feeder2_line125 | 2 | 99 | 5.6245e-07 | 8.8431e-07 | 5.6813e-07 | 8.9324e-07
270 | feeder2_line125 | 3 | 99 | 0.15682 | 0.15692 | 0.1584 | 0.15851
270 | feeder2_line126 | 1 | 354.6 | 0.97224 | 0.97192 | 0.27418 | 0.27409
270 | feeder2_line126 | 2 | 354.6 | 0.18033 | 0.18003 | 0.050854 | 0.050769
270 | feeder2_line126 | 3 | 354.6 | 0.58698 | 0.5867 | 0.16553 | 0.16546
270 | feeder2_line127 | 1 | 99 | 5.6265e-07 | 1.059e-06 | 5.6833e-07 | 1.0697e-06
270 | feeder2_line127 | 2 | 99 | 5.6246e-07 | 1.0587e-06 | 5.6814e-07 | 1.0693e-06
270 | feeder2_line127 | 3 | 99 | 0.21242 | 0.21243 | 0.21456 | 0.21458
270 | feeder2_line128 | 1 | 354.6 | 0.97222 | 0.97192 | 0.27417 | 0.27409
270 | feeder2_line128 | 2 | 354.6 | 0.18025 | 0.18003 | 0.050831 | 0.050769
270 | feeder2_line128 | 3 | 354.6 | 0.37449 | 0.37429 | 0.10561 | 0.10555
270 | feeder2_line129 | 1 | 99 | 5.3816e-07 | 8.5871e-07 | 5.436e-07 | 8.6739e-07
270 | feeder2_line129 | 2 | 99 | 0.18003 | 0.18003 | 0.18185 | 0.18185
270 | feeder2_line129 | 3 | 99 | 5.3986e-07 | 8.6121e-07 | 5.4531e-07 | 8.6991e-07
270 | feeder2_line130 | 1 | 354.6 | 0.97226 | 0.97192 | 0.27418 | 0.27409
270 | feeder2_line130 | 2 | 354.6 | 0.00030202 | 4.5429e-06 | 8.5173e-05 | 1.2811e-06
270 | feeder2_line130 | 3 | 354.6 | 0.37451 | 0.37429 | 0.10561 | 0.10555
270 | feeder2_line131 | 1 | 99 | 5.6265e-07 | 9.5174e-07 | 5.6833e-07 | 9.6136e-07
270 | feeder2_line131 | 2 | 99 | 5.6245e-07 | 9.5142e-07 | 5.6813e-07 | 9.6103e-07
270 | feeder2_line131 | 3 | 99 | 0.1619 | 0.16191 | 0.16353 | 0.16354
270 | feeder2_line132 | 1 | 354.6 | 0.97208 | 0.97192 | 0.27413 | 0.27409
270 | feeder2_line132 | 2 | 354.6 | 0.00012304 | 2.8562e-06 | 3.47e-05 | 8.0547e-07
270 | feeder2_line132 | 3 | 354.6 | 0.21249 | 0.21243 | 0.059925 | 0.059907
270 | feeder2_line133 | 1 | 99 | 0.97196 | 0.97192 | 0.98178 | 0.98174
270 | feeder2_line133 | 2 | 99 | 2.9349e-07 | 9.5902e-07 | 2.9646e-07 | 9.6871e-07
270 | feeder2_line133 | 3 | 99 | 2.9436e-07 | 9.6213e-07 | 2.9733e-07 | 9.7185e-07
270 | feeder2_line134 | 1 | 354.6 | 8.2136e-12 | 1.7495e-06 | 2.3163e-12 | 4.9338e-07
270 | feeder2_line134 | 2 | 354.6 | 8.4659e-12 | 1.749e-06 | 2.3874e-12 | 4.9324e-07
270 | feeder2_line134 | 3 | 354.6 | 0.21242 | 0.21243 | 0.059904 | 0.059907
270 | feeder2_line135 | 1 | 99 | 0.3216 | 0.32159 | 0.32484 | 0.32484
270 | feeder2_line135 | 2 | 99 | 4.8995e-08 | 5.7167e-07 | 4.949e-08 | 5.7744e-07
270 | feeder2_line135 | 3 | 99 | 4.8734e-08 | 5.7379e-07 | 4.9226e-08 | 5.7958e-07
270 | feeder2_line136 | 1 | 354.6 | 97.3334 | 97.3332 | 27.4488 | 27.4487
270 | feeder2_line136 | 2 | 354.6 | 97.4062 | 97.3943 | 27.4693 | 27.466
270 | feeder2_line136 | 3 | 354.6 | 94.5358 | 94.552 | 26.6598 | 26.6644
270 | feeder2_line137 | 1 | 99 | 0.82759 | 0.82752 | 0.83595 | 0.83588
270 | feeder2_line137 | 2 | 99 | 8.2941e-07 | 1.5395e-06 | 8.3779e-07 | 1.555e-06
270 | feeder2_line137 | 3 | 99 | 8.3263e-07 | 1.5452e-06 | 8.4104e-07 | 1.5608e-06
270 | feeder2_line138 | 1 | 354.6 | 96.7755 | 96.7753 | 27.2914 | 27.2914
270 | feeder2_line138 | 2 | 354.6 | 97.4063 | 97.3943 | 27.4693 | 27.466
270 | feeder2_line138 | 3 | 354.6 | 94.5359 | 94.5521 | 26.6599 | 26.6644
270 | feeder2_line139 | 1 | 99 | 4.8864e-08 | 4.7983e-07 | 4.9357e-08 | 4.8468e-07
270 | feeder2_line139 | 2 | 99 | 4.8981e-08 | 4.7959e-07 | 4.9476e-08 | 4.8443e-07
270 | feeder2_line139 | 3 | 99 | 0.13787 | 0.13896 | 0.13926 | 0.14036
270 | feeder2_line140 | 1 | 354.6 | 96.7754 | 96.7753 | 27.2914 | 27.2914
270 | feeder2_line140 | 2 | 354.6 | 97.4062 | 97.3943 | 27.4693 | 27.466
270 | feeder2_line140 | 3 | 354.6 | 94.5941 | 94.6112 | 26.6763 | 26.6811
270 | feeder2_line141 | 1 | 99 | 2.4643e-06 | 4.7455e-07 | 2.4892e-06 | 4.7934e-07
270 | feeder2_line141 | 2 | 99 | 0.19009 | 0.19009 | 0.19201 | 0.19201
270 | feeder2_line141 | 3 | 99 | 2.4744e-06 | 4.7609e-07 | 2.4994e-06 | 4.809e-07
270 | feeder2_line142 | 1 | 354.6 | 96.7755 | 96.7753 | 27.2914 | 27.2914
270 | feeder2_line142 | 2 | 354.6 | 97.4343 | 97.4223 | 27.4772 | 27.4738
270 | feeder2_line142 | 3 | 354.6 | 94.5942 | 94.6112 | 26.6763 | 26.6811
270 | feeder2_line143 | 1 | 99 | 8.2962e-07 | 1.6861e-06 | 8.38e-07 | 1.7032e-06
270 | feeder2_line143 | 2 | 99 | 0.97942 | 0.97945 | 0.98931 | 0.98934
270 | feeder2_line143 | 3 | 99 | 8.324e-07 | 1.6916e-06 | 8.4081e-07 | 1.7087e-06
270 | feeder2_line144 | 1 | 354.6 | 96.7754 | 96.7753 | 27.2914 | 27.2914
270 | feeder2_line144 | 2 | 354.6 | 96.7885 | 96.7765 | 27.2951 | 27.2917
270 | feeder2_line144 | 3 | 354.6 | 94.594 | 94.6112 | 26.6763 | 26.6811
270 | feeder2_line145 | 1 | 99 | 2.4421e-08 | 4.7275e-07 | 2.4668e-08 | 4.7752e-07
270 | feeder2_line145 | 2 | 99 | 1.1533 | 1.1533 | 1.165 | 1.165
270 | feeder2_line145 | 3 | 99 | 2.4354e-08 | 4.743e-07 | 2.46e-08 | 4.7909e-07
270 | feeder2_line146 | 1 | 354.6 | 96.7754 | 96.7753 | 27.2914 | 27.2914
270 | feeder2_line146 | 2 | 354.6 | 96.0978 | 96.0858 | 27.1003 | 27.097
270 | feeder2_line146 | 3 | 354.6 | 94.5941 | 94.6112 | 26.6763 | 26.6811
270 | feeder2_line147 | 1 | 99 | 0.10987 | 0.10986 | 0.11098 | 0.11096
270 | feeder2_line147 | 2 | 99 | 1.1217e-06 | 2.1792e-06 | 1.133e-06 | 2.2012e-06
270 | feeder2_line147 | 3 | 99 | 1.126e-06 | 2.1874e-06 | 1.1374e-06 | 2.2095e-06
270 | feeder2_line148 | 1 | 99 | 0.22056 | 0.22055 | 0.22279 | 0.22277
270 | feeder2_line148 | 2 | 99 | 5.8534e-07 | 1.4602e-06 | 5.9125e-07 | 1.475e-06
270 | feeder2_line148 | 3 | 99 | 5.8734e-07 | 1.4657e-06 | 5.9328e-07 | 1.4806e-06
270 | feeder2_line149 | 1 | 354.6 | 96.839 | 96.8388 | 27.3094 | 27.3093
270 | feeder2_line149 | 2 | 354.6 | 96.0979 | 96.0858 | 27.1004 | 27.097
270 | feeder2_line149 | 3 | 354.6 | 94.5942 | 94.6112 | 26.6763 | 26.6811
270 | feeder2_line150 | 1 | 354.6 | 96.839 | 96.8388 | 27.3094 | 27.3093
270 | feeder2_line150 | 2 | 354.6 | 95.1207 | 95.1086 | 26.8248 | 26.8214
270 | feeder2_line150 | 3 | 354.6 | 94.5942 | 94.6112 | 26.6763 | 26.6811
270 | feeder2_line151 | 1 | 99 | 9.5116e-06 | 1.7342e-06 | 9.6076e-06 | 1.7517e-06
270 | feeder2_line151 | 2 | 99 | 1.5185 | 1.5185 | 1.5338 | 1.5339
270 | feeder2_line151 | 3 | 99 | 9.5554e-06 | 1.7399e-06 | 9.6519e-06 | 1.7575e-06
270 | feeder2_line152 | 1 | 354.6 | 9.3291e-12 | 1.1552e-06 | 2.6309e-12 | 3.2577e-07
270 | feeder2_line152 | 2 | 354.6 | 2.1909e-11 | 1.1547e-06 | 6.1786e-12 | 3.2563e-07
270 | feeder2_line152 | 3 | 354.6 | 0.078395 | 0.078405 | 0.022108 | 0.022111
270 | feeder2_line153 | 1 | 99 | 1.3048 | 1.3048 | 1.318 | 1.318
270 | feeder2_line153 | 2 | 99 | 4.8947e-08 | 5.7765e-07 | 4.9441e-08 | 5.8349e-07
270 | feeder2_line153 | 3 | 99 | 4.867e-08 | 5.7987e-07 | 4.9162e-08 | 5.8573e-07
270 | feeder2_line154 | 1 | 99 | 5.6081e-07 | 8.6002e-07 | 5.6647e-07 | 8.687e-07
270 | feeder2_line154 | 2 | 99 | 5.6051e-07 | 8.5957e-07 | 5.6617e-07 | 8.6826e-07
270 | feeder2_line154 | 3 | 99 | 0.041407 | 0.041534 | 0.041825 | 0.041954
270 | feeder2_line155 | 1 | 99 | 95.9118 | 95.9114 | 96.8806 | 96.8802
270 | feeder2_line155 | 2 | 99 | 95.1207 | 95.1086 | 96.0815 | 96.0693
270 | feeder2_line155 | 3 | 99 | 94.6195 | 94.6365 | 95.5752 | 95.5925
270 | feeder2_line156 | 1 | 99 | 5.8538e-07 | 1.1324e-06 | 5.9129e-07 | 1.1439e-06
270 | feeder2_line156 | 2 | 99 | 0.097946 | 0.097945 | 0.098935 | 0.098934
270 | feeder2_line156 | 3 | 99 | 5.8717e-07 | 1.1362e-06 | 5.931e-07 | 1.1476e-06
270 | feeder2_line157 | 1 | 99 | 2.4411e-08 | 2.4584e-07 | 2.4658e-08 | 2.4832e-07
270 | feeder2_line157 | 2 | 99 | 1.4677 | 1.4677 | 1.4825 | 1.4825
270 | feeder2_line157 | 3 | 99 | 2.4343e-08 | 2.4666e-07 | 2.4589e-08 | 2.4915e-07
300 | feeder2_line1 | 1 | 354.6 | 100.6887 | 100.6868 | 28.395 | 28.3945
300 | feeder2_line1 | 2 | 354.6 | 100.665 | 100.6808 | 28.3883 | 28.3928
300 | feeder2_line1 | 3 | 354.6 | 101.3488 | 101.3451 | 28.5812 | 28.5801
300 | feeder2_line2 | 1 | 354.6 | 99.6805 | 99.6784 | 28.1107 | 28.1101
300 | feeder2_line2 | 2 | 354.6 | 100.6651 | 100.6808 | 28.3884 | 28.3928
300 | feeder2_line2 | 3 | 354.6 | 101.349 | 101.3451 | 28.5812 | 28.5801
300 | feeder2_line3 | 1 | 80.1 | 1.5696 | 1.5697 | 1.9596 | 1.9596
300 | feeder2_line3 | 2 | 80.1 | 5.6818e-07 | 1.05e-06 | 7.0933e-07 | 1.3108e-06
300 | feeder2_line3 | 3 | 80.1 | 5.6816e-07 | 1.05e-06 | 7.0932e-07 | 1.3108e-06
300 | feeder2_line4 | 1 | 354.6 | 99.6805 | 99.6784 | 28.1107 | 28.1101
300 | feeder2_line4 | 2 | 354.6 | 100.7227 | 100.7384 | 28.4046 | 28.409
300 | feeder2_line4 | 3 | 354.6 | 101.349 | 101.3451 | 28.5812 | 28.5801
300 | feeder2_line5 | 1 | 80.1 | 5.6764e-07 | 9.9048e-07 | 7.0866e-07 | 1.2366e-06
300 | feeder2_line5 | 2 | 80.1 | 0.27908 | 0.27908 | 0.34841 | 0.34841
300 | feeder2_line5 | 3 | 80.1 | 5.6814e-07 | 9.9135e-07 | 7.0929e-07 | 1.2376e-06
300 | feeder2_line6 | 1 | 80.1 | 5.6756e-07 | 1.165e-06 | 7.0857e-07 | 1.4545e-06
300 | feeder2_line6 | 2 | 80.1 | 5.681e-07 | 1.1661e-06 | 7.0923e-07 | 1.4558e-06
300 | feeder2_line6 | 3 | 80.1 | 0.085906 | 0.085901 | 0.10725 | 0.10724
300 | feeder2_line7 | 1 | 354.6 | 99.6805 | 99.6784 | 28.1107 | 28.1101
300 | feeder2_line7 | 2 | 354.6 | 100.7227 | 100.7384 | 28.4046 | 28.409
300 | feeder2_line7 | 3 | 354.6 | 101.3702 | 101.3663 | 28.5872 | 28.5861
300 | feeder2_line8 | 1 | 80.1 | 0.073286 | 0.073286 | 0.091493 | 0.091494
300 | feeder2_line8 | 2 | 80.1 | 5.6796e-07 | 1.1241e-06 | 7.0906e-07 | 1.4034e-06
300 | feeder2_line8 | 3 | 80.1 | 5.6793e-07 | 1.1241e-06 | 7.0903e-07 | 1.4033e-06
300 | feeder2_line9 | 1 | 354.6 | 99.6928 | 99.6908 | 28.1142 | 28.1136
300 | feeder2_line9 | 2 | 354.6 | 100.7226 | 100.7384 | 28.4046 | 28.409
300 | feeder2_line9 | 3 | 354.6 | 101.3701 | 101.3663 | 28.5872 | 28.5861
300 | feeder2_line10 | 1 | 80.1 | 8.3862e-07 | 1.4826e-06 | 1.047e-06 | 1.851e-06
300 | feeder2_line10 | 2 | 80.1 | 0.073164 | 0.073165 | 0.091341 | 0.091342
300 | feeder2_line10 | 3 | 80.1 | 8.3953e-07 | 1.4842e-06 | 1.0481e-06 | 1.8529e-06
300 | feeder2_line11 | 1 | 354.6 | 99.6929 | 99.6908 | 28.1142 | 28.1136
300 | feeder2_line11 | 2 | 354.6 | 100.7423 | 100.7579 | 28.4101 | 28.4145
300 | feeder2_line11 | 3 | 354.6 | 101.3702 | 101.3663 | 28.5872 | 28.5861
300 | feeder2_line12 | 1 | 80.1 | 5.4252e-07 | 9.8331e-07 | 6.773e-07 | 1.2276e-06
300 | feeder2_line12 | 2 | 80.1 | 5.4323e-07 | 9.8441e-07 | 6.782e-07 | 1.229e-06
300 | feeder2_line12 | 3 | 80.1 | 0.81654 | 0.81656 | 1.0194 | 1.0194
300 | feeder2_line13 | 1 | 354.6 | 99.693 | 99.6908 | 28.1142 | 28.1136
300 | feeder2_line13 | 2 | 354.6 | 100.7424 | 100.7579 | 28.4101 | 28.4145
300 | feeder2_line13 | 3 | 354.6 | 100.8344 | 100.8304 | 28.4361 | 28.435
300 | feeder2_line14 | 1 | 80.1 | 1.5948 | 1.5948 | 1.991 | 1.991
300 | feeder2_line14 | 2 | 80.1 | 2.9623e-07 | 6.4186e-07 | 3.6983e-07 | 8.0132e-07
300 | feeder2_line14 | 3 | 80.1 | 2.9624e-07 | 6.4183e-07 | 3.6983e-07 | 8.0128e-07
300 | feeder2_line15 | 1 | 354.6 | 98.6425 | 98.6404 | 27.818 | 27.8174
300 | feeder2_line15 | 2 | 354.6 | 100.7424 | 100.7579 | 28.4101 | 28.4145
300 | feeder2_line15 | 3 | 354.6 | 100.8344 | 100.8304 | 28.4361 | 28.435
300 | feeder2_line16 | 1 | 80.1 | 5.6704e-07 | 1.0216e-06 | 7.0792e-07 | 1.2754e-06
300 | feeder2_line16 | 2 | 80.1 | 1.0227 | 1.0227 | 1.2768 | 1.2768
300 | feeder2_line16 | 3 | 80.1 | 5.6772e-07 | 1.0228e-06 | 7.0876e-07 | 1.2769e-06
300 | feeder2_line17 | 1 | 354.6 | 98.6426 | 98.6404 | 27.818 | 27.8174
300 | feeder2_line17 | 2 | 354.6 | 100.1988 | 100.2144 | 28.2568 | 28.2613
300 | feeder2_line17 | 3 | 354.6 | 100.8344 | 100.8304 | 28.4361 | 28.435
300 | feeder2_line18 | 1 | 80.1 | 5.4183e-07 | 7.3059e-07 | 6.7644e-07 | 9.121e-07
300 | feeder2_line18 | 2 | 80.1 | 5.4281e-07 | 7.3171e-07 | 6.7766e-07 | 9.135e-07
300 | feeder2_line18 | 3 | 80.1 | 1.4109 | 1.4109 | 1.7614 | 1.7614
300 | feeder2_line19 | 1 | 354.6 | 98.6426 | 98.6404 | 27.818 | 27.8174
300 | feeder2_line19 | 2 | 354.6 | 100.1988 | 100.2144 | 28.2569 | 28.2613
300 | feeder2_line19 | 3 | 354.6 | 100.1781 | 100.174 | 28.251 | 28.2499
300 | feeder2_line20 | 1 | 99 | 5.4164e-07 | 8.7565e-07 | 5.4711e-07 | 8.8449e-07
300 | feeder2_line20 | 2 | 99 | 5.4269e-07 | 8.7708e-07 | 5.4817e-07 | 8.8594e-07
300 | feeder2_line20 | 3 | 99 | 0.35576 | 0.35575 | 0.35936 | 0.35934
300 | feeder2_line21 | 1 | 354.6 | 98.6426 | 98.6404 | 27.818 | 27.8174
300 | feeder2_line21 | 2 | 354.6 | 100.1988 | 100.2144 | 28.2569 | 28.2613
300 | feeder2_line21 | 3 | 354.6 | 100.2532 | 100.2491 | 28.2722 | 28.271
300 | feeder2_line22 | 1 | 99 | 5.6623e-07 | 1.0036e-06 | 5.7195e-07 | 1.0138e-06
300 | feeder2_line22 | 2 | 99 | 0.094628 | 0.094631 | 0.095584 | 0.095586
300 | feeder2_line22 | 3 | 99 | 5.6713e-07 | 1.0052e-06 | 5.7285e-07 | 1.0153e-06
300 | feeder2_line23 | 1 | 99 | 5.6623e-07 | 9.3948e-07 | 5.7195e-07 | 9.4897e-07
300 | feeder2_line23 | 2 | 99 | 5.672e-07 | 9.4107e-07 | 5.7293e-07 | 9.5058e-07
300 | feeder2_line23 | 3 | 99 | 1.407 | 1.407 | 1.4212 | 1.4212
300 | feeder2_line24 | 1 | 354.6 | 98.6426 | 98.6404 | 27.818 | 27.8174
300 | feeder2_line24 | 2 | 354.6 | 100.224 | 100.2395 | 28.2639 | 28.2683
300 | feeder2_line24 | 3 | 354.6 | 99.3812 | 99.377 | 28.0263 | 28.0251
300 | feeder2_line25 | 1 | 99 | 0.094867 | 0.094869 | 0.095825 | 0.095827
300 | feeder2_line25 | 2 | 99 | 4.9162e-08 | 6.8401e-07 | 4.9659e-08 | 6.9092e-07
300 | feeder2_line25 | 3 | 99 | 4.9267e-08 | 6.8393e-07 | 4.9765e-08 | 6.9084e-07
300 | feeder2_line26 | 1 | 99 | 0.22053 | 0.22053 | 0.22276 | 0.22276
300 | feeder2_line26 | 2 | 99 | 5.4248e-07 | 8.4744e-07 | 5.4796e-07 | 8.56e-07
300 | feeder2_line26 | 3 | 99 | 5.4236e-07 | 8.4734e-07 | 5.4784e-07 | 8.559e-07
300 | feeder2_line27 | 1 | 354.6 | 98.6877 | 98.6855 | 27.8307 | 27.8301
300 | feeder2_line27 | 2 | 354.6 | 100.224 | 100.2395 | 28.264 | 28.2683
300 | feeder2_line27 | 3 | 354.6 | 99.3812 | 99.377 | 28.0263 | 28.0251
300 | feeder2_line28 | 1 | 99 | 2.5074e-06 | 7.0178e-07 | 2.5327e-06 | 7.0887e-07
300 | feeder2_line28 | 2 | 99 | 0.10944 | 0.10944 | 0.11054 | 0.11054
300 | feeder2_line28 | 3 | 99 | 2.5138e-06 | 7.031e-07 | 2.5392e-06 | 7.102e-07
300 | feeder2_line29 | 1 | 354.6 | 98.6877 | 98.6855 | 27.8307 | 27.8301
300 | feeder2_line29 | 2 | 354.6 | 100.2634 | 100.2789 | 28.2751 | 28.2795
300 | feeder2_line29 | 3 | 354.6 | 99.3812 | 99.377 | 28.0263 | 28.0251
300 | feeder2_line30 | 1 | 266.4 | 11.8283 | 11.8281 | 4.4401 | 4.44
300 | feeder2_line30 | 2 | 266.4 | 0.34816 | 0.34788 | 0.13069 | 0.13058
300 | feeder2_line30 | 3 | 266.4 | 2.5222 | 2.5223 | 0.94677 | 0.94683
300 | feeder2_line31 | 1 | 354.6 | 99.7952 | 99.7923 | 28.143 | 28.1422
300 | feeder2_line31 | 2 | 354.6 | 100.3511 | 100.3661 | 28.2998 | 28.304
300 | feeder2_line31 | 3 | 354.6 | 98.0518 | 98.0468 | 27.6514 | 27.65
300 | feeder2_line32 | 1 | 354.6 | 99.7952 | 99.7923 | 28.143 | 28.1422
300 | feeder2_line32 | 2 | 354.6 | 100.4102 | 100.4252 | 28.3165 | 28.3207
300 | feeder2_line32 | 3 | 354.6 | 98.0518 | 98.0468 | 27.6514 | 27.65
300 | feeder2_line33 | 1 | 99 | 4.9366e-08 | 6.7629e-07 | 4.9864e-08 | 6.8312e-07
300 | feeder2_line33 | 2 | 99 | 0.25726 | 0.25727 | 0.25986 | 0.25987
300 | feeder2_line33 | 3 | 99 | 4.9186e-08 | 6.7775e-07 | 4.9683e-08 | 6.8459e-07
300 | feeder2_line34 | 1 | 354.6 | 99.7952 | 99.7923 | 28.143 | 28.1422
300 | feeder2_line34 | 2 | 354.6 | 100.4102 | 100.4252 | 28.3165 | 28.3207
300 | feeder2_line34 | 3 | 354.6 | 98.1183 | 98.1133 | 27.6701 | 27.6687
300 | feeder2_line35 | 1 | 99 | 2.9484e-07 | 7.488e-07 | 2.9781e-07 | 7.5637e-07
300 | feeder2_line35 | 2 | 99 | 2.9538e-07 | 7.5042e-07 | 2.9837e-07 | 7.58e-07
300 | feeder2_line35 | 3 | 99 | 0.27482 | 0.27482 | 0.2776 | 0.27759
300 | feeder2_line36 | 1 | 354.6 | 99.8032 | 99.8 | 28.1453 | 28.1444
300 | feeder2_line36 | 2 | 354.6 | 100.4102 | 100.4252 | 28.3165 | 28.3207
300 | feeder2_line36 | 3 | 354.6 | 98.1183 | 98.1133 | 27.6701 | 27.6687
300 | feeder2_line37 | 1 | 99 | 0.028568 | 0.028644 | 0.028856 | 0.028934
300 | feeder2_line37 | 2 | 99 | 2.9533e-07 | 8.3016e-07 | 2.9831e-07 | 8.3855e-07
300 | feeder2_line37 | 3 | 99 | 2.9536e-07 | 8.3018e-07 | 2.9834e-07 | 8.3856e-07
300 | feeder2_line38 | 1 | 99 | 3.1963e-07 | 7.6483e-07 | 3.2286e-07 | 7.7256e-07
300 | feeder2_line38 | 2 | 99 | 0.21244 | 0.21244 | 0.21458 | 0.21459
300 | feeder2_line38 | 3 | 99 | 3.2013e-07 | 7.6655e-07 | 3.2336e-07 | 7.7429e-07
300 | feeder2_line39 | 1 | 266.4 | 11.8283 | 11.8281 | 4.4401 | 4.44
300 | feeder2_line39 | 2 | 266.4 | 0.13582 | 0.13551 | 0.050983 | 0.050867
300 | feeder2_line39 | 3 | 266.4 | 2.5222 | 2.5223 | 0.94678 | 0.94683
300 | feeder2_line40 | 1 | 354.6 | 99.8311 | 99.8279 | 28.1531 | 28.1523
300 | feeder2_line40 | 2 | 354.6 | 100.4101 | 100.4252 | 28.3165 | 28.3207
300 | feeder2_line40 | 3 | 354.6 | 98.1182 | 98.1133 | 27.6701 | 27.6687
300 | feeder2_line41 | 1 | 99 | 0.095037 | 0.095039 | 0.095997 | 0.095999
300 | feeder2_line41 | 2 | 99 | 4.9058e-08 | 7.2535e-07 | 4.9553e-08 | 7.3267e-07
300 | feeder2_line41 | 3 | 99 | 4.9165e-08 | 7.2536e-07 | 4.9662e-08 | 7.3269e-07
300 | feeder2_line42 | 1 | 99 | 2.9489e-07 | 7.3814e-07 | 2.9787e-07 | 7.4559e-07
300 | feeder2_line42 | 2 | 99 | 2.9553e-07 | 7.3998e-07 | 2.9851e-07 | 7.4745e-07
300 | feeder2_line42 | 3 | 99 | 0.19 | 0.18999 | 0.19192 | 0.19191
300 | feeder2_line43 | 1 | 266.4 | 11.8283 | 11.8281 | 4.44 | 4.44
300 | feeder2_line43 | 2 | 266.4 | 0.1357 | 0.13551 | 0.05094 | 0.050867
300 | feeder2_line43 | 3 | 266.4 | 2.3953 | 2.3954 | 0.89915 | 0.89918
300 | feeder2_line44 | 1 | 354.6 | 99.8311 | 99.8279 | 28.1532 | 28.1523
300 | feeder2_line44 | 2 | 354.6 | 100.4102 | 100.4252 | 28.3165 | 28.3207
300 | feeder2_line44 | 3 | 354.6 | 98.2087 | 98.2038 | 27.6956 | 27.6942
300 | feeder2_line45 | 1 | 99 | 4.9336e-08 | 5.7075e-07 | 4.9834e-08 | 5.7652e-07
300 | feeder2_line45 | 2 | 99 | 4.9059e-08 | 5.7196e-07 | 4.9554e-08 | 5.7774e-07
300 | feeder2_line45 | 3 | 99 | 0.35561 | 0.35558 | 0.3592 | 0.35917
300 | feeder2_line46 | 1 | 99 | 5.6509e-07 | 1.3381e-06 | 5.708e-07 | 1.3516e-06
300 | feeder2_line46 | 2 | 99 | 5.6652e-07 | 1.3414e-06 | 5.7224e-07 | 1.355e-06
300 | feeder2_line46 | 3 | 99 | 1.5223 | 1.5222 | 1.5376 | 1.5376
300 | feeder2_line47 | 1 | 266.4 | 11.8283 | 11.8281 | 4.44 | 4.44
300 | feeder2_line47 | 2 | 266.4 | 0.1357 | 0.13551 | 0.050938 | 0.050867
300 | feeder2_line47 | 3 | 266.4 | 0.87534 | 0.8753 | 0.32858 | 0.32857
300 | feeder2_line48 | 1 | 99 | 1.1247 | 1.1247 | 1.136 | 1.136
300 | feeder2_line48 | 2 | 99 | 4.9062e-08 | 7.2227e-07 | 4.9557e-08 | 7.2956e-07
300 | feeder2_line48 | 3 | 99 | 4.919e-08 | 7.2218e-07 | 4.9687e-08 | 7.2948e-07
300 | feeder2_line49 | 1 | 266.4 | 11.0437 | 11.0435 | 4.1455 | 4.1455
300 | feeder2_line49 | 2 | 266.4 | 0.13568 | 0.13551 | 0.050931 | 0.050867
300 | feeder2_line49 | 3 | 266.4 | 0.87532 | 0.8753 | 0.32857 | 0.32857
300 | feeder2_line50 | 1 | 99 | 5.6503e-07 | 1.2176e-06 | 5.7074e-07 | 1.2299e-06
300 | feeder2_line50 | 2 | 99 | 0.086076 | 0.086144 | 0.086945 | 0.087014
300 | feeder2_line50 | 3 | 99 | 5.6647e-07 | 1.2207e-06 | 5.7219e-07 | 1.233e-06
300 | feeder2_line51 | 1 | 99 | 10.391 | 10.391 | 10.496 | 10.496
300 | feeder2_line51 | 2 | 99 | 5.6651e-07 | 1.3253e-06 | 5.7223e-07 | 1.3387e-06
300 | feeder2_line51 | 3 | 99 | 5.6645e-07 | 1.3252e-06 | 5.7217e-07 | 1.3386e-06
300 | feeder2_line52 | 1 | 266.4 | 0.65261 | 0.65252 | 0.24497 | 0.24494
300 | feeder2_line52 | 2 | 266.4 | 0.049472 | 0.04937 | 0.01857 | 0.018532
300 | feeder2_line52 | 3 | 266.4 | 0.87525 | 0.8753 | 0.32855 | 0.32857
300 | feeder2_line53 | 1 | 99 | 5.4032e-07 | 7.4315e-07 | 5.4578e-07 | 7.5065e-07
300 | feeder2_line53 | 2 | 99 | 0.049368 | 0.04937 | 0.049867 | 0.049869
300 | feeder2_line53 | 3 | 99 | 5.4187e-07 | 7.4501e-07 | 5.4734e-07 | 7.5254e-07
300 | feeder2_line54 | 1 | 266.4 | 0.65243 | 0.65252 | 0.24491 | 0.24494
300 | feeder2_line54 | 2 | 266.4 | 8.4494e-05 | 4.5706e-06 | 3.1717e-05 | 1.7157e-06
300 | feeder2_line54 | 3 | 266.4 | 0.87521 | 0.8753 | 0.32853 | 0.32857
300 | feeder2_line55 | 1 | 99 | 0.1802 | 0.1802 | 0.18202 | 0.18202
300 | feeder2_line55 | 2 | 99 | 4.9044e-08 | 7.2024e-07 | 4.9539e-08 | 7.2752e-07
300 | feeder2_line55 | 3 | 99 | 4.9139e-08 | 7.2032e-07 | 4.9635e-08 | 7.2759e-07
300 | feeder2_line56 | 1 | 354.6 | 99.8741 | 99.8709 | 28.1653 | 28.1644
300 | feeder2_line56 | 2 | 354.6 | 100.4102 | 100.4252 | 28.3165 | 28.3207
300 | feeder2_line56 | 3 | 354.6 | 98.2087 | 98.2038 | 27.6956 | 27.6942
300 | feeder2_line57 | 1 | 99 | 7.411e-07 | 1.5222e-06 | 7.4858e-07 | 1.5376e-06
300 | feeder2_line57 | 2 | 99 | 7.3583e-07 | 1.5262e-06 | 7.4326e-07 | 1.5416e-06
300 | feeder2_line57 | 3 | 99 | 0.87529 | 0.87531 | 0.88413 | 0.88415
300 | feeder2_line58 | 1 | 266.4 | 0.6525 | 0.65252 | 0.24493 | 0.24494
300 | feeder2_line58 | 2 | 266.4 | 1.8725e-05 | 2.6536e-06 | 7.029e-06 | 9.9609e-07
300 | feeder2_line58 | 3 | 266.4 | 1.8729e-05 | 2.6533e-06 | 7.0305e-06 | 9.96e-07
300 | feeder2_line59 | 1 | 99 | 4.9406e-08 | 5.2912e-07 | 4.9905e-08 | 5.3447e-07
300 | feeder2_line59 | 2 | 99 | 4.9057e-08 | 5.3053e-07 | 4.9553e-08 | 5.3589e-07
300 | feeder2_line59 | 3 | 99 | 0.10918 | 0.10918 | 0.11028 | 0.11028
300 | feeder2_line60 | 1 | 99 | 2.9487e-07 | 7.9967e-07 | 2.9784e-07 | 8.0775e-07
300 | feeder2_line60 | 2 | 99 | 2.9553e-07 | 8.0178e-07 | 2.9852e-07 | 8.0988e-07
300 | feeder2_line60 | 3 | 99 | 0.81602 | 0.81604 | 0.82426 | 0.82429
300 | feeder2_line61 | 1 | 266.4 | 1.5399 | 1.5401 | 0.57805 | 0.57812
300 | feeder2_line61 | 2 | 266.4 | 1.2528 | 1.253 | 0.47026 | 0.47034
300 | feeder2_line61 | 3 | 266.4 | 1.0436 | 1.0437 | 0.39174 | 0.3918
300 | feeder2_line62 | 1 | 354.6 | 98.999 | 98.9958 | 27.9185 | 27.9176
300 | feeder2_line62 | 2 | 354.6 | 100.0468 | 100.0619 | 28.214 | 28.2183
300 | feeder2_line62 | 3 | 354.6 | 97.8114 | 97.8064 | 27.5836 | 27.5822
300 | feeder2_line63 | 1 | 99 | 0.35888 | 0.35888 | 0.3625 | 0.3625
300 | feeder2_line63 | 2 | 99 | 5.6653e-07 | 1.2055e-06 | 5.7226e-07 | 1.2176e-06
300 | feeder2_line63 | 3 | 99 | 5.6646e-07 | 1.2053e-06 | 5.7219e-07 | 1.2175e-06
300 | feeder2_line64 | 1 | 99 | 0.29365 | 0.29365 | 0.29661 | 0.29662
300 | feeder2_line64 | 2 | 99 | 4.5277e-12 | 3.1754e-07 | 4.5734e-12 | 3.2075e-07
300 | feeder2_line64 | 3 | 99 | 2.4136e-12 | 3.1751e-07 | 2.438e-12 | 3.2071e-07
300 | feeder2_line65 | 1 | 99 | 4.9272e-08 | 6.3088e-07 | 4.977e-08 | 6.3725e-07
300 | feeder2_line65 | 2 | 99 | 0.27893 | 0.27894 | 0.28175 | 0.28176
300 | feeder2_line65 | 3 | 99 | 4.9105e-08 | 6.3222e-07 | 4.9601e-08 | 6.386e-07
300 | feeder2_line66 | 1 | 354.6 | 98.9989 | 98.9958 | 27.9185 | 27.9176
300 | feeder2_line66 | 2 | 354.6 | 100.116 | 100.1312 | 28.2335 | 28.2378
300 | feeder2_line66 | 3 | 354.6 | 97.8114 | 97.8064 | 27.5836 | 27.5822
300 | feeder2_line67 | 1 | 99 | 2.4644e-08 | 3.5677e-07 | 2.4893e-08 | 3.6038e-07
300 | feeder2_line67 | 2 | 99 | 2.4515e-08 | 3.575e-07 | 2.4763e-08 | 3.6111e-07
300 | feeder2_line67 | 3 | 99 | 0.09486 | 0.094855 | 0.095819 | 0.095813
300 | feeder2_line68 | 1 | 266.4 | 1.54 | 1.5401 | 0.57807 | 0.57812
300 | feeder2_line68 | 2 | 266.4 | 1.2528 | 1.253 | 0.47028 | 0.47034
300 | feeder2_line68 | 3 | 266.4 | 0.97349 | 0.9736 | 0.36542 | 0.36547
300 | feeder2_line69 | 1 | 99 | 0.21448 | 0.21445 | 0.21664 | 0.21662
300 | feeder2_line69 | 2 | 99 | 2.5078e-06 | 6.561e-07 | 2.5331e-06 | 6.6272e-07
300 | feeder2_line69 | 3 | 99 | 2.5078e-06 | 6.5623e-07 | 2.5332e-06 | 6.6286e-07
300 | feeder2_line70 | 1 | 354.6 | 99.0571 | 99.0539 | 27.9349 | 27.934
300 | feeder2_line70 | 2 | 354.6 | 100.116 | 100.1312 | 28.2335 | 28.2378
300 | feeder2_line70 | 3 | 354.6 | 97.8115 | 97.8064 | 27.5836 | 27.5822
300 | feeder2_line71 | 1 | 99 | 4.9252e-08 | 7.0363e-07 | 4.975e-08 | 7.1074e-07
300 | feeder2_line71 | 2 | 99 | 1.4208 | 1.4208 | 1.4351 | 1.4351
300 | feeder2_line71 | 3 | 99 | 4.9094e-08 | 7.0512e-07 | 4.9589e-08 | 7.1225e-07
300 | feeder2_line72 | 1 | 354.6 | 99.0572 | 99.0539 | 27.9349 | 27.934
300 | feeder2_line72 | 2 | 354.6 | 99.3949 | 99.4101 | 28.0302 | 28.0344
300 | feeder2_line72 | 3 | 354.6 | 97.8115 | 97.8064 | 27.5836 | 27.5822
300 | feeder2_line73 | 1 | 99 | 5.8906e-07 | 1.5104e-06 | 5.9501e-07 | 1.5257e-06
300 | feeder2_line73 | 2 | 99 | 0.25722 | 0.25723 | 0.25982 | 0.25983
300 | feeder2_line73 | 3 | 99 | 5.902e-07 | 1.5137e-06 | 5.9616e-07 | 1.529e-06
300 | feeder2_line74 | 1 | 99 | 4.929e-08 | 4.5049e-07 | 4.9788e-08 | 4.5504e-07
300 | feeder2_line74 | 2 | 99 | 0.97363 | 0.97367 | 0.98346 | 0.9835
300 | feeder2_line74 | 3 | 99 | 4.912e-08 | 4.5146e-07 | 4.9616e-08 | 4.5602e-07
300 | feeder2_line75 | 1 | 266.4 | 1.5401 | 1.5401 | 0.5781 | 0.57812
300 | feeder2_line75 | 2 | 266.4 | 0.090809 | 0.090845 | 0.034087 | 0.034101
300 | feeder2_line75 | 3 | 266.4 | 0.97358 | 0.9736 | 0.36546 | 0.36547
300 | feeder2_line76 | 1 | 99 | 1.5401 | 1.5401 | 1.5557 | 1.5557
300 | feeder2_line76 | 2 | 99 | 8.3607e-07 | 1.5612e-06 | 8.4451e-07 | 1.577e-06
300 | feeder2_line76 | 3 | 99 | 8.3617e-07 | 1.5614e-06 | 8.4461e-07 | 1.5772e-06
300 | feeder2_line77 | 1 | 99 | 2.4646e-08 | 5.6611e-07 | 2.4895e-08 | 5.7183e-07
300 | feeder2_line77 | 2 | 99 | 2.4514e-08 | 5.6724e-07 | 2.4761e-08 | 5.7297e-07
300 | feeder2_line77 | 3 | 99 | 0.97361 | 0.9736 | 0.98345 | 0.98344
300 | feeder2_line78 | 1 | 266.4 | 7.5319e-12 | 9.3903e-07 | 2.8273e-12 | 3.5249e-07
300 | feeder2_line78 | 2 | 266.4 | 0.09084 | 0.090845 | 0.034099 | 0.034101
300 | feeder2_line78 | 3 | 266.4 | 1.2511e-11 | 9.4086e-07 | 4.6964e-12 | 3.5318e-07
300 | feeder2_line79 | 1 | 354.6 | 1.317 | 1.3168 | 0.37141 | 0.37134
300 | feeder2_line79 | 2 | 354.6 | 1.9433 | 1.943 | 0.54802 | 0.54795
300 | feeder2_line79 | 3 | 354.6 | 3.4128 | 3.4123 | 0.96243 | 0.9623
300 | feeder2_line80 | 1 | 354.6 | 98.704 | 98.7004 | 27.8353 | 27.8343
300 | feeder2_line80 | 2 | 354.6 | 98.7114 | 98.7265 | 27.8374 | 27.8417
300 | feeder2_line80 | 3 | 354.6 | 97.1206 | 97.1151 | 27.3888 | 27.3872
300 | feeder2_line81 | 1 | 354.6 | 98.7039 | 98.7004 | 27.8353 | 27.8343
300 | feeder2_line81 | 2 | 354.6 | 98.7112 | 98.7265 | 27.8373 | 27.8417
300 | feeder2_line81 | 3 | 354.6 | 97.1958 | 97.1904 | 27.41 | 27.4085
300 | feeder2_line82 | 1 | 354.6 | 2.9068e-11 | 7.2132e-07 | 8.1975e-12 | 2.0342e-07
300 | feeder2_line82 | 2 | 354.6 | 1.6458e-11 | 7.2253e-07 | 4.6412e-12 | 2.0376e-07
300 | feeder2_line82 | 3 | 354.6 | 0.24954 | 0.24954 | 0.070374 | 0.070371
300 | feeder2_line83 | 1 | 354.6 | 98.704 | 98.7004 | 27.8353 | 27.8343
300 | feeder2_line83 | 2 | 354.6 | 97.9519 | 97.9672 | 27.6232 | 27.6275
300 | feeder2_line83 | 3 | 354.6 | 97.1959 | 97.1904 | 27.41 | 27.4085
300 | feeder2_line84 | 1 | 354.6 | 7.816e-12 | 1.2745e-06 | 2.2042e-12 | 3.5943e-07
300 | feeder2_line84 | 2 | 354.6 | 1.3338 | 1.3338 | 0.37615 | 0.37615
300 | feeder2_line84 | 3 | 354.6 | 1.1068e-11 | 1.2771e-06 | 3.1213e-12 | 3.6015e-07
300 | feeder2_line85 | 1 | 99 | 0.21241 | 0.21241 | 0.21456 | 0.21456
300 | feeder2_line85 | 2 | 99 | 4.8985e-08 | 4.5566e-07 | 4.948e-08 | 4.6026e-07
300 | feeder2_line85 | 3 | 99 | 4.9059e-08 | 4.5579e-07 | 4.9555e-08 | 4.6039e-07
300 | feeder2_line86 | 1 | 354.6 | 98.7661 | 98.7626 | 27.8528 | 27.8518
300 | feeder2_line86 | 2 | 354.6 | 97.9519 | 97.9672 | 27.6232 | 27.6275
300 | feeder2_line86 | 3 | 354.6 | 97.1959 | 97.1904 | 27.41 | 27.4085
300 | feeder2_line87 | 1 | 354.6 | 98.7662 | 98.7626 | 27.8528 | 27.8518
300 | feeder2_line87 | 2 | 354.6 | 97.1976 | 97.213 | 27.4105 | 27.4148
300 | feeder2_line87 | 3 | 354.6 | 97.2771 | 97.2716 | 27.4329 | 27.4314
300 | feeder2_line88 | 1 | 354.6 | 0.00011147 | 3.302e-06 | 3.1436e-05 | 9.3118e-07
300 | feeder2_line88 | 2 | 354.6 | 1.3378 | 1.3379 | 0.37728 | 0.3773
300 | feeder2_line88 | 3 | 354.6 | 0.26188 | 0.26175 | 0.073853 | 0.073815
300 | feeder2_line89 | 1 | 354.6 | 98.7653 | 98.7626 | 27.8526 | 27.8518
300 | feeder2_line89 | 2 | 354.6 | 96.0123 | 96.0289 | 27.0762 | 27.0809
300 | feeder2_line89 | 3 | 354.6 | 97.2762 | 97.2716 | 27.4327 | 27.4314
300 | feeder2_line90 | 1 | 354.6 | 0.0007097 | 1.9926e-06 | 0.00020014 | 5.6192e-07
300 | feeder2_line90 | 2 | 354.6 | 2.3043 | 2.3042 | 0.64982 | 0.64982
300 | feeder2_line90 | 3 | 354.6 | 0.00071194 | 1.9967e-06 | 0.00020077 | 5.6308e-07
300 | feeder2_line91 | 1 | 354.6 | 98.7654 | 98.7626 | 27.8526 | 27.8518
300 | feeder2_line91 | 2 | 354.6 | 96.0125 | 96.0289 | 27.0763 | 27.0809
300 | feeder2_line91 | 3 | 354.6 | 96.8244 | 96.8196 | 27.3052 | 27.3039
300 | feeder2_line92 | 1 | 354.6 | 6.5159e-12 | 1.005e-06 | 1.8375e-12 | 2.8342e-07
300 | feeder2_line92 | 2 | 354.6 | 6.5159e-12 | 1.0067e-06 | 1.8375e-12 | 2.8391e-07
300 | feeder2_line92 | 3 | 354.6 | 0.81538 | 0.8154 | 0.22994 | 0.22995
300 | feeder2_line93 | 1 | 99 | 2.46e-08 | 3.3547e-07 | 2.4848e-08 | 3.3886e-07
300 | feeder2_line93 | 2 | 99 | 1.3337 | 1.3337 | 1.3472 | 1.3472
300 | feeder2_line93 | 3 | 99 | 2.4518e-08 | 3.362e-07 | 2.4766e-08 | 3.396e-07
300 | feeder2_line94 | 1 | 354.6 | 2.4603e-06 | 1.6334e-06 | 6.9383e-07 | 4.6063e-07
300 | feeder2_line94 | 2 | 354.6 | 0.97272 | 0.97274 | 0.27431 | 0.27432
300 | feeder2_line94 | 3 | 354.6 | 2.4518e-06 | 1.6368e-06 | 6.9144e-07 | 4.6158e-07
300 | feeder2_line95 | 1 | 99 | 3.4995e-06 | 2.5605e-06 | 3.5349e-06 | 2.5864e-06
300 | feeder2_line95 | 2 | 99 | 1.3378 | 1.3379 | 1.3513 | 1.3514
300 | feeder2_line95 | 3 | 99 | 3.5098e-06 | 2.5661e-06 | 3.5453e-06 | 2.592e-06
300 | feeder2_line96 | 1 | 354.6 | 0.00011881 | 6.1032e-07 | 3.3506e-05 | 1.7211e-07
300 | feeder2_line96 | 2 | 354.6 | 0.00011907 | 6.1166e-07 | 3.3579e-05 | 1.7249e-07
300 | feeder2_line96 | 3 | 354.6 | 0.26187 | 0.26175 | 0.073848 | 0.073815
300 | feeder2_line97 | 1 | 354.6 | 98.8338 | 98.8307 | 27.8719 | 27.871
300 | feeder2_line97 | 2 | 354.6 | 96.0128 | 96.0289 | 27.0764 | 27.0809
300 | feeder2_line97 | 3 | 354.6 | 96.8247 | 96.8196 | 27.3053 | 27.3039
300 | feeder2_line98 | 1 | 354.6 | 0.15876 | 0.15706 | 0.044773 | 0.044293
300 | feeder2_line98 | 2 | 354.6 | 0.001675 | 6.1374e-07 | 0.00047236 | 1.7308e-07
300 | feeder2_line98 | 3 | 354.6 | 0.0016713 | 6.1099e-07 | 0.00047132 | 1.723e-07
300 | feeder2_line99 | 1 | 99 | 2.4605e-08 | 4.388e-07 | 2.4854e-08 | 4.4323e-07
300 | feeder2_line99 | 2 | 99 | 2.4487e-08 | 4.396e-07 | 2.4735e-08 | 4.4404e-07
300 | feeder2_line99 | 3 | 99 | 0.26178 | 0.26175 | 0.26442 | 0.26439
300 | feeder2_line100 | 1 | 99 | 0.1571 | 0.15706 | 0.15868 | 0.15865
300 | feeder2_line100 | 2 | 99 | 2.448e-08 | 6.0317e-07 | 2.4727e-08 | 6.0926e-07
300 | feeder2_line100 | 3 | 99 | 2.4513e-08 | 6.0338e-07 | 2.4761e-08 | 6.0948e-07
300 | feeder2_line101 | 1 | 354.6 | 0.97247 | 0.9723 | 0.27424 | 0.2742
300 | feeder2_line101 | 2 | 354.6 | 1.9433 | 1.943 | 0.54801 | 0.54795
300 | feeder2_line101 | 3 | 354.6 | 3.4128 | 3.4123 | 0.96243 | 0.9623
300 | feeder2_line102 | 1 | 99 | 0.448 | 0.44799 | 0.45253 | 0.45251
300 | feeder2_line102 | 2 | 99 | 2.3001e-06 | 8.6404e-07 | 2.3233e-06 | 8.7277e-07
300 | feeder2_line102 | 3 | 99 | 2.2977e-06 | 8.6423e-07 | 2.3209e-06 | 8.7296e-07
300 | feeder2_line103 | 1 | 99 | 5.3932e-07 | 7.894e-07 | 5.4477e-07 | 7.9737e-07
300 | feeder2_line103 | 2 | 99 | 0.097447 | 0.097452 | 0.098432 | 0.098436
300 | feeder2_line103 | 3 | 99 | 5.4057e-07 | 7.9102e-07 | 5.4603e-07 | 7.9901e-07
300 | feeder2_line104 | 1 | 354.6 | 0.97246 | 0.97231 | 0.27424 | 0.2742
300 | feeder2_line104 | 2 | 354.6 | 1.8745 | 1.8743 | 0.52862 | 0.52857
300 | feeder2_line104 | 3 | 354.6 | 3.4127 | 3.4123 | 0.96241 | 0.9623
300 | feeder2_line105 | 1 | 99 | 2.4996e-06 | 7.2635e-07 | 2.5249e-06 | 7.3369e-07
300 | feeder2_line105 | 2 | 99 | 2.5065e-06 | 7.2769e-07 | 2.5318e-06 | 7.3504e-07
300 | feeder2_line105 | 3 | 99 | 1.4096 | 1.4095 | 1.4238 | 1.4238
300 | feeder2_line106 | 1 | 354.6 | 0.97243 | 0.97231 | 0.27423 | 0.2742
300 | feeder2_line106 | 2 | 354.6 | 1.8744 | 1.8743 | 0.52861 | 0.52857
300 | feeder2_line106 | 3 | 354.6 | 2.0469 | 2.0466 | 0.57725 | 0.57716
300 | feeder2_line107 | 1 | 99 | 3.1889e-07 | 8.8516e-07 | 3.2211e-07 | 8.941e-07
300 | feeder2_line107 | 2 | 99 | 0.11756 | 0.11765 | 0.11875 | 0.11884
300 | feeder2_line107 | 3 | 99 | 3.1935e-07 | 8.8695e-07 | 3.2258e-07 | 8.9591e-07
300 | feeder2_line108 | 1 | 354.6 | 0.97244 | 0.97231 | 0.27424 | 0.2742
300 | feeder2_line108 | 2 | 354.6 | 1.794 | 1.7939 | 0.50593 | 0.50588
300 | feeder2_line108 | 3 | 354.6 | 2.0469 | 2.0466 | 0.57725 | 0.57716
300 | feeder2_line109 | 1 | 354.6 | 98.0901 | 98.0868 | 27.6622 | 27.6613
300 | feeder2_line109 | 2 | 354.6 | 96.013 | 96.0289 | 27.0764 | 27.0809
300 | feeder2_line109 | 3 | 354.6 | 96.8249 | 96.8196 | 27.3054 | 27.3039
300 | feeder2_line110 | 1 | 99 | 1.4749 | 1.4744 | 1.4898 | 1.4893
300 | feeder2_line110 | 2 | 99 | 0.00079009 | 8.9249e-07 | 0.00079807 | 9.015e-07
300 | feeder2_line110 | 3 | 99 | 0.00079028 | 8.9271e-07 | 0.00079827 | 9.0173e-07
300 | feeder2_line111 | 1 | 99 | 2.4602e-08 | 3.7477e-07 | 2.485e-08 | 3.7855e-07
300 | feeder2_line111 | 2 | 99 | 0.073181 | 0.07326 | 0.07392 | 0.074
300 | feeder2_line111 | 3 | 99 | 2.4525e-08 | 3.7558e-07 | 2.4773e-08 | 3.7938e-07
300 | feeder2_line112 | 1 | 99 | 3.1875e-07 | 9.0058e-07 | 3.2197e-07 | 9.0968e-07
300 | feeder2_line112 | 2 | 99 | 1.3043 | 1.3044 | 1.3175 | 1.3176
300 | feeder2_line112 | 3 | 99 | 3.1925e-07 | 9.0255e-07 | 3.2248e-07 | 9.1166e-07
300 | feeder2_line113 | 1 | 99 | 1.4148 | 1.4148 | 1.4291 | 1.4291
300 | feeder2_line113 | 2 | 99 | 3.1893e-07 | 8.8912e-07 | 3.2216e-07 | 8.981e-07
300 | feeder2_line113 | 3 | 99 | 3.1908e-07 | 8.8945e-07 | 3.2231e-07 | 8.9844e-07
300 | feeder2_line114 | 1 | 99 | 0.097612 | 0.097614 | 0.098598 | 0.0986
300 | feeder2_line114 | 2 | 99 | 2.4498e-08 | 4.2966e-07 | 2.4746e-08 | 4.34e-07
300 | feeder2_line114 | 3 | 99 | 2.4539e-08 | 4.2974e-07 | 2.4787e-08 | 4.3409e-07
300 | feeder2_line115 | 1 | 99 | 2.4616e-08 | 5.5239e-07 | 2.4864e-08 | 5.5797e-07
300 | feeder2_line115 | 2 | 99 | 0.33048 | 0.33048 | 0.33381 | 0.33382
300 | feeder2_line115 | 3 | 99 | 2.454e-08 | 5.5349e-07 | 2.4788e-08 | 5.5908e-07
300 | feeder2_line116 | 1 | 354.6 | 0.97245 | 0.97231 | 0.27424 | 0.2742
300 | feeder2_line116 | 2 | 354.6 | 1.5575 | 1.5574 | 0.43924 | 0.43919
300 | feeder2_line116 | 3 | 354.6 | 2.0469 | 2.0466 | 0.57726 | 0.57716
300 | feeder2_line117 | 1 | 99 | 4.9189e-08 | 6.2973e-07 | 4.9686e-08 | 6.3609e-07
300 | feeder2_line117 | 2 | 99 | 1.5207 | 1.5207 | 1.5361 | 1.5361
300 | feeder2_line117 | 3 | 99 | 4.9e-08 | 6.312e-07 | 4.9494e-08 | 6.3758e-07
300 | feeder2_line118 | 1 | 354.6 | 98.0901 | 98.0868 | 27.6622 | 27.6613
300 | feeder2_line118 | 2 | 354.6 | 95.2174 | 95.2335 | 26.8521 | 26.8566
300 | feeder2_line118 | 3 | 354.6 | 96.8249 | 96.8196 | 27.3054 | 27.3039
300 | feeder2_line119 | 1 | 99 | 2.4613e-08 | 5.9438e-07 | 2.4861e-08 | 6.0039e-07
300 | feeder2_line119 | 2 | 99 | 2.4498e-08 | 5.9547e-07 | 2.4746e-08 | 6.0148e-07
300 | feeder2_line119 | 3 | 99 | 0.54276 | 0.54275 | 0.54824 | 0.54823
300 | feeder2_line120 | 1 | 354.6 | 0.97245 | 0.97231 | 0.27424 | 0.2742
300 | feeder2_line120 | 2 | 354.6 | 1.5575 | 1.5574 | 0.43924 | 0.43919
300 | feeder2_line120 | 3 | 354.6 | 1.5481 | 1.5478 | 0.43657 | 0.43649
300 | feeder2_line121 | 1 | 99 | 3.1888e-07 | 9.2043e-07 | 3.221e-07 | 9.2973e-07
300 | feeder2_line121 | 2 | 99 | 0.044782 | 0.044784 | 0.045234 | 0.045237
300 | feeder2_line121 | 3 | 99 | 3.1934e-07 | 9.2223e-07 | 3.2256e-07 | 9.3155e-07
300 | feeder2_line122 | 1 | 354.6 | 0.97242 | 0.97231 | 0.27423 | 0.2742
300 | feeder2_line122 | 2 | 354.6 | 1.5285 | 1.5284 | 0.43105 | 0.43102
300 | feeder2_line122 | 3 | 354.6 | 1.5481 | 1.5478 | 0.43657 | 0.43649
300 | feeder2_line123 | 1 | 99 | 5.6393e-07 | 9.5377e-07 | 5.6962e-07 | 9.6341e-07
300 | feeder2_line123 | 2 | 99 | 5.6496e-07 | 9.555e-07 | 5.7067e-07 | 9.6515e-07
300 | feeder2_line123 | 3 | 99 | 0.1097 | 0.10969 | 0.1108 | 0.1108
300 | feeder2_line124 | 1 | 354.6 | 0.97246 | 0.97231 | 0.27424 | 0.2742
300 | feeder2_line124 | 2 | 354.6 | 1.5286 | 1.5284 | 0.43107 | 0.43102
300 | feeder2_line124 | 3 | 354.6 | 1.4609 | 1.4607 | 0.41199 | 0.41192
300 | feeder2_line125 | 1 | 99 | 5.6393e-07 | 8.8663e-07 | 5.6962e-07 | 8.9559e-07
300 | feeder2_line125 | 2 | 99 | 5.6496e-07 | 8.8823e-07 | 5.7066e-07 | 8.9721e-07
300 | feeder2_line125 | 3 | 99 | 0.15673 | 0.15671 | 0.15832 | 0.1583
300 | feeder2_line126 | 1 | 354.6 | 0.97259 | 0.97231 | 0.27428 | 0.2742
300 | feeder2_line126 | 2 | 354.6 | 1.5287 | 1.5284 | 0.4311 | 0.43102
300 | feeder2_line126 | 3 | 354.6 | 1.3437 | 1.3433 | 0.37892 | 0.37882
300 | feeder2_line127 | 1 | 99 | 5.6393e-07 | 1.0614e-06 | 5.6962e-07 | 1.0722e-06
300 | feeder2_line127 | 2 | 99 | 5.6495e-07 | 1.0633e-06 | 5.7066e-07 | 1.0741e-06
300 | feeder2_line127 | 3 | 99 | 1.0558 | 1.0558 | 1.0664 | 1.0664
300 | feeder2_line128 | 1 | 354.6 | 0.97256 | 0.97232 | 0.27427 | 0.2742
300 | feeder2_line128 | 2 | 354.6 | 1.5287 | 1.5284 | 0.4311 | 0.43102
300 | feeder2_line128 | 3 | 354.6 | 0.37452 | 0.37429 | 0.10562 | 0.10555
300 | feeder2_line129 | 1 | 99 | 5.3931e-07 | 8.6066e-07 | 5.4476e-07 | 8.6936e-07
300 | feeder2_line129 | 2 | 99 | 1.5284 | 1.5284 | 1.5438 | 1.5438
300 | feeder2_line129 | 3 | 99 | 5.4049e-07 | 8.6235e-07 | 5.4595e-07 | 8.7106e-07
300 | feeder2_line130 | 1 | 354.6 | 0.9726 | 0.97232 | 0.27428 | 0.2742
300 | feeder2_line130 | 2 | 354.6 | 0.00030324 | 4.5626e-06 | 8.5515e-05 | 1.2867e-06
300 | feeder2_line130 | 3 | 354.6 | 0.37454 | 0.37429 | 0.10562 | 0.10555
300 | feeder2_line131 | 1 | 99 | 5.6392e-07 | 9.5391e-07 | 5.6962e-07 | 9.6355e-07
300 | feeder2_line131 | 2 | 99 | 5.6495e-07 | 9.5563e-07 | 5.7066e-07 | 9.6528e-07
300 | feeder2_line131 | 3 | 99 | 0.16192 | 0.16192 | 0.16356 | 0.16355
300 | feeder2_line132 | 1 | 354.6 | 0.97242 | 0.97232 | 0.27423 | 0.2742
300 | feeder2_line132 | 2 | 354.6 | 0.00012367 | 2.8686e-06 | 3.4876e-05 | 8.0897e-07
300 | feeder2_line132 | 3 | 354.6 | 0.2125 | 0.21241 | 0.059926 | 0.059903
300 | feeder2_line133 | 1 | 99 | 0.9723 | 0.97232 | 0.98212 | 0.98214
300 | feeder2_line133 | 2 | 99 | 2.9473e-07 | 9.6326e-07 | 2.977e-07 | 9.7299e-07
300 | feeder2_line133 | 3 | 99 | 2.9479e-07 | 9.634e-07 | 2.9776e-07 | 9.7313e-07
300 | feeder2_line134 | 1 | 354.6 | 3.8249e-12 | 1.7536e-06 | 1.0786e-12 | 4.9454e-07
300 | feeder2_line134 | 2 | 354.6 | 9.9937e-12 | 1.7565e-06 | 2.8183e-12 | 4.9535e-07
300 | feeder2_line134 | 3 | 354.6 | 0.21242 | 0.21241 | 0.059905 | 0.059902
300 | feeder2_line135 | 1 | 99 | 1.419 | 1.419 | 1.4333 | 1.4333
300 | feeder2_line135 | 2 | 99 | 4.8927e-08 | 5.7471e-07 | 4.9421e-08 | 5.8051e-07
300 | feeder2_line135 | 3 | 99 | 4.898e-08 | 5.7493e-07 | 4.9475e-08 | 5.8074e-07
300 | feeder2_line136 | 1 | 354.6 | 97.4422 | 97.4389 | 27.4795 | 27.4786
300 | feeder2_line136 | 2 | 354.6 | 95.2174 | 95.2335 | 26.8521 | 26.8566
300 | feeder2_line136 | 3 | 354.6 | 96.8249 | 96.8196 | 27.3054 | 27.3039
300 | feeder2_line137 | 1 | 99 | 1.9651 | 1.9651 | 1.985 | 1.9849
300 | feeder2_line137 | 2 | 99 | 8.3397e-07 | 1.5477e-06 | 8.424e-07 | 1.5634e-06
300 | feeder2_line137 | 3 | 99 | 8.3428e-07 | 1.5483e-06 | 8.4271e-07 | 1.564e-06
300 | feeder2_line138 | 1 | 354.6 | 96.3215 | 96.3182 | 27.1634 | 27.1625
300 | feeder2_line138 | 2 | 354.6 | 95.2175 | 95.2335 | 26.8521 | 26.8566
300 | feeder2_line138 | 3 | 354.6 | 96.825 | 96.8196 | 27.3054 | 27.3039
300 | feeder2_line139 | 1 | 99 | 4.9173e-08 | 4.8122e-07 | 4.967e-08 | 4.8608e-07
300 | feeder2_line139 | 2 | 99 | 4.8924e-08 | 4.8219e-07 | 4.9418e-08 | 4.8706e-07
300 | feeder2_line139 | 3 | 99 | 1.3269 | 1.3263 | 1.3403 | 1.3397
300 | feeder2_line140 | 1 | 354.6 | 96.3214 | 96.3182 | 27.1634 | 27.1625
300 | feeder2_line140 | 2 | 354.6 | 95.2174 | 95.2335 | 26.8521 | 26.8566
300 | feeder2_line140 | 3 | 354.6 | 96.1423 | 96.1369 | 27.1129 | 27.1114
300 | feeder2_line141 | 1 | 99 | 2.4703e-06 | 4.7595e-07 | 2.4952e-06 | 4.8075e-07
300 | feeder2_line141 | 2 | 99 | 0.19003 | 0.19004 | 0.19195 | 0.19196
300 | feeder2_line141 | 3 | 99 | 2.4786e-06 | 4.771e-07 | 2.5036e-06 | 4.8192e-07
300 | feeder2_line142 | 1 | 354.6 | 96.3215 | 96.3182 | 27.1634 | 27.1625
300 | feeder2_line142 | 2 | 354.6 | 95.2838 | 95.2998 | 26.8708 | 26.8753
300 | feeder2_line142 | 3 | 354.6 | 96.1424 | 96.1369 | 27.1129 | 27.1114
300 | feeder2_line143 | 1 | 99 | 8.3202e-07 | 1.6911e-06 | 8.4042e-07 | 1.7082e-06
300 | feeder2_line143 | 2 | 99 | 0.1177 | 0.11782 | 0.11889 | 0.11901
300 | feeder2_line143 | 3 | 99 | 8.3413e-07 | 1.6952e-06 | 8.4256e-07 | 1.7123e-06
300 | feeder2_line144 | 1 | 354.6 | 96.3213 | 96.3182 | 27.1634 | 27.1625
300 | feeder2_line144 | 2 | 354.6 | 95.3371 | 95.3534 | 26.8858 | 26.8904
300 | feeder2_line144 | 3 | 354.6 | 96.1422 | 96.1369 | 27.1129 | 27.1114
300 | feeder2_line145 | 1 | 99 | 2.4579e-08 | 4.7416e-07 | 2.4827e-08 | 4.7895e-07
300 | feeder2_line145 | 2 | 99 | 0.24946 | 0.24947 | 0.25198 | 0.25199
300 | feeder2_line145 | 3 | 99 | 2.4483e-08 | 4.7531e-07 | 2.473e-08 | 4.8011e-07
300 | feeder2_line146 | 1 | 354.6 | 96.3213 | 96.3182 | 27.1634 | 27.1625
300 | feeder2_line146 | 2 | 354.6 | 95.4209 | 95.4373 | 26.9095 | 26.9141
300 | feeder2_line146 | 3 | 354.6 | 96.1422 | 96.1369 | 27.1129 | 27.1114
300 | feeder2_line147 | 1 | 99 | 0.10967 | 0.10968 | 0.11078 | 0.11079
300 | feeder2_line147 | 2 | 99 | 1.128e-06 | 2.1913e-06 | 1.1394e-06 | 2.2135e-06
300 | feeder2_line147 | 3 | 99 | 1.1284e-06 | 2.1922e-06 | 1.1398e-06 | 2.2143e-06
300 | feeder2_line148 | 1 | 99 | 0.22055 | 0.22055 | 0.22278 | 0.22278
300 | feeder2_line148 | 2 | 99 | 5.8845e-07 | 1.4684e-06 | 5.9439e-07 | 1.4832e-06
300 | feeder2_line148 | 3 | 99 | 5.8869e-07 | 1.4689e-06 | 5.9464e-07 | 1.4838e-06
300 | feeder2_line149 | 1 | 354.6 | 96.446 | 96.4427 | 27.1985 | 27.1976
300 | feeder2_line149 | 2 | 354.6 | 95.4211 | 95.4373 | 26.9095 | 26.9141
300 | feeder2_line149 | 3 | 354.6 | 96.1423 | 96.1369 | 27.1129 | 27.1114
300 | feeder2_line150 | 1 | 354.6 | 96.446 | 96.4427 | 27.1985 | 27.1976
300 | feeder2_line150 | 2 | 354.6 | 95.503 | 95.5191 | 26.9326 | 26.9372
300 | feeder2_line150 | 3 | 354.6 | 96.1423 | 96.1369 | 27.1129 | 27.1114
300 | feeder2_line151 | 1 | 99 | 9.5362e-06 | 1.7396e-06 | 9.6326e-06 | 1.7572e-06
300 | feeder2_line151 | 2 | 99 | 0.18846 | 0.18849 | 0.19037 | 0.19039
300 | feeder2_line151 | 3 | 99 | 9.57e-06 | 1.7439e-06 | 9.6666e-06 | 1.7615e-06
300 | feeder2_line152 | 1 | 354.6 | 1.2767e-11 | 1.159e-06 | 3.6003e-12 | 3.2685e-07
300 | feeder2_line152 | 2 | 354.6 | 6.3616e-12 | 1.1612e-06 | 1.794e-12 | 3.2747e-07
300 | feeder2_line152 | 3 | 354.6 | 0.078264 | 0.078256 | 0.022071 | 0.022069
300 | feeder2_line153 | 1 | 99 | 0.04502 | 0.045021 | 0.045475 | 0.045476
300 | feeder2_line153 | 2 | 99 | 4.8898e-08 | 5.8102e-07 | 4.9392e-08 | 5.8689e-07
300 | feeder2_line153 | 3 | 99 | 4.8944e-08 | 5.8123e-07 | 4.9439e-08 | 5.871e-07
300 | feeder2_line154 | 1 | 99 | 5.6261e-07 | 8.6279e-07 | 5.6829e-07 | 8.715e-07
300 | feeder2_line154 | 2 | 99 | 5.6379e-07 | 8.6458e-07 | 5.6948e-07 | 8.7331e-07
300 | feeder2_line154 | 3 | 99 | 1.2333 | 1.2332 | 1.2457 | 1.2457
300 | feeder2_line155 | 1 | 99 | 96.4611 | 96.4578 | 97.4355 | 97.4322
300 | feeder2_line155 | 2 | 99 | 95.5029 | 95.5192 | 96.4676 | 96.484
300 | feeder2_line155 | 3 | 99 | 95.4767 | 95.4712 | 96.4411 | 96.4355
300 | feeder2_line156 | 1 | 99 | 5.8729e-07 | 1.136e-06 | 5.9322e-07 | 1.1474e-06
300 | feeder2_line156 | 2 | 99 | 0.09756 | 0.097567 | 0.098546 | 0.098552
300 | feeder2_line156 | 3 | 99 | 5.8857e-07 | 1.1387e-06 | 5.9451e-07 | 1.1502e-06
300 | feeder2_line157 | 1 | 99 | 2.4578e-08 | 2.4663e-07 | 2.4827e-08 | 2.4912e-07
300 | feeder2_line157 | 2 | 99 | 0.091063 | 0.09107 | 0.091983 | 0.09199
300 | feeder2_line157 | 3 | 99 | 2.4476e-08 | 2.4721e-07 | 2.4724e-08 | 2.4971e-07
330 | feeder2_line1 | 1 | 354.6 | 100.8483 | 100.8515 | 28.44 | 28.4409
330 | feeder2_line1 | 2 | 354.6 | 105.4465 | 105.4455 | 29.7367 | 29.7365
330 | feeder2_line1 | 3 | 354.6 | 104.5912 | 104.5885 | 29.4955 | 29.4948
330 | feeder2_line2 | 1 | 354.6 | 100.8525 | 100.8557 | 28.4412 | 28.4421
330 | feeder2_line2 | 2 | 354.6 | 105.4466 | 105.4455 | 29.7368 | 29.7365
330 | feeder2_line2 | 3 | 354.6 | 104.5913 | 104.5885 | 29.4956 | 29.4948
330 | feeder2_line3 | 1 | 80.1 | 0.33899 | 0.339 | 0.42321 | 0.42322
330 | feeder2_line3 | 2 | 80.1 | 5.6773e-07 | 1.0491e-06 | 7.0877e-07 | 1.3098e-06
330 | feeder2_line3 | 3 | 80.1 | 5.677e-07 | 1.0491e-06 | 7.0873e-07 | 1.3097e-06
330 | feeder2_line4 | 1 | 354.6 | 100.8525 | 100.8557 | 28.4412 | 28.4421
330 | feeder2_line4 | 2 | 354.6 | 104.4187 | 104.4177 | 29.4469 | 29.4466
330 | feeder2_line4 | 3 | 354.6 | 104.5913 | 104.5885 | 29.4956 | 29.4948
330 | feeder2_line5 | 1 | 80.1 | 5.675e-07 | 9.9024e-07 | 7.0849e-07 | 1.2363e-06
330 | feeder2_line5 | 2 | 80.1 | 1.5263 | 1.5263 | 1.9055 | 1.9055
330 | feeder2_line5 | 3 | 80.1 | 5.6766e-07 | 9.9051e-07 | 7.0868e-07 | 1.2366e-06
330 | feeder2_line6 | 1 | 80.1 | 5.6742e-07 | 1.1647e-06 | 7.0839e-07 | 1.4541e-06
330 | feeder2_line6 | 2 | 80.1 | 5.6762e-07 | 1.1651e-06 | 7.0864e-07 | 1.4546e-06
330 | feeder2_line6 | 3 | 80.1 | 1.2566 | 1.2567 | 1.5688 | 1.5689
330 | feeder2_line7 | 1 | 354.6 | 100.8525 | 100.8557 | 28.4412 | 28.4421
330 | feeder2_line7 | 2 | 354.6 | 104.4187 | 104.4177 | 29.4469 | 29.4466
330 | feeder2_line7 | 3 | 354.6 | 103.6626 | 103.6598 | 29.2337 | 29.2329
330 | feeder2_line8 | 1 | 80.1 | 0.073294 | 0.073295 | 0.091503 | 0.091504
330 | feeder2_line8 | 2 | 80.1 | 5.6744e-07 | 1.1231e-06 | 7.0841e-07 | 1.4021e-06
330 | feeder2_line8 | 3 | 80.1 | 5.6739e-07 | 1.123e-06 | 7.0835e-07 | 1.402e-06
330 | feeder2_line9 | 1 | 354.6 | 100.8585 | 100.8617 | 28.4429 | 28.4438
330 | feeder2_line9 | 2 | 354.6 | 104.4186 | 104.4177 | 29.4469 | 29.4466
330 | feeder2_line9 | 3 | 354.6 | 103.6625 | 103.6598 | 29.2336 | 29.2329
330 | feeder2_line10 | 1 | 80.1 | 8.3839e-07 | 1.4822e-06 | 1.0467e-06 | 1.8504e-06
330 | feeder2_line10 | 2 | 80.1 | 0.073236 | 0.073235 | 0.09143 | 0.09143
330 | feeder2_line10 | 3 | 80.1 | 8.387e-07 | 1.4827e-06 | 1.0471e-06 | 1.8511e-06
330 | feeder2_line11 | 1 | 354.6 | 100.8586 | 100.8617 | 28.4429 | 28.4438
330 | feeder2_line11 | 2 | 354.6 | 104.43 | 104.429 | 29.4501 | 29.4498
330 | feeder2_line11 | 3 | 354.6 | 103.6626 | 103.6598 | 29.2337 | 29.2329
330 | feeder2_line12 | 1 | 80.1 | 5.4238e-07 | 9.8301e-07 | 6.7713e-07 | 1.2272e-06
330 | feeder2_line12 | 2 | 80.1 | 5.4271e-07 | 9.8348e-07 | 6.7754e-07 | 1.2278e-06
330 | feeder2_line12 | 3 | 80.1 | 0.81628 | 0.8163 | 1.0191 | 1.0191
330 | feeder2_line13 | 1 | 354.6 | 100.8586 | 100.8617 | 28.4429 | 28.4438
330 | feeder2_line13 | 2 | 354.6 | 104.4301 | 104.429 | 29.4501 | 29.4498
330 | feeder2_line13 | 3 | 354.6 | 103.0678 | 103.0649 | 29.0659 | 29.0651
330 | feeder2_line14 | 1 | 80.1 | 0.27492 | 0.27492 | 0.34322 | 0.34322
330 | feeder2_line14 | 2 | 80.1 | 2.9595e-07 | 6.4124e-07 | 3.6948e-07 | 8.0054e-07
330 | feeder2_line14 | 3 | 80.1 | 2.9594e-07 | 6.4117e-07 | 3.6947e-07 | 8.0046e-07
330 | feeder2_line15 | 1 | 354.6 | 100.8645 | 100.8676 | 28.4446 | 28.4455
330 | feeder2_line15 | 2 | 354.6 | 104.4301 | 104.429 | 29.4501 | 29.4498
330 | feeder2_line15 | 3 | 354.6 | 103.0678 | 103.0649 | 29.0659 | 29.0651
330 | feeder2_line16 | 1 | 80.1 | 5.6685e-07 | 1.0212e-06 | 7.0767e-07 | 1.2749e-06
330 | feeder2_line16 | 2 | 80.1 | 1.0224 | 1.0224 | 1.2764 | 1.2764
330 | feeder2_line16 | 3 | 80.1 | 5.671e-07 | 1.0217e-06 | 7.08e-07 | 1.2755e-06
330 | feeder2_line17 | 1 | 354.6 | 100.8645 | 100.8676 | 28.4446 | 28.4455
330 | feeder2_line17 | 2 | 354.6 | 103.7905 | 103.7894 | 29.2697 | 29.2694
330 | feeder2_line17 | 3 | 354.6 | 103.0678 | 103.0649 | 29.0659 | 29.0651
330 | feeder2_line18 | 1 | 80.1 | 5.4161e-07 | 7.3025e-07 | 6.7616e-07 | 9.1167e-07
330 | feeder2_line18 | 2 | 80.1 | 5.4213e-07 | 7.3082e-07 | 6.7682e-07 | 9.1238e-07
330 | feeder2_line18 | 3 | 80.1 | 0.48927 | 0.48926 | 0.61082 | 0.61081
330 | feeder2_line19 | 1 | 354.6 | 100.8645 | 100.8676 | 28.4446 | 28.4455
330 | feeder2_line19 | 2 | 354.6 | 103.7905 | 103.7894 | 29.2697 | 29.2694
330 | feeder2_line19 | 3 | 354.6 | 103.1062 | 103.1032 | 29.0768 | 29.0759
330 | feeder2_line20 | 1 | 99 | 5.414e-07 | 8.752e-07 | 5.4687e-07 | 8.8404e-07
330 | feeder2_line20 | 2 | 99 | 5.4197e-07 | 8.7594e-07 | 5.4745e-07 | 8.8479e-07
330 | feeder2_line20 | 3 | 99 | 0.35564 | 0.35563 | 0.35924 | 0.35922
330 | feeder2_line21 | 1 | 354.6 | 100.8645 | 100.8676 | 28.4446 | 28.4455
330 | feeder2_line21 | 2 | 354.6 | 103.7905 | 103.7894 | 29.2698 | 29.2694
330 | feeder2_line21 | 3 | 354.6 | 103.1428 | 103.1397 | 29.0871 | 29.0862
330 | feeder2_line22 | 1 | 99 | 5.6592e-07 | 1.0031e-06 | 5.7164e-07 | 1.0132e-06
330 | feeder2_line22 | 2 | 99 | 0.094738 | 0.094737 | 0.095695 | 0.095694
330 | feeder2_line22 | 3 | 99 | 5.6634e-07 | 1.0038e-06 | 5.7206e-07 | 1.0139e-06
330 | feeder2_line23 | 1 | 99 | 5.6592e-07 | 9.3896e-07 | 5.7164e-07 | 9.4845e-07
330 | feeder2_line23 | 2 | 99 | 5.6644e-07 | 9.3981e-07 | 5.7216e-07 | 9.493e-07
330 | feeder2_line23 | 3 | 99 | 1.4065 | 1.4065 | 1.4207 | 1.4207
330 | feeder2_line24 | 1 | 354.6 | 100.8646 | 100.8676 | 28.4446 | 28.4455
330 | feeder2_line24 | 2 | 354.6 | 103.8049 | 103.8037 | 29.2738 | 29.2735
330 | feeder2_line24 | 3 | 354.6 | 102.1559 | 102.1529 | 28.8088 | 28.8079
330 | feeder2_line25 | 1 | 99 | 0.094894 | 0.094896 | 0.095853 | 0.095854
330 | feeder2_line25 | 2 | 99 | 4.9107e-08 | 6.8304e-07 | 4.9603e-08 | 6.8994e-07
330 | feeder2_line25 | 3 | 99 | 4.9255e-08 | 6.8293e-07 | 4.9753e-08 | 6.8983e-07
330 | feeder2_line26 | 1 | 99 | 0.22053 | 0.22053 | 0.22276 | 0.22276
330 | feeder2_line26 | 2 | 99 | 5.417e-07 | 8.4624e-07 | 5.4718e-07 | 8.5479e-07
330 | feeder2_line26 | 3 | 99 | 5.4153e-07 | 8.4611e-07 | 5.47e-07 | 8.5465e-07
330 | feeder2_line27 | 1 | 354.6 | 100.8792 | 100.8822 | 28.4487 | 28.4496
330 | feeder2_line27 | 2 | 354.6 | 103.8049 | 103.8037 | 29.2738 | 29.2735
330 | feeder2_line27 | 3 | 354.6 | 102.1559 | 102.1529 | 28.8088 | 28.8079
330 | feeder2_line28 | 1 | 99 | 2.5063e-06 | 7.0129e-07 | 2.5316e-06 | 7.0838e-07
330 | feeder2_line28 | 2 | 99 | 1.2593 | 1.2593 | 1.272 | 1.272
330 | feeder2_line28 | 3 | 99 | 2.5094e-06 | 7.0197e-07 | 2.5347e-06 | 7.0906e-07
330 | feeder2_line29 | 1 | 354.6 | 100.8792 | 100.8822 | 28.4487 | 28.4496
330 | feeder2_line29 | 2 | 354.6 | 102.9141 | 102.9129 | 29.0226 | 29.0222
330 | feeder2_line29 | 3 | 354.6 | 102.1559 | 102.1529 | 28.8088 | 28.8079
330 | feeder2_line30 | 1 | 266.4 | 12.679 | 12.6787 | 4.7594 | 4.7593
330 | feeder2_line30 | 2 | 266.4 | 2.6929 | 2.6932 | 1.0109 | 1.0109
330 | feeder2_line30 | 3 | 266.4 | 3.081 | 3.0813 | 1.1565 | 1.1566
330 | feeder2_line31 | 1 | 354.6 | 99.8849 | 99.8876 | 28.1683 | 28.1691
330 | feeder2_line31 | 2 | 354.6 | 101.0976 | 101.0957 | 28.5103 | 28.5098
330 | feeder2_line31 | 3 | 354.6 | 100.1803 | 100.1765 | 28.2516 | 28.2506
330 | feeder2_line32 | 1 | 354.6 | 99.8849 | 99.8876 | 28.1683 | 28.1691
330 | feeder2_line32 | 2 | 354.6 | 101.1333 | 101.1314 | 28.5204 | 28.5198
330 | feeder2_line32 | 3 | 354.6 | 100.1803 | 100.1765 | 28.2516 | 28.2506
330 | feeder2_line33 | 1 | 99 | 4.9231e-08 | 6.7569e-07 | 4.9729e-08 | 6.8252e-07
330 | feeder2_line33 | 2 | 99 | 0.25721 | 0.25721 | 0.25981 | 0.25981
330 | feeder2_line33 | 3 | 99 | 4.9167e-08 | 6.7647e-07 | 4.9664e-08 | 6.8331e-07
330 | feeder2_line34 | 1 | 354.6 | 99.8849 | 99.8876 | 28.1683 | 28.1691
330 | feeder2_line34 | 2 | 354.6 | 101.1333 | 101.1314 | 28.5204 | 28.5198
330 | feeder2_line34 | 3 | 354.6 | 100.2172 | 100.2135 | 28.262 | 28.261
330 | feeder2_line35 | 1 | 99 | 2.9454e-07 | 7.4812e-07 | 2.9752e-07 | 7.5567e-07
330 | feeder2_line35 | 2 | 99 | 2.9486e-07 | 7.4908e-07 | 2.9784e-07 | 7.5665e-07
330 | feeder2_line35 | 3 | 99 | 0.27475 | 0.27475 | 0.27752 | 0.27752
330 | feeder2_line36 | 1 | 354.6 | 99.8903 | 99.893 | 28.1699 | 28.1706
330 | feeder2_line36 | 2 | 354.6 | 101.1333 | 101.1314 | 28.5204 | 28.5199
330 | feeder2_line36 | 3 | 354.6 | 100.2172 | 100.2135 | 28.262 | 28.261
330 | feeder2_line37 | 1 | 99 | 0.028587 | 0.028667 | 0.028876 | 0.028956
330 | feeder2_line37 | 2 | 99 | 2.948e-07 | 8.2865e-07 | 2.9778e-07 | 8.3702e-07
330 | feeder2_line37 | 3 | 99 | 2.948e-07 | 8.2854e-07 | 2.9777e-07 | 8.3691e-07
330 | feeder2_line38 | 1 | 99 | 3.193e-07 | 7.642e-07 | 3.2252e-07 | 7.7192e-07
330 | feeder2_line38 | 2 | 99 | 1.4089 | 1.4089 | 1.4232 | 1.4232
330 | feeder2_line38 | 3 | 99 | 3.1961e-07 | 7.6518e-07 | 3.2284e-07 | 7.7291e-07
330 | feeder2_line39 | 1 | 266.4 | 12.679 | 12.6787 | 4.7594 | 4.7593
330 | feeder2_line39 | 2 | 266.4 | 1.2844 | 1.2846 | 0.48213 | 0.48223
330 | feeder2_line39 | 3 | 266.4 | 3.081 | 3.0813 | 1.1565 | 1.1566
330 | feeder2_line40 | 1 | 354.6 | 99.91 | 99.9127 | 28.1754 | 28.1762
330 | feeder2_line40 | 2 | 354.6 | 101.1333 | 101.1314 | 28.5204 | 28.5199
330 | feeder2_line40 | 3 | 354.6 | 100.2172 | 100.2135 | 28.262 | 28.261
330 | feeder2_line41 | 1 | 99 | 0.09509 | 0.095092 | 0.096051 | 0.096053
330 | feeder2_line41 | 2 | 99 | 4.8983e-08 | 7.2401e-07 | 4.9478e-08 | 7.3132e-07
330 | feeder2_line41 | 3 | 99 | 4.9145e-08 | 7.2392e-07 | 4.9642e-08 | 7.3123e-07
330 | feeder2_line42 | 1 | 99 | 2.9463e-07 | 7.3752e-07 | 2.9761e-07 | 7.4497e-07
330 | feeder2_line42 | 2 | 99 | 2.9502e-07 | 7.3868e-07 | 2.98e-07 | 7.4615e-07
330 | feeder2_line42 | 3 | 99 | 1.2525 | 1.2525 | 1.2652 | 1.2652
330 | feeder2_line43 | 1 | 266.4 | 12.6789 | 12.6787 | 4.7593 | 4.7593
330 | feeder2_line43 | 2 | 266.4 | 1.2845 | 1.2846 | 0.48217 | 0.48223
330 | feeder2_line43 | 3 | 266.4 | 1.829 | 1.8291 | 0.68654 | 0.6866
330 | feeder2_line44 | 1 | 354.6 | 99.91 | 99.9127 | 28.1754 | 28.1762
330 | feeder2_line44 | 2 | 354.6 | 101.1333 | 101.1314 | 28.5204 | 28.5199
330 | feeder2_line44 | 3 | 354.6 | 100.2695 | 100.2658 | 28.2768 | 28.2757
330 | feeder2_line45 | 1 | 99 | 4.9197e-08 | 5.7019e-07 | 4.9694e-08 | 5.7595e-07
330 | feeder2_line45 | 2 | 99 | 4.8978e-08 | 5.709e-07 | 4.9473e-08 | 5.7666e-07
330 | feeder2_line45 | 3 | 99 | 0.35543 | 0.3554 | 0.35902 | 0.35899
330 | feeder2_line46 | 1 | 99 | 5.6463e-07 | 1.337e-06 | 5.7033e-07 | 1.3505e-06
330 | feeder2_line46 | 2 | 99 | 5.6554e-07 | 1.3391e-06 | 5.7125e-07 | 1.3527e-06
330 | feeder2_line46 | 3 | 99 | 0.95427 | 0.95429 | 0.96391 | 0.96393
330 | feeder2_line47 | 1 | 266.4 | 12.6789 | 12.6787 | 4.7594 | 4.7593
330 | feeder2_line47 | 2 | 266.4 | 1.2847 | 1.2846 | 0.48223 | 0.48223
330 | feeder2_line47 | 3 | 266.4 | 0.8751 | 0.87506 | 0.32849 | 0.32848
330 | feeder2_line48 | 1 | 99 | 0.13753 | 0.13753 | 0.13892 | 0.13892
330 | feeder2_line48 | 2 | 99 | 4.8998e-08 | 7.2101e-07 | 4.9493e-08 | 7.2829e-07
330 | feeder2_line48 | 3 | 99 | 4.9173e-08 | 7.2089e-07 | 4.967e-08 | 7.2818e-07
330 | feeder2_line49 | 1 | 266.4 | 12.5504 | 12.5502 | 4.7111 | 4.711
330 | feeder2_line49 | 2 | 266.4 | 1.2846 | 1.2847 | 0.48222 | 0.48223
330 | feeder2_line49 | 3 | 266.4 | 0.87508 | 0.87506 | 0.32848 | 0.32848
330 | feeder2_line50 | 1 | 99 | 5.6455e-07 | 1.2166e-06 | 5.7026e-07 | 1.2289e-06
330 | feeder2_line50 | 2 | 99 | 1.2556 | 1.2556 | 1.2683 | 1.2683
330 | feeder2_line50 | 3 | 99 | 5.6545e-07 | 1.2185e-06 | 5.7116e-07 | 1.2308e-06
330 | feeder2_line51 | 1 | 99 | 10.3853 | 10.3854 | 10.4902 | 10.4903
330 | feeder2_line51 | 2 | 99 | 5.6552e-07 | 1.323e-06 | 5.7123e-07 | 1.3364e-06
330 | feeder2_line51 | 3 | 99 | 5.6543e-07 | 1.3228e-06 | 5.7114e-07 | 1.3362e-06
330 | feeder2_line52 | 1 | 266.4 | 2.7749 | 2.775 | 1.0416 | 1.0417
330 | feeder2_line52 | 2 | 266.4 | 0.049546 | 0.049442 | 0.018598 | 0.018559
330 | feeder2_line52 | 3 | 266.4 | 0.875 | 0.87506 | 0.32845 | 0.32848
330 | feeder2_line53 | 1 | 99 | 5.3992e-07 | 7.4252e-07 | 5.4537e-07 | 7.5002e-07
330 | feeder2_line53 | 2 | 99 | 0.049443 | 0.049442 | 0.049942 | 0.049941
330 | feeder2_line53 | 3 | 99 | 5.4086e-07 | 7.4368e-07 | 5.4633e-07 | 7.5119e-07
330 | feeder2_line54 | 1 | 266.4 | 2.7749 | 2.775 | 1.0416 | 1.0417
330 | feeder2_line54 | 2 | 266.4 | 8.4345e-05 | 4.5626e-06 | 3.1661e-05 | 1.7127e-06
330 | feeder2_line54 | 3 | 266.4 | 0.87497 | 0.87506 | 0.32844 | 0.32848
330 | feeder2_line55 | 1 | 99 | 0.18016 | 0.18016 | 0.18198 | 0.18198
330 | feeder2_line55 | 2 | 99 | 4.8952e-08 | 7.1886e-07 | 4.9446e-08 | 7.2612e-07
330 | feeder2_line55 | 3 | 99 | 4.9116e-08 | 7.1877e-07 | 4.9613e-08 | 7.2603e-07
330 | feeder2_line56 | 1 | 354.6 | 99.937 | 99.9398 | 28.183 | 28.1838
330 | feeder2_line56 | 2 | 354.6 | 101.1333 | 101.1314 | 28.5204 | 28.5199
330 | feeder2_line56 | 3 | 354.6 | 100.2696 | 100.2658 | 28.2768 | 28.2757
330 | feeder2_line57 | 1 | 99 | 7.3909e-07 | 1.5209e-06 | 7.4655e-07 | 1.5363e-06
330 | feeder2_line57 | 2 | 99 | 7.3491e-07 | 1.5235e-06 | 7.4234e-07 | 1.5389e-06
330 | feeder2_line57 | 3 | 99 | 0.87504 | 0.87506 | 0.88388 | 0.8839
330 | feeder2_line58 | 1 | 266.4 | 2.7749 | 2.775 | 1.0416 | 1.0417
330 | feeder2_line58 | 2 | 266.4 | 1.8694e-05 | 2.6489e-06 | 7.0171e-06 | 9.9435e-07
330 | feeder2_line58 | 3 | 266.4 | 1.8693e-05 | 2.6487e-06 | 7.017e-06 | 9.9425e-07
330 | feeder2_line59 | 1 | 99 | 4.9278e-08 | 5.2867e-07 | 4.9776e-08 | 5.3401e-07
330 | feeder2_line59 | 2 | 99 | 4.8991e-08 | 5.296e-07 | 4.9486e-08 | 5.3495e-07
330 | feeder2_line59 | 3 | 99 | 0.10934 | 0.10934 | 0.11044 | 0.11044
330 | feeder2_line60 | 1 | 99 | 2.9459e-07 | 7.9899e-07 | 2.9757e-07 | 8.0706e-07
330 | feeder2_line60 | 2 | 99 | 2.9502e-07 | 8.0037e-07 | 2.98e-07 | 8.0846e-07
330 | feeder2_line60 | 3 | 99 | 0.81557 | 0.81559 | 0.82381 | 0.82383
330 | feeder2_line61 | 1 | 266.4 | 0.19856 | 0.19873 | 0.074535 | 0.074599
330 | feeder2_line61 | 2 | 266.4 | 1.2528 | 1.2529 | 0.47025 | 0.47032
330 | feeder2_line61 | 3 | 266.4 | 1.0435 | 1.0437 | 0.39169 | 0.39176
330 | feeder2_line62 | 1 | 354.6 | 99.9723 | 99.9751 | 28.193 | 28.1938
330 | feeder2_line62 | 2 | 354.6 | 100.6613 | 100.6593 | 28.3873 | 28.3867
330 | feeder2_line62 | 3 | 354.6 | 99.7704 | 99.7665 | 28.136 | 28.1349
330 | feeder2_line63 | 1 | 99 | 1.5835 | 1.5835 | 1.5995 | 1.5995
330 | feeder2_line63 | 2 | 99 | 5.6555e-07 | 1.2034e-06 | 5.7126e-07 | 1.2155e-06
330 | feeder2_line63 | 3 | 99 | 5.6545e-07 | 1.2032e-06 | 5.7116e-07 | 1.2153e-06
330 | feeder2_line64 | 1 | 99 | 1.1916 | 1.1915 | 1.2036 | 1.2036
330 | feeder2_line64 | 2 | 99 | 1.2894e-11 | 3.1698e-07 | 1.3024e-11 | 3.2019e-07
330 | feeder2_line64 | 3 | 99 | 7.3722e-12 | 3.1694e-07 | 7.4467e-12 | 3.2014e-07
330 | feeder2_line65 | 1 | 99 | 4.9121e-08 | 6.3009e-07 | 4.9617e-08 | 6.3645e-07
330 | feeder2_line65 | 2 | 99 | 1.5242 | 1.5242 | 1.5396 | 1.5396
330 | feeder2_line65 | 3 | 99 | 4.9079e-08 | 6.3074e-07 | 4.9575e-08 | 6.3711e-07
330 | feeder2_line66 | 1 | 354.6 | 99.9723 | 99.9751 | 28.193 | 28.1938
330 | feeder2_line66 | 2 | 354.6 | 99.725 | 99.723 | 28.1232 | 28.1227
330 | feeder2_line66 | 3 | 354.6 | 99.7703 | 99.7665 | 28.136 | 28.1349
330 | feeder2_line67 | 1 | 99 | 2.4573e-08 | 3.5637e-07 | 2.4821e-08 | 3.5997e-07
330 | feeder2_line67 | 2 | 99 | 2.4467e-08 | 3.5676e-07 | 2.4714e-08 | 3.6037e-07
330 | feeder2_line67 | 3 | 99 | 0.095058 | 0.095058 | 0.096018 | 0.096018
330 | feeder2_line68 | 1 | 266.4 | 0.1986 | 0.19873 | 0.074549 | 0.074599
330 | feeder2_line68 | 2 | 266.4 | 1.2528 | 1.2529 | 0.47027 | 0.47032
330 | feeder2_line68 | 3 | 266.4 | 0.97315 | 0.97329 | 0.36529 | 0.36535
330 | feeder2_line69 | 1 | 99 | 0.21451 | 0.21453 | 0.21668 | 0.21669
330 | feeder2_line69 | 2 | 99 | 2.5026e-06 | 6.5473e-07 | 2.5279e-06 | 6.6135e-07
330 | feeder2_line69 | 3 | 99 | 2.5013e-06 | 6.5467e-07 | 2.5265e-06 | 6.6128e-07
330 | feeder2_line70 | 1 | 354.6 | 100.0095 | 100.0121 | 28.2035 | 28.2042
330 | feeder2_line70 | 2 | 354.6 | 99.7251 | 99.723 | 28.1233 | 28.1227
330 | feeder2_line70 | 3 | 354.6 | 99.7704 | 99.7665 | 28.136 | 28.1349
330 | feeder2_line71 | 1 | 99 | 4.9109e-08 | 7.027e-07 | 4.9605e-08 | 7.098e-07
330 | feeder2_line71 | 2 | 99 | 0.32213 | 0.32212 | 0.32538 | 0.32537
330 | feeder2_line71 | 3 | 99 | 4.9063e-08 | 7.0342e-07 | 4.9559e-08 | 7.1053e-07
330 | feeder2_line72 | 1 | 354.6 | 100.0095 | 100.0121 | 28.2035 | 28.2042
330 | feeder2_line72 | 2 | 354.6 | 99.7739 | 99.7718 | 28.137 | 28.1364
330 | feeder2_line72 | 3 | 354.6 | 99.7704 | 99.7665 | 28.136 | 28.1349
330 | feeder2_line73 | 1 | 99 | 5.8835e-07 | 1.5087e-06 | 5.9429e-07 | 1.5239e-06
330 | feeder2_line73 | 2 | 99 | 0.25716 | 0.25716 | 0.25976 | 0.25976
330 | feeder2_line73 | 3 | 99 | 5.8891e-07 | 1.5102e-06 | 5.9485e-07 | 1.5255e-06
330 | feeder2_line74 | 1 | 99 | 4.9152e-08 | 4.4997e-07 | 4.9648e-08 | 4.5452e-07
330 | feeder2_line74 | 2 | 99 | 0.97336 | 0.97337 | 0.98319 | 0.9832
330 | feeder2_line74 | 3 | 99 | 4.9098e-08 | 4.5044e-07 | 4.9594e-08 | 4.5499e-07
330 | feeder2_line75 | 1 | 266.4 | 0.1987 | 0.19873 | 0.074586 | 0.074599
330 | feeder2_line75 | 2 | 266.4 | 0.090956 | 0.090986 | 0.034143 | 0.034154
330 | feeder2_line75 | 3 | 266.4 | 0.97323 | 0.97329 | 0.36533 | 0.36535
330 | feeder2_line76 | 1 | 99 | 0.19873 | 0.19873 | 0.20074 | 0.20074
330 | feeder2_line76 | 2 | 99 | 8.3441e-07 | 1.5581e-06 | 8.4284e-07 | 1.5738e-06
330 | feeder2_line76 | 3 | 99 | 8.3426e-07 | 1.5579e-06 | 8.4268e-07 | 1.5736e-06
330 | feeder2_line77 | 1 | 99 | 2.4572e-08 | 5.6547e-07 | 2.482e-08 | 5.7118e-07
330 | feeder2_line77 | 2 | 99 | 2.4466e-08 | 5.6612e-07 | 2.4713e-08 | 5.7184e-07
330 | feeder2_line77 | 3 | 99 | 0.97327 | 0.97329 | 0.9831 | 0.98312
330 | feeder2_line78 | 1 | 266.4 | 7.4056e-12 | 9.379e-07 | 2.7799e-12 | 3.5207e-07
330 | feeder2_line78 | 2 | 266.4 | 0.090988 | 0.090986 | 0.034154 | 0.034154
330 | feeder2_line78 | 3 | 266.4 | 2.0264e-11 | 9.388e-07 | 7.6067e-12 | 3.524e-07
330 | feeder2_line79 | 1 | 354.6 | 2.9558 | 2.9557 | 0.83357 | 0.83352
330 | feeder2_line79 | 2 | 354.6 | 1.7431 | 1.7427 | 0.49156 | 0.49147
330 | feeder2_line79 | 3 | 354.6 | 6.0066 | 6.0063 | 1.6939 | 1.6938
330 | feeder2_line80 | 1 | 354.6 | 98.328 | 98.3305 | 27.7293 | 27.73
330 | feeder2_line80 | 2 | 354.6 | 99.0774 | 99.0751 | 27.9406 | 27.94
330 | feeder2_line80 | 3 | 354.6 | 96.8088 | 96.8045 | 27.3008 | 27.2996
330 | feeder2_line81 | 1 | 354.6 | 98.3278 | 98.3305 | 27.7292 | 27.73
330 | feeder2_line81 | 2 | 354.6 | 99.0772 | 99.0751 | 27.9406 | 27.94
330 | feeder2_line81 | 3 | 354.6 | 96.8619 | 96.8578 | 27.3158 | 27.3147
330 | feeder2_line82 | 1 | 354.6 | 3.7715e-11 | 7.2028e-07 | 1.0636e-11 | 2.0312e-07
330 | feeder2_line82 | 2 | 354.6 | 1.2175e-11 | 7.2089e-07 | 3.4335e-12 | 2.033e-07
330 | feeder2_line82 | 3 | 354.6 | 0.24941 | 0.24941 | 0.070337 | 0.070337
330 | feeder2_line83 | 1 | 354.6 | 98.3279 | 98.3305 | 27.7292 | 27.73
330 | feeder2_line83 | 2 | 354.6 | 98.4187 | 98.4164 | 27.7549 | 27.7542
330 | feeder2_line83 | 3 | 354.6 | 96.862 | 96.8578 | 27.3159 | 27.3147
330 | feeder2_line84 | 1 | 354.6 | 1.59e-12 | 1.2726e-06 | 4.4841e-13 | 3.5889e-07
330 | feeder2_line84 | 2 | 354.6 | 1.0493 | 1.0493 | 0.29591 | 0.29591
330 | feeder2_line84 | 3 | 354.6 | 4.4408e-12 | 1.2739e-06 | 1.2523e-12 | 3.5924e-07
330 | feeder2_line85 | 1 | 99 | 1.407 | 1.407 | 1.4212 | 1.4212
330 | feeder2_line85 | 2 | 99 | 4.8871e-08 | 4.5463e-07 | 4.9364e-08 | 4.5922e-07
330 | feeder2_line85 | 3 | 99 | 4.9022e-08 | 4.5461e-07 | 4.9517e-08 | 4.592e-07
330 | feeder2_line86 | 1 | 354.6 | 97.4833 | 97.486 | 27.4911 | 27.4918
330 | feeder2_line86 | 2 | 354.6 | 98.4187 | 98.4164 | 27.7548 | 27.7542
330 | feeder2_line86 | 3 | 354.6 | 96.862 | 96.8578 | 27.3159 | 27.3147
330 | feeder2_line87 | 1 | 354.6 | 97.4833 | 97.486 | 27.4911 | 27.4918
330 | feeder2_line87 | 2 | 354.6 | 97.5614 | 97.559 | 27.5131 | 27.5124
330 | feeder2_line87 | 3 | 354.6 | 96.0561 | 96.0518 | 27.0886 | 27.0874
330 | feeder2_line88 | 1 | 354.6 | 0.00011157 | 3.2971e-06 | 3.1465e-05 | 9.2981e-07
330 | feeder2_line88 | 2 | 354.6 | 1.3369 | 1.3369 | 0.37703 | 0.37701
330 | feeder2_line88 | 3 | 354.6 | 1.4423 | 1.4423 | 0.40673 | 0.40673
330 | feeder2_line89 | 1 | 354.6 | 97.4827 | 97.486 | 27.4909 | 27.4918
330 | feeder2_line89 | 2 | 354.6 | 96.9634 | 96.9618 | 27.3445 | 27.344
330 | feeder2_line89 | 3 | 354.6 | 96.0553 | 96.0518 | 27.0884 | 27.0874
330 | feeder2_line90 | 1 | 354.6 | 0.0007089 | 1.9904e-06 | 0.00019991 | 5.6131e-07
330 | feeder2_line90 | 2 | 354.6 | 1.1823 | 1.1823 | 0.33341 | 0.33342
330 | feeder2_line90 | 3 | 354.6 | 0.00070978 | 1.9915e-06 | 0.00020016 | 5.6162e-07
330 | feeder2_line91 | 1 | 354.6 | 97.4828 | 97.486 | 27.4909 | 27.4918
330 | feeder2_line91 | 2 | 354.6 | 96.9636 | 96.9618 | 27.3445 | 27.344
330 | feeder2_line91 | 3 | 354.6 | 95.5515 | 95.5479 | 26.9463 | 26.9453
330 | feeder2_line92 | 1 | 354.6 | 1.2487e-12 | 1.0034e-06 | 3.5215e-13 | 2.8297e-07
330 | feeder2_line92 | 2 | 354.6 | 2.1219e-11 | 1.0044e-06 | 5.984e-12 | 2.8324e-07
330 | feeder2_line92 | 3 | 354.6 | 0.81472 | 0.81475 | 0.22976 | 0.22977
330 | feeder2_line93 | 1 | 99 | 2.4521e-08 | 3.3495e-07 | 2.4769e-08 | 3.3833e-07
330 | feeder2_line93 | 2 | 99 | 1.0492 | 1.0492 | 1.0598 | 1.0598
330 | feeder2_line93 | 3 | 99 | 2.4499e-08 | 3.353e-07 | 2.4747e-08 | 3.3869e-07
330 | feeder2_line94 | 1 | 354.6 | 2.4523e-06 | 1.6308e-06 | 6.9156e-07 | 4.599e-07
330 | feeder2_line94 | 2 | 354.6 | 0.19465 | 0.19464 | 0.054893 | 0.054891
330 | feeder2_line94 | 3 | 354.6 | 2.4499e-06 | 1.6325e-06 | 6.9089e-07 | 4.6037e-07
330 | feeder2_line95 | 1 | 99 | 3.4944e-06 | 2.5567e-06 | 3.5297e-06 | 2.5825e-06
330 | feeder2_line95 | 2 | 99 | 1.3369 | 1.3369 | 1.3504 | 1.3504
330 | feeder2_line95 | 3 | 99 | 3.4998e-06 | 2.5593e-06 | 3.5351e-06 | 2.5852e-06
330 | feeder2_line96 | 1 | 354.6 | 0.00011864 | 6.0929e-07 | 3.3459e-05 | 1.7182e-07
330 | feeder2_line96 | 2 | 354.6 | 0.0001188 | 6.1016e-07 | 3.3502e-05 | 1.7207e-07
330 | feeder2_line96 | 3 | 354.6 | 1.4422 | 1.4423 | 0.40672 | 0.40673
330 | feeder2_line97 | 1 | 354.6 | 97.5397 | 97.5426 | 27.507 | 27.5078
330 | feeder2_line97 | 2 | 354.6 | 96.9639 | 96.9618 | 27.3446 | 27.344
330 | feeder2_line97 | 3 | 354.6 | 95.5518 | 95.5479 | 26.9464 | 26.9453
330 | feeder2_line98 | 1 | 354.6 | 0.15889 | 0.15725 | 0.04481 | 0.044345
330 | feeder2_line98 | 2 | 354.6 | 0.0016699 | 6.0534e-07 | 0.00047092 | 1.7071e-07
330 | feeder2_line98 | 3 | 354.6 | 0.0016663 | 6.1105e-07 | 0.0004699 | 1.7232e-07
330 | feeder2_line99 | 1 | 99 | 2.4533e-08 | 4.3813e-07 | 2.4781e-08 | 4.4255e-07
330 | feeder2_line99 | 2 | 99 | 2.4427e-08 | 4.386e-07 | 2.4673e-08 | 4.4303e-07
330 | feeder2_line99 | 3 | 99 | 1.4422 | 1.4423 | 1.4568 | 1.4568
330 | feeder2_line100 | 1 | 99 | 0.15723 | 0.15725 | 0.15882 | 0.15884
330 | feeder2_line100 | 2 | 99 | 2.442e-08 | 6.0172e-07 | 2.4667e-08 | 6.078e-07
330 | feeder2_line100 | 3 | 99 | 2.4494e-08 | 6.0174e-07 | 2.4741e-08 | 6.0782e-07
330 | feeder2_line101 | 1 | 354.6 | 0.19506 | 0.19467 | 0.055008 | 0.054898
330 | feeder2_line101 | 2 | 354.6 | 1.743 | 1.7427 | 0.49155 | 0.49147
330 | feeder2_line101 | 3 | 354.6 | 6.0065 | 6.0063 | 1.6939 | 1.6938
330 | feeder2_line102 | 1 | 99 | 2.8238 | 2.8238 | 2.8523 | 2.8523
330 | feeder2_line102 | 2 | 99 | 2.2947e-06 | 8.6218e-07 | 2.3179e-06 | 8.7089e-07
330 | feeder2_line102 | 3 | 99 | 2.2911e-06 | 8.6203e-07 | 2.3142e-06 | 8.7073e-07
330 | feeder2_line103 | 1 | 99 | 5.3857e-07 | 7.8824e-07 | 5.4401e-07 | 7.9621e-07
330 | feeder2_line103 | 2 | 99 | 1.2538 | 1.2538 | 1.2665 | 1.2665
330 | feeder2_line103 | 3 | 99 | 5.3913e-07 | 7.89e-07 | 5.4458e-07 | 7.9697e-07
330 | feeder2_line104 | 1 | 354.6 | 0.19496 | 0.19467 | 0.05498 | 0.054898
330 | feeder2_line104 | 2 | 354.6 | 0.67229 | 0.67196 | 0.18959 | 0.1895
330 | feeder2_line104 | 3 | 354.6 | 6.0065 | 6.0063 | 1.6939 | 1.6938
330 | feeder2_line105 | 1 | 99 | 2.4965e-06 | 7.2529e-07 | 2.5217e-06 | 7.3262e-07
330 | feeder2_line105 | 2 | 99 | 2.5013e-06 | 7.2615e-07 | 2.5266e-06 | 7.3348e-07
330 | feeder2_line105 | 3 | 99 | 0.48817 | 0.48815 | 0.49311 | 0.49308
330 | feeder2_line106 | 1 | 354.6 | 0.1949 | 0.19467 | 0.054964 | 0.054898
330 | feeder2_line106 | 2 | 354.6 | 0.67223 | 0.67196 | 0.18958 | 0.1895
330 | feeder2_line106 | 3 | 354.6 | 5.6367 | 5.6366 | 1.5896 | 1.5896
330 | feeder2_line107 | 1 | 99 | 3.1837e-07 | 8.8387e-07 | 3.2159e-07 | 8.9279e-07
330 | feeder2_line107 | 2 | 99 | 0.11772 | 0.11771 | 0.11891 | 0.1189
330 | feeder2_line107 | 3 | 99 | 3.1859e-07 | 8.8465e-07 | 3.2181e-07 | 8.9358e-07
330 | feeder2_line108 | 1 | 354.6 | 0.19489 | 0.19467 | 0.054962 | 0.054898
330 | feeder2_line108 | 2 | 354.6 | 0.55526 | 0.55502 | 0.15659 | 0.15652
330 | feeder2_line108 | 3 | 354.6 | 5.6367 | 5.6366 | 1.5896 | 1.5896
330 | feeder2_line109 | 1 | 354.6 | 95.8297 | 95.8325 | 27.0247 | 27.0255
330 | feeder2_line109 | 2 | 354.6 | 96.964 | 96.9618 | 27.3446 | 27.344
330 | feeder2_line109 | 3 | 354.6 | 95.552 | 95.5479 | 26.9464 | 26.9453
330 | feeder2_line110 | 1 | 99 | 2.7483 | 2.7479 | 2.7761 | 2.7756
330 | feeder2_line110 | 2 | 99 | 0.00078815 | 8.8963e-07 | 0.00079611 | 8.9862e-07
330 | feeder2_line110 | 3 | 99 | 0.00078784 | 8.9029e-07 | 0.0007958 | 8.9928e-07
330 | feeder2_line111 | 1 | 99 | 2.4531e-08 | 3.742e-07 | 2.4779e-08 | 3.7798e-07
330 | feeder2_line111 | 2 | 99 | 0.073252 | 0.073244 | 0.073992 | 0.073984
330 | feeder2_line111 | 3 | 99 | 2.4508e-08 | 3.746e-07 | 2.4755e-08 | 3.7838e-07
330 | feeder2_line112 | 1 | 99 | 3.182e-07 | 8.9922e-07 | 3.2142e-07 | 9.0831e-07
330 | feeder2_line112 | 2 | 99 | 1.3033 | 1.3033 | 1.3165 | 1.3165
330 | feeder2_line112 | 3 | 99 | 3.1848e-07 | 9.0017e-07 | 3.2169e-07 | 9.0927e-07
330 | feeder2_line113 | 1 | 99 | 2.6932 | 2.6933 | 2.7204 | 2.7205
330 | feeder2_line113 | 2 | 99 | 3.1815e-07 | 8.8693e-07 | 3.2137e-07 | 8.9589e-07
330 | feeder2_line113 | 3 | 99 | 3.1827e-07 | 8.8699e-07 | 3.2148e-07 | 8.9595e-07
330 | feeder2_line114 | 1 | 99 | 1.2532 | 1.2531 | 1.2658 | 1.2658
330 | feeder2_line114 | 2 | 99 | 2.4445e-08 | 4.2873e-07 | 2.4692e-08 | 4.3306e-07
330 | feeder2_line114 | 3 | 99 | 2.452e-08 | 4.2865e-07 | 2.4767e-08 | 4.3298e-07
330 | feeder2_line115 | 1 | 99 | 2.4539e-08 | 5.5157e-07 | 2.4787e-08 | 5.5714e-07
330 | feeder2_line115 | 2 | 99 | 0.33029 | 0.33029 | 0.33363 | 0.33362
330 | feeder2_line115 | 3 | 99 | 2.4527e-08 | 5.5203e-07 | 2.4774e-08 | 5.576e-07
330 | feeder2_line116 | 1 | 354.6 | 0.1949 | 0.19467 | 0.054963 | 0.054898
330 | feeder2_line116 | 2 | 354.6 | 0.22502 | 0.22477 | 0.063456 | 0.063386
330 | feeder2_line116 | 3 | 354.6 | 5.6367 | 5.6366 | 1.5896 | 1.5896
330 | feeder2_line117 | 1 | 99 | 4.9008e-08 | 6.2872e-07 | 4.9503e-08 | 6.3507e-07
330 | feeder2_line117 | 2 | 99 | 0.95344 | 0.95344 | 0.96307 | 0.96307
330 | feeder2_line117 | 3 | 99 | 4.896e-08 | 6.2942e-07 | 4.9454e-08 | 6.3577e-07
330 | feeder2_line118 | 1 | 354.6 | 95.8297 | 95.8325 | 27.0247 | 27.0255
330 | feeder2_line118 | 2 | 354.6 | 96.4203 | 96.418 | 27.1913 | 27.1906
330 | feeder2_line118 | 3 | 354.6 | 95.552 | 95.5479 | 26.9464 | 26.9453
330 | feeder2_line119 | 1 | 99 | 2.4547e-08 | 5.9351e-07 | 2.4795e-08 | 5.9951e-07
330 | feeder2_line119 | 2 | 99 | 2.4425e-08 | 5.9426e-07 | 2.4672e-08 | 6.0027e-07
330 | feeder2_line119 | 3 | 99 | 1.7204 | 1.7204 | 1.7378 | 1.7378
330 | feeder2_line120 | 1 | 354.6 | 0.1949 | 0.19467 | 0.054964 | 0.054898
330 | feeder2_line120 | 2 | 354.6 | 0.22502 | 0.22477 | 0.063457 | 0.063386
330 | feeder2_line120 | 3 | 354.6 | 3.9195 | 3.9193 | 1.1053 | 1.1053
330 | feeder2_line121 | 1 | 99 | 3.1836e-07 | 9.1906e-07 | 3.2158e-07 | 9.2835e-07
330 | feeder2_line121 | 2 | 99 | 0.044864 | 0.044863 | 0.045317 | 0.045316
330 | feeder2_line121 | 3 | 99 | 3.1855e-07 | 9.1973e-07 | 3.2177e-07 | 9.2902e-07
330 | feeder2_line122 | 1 | 354.6 | 0.19489 | 0.19467 | 0.05496 | 0.054898
330 | feeder2_line122 | 2 | 354.6 | 0.18014 | 0.17991 | 0.050802 | 0.050735
330 | feeder2_line122 | 3 | 354.6 | 3.9195 | 3.9193 | 1.1053 | 1.1053
330 | feeder2_line123 | 1 | 99 | 5.6309e-07 | 9.5236e-07 | 5.6878e-07 | 9.6198e-07
330 | feeder2_line123 | 2 | 99 | 5.6385e-07 | 9.5362e-07 | 5.6954e-07 | 9.6325e-07
330 | feeder2_line123 | 3 | 99 | 1.2578 | 1.2578 | 1.2705 | 1.2705
330 | feeder2_line124 | 1 | 354.6 | 0.1948 | 0.19467 | 0.054935 | 0.054898
330 | feeder2_line124 | 2 | 354.6 | 0.18006 | 0.17991 | 0.050777 | 0.050735
330 | feeder2_line124 | 3 | 354.6 | 2.6723 | 2.6722 | 0.75362 | 0.75357
330 | feeder2_line125 | 1 | 99 | 5.6309e-07 | 8.8531e-07 | 5.6878e-07 | 8.9425e-07
330 | feeder2_line125 | 2 | 99 | 5.6386e-07 | 8.8649e-07 | 5.6955e-07 | 8.9544e-07
330 | feeder2_line125 | 3 | 99 | 0.15705 | 0.15702 | 0.15864 | 0.15861
330 | feeder2_line126 | 1 | 354.6 | 0.19496 | 0.19467 | 0.054979 | 0.054898
330 | feeder2_line126 | 2 | 354.6 | 0.18021 | 0.17991 | 0.050821 | 0.050735
330 | feeder2_line126 | 3 | 354.6 | 2.577 | 2.5767 | 0.72672 | 0.72664
330 | feeder2_line127 | 1 | 99 | 5.6309e-07 | 1.0599e-06 | 5.6878e-07 | 1.0706e-06
330 | feeder2_line127 | 2 | 99 | 5.6385e-07 | 1.0613e-06 | 5.6955e-07 | 1.072e-06
330 | feeder2_line127 | 3 | 99 | 1.0551 | 1.0551 | 1.0658 | 1.0657
330 | feeder2_line128 | 1 | 354.6 | 0.19487 | 0.19467 | 0.054956 | 0.054898
330 | feeder2_line128 | 2 | 354.6 | 0.18013 | 0.17991 | 0.050798 | 0.050735
330 | feeder2_line128 | 3 | 354.6 | 1.5222 | 1.522 | 0.42928 | 0.42921
330 | feeder2_line129 | 1 | 99 | 5.3855e-07 | 8.5939e-07 | 5.4399e-07 | 8.6808e-07
330 | feeder2_line129 | 2 | 99 | 0.17991 | 0.17991 | 0.18173 | 0.18172
330 | feeder2_line129 | 3 | 99 | 5.3894e-07 | 8.5997e-07 | 5.4438e-07 | 8.6866e-07
330 | feeder2_line130 | 1 | 354.6 | 0.19489 | 0.19467 | 0.05496 | 0.054898
330 | feeder2_line130 | 2 | 354.6 | 0.00030272 | 4.5538e-06 | 8.5368e-05 | 1.2842e-06
330 | feeder2_line130 | 3 | 354.6 | 1.5223 | 1.522 | 0.42929 | 0.42921
330 | feeder2_line131 | 1 | 99 | 5.6309e-07 | 9.525e-07 | 5.6878e-07 | 9.6212e-07
330 | feeder2_line131 | 2 | 99 | 5.6386e-07 | 9.5378e-07 | 5.6955e-07 | 9.6341e-07
330 | feeder2_line131 | 3 | 99 | 0.16183 | 0.16183 | 0.16346 | 0.16346
330 | feeder2_line132 | 1 | 354.6 | 0.19473 | 0.19467 | 0.054915 | 0.054898
330 | feeder2_line132 | 2 | 354.6 | 0.00012345 | 2.863e-06 | 3.4814e-05 | 8.0738e-07
330 | feeder2_line132 | 3 | 354.6 | 1.4075 | 1.4074 | 0.39693 | 0.3969
330 | feeder2_line133 | 1 | 99 | 0.19465 | 0.19467 | 0.19662 | 0.19663
330 | feeder2_line133 | 2 | 99 | 2.9414e-07 | 9.614e-07 | 2.9711e-07 | 9.7111e-07
330 | feeder2_line133 | 3 | 99 | 2.94e-07 | 9.6074e-07 | 2.9697e-07 | 9.7045e-07
330 | feeder2_line134 | 1 | 354.6 | 9.429e-12 | 1.751e-06 | 2.6591e-12 | 4.9379e-07
330 | feeder2_line134 | 2 | 354.6 | 8.9978e-12 | 1.7531e-06 | 2.5375e-12 | 4.9438e-07
330 | feeder2_line134 | 3 | 354.6 | 1.4074 | 1.4074 | 0.3969 | 0.3969
330 | feeder2_line135 | 1 | 99 | 0.3217 | 0.32172 | 0.32495 | 0.32497
330 | feeder2_line135 | 2 | 99 | 4.8808e-08 | 5.7319e-07 | 4.9301e-08 | 5.7898e-07
330 | feeder2_line135 | 3 | 99 | 4.8942e-08 | 5.7326e-07 | 4.9437e-08 | 5.7905e-07
330 | feeder2_line136 | 1 | 354.6 | 95.8999 | 95.9028 | 27.0445 | 27.0453
330 | feeder2_line136 | 2 | 354.6 | 96.4203 | 96.418 | 27.1913 | 27.1906
330 | feeder2_line136 | 3 | 354.6 | 95.552 | 95.5479 | 26.9464 | 26.9453
330 | feeder2_line137 | 1 | 99 | 0.087263 | 0.087281 | 0.088144 | 0.088163
330 | feeder2_line137 | 2 | 99 | 8.3174e-07 | 1.5436e-06 | 8.4014e-07 | 1.5592e-06
330 | feeder2_line137 | 3 | 99 | 8.3181e-07 | 1.5438e-06 | 8.4022e-07 | 1.5594e-06
330 | feeder2_line138 | 1 | 354.6 | 95.9256 | 95.9284 | 27.0518 | 27.0526
330 | feeder2_line138 | 2 | 354.6 | 96.4204 | 96.418 | 27.1913 | 27.1906
330 | feeder2_line138 | 3 | 354.6 | 95.552 | 95.5479 | 26.9464 | 26.9453
330 | feeder2_line139 | 1 | 99 | 4.8989e-08 | 4.8042e-07 | 4.9484e-08 | 4.8528e-07
330 | feeder2_line139 | 2 | 99 | 4.8807e-08 | 4.8088e-07 | 4.93e-08 | 4.8574e-07
330 | feeder2_line139 | 3 | 99 | 0.13795 | 0.13777 | 0.13935 | 0.13916
330 | feeder2_line140 | 1 | 354.6 | 95.9256 | 95.9284 | 27.0518 | 27.0526
330 | feeder2_line140 | 2 | 354.6 | 96.4203 | 96.418 | 27.1913 | 27.1906
330 | feeder2_line140 | 3 | 354.6 | 95.6204 | 95.6159 | 26.9657 | 26.9644
330 | feeder2_line141 | 1 | 99 | 2.4669e-06 | 4.7515e-07 | 2.4919e-06 | 4.7995e-07
330 | feeder2_line141 | 2 | 99 | 1.2511 | 1.2511 | 1.2637 | 1.2637
330 | feeder2_line141 | 3 | 99 | 2.4704e-06 | 4.7568e-07 | 2.4954e-06 | 4.8049e-07
330 | feeder2_line142 | 1 | 354.6 | 95.9257 | 95.9284 | 27.0518 | 27.0526
330 | feeder2_line142 | 2 | 354.6 | 95.7033 | 95.7009 | 26.9891 | 26.9884
330 | feeder2_line142 | 3 | 354.6 | 95.6205 | 95.6159 | 26.9657 | 26.9644
330 | feeder2_line143 | 1 | 99 | 8.3065e-07 | 1.6883e-06 | 8.3904e-07 | 1.7053e-06
330 | feeder2_line143 | 2 | 99 | 0.11793 | 0.11791 | 0.11912 | 0.1191
330 | feeder2_line143 | 3 | 99 | 8.3161e-07 | 1.6902e-06 | 8.4001e-07 | 1.7072e-06
330 | feeder2_line144 | 1 | 354.6 | 95.9255 | 95.9284 | 27.0518 | 27.0526
330 | feeder2_line144 | 2 | 354.6 | 95.7454 | 95.7432 | 27.001 | 27.0003
330 | feeder2_line144 | 3 | 354.6 | 95.6204 | 95.6159 | 26.9657 | 26.9644
330 | feeder2_line145 | 1 | 99 | 2.449e-08 | 4.7335e-07 | 2.4737e-08 | 4.7813e-07
330 | feeder2_line145 | 2 | 99 | 0.24934 | 0.24933 | 0.25185 | 0.25185
330 | feeder2_line145 | 3 | 99 | 2.4462e-08 | 4.7389e-07 | 2.4709e-08 | 4.7868e-07
330 | feeder2_line146 | 1 | 354.6 | 95.9255 | 95.9284 | 27.0518 | 27.0526
330 | feeder2_line146 | 2 | 354.6 | 95.804 | 95.8017 | 27.0175 | 27.0168
330 | feeder2_line146 | 3 | 354.6 | 95.6204 | 95.6159 | 26.9657 | 26.9644
330 | feeder2_line147 | 1 | 99 | 0.10978 | 0.10978 | 0.11089 | 0.11089
330 | feeder2_line147 | 2 | 99 | 1.1248e-06 | 2.1852e-06 | 1.1362e-06 | 2.2073e-06
330 | feeder2_line147 | 3 | 99 | 1.125e-06 | 2.1856e-06 | 1.1364e-06 | 2.2077e-06
330 | feeder2_line148 | 1 | 99 | 0.22056 | 0.22056 | 0.22278 | 0.22279
330 | feeder2_line148 | 2 | 99 | 5.8682e-07 | 1.4643e-06 | 5.9274e-07 | 1.4791e-06
330 | feeder2_line148 | 3 | 99 | 5.8697e-07 | 1.4645e-06 | 5.929e-07 | 1.4793e-06
330 | feeder2_line149 | 1 | 354.6 | 96.0204 | 96.0231 | 27.0785 | 27.0793
330 | feeder2_line149 | 2 | 354.6 | 95.8041 | 95.8017 | 27.0175 | 27.0168
330 | feeder2_line149 | 3 | 354.6 | 95.6205 | 95.6159 | 26.9657 | 26.9644
330 | feeder2_line150 | 1 | 354.6 | 96.0204 | 96.0231 | 27.0785 | 27.0793
330 | feeder2_line150 | 2 | 354.6 | 95.0723 | 95.07 | 26.8111 | 26.8105
330 | feeder2_line150 | 3 | 354.6 | 95.6205 | 95.6159 | 26.9657 | 26.9644
330 | feeder2_line151 | 1 | 99 | 9.5239e-06 | 1.7366e-06 | 9.6201e-06 | 1.7541e-06
330 | feeder2_line151 | 2 | 99 | 1.3075 | 1.3075 | 1.3207 | 1.3207
330 | feeder2_line151 | 3 | 99 | 9.5373e-06 | 1.7385e-06 | 9.6336e-06 | 1.7561e-06
330 | feeder2_line152 | 1 | 354.6 | 9.338e-12 | 1.1568e-06 | 2.6334e-12 | 3.2624e-07
330 | feeder2_line152 | 2 | 354.6 | 7.9733e-12 | 1.1578e-06 | 2.2485e-12 | 3.2652e-07
330 | feeder2_line152 | 3 | 354.6 | 0.078508 | 0.078507 | 0.02214 | 0.02214
330 | feeder2_line153 | 1 | 99 | 0.045085 | 0.045086 | 0.04554 | 0.045542
330 | feeder2_line153 | 2 | 99 | 4.8767e-08 | 5.7933e-07 | 4.9259e-08 | 5.8518e-07
330 | feeder2_line153 | 3 | 99 | 4.8895e-08 | 5.7942e-07 | 4.9389e-08 | 5.8528e-07
330 | feeder2_line154 | 1 | 99 | 5.6159e-07 | 8.6123e-07 | 5.6727e-07 | 8.6993e-07
330 | feeder2_line154 | 2 | 99 | 5.6215e-07 | 8.6207e-07 | 5.6783e-07 | 8.7078e-07
330 | feeder2_line154 | 3 | 99 | 0.87611 | 0.87611 | 0.88496 | 0.88496
330 | feeder2_line155 | 1 | 99 | 96.0314 | 96.0341 | 97.0014 | 97.0042
330 | feeder2_line155 | 2 | 99 | 95.0723 | 95.07 | 96.0326 | 96.0303
330 | feeder2_line155 | 3 | 99 | 95.0935 | 95.0889 | 96.0541 | 96.0494
330 | feeder2_line156 | 1 | 99 | 5.8619e-07 | 1.134e-06 | 5.9211e-07 | 1.1454e-06
330 | feeder2_line156 | 2 | 99 | 1.2529 | 1.2529 | 1.2656 | 1.2655
330 | feeder2_line156 | 3 | 99 | 5.8682e-07 | 1.1352e-06 | 5.9274e-07 | 1.1467e-06
330 | feeder2_line157 | 1 | 99 | 2.447e-08 | 2.4618e-07 | 2.4717e-08 | 2.4866e-07
330 | feeder2_line157 | 2 | 99 | 0.09128 | 0.091278 | 0.092202 | 0.0922
330 | feeder2_line157 | 3 | 99 | 2.4453e-08 | 2.4646e-07 | 2.47e-08 | 2.4895e-07
360 | feeder2_line1 | 1 | 354.6 | 97.9896 | 97.9851 | 27.6338 | 27.6326
360 | feeder2_line1 | 2 | 354.6 | 102.7761 | 102.779 | 28.9837 | 28.9845
360 | feeder2_line1 | 3 | 354.6 | 95.6352 | 95.6394 | 26.9699 | 26.9711
360 | feeder2_line2 | 1 | 354.6 | 98.1096 | 98.1049 | 27.6677 | 27.6664
360 | feeder2_line2 | 2 | 354.6 | 102.7762 | 102.779 | 28.9837 | 28.9845
360 | feeder2_line2 | 3 | 354.6 | 95.6354 | 95.6394 | 26.9699 | 26.9711
360 | feeder2_line3 | 1 | 80.1 | 0.33925 | 0.33924 | 0.42353 | 0.42352
360 | feeder2_line3 | 2 | 80.1 | 5.6848e-07 | 1.0505e-06 | 7.0971e-07 | 1.3115e-06
360 | feeder2_line3 | 3 | 80.1 | 5.6786e-07 | 1.0494e-06 | 7.0895e-07 | 1.3101e-06
360 | feeder2_line4 | 1 | 354.6 | 98.1096 | 98.1049 | 27.6677 | 27.6664
360 | feeder2_line4 | 2 | 354.6 | 102.8581 | 102.8608 | 29.0068 | 29.0076
360 | feeder2_line4 | 3 | 354.6 | 95.6353 | 95.6394 | 26.9699 | 26.9711
360 | feeder2_line5 | 1 | 80.1 | 5.6883e-07 | 9.9255e-07 | 7.1015e-07 | 1.2391e-06
360 | feeder2_line5 | 2 | 80.1 | 0.27909 | 0.27909 | 0.34842 | 0.34842
360 | feeder2_line5 | 3 | 80.1 | 5.6782e-07 | 9.9081e-07 | 7.0889e-07 | 1.237e-06
360 | feeder2_line6 | 1 | 80.1 | 5.6881e-07 | 1.1676e-06 | 7.1013e-07 | 1.4576e-06
360 | feeder2_line6 | 2 | 80.1 | 5.6841e-07 | 1.1668e-06 | 7.0963e-07 | 1.4566e-06
360 | feeder2_line6 | 3 | 80.1 | 0.085997 | 0.086005 | 0.10736 | 0.10737
360 | feeder2_line7 | 1 | 354.6 | 98.1097 | 98.1049 | 27.6677 | 27.6664
360 | feeder2_line7 | 2 | 354.6 | 102.8581 | 102.8608 | 29.0068 | 29.0076
360 | feeder2_line7 | 3 | 354.6 | 95.655 | 95.6591 | 26.9755 | 26.9766
360 | feeder2_line8 | 1 | 80.1 | 0.07303 | 0.073029 | 0.091173 | 0.091173
360 | feeder2_line8 | 2 | 80.1 | 5.683e-07 | 1.1248e-06 | 7.0949e-07 | 1.4043e-06
360 | feeder2_line8 | 3 | 80.1 | 5.6753e-07 | 1.1233e-06 | 7.0853e-07 | 1.4024e-06
360 | feeder2_line9 | 1 | 354.6 | 98.1401 | 98.1354 | 27.6763 | 27.675
360 | feeder2_line9 | 2 | 354.6 | 102.858 | 102.8608 | 29.0068 | 29.0076
360 | feeder2_line9 | 3 | 354.6 | 95.6549 | 95.6591 | 26.9754 | 26.9766
360 | feeder2_line10 | 1 | 80.1 | 8.4081e-07 | 1.4863e-06 | 1.0497e-06 | 1.8556e-06
360 | feeder2_line10 | 2 | 80.1 | 0.073141 | 0.073142 | 0.091313 | 0.091313
360 | feeder2_line10 | 3 | 80.1 | 8.3887e-07 | 1.4831e-06 | 1.0473e-06 | 1.8516e-06
360 | feeder2_line11 | 1 | 354.6 | 98.1402 | 98.1354 | 27.6763 | 27.675
360 | feeder2_line11 | 2 | 354.6 | 102.8839 | 102.8867 | 29.0141 | 29.0149
360 | feeder2_line11 | 3 | 354.6 | 95.655 | 95.6591 | 26.9755 | 26.9766
360 | feeder2_line12 | 1 | 80.1 | 5.441e-07 | 9.8586e-07 | 6.7928e-07 | 1.2308e-06
360 | feeder2_line12 | 2 | 80.1 | 5.4353e-07 | 9.8505e-07 | 6.7857e-07 | 1.2298e-06
360 | feeder2_line12 | 3 | 80.1 | 0.062204 | 0.062204 | 0.077658 | 0.077658
360 | feeder2_line13 | 1 | 354.6 | 98.1402 | 98.1354 | 27.6763 | 27.675
360 | feeder2_line13 | 2 | 354.6 | 102.884 | 102.8867 | 29.0141 | 29.0149
360 | feeder2_line13 | 3 | 354.6 | 95.6695 | 95.6735 | 26.9796 | 26.9807
360 | feeder2_line14 | 1 | 80.1 | 1.5964 | 1.5963 | 1.993 | 1.9929
360 | feeder2_line14 | 2 | 80.1 | 2.9646e-07 | 6.4229e-07 | 3.7011e-07 | 8.0185e-07
360 | feeder2_line14 | 3 | 80.1 | 2.9606e-07 | 6.4132e-07 | 3.6961e-07 | 8.0065e-07
360 | feeder2_line15 | 1 | 354.6 | 97.4329 | 97.4281 | 27.4768 | 27.4755
360 | feeder2_line15 | 2 | 354.6 | 102.884 | 102.8867 | 29.0141 | 29.0149
360 | feeder2_line15 | 3 | 354.6 | 95.6695 | 95.6735 | 26.9796 | 26.9807
360 | feeder2_line16 | 1 | 80.1 | 5.6867e-07 | 1.0245e-06 | 7.0995e-07 | 1.279e-06
360 | feeder2_line16 | 2 | 80.1 | 0.25361 | 0.25361 | 0.31662 | 0.31661
360 | feeder2_line16 | 3 | 80.1 | 5.6722e-07 | 1.0219e-06 | 7.0814e-07 | 1.2758e-06
360 | feeder2_line17 | 1 | 354.6 | 97.4329 | 97.4281 | 27.4769 | 27.4755
360 | feeder2_line17 | 2 | 354.6 | 102.9551 | 102.9578 | 29.0342 | 29.0349
360 | feeder2_line17 | 3 | 354.6 | 95.6695 | 95.6735 | 26.9796 | 26.9807
360 | feeder2_line18 | 1 | 80.1 | 5.4398e-07 | 7.3316e-07 | 6.7913e-07 | 9.1531e-07
360 | feeder2_line18 | 2 | 80.1 | 5.4318e-07 | 7.3231e-07 | 6.7813e-07 | 9.1424e-07
360 | feeder2_line18 | 3 | 80.1 | 0.48911 | 0.48912 | 0.61062 | 0.61063
360 | feeder2_line19 | 1 | 354.6 | 97.433 | 97.4281 | 27.4769 | 27.4755
360 | feeder2_line19 | 2 | 354.6 | 102.9551 | 102.9578 | 29.0342 | 29.0349
360 | feeder2_line19 | 3 | 354.6 | 95.7453 | 95.7493 | 27.0009 | 27.002
360 | feeder2_line20 | 1 | 99 | 5.4395e-07 | 8.7895e-07 | 5.4945e-07 | 8.8782e-07
360 | feeder2_line20 | 2 | 99 | 5.4308e-07 | 8.7784e-07 | 5.4857e-07 | 8.8671e-07
360 | feeder2_line20 | 3 | 99 | 1.5795 | 1.5795 | 1.5954 | 1.5955
360 | feeder2_line21 | 1 | 354.6 | 97.433 | 97.4281 | 27.4769 | 27.4755
360 | feeder2_line21 | 2 | 354.6 | 102.9552 | 102.9578 | 29.0342 | 29.0349
360 | feeder2_line21 | 3 | 354.6 | 94.8541 | 94.858 | 26.7496 | 26.7507
360 | feeder2_line22 | 1 | 99 | 5.6847e-07 | 1.0076e-06 | 5.7421e-07 | 1.0177e-06
360 | feeder2_line22 | 2 | 99 | 0.094593 | 0.094595 | 0.095548 | 0.09555
360 | feeder2_line22 | 3 | 99 | 5.6636e-07 | 1.0039e-06 | 5.7208e-07 | 1.014e-06
360 | feeder2_line23 | 1 | 99 | 5.6847e-07 | 9.4315e-07 | 5.7421e-07 | 9.5268e-07
360 | feeder2_line23 | 2 | 99 | 5.677e-07 | 9.4191e-07 | 5.7344e-07 | 9.5143e-07
360 | feeder2_line23 | 3 | 99 | 0.83894 | 0.83895 | 0.84742 | 0.84742
360 | feeder2_line24 | 1 | 354.6 | 97.4331 | 97.4281 | 27.4769 | 27.4755
360 | feeder2_line24 | 2 | 354.6 | 102.988 | 102.9905 | 29.0434 | 29.0441
360 | feeder2_line24 | 3 | 354.6 | 94.3586 | 94.3624 | 26.6099 | 26.611
360 | feeder2_line25 | 1 | 99 | 0.094408 | 0.094407 | 0.095361 | 0.09536
360 | feeder2_line25 | 2 | 99 | 4.9354e-08 | 6.8465e-07 | 4.9852e-08 | 6.9157e-07
360 | feeder2_line25 | 3 | 99 | 4.9611e-08 | 6.8294e-07 | 5.0112e-08 | 6.8984e-07
360 | feeder2_line26 | 1 | 99 | 0.22051 | 0.22051 | 0.22274 | 0.22274
360 | feeder2_line26 | 2 | 99 | 5.4292e-07 | 8.4824e-07 | 5.484e-07 | 8.5681e-07
360 | feeder2_line26 | 3 | 99 | 5.4135e-07 | 8.4612e-07 | 5.4682e-07 | 8.5466e-07
360 | feeder2_line27 | 1 | 354.6 | 97.5575 | 97.5525 | 27.512 | 27.5106
360 | feeder2_line27 | 2 | 354.6 | 102.988 | 102.9905 | 29.0434 | 29.0441
360 | feeder2_line27 | 3 | 354.6 | 94.3586 | 94.3624 | 26.6099 | 26.611
360 | feeder2_line28 | 1 | 99 | 2.5232e-06 | 7.0503e-07 | 2.5487e-06 | 7.1215e-07
360 | feeder2_line28 | 2 | 99 | 0.1094 | 0.1094 | 0.1105 | 0.1105
360 | feeder2_line28 | 3 | 99 | 2.5065e-06 | 7.0194e-07 | 2.5319e-06 | 7.0903e-07
360 | feeder2_line29 | 1 | 354.6 | 97.5575 | 97.5525 | 27.512 | 27.5106
360 | feeder2_line29 | 2 | 354.6 | 103.036 | 103.0385 | 29.057 | 29.0577
360 | feeder2_line29 | 3 | 354.6 | 94.3586 | 94.3624 | 26.6099 | 26.611
360 | feeder2_line30 | 1 | 266.4 | 0.87825 | 0.87776 | 0.32967 | 0.32949
360 | feeder2_line30 | 2 | 266.4 | 1.2627 | 1.263 | 0.474 | 0.47408
360 | feeder2_line30 | 3 | 266.4 | 17.4254 | 17.4251 | 6.5411 | 6.541
360 | feeder2_line31 | 1 | 354.6 | 97.9271 | 97.9213 | 27.6162 | 27.6146
360 | feeder2_line31 | 2 | 354.6 | 102.4148 | 102.4167 | 28.8818 | 28.8823
360 | feeder2_line31 | 3 | 354.6 | 98.9814 | 98.9847 | 27.9135 | 27.9145
360 | feeder2_line32 | 1 | 354.6 | 97.9271 | 97.9213 | 27.6162 | 27.6146
360 | feeder2_line32 | 2 | 354.6 | 102.4971 | 102.499 | 28.905 | 28.9055
360 | feeder2_line32 | 3 | 354.6 | 98.9814 | 98.9847 | 27.9135 | 27.9145
360 | feeder2_line33 | 1 | 99 | 4.8909e-08 | 6.7995e-07 | 4.9403e-08 | 6.8682e-07
360 | feeder2_line33 | 2 | 99 | 0.25728 | 0.25729 | 0.25988 | 0.25989
360 | feeder2_line33 | 3 | 99 | 4.9641e-08 | 6.7648e-07 | 5.0143e-08 | 6.8331e-07
360 | feeder2_line34 | 1 | 354.6 | 97.9271 | 97.9213 | 27.6162 | 27.6146
360 | feeder2_line34 | 2 | 354.6 | 102.4971 | 102.499 | 28.905 | 28.9055
360 | feeder2_line34 | 3 | 354.6 | 99.0805 | 99.0838 | 27.9415 | 27.9424
360 | feeder2_line35 | 1 | 99 | 2.9628e-07 | 7.5291e-07 | 2.9928e-07 | 7.6051e-07
360 | feeder2_line35 | 2 | 99 | 2.9579e-07 | 7.5134e-07 | 2.9878e-07 | 7.5893e-07
360 | feeder2_line35 | 3 | 99 | 0.2747 | 0.2747 | 0.27747 | 0.27747
360 | feeder2_line36 | 1 | 354.6 | 97.2796 | 97.2736 | 27.4336 | 27.4319
360 | feeder2_line36 | 2 | 354.6 | 102.4971 | 102.499 | 28.905 | 28.9055
360 | feeder2_line36 | 3 | 354.6 | 99.0806 | 99.0838 | 27.9415 | 27.9424
360 | feeder2_line37 | 1 | 99 | 1.2301 | 1.2301 | 1.2425 | 1.2425
360 | feeder2_line37 | 2 | 99 | 2.9574e-07 | 8.3121e-07 | 2.9873e-07 | 8.396e-07
360 | feeder2_line37 | 3 | 99 | 2.9495e-07 | 8.2868e-07 | 2.9793e-07 | 8.3705e-07
360 | feeder2_line38 | 1 | 99 | 3.2081e-07 | 7.6894e-07 | 3.2405e-07 | 7.7671e-07
360 | feeder2_line38 | 2 | 99 | 0.078005 | 0.078008 | 0.078793 | 0.078796
360 | feeder2_line38 | 3 | 99 | 3.1988e-07 | 7.6498e-07 | 3.2311e-07 | 7.7271e-07
360 | feeder2_line39 | 1 | 266.4 | 0.87826 | 0.87776 | 0.32968 | 0.32949
360 | feeder2_line39 | 2 | 266.4 | 1.2161 | 1.2163 | 0.45648 | 0.45657
360 | feeder2_line39 | 3 | 266.4 | 17.4254 | 17.4251 | 6.5411 | 6.541
360 | feeder2_line40 | 1 | 354.6 | 97.3215 | 97.3155 | 27.4454 | 27.4438
360 | feeder2_line40 | 2 | 354.6 | 102.4971 | 102.499 | 28.905 | 28.9055
360 | feeder2_line40 | 3 | 354.6 | 99.0805 | 99.0838 | 27.9415 | 27.9424
360 | feeder2_line41 | 1 | 99 | 0.094425 | 0.094424 | 0.095379 | 0.095377
360 | feeder2_line41 | 2 | 99 | 4.9305e-08 | 7.2626e-07 | 4.9803e-08 | 7.336e-07
360 | feeder2_line41 | 3 | 99 | 4.9634e-08 | 7.2407e-07 | 5.0135e-08 | 7.3138e-07
360 | feeder2_line42 | 1 | 99 | 2.9636e-07 | 7.4222e-07 | 2.9935e-07 | 7.4972e-07
360 | feeder2_line42 | 2 | 99 | 2.959e-07 | 7.4082e-07 | 2.9889e-07 | 7.483e-07
360 | feeder2_line42 | 3 | 99 | 0.19003 | 0.19003 | 0.19195 | 0.19195
360 | feeder2_line43 | 1 | 266.4 | 0.87815 | 0.87776 | 0.32963 | 0.32949
360 | feeder2_line43 | 2 | 266.4 | 1.2162 | 1.2163 | 0.45651 | 0.45657
360 | feeder2_line43 | 3 | 266.4 | 17.2354 | 17.2352 | 6.4697 | 6.4697
360 | feeder2_line44 | 1 | 354.6 | 97.3215 | 97.3155 | 27.4454 | 27.4438
360 | feeder2_line44 | 2 | 354.6 | 102.4971 | 102.4991 | 28.905 | 28.9055
360 | feeder2_line44 | 3 | 354.6 | 98.473 | 98.4762 | 27.7702 | 27.7711
360 | feeder2_line45 | 1 | 99 | 4.8882e-08 | 5.7398e-07 | 4.9376e-08 | 5.7978e-07
360 | feeder2_line45 | 2 | 99 | 4.9301e-08 | 5.727e-07 | 4.9799e-08 | 5.7848e-07
360 | feeder2_line45 | 3 | 99 | 1.5784 | 1.5784 | 1.5943 | 1.5944
360 | feeder2_line46 | 1 | 99 | 5.6826e-07 | 1.3455e-06 | 5.74e-07 | 1.3591e-06
360 | feeder2_line46 | 2 | 99 | 5.6716e-07 | 1.343e-06 | 5.7289e-07 | 1.3565e-06
360 | feeder2_line46 | 3 | 99 | 0.16297 | 0.16299 | 0.16462 | 0.16463
360 | feeder2_line47 | 1 | 266.4 | 0.87814 | 0.87776 | 0.32963 | 0.32949
360 | feeder2_line47 | 2 | 266.4 | 1.2163 | 1.2163 | 0.45658 | 0.45658
360 | feeder2_line47 | 3 | 266.4 | 17.0725 | 17.0723 | 6.4086 | 6.4085
360 | feeder2_line48 | 1 | 99 | 0.1369 | 0.1369 | 0.13828 | 0.13828
360 | feeder2_line48 | 2 | 99 | 4.9302e-08 | 7.2309e-07 | 4.98e-08 | 7.3039e-07
360 | feeder2_line48 | 3 | 99 | 4.9675e-08 | 7.2049e-07 | 5.0177e-08 | 7.2777e-07
360 | feeder2_line49 | 1 | 266.4 | 0.74303 | 0.74268 | 0.27892 | 0.27878
360 | feeder2_line49 | 2 | 266.4 | 1.2163 | 1.2163 | 0.45657 | 0.45658
360 | feeder2_line49 | 3 | 266.4 | 17.0724 | 17.0723 | 6.4086 | 6.4085
360 | feeder2_line50 | 1 | 99 | 5.6827e-07 | 1.2245e-06 | 5.7401e-07 | 1.2369e-06
360 | feeder2_line50 | 2 | 99 | 0.08603 | 0.086034 | 0.086899 | 0.086903
360 | feeder2_line50 | 3 | 99 | 5.6507e-07 | 1.2177e-06 | 5.7078e-07 | 1.23e-06
360 | feeder2_line51 | 1 | 99 | 0.090514 | 0.090378 | 0.091428 | 0.091291
360 | feeder2_line51 | 2 | 99 | 5.6717e-07 | 1.3269e-06 | 5.729e-07 | 1.3403e-06
360 | feeder2_line51 | 3 | 99 | 5.6507e-07 | 1.322e-06 | 5.7078e-07 | 1.3353e-06
360 | feeder2_line52 | 1 | 266.4 | 0.65425 | 0.65415 | 0.24559 | 0.24555
360 | feeder2_line52 | 2 | 266.4 | 1.1676 | 1.1677 | 0.43829 | 0.43832
360 | feeder2_line52 | 3 | 266.4 | 17.0723 | 17.0723 | 6.4085 | 6.4085
360 | feeder2_line53 | 1 | 99 | 5.4382e-07 | 7.4736e-07 | 5.4931e-07 | 7.5491e-07
360 | feeder2_line53 | 2 | 99 | 1.1677 | 1.1677 | 1.1795 | 1.1795
360 | feeder2_line53 | 3 | 99 | 5.4021e-07 | 7.4319e-07 | 5.4567e-07 | 7.507e-07
360 | feeder2_line54 | 1 | 266.4 | 0.65407 | 0.65415 | 0.24552 | 0.24555
360 | feeder2_line54 | 2 | 266.4 | 8.4574e-05 | 4.5761e-06 | 3.1747e-05 | 1.7177e-06
360 | feeder2_line54 | 3 | 266.4 | 17.0721 | 17.0723 | 6.4085 | 6.4085
360 | feeder2_line55 | 1 | 99 | 1.1828 | 1.1828 | 1.1948 | 1.1948
360 | feeder2_line55 | 2 | 99 | 4.9297e-08 | 7.2123e-07 | 4.9795e-08 | 7.2852e-07
360 | feeder2_line55 | 3 | 99 | 4.9623e-08 | 7.1912e-07 | 5.0124e-08 | 7.2638e-07
360 | feeder2_line56 | 1 | 354.6 | 96.8241 | 96.8181 | 27.3052 | 27.3035
360 | feeder2_line56 | 2 | 354.6 | 102.4972 | 102.4991 | 28.905 | 28.9055
360 | feeder2_line56 | 3 | 354.6 | 98.473 | 98.4762 | 27.7702 | 27.7711
360 | feeder2_line57 | 1 | 99 | 7.3325e-07 | 1.5309e-06 | 7.4065e-07 | 1.5463e-06
360 | feeder2_line57 | 2 | 99 | 7.3935e-07 | 1.5279e-06 | 7.4682e-07 | 1.5434e-06
360 | feeder2_line57 | 3 | 99 | 17.0722 | 17.0723 | 17.2447 | 17.2447
360 | feeder2_line58 | 1 | 266.4 | 0.65413 | 0.65415 | 0.24555 | 0.24555
360 | feeder2_line58 | 2 | 266.4 | 1.8759e-05 | 2.6568e-06 | 7.0418e-06 | 9.9729e-07
360 | feeder2_line58 | 3 | 266.4 | 1.8655e-05 | 2.6471e-06 | 7.0027e-06 | 9.9366e-07
360 | feeder2_line59 | 1 | 99 | 4.8869e-08 | 5.3212e-07 | 4.9363e-08 | 5.375e-07
360 | feeder2_line59 | 2 | 99 | 4.9284e-08 | 5.3112e-07 | 4.9781e-08 | 5.3649e-07
360 | feeder2_line59 | 3 | 99 | 17.01 | 17.0101 | 17.1818 | 17.1819
360 | feeder2_line60 | 1 | 99 | 2.9636e-07 | 8.0422e-07 | 2.9935e-07 | 8.1234e-07
360 | feeder2_line60 | 2 | 99 | 2.9591e-07 | 8.027e-07 | 2.989e-07 | 8.1081e-07
360 | feeder2_line60 | 3 | 99 | 0.062452 | 0.062452 | 0.063082 | 0.063082
360 | feeder2_line61 | 1 | 266.4 | 0.086272 | 0.086435 | 0.032384 | 0.032446
360 | feeder2_line61 | 2 | 266.4 | 1.8542 | 1.8544 | 0.69602 | 0.69609
360 | feeder2_line61 | 3 | 266.4 | 0.38598 | 0.38616 | 0.14489 | 0.14496
360 | feeder2_line62 | 1 | 354.6 | 96.8647 | 96.8587 | 27.3166 | 27.3149
360 | feeder2_line62 | 2 | 354.6 | 101.8665 | 101.8684 | 28.7272 | 28.7277
360 | feeder2_line62 | 3 | 354.6 | 98.6292 | 98.6326 | 27.8142 | 27.8152
360 | feeder2_line63 | 1 | 99 | 0.35943 | 0.35943 | 0.36306 | 0.36306
360 | feeder2_line63 | 2 | 99 | 5.6718e-07 | 1.2069e-06 | 5.7291e-07 | 1.219e-06
360 | feeder2_line63 | 3 | 99 | 5.65e-07 | 1.2023e-06 | 5.7071e-07 | 1.2144e-06
360 | feeder2_line64 | 1 | 99 | 0.29473 | 0.29473 | 0.29771 | 0.29771
360 | feeder2_line64 | 2 | 99 | 3.9616e-12 | 3.1791e-07 | 4.0016e-12 | 3.2112e-07
360 | feeder2_line64 | 3 | 99 | 3.9613e-12 | 3.167e-07 | 4.0014e-12 | 3.199e-07
360 | feeder2_line65 | 1 | 99 | 4.8809e-08 | 6.3481e-07 | 4.9302e-08 | 6.4123e-07
360 | feeder2_line65 | 2 | 99 | 0.27896 | 0.27896 | 0.28178 | 0.28178
360 | feeder2_line65 | 3 | 99 | 4.9615e-08 | 6.3126e-07 | 5.0117e-08 | 6.3764e-07
360 | feeder2_line66 | 1 | 354.6 | 96.8647 | 96.8587 | 27.3166 | 27.3149
360 | feeder2_line66 | 2 | 354.6 | 101.9622 | 101.9642 | 28.7541 | 28.7547
360 | feeder2_line66 | 3 | 354.6 | 98.6292 | 98.6326 | 27.8142 | 27.8152
360 | feeder2_line67 | 1 | 99 | 2.4407e-08 | 3.5894e-07 | 2.4654e-08 | 3.6256e-07
360 | feeder2_line67 | 2 | 99 | 2.4645e-08 | 3.5799e-07 | 2.4894e-08 | 3.6161e-07
360 | feeder2_line67 | 3 | 99 | 0.095126 | 0.095126 | 0.096087 | 0.096087
360 | feeder2_line68 | 1 | 266.4 | 0.08631 | 0.086435 | 0.032399 | 0.032446
360 | feeder2_line68 | 2 | 266.4 | 1.8543 | 1.8544 | 0.69604 | 0.69609
360 | feeder2_line68 | 3 | 266.4 | 0.29096 | 0.29111 | 0.10922 | 0.10927
360 | feeder2_line69 | 1 | 99 | 0.2142 | 0.21416 | 0.21636 | 0.21633
360 | feeder2_line69 | 2 | 99 | 2.5104e-06 | 6.571e-07 | 2.5357e-06 | 6.6374e-07
360 | feeder2_line69 | 3 | 99 | 2.5002e-06 | 6.5526e-07 | 2.5254e-06 | 6.6188e-07
360 | feeder2_line70 | 1 | 354.6 | 96.9548 | 96.9488 | 27.342 | 27.3403
360 | feeder2_line70 | 2 | 354.6 | 101.9622 | 101.9642 | 28.7542 | 28.7547
360 | feeder2_line70 | 3 | 354.6 | 98.6293 | 98.6326 | 27.8142 | 27.8152
360 | feeder2_line71 | 1 | 99 | 4.8787e-08 | 7.081e-07 | 4.9279e-08 | 7.1526e-07
360 | feeder2_line71 | 2 | 99 | 1.4211 | 1.4211 | 1.4355 | 1.4355
360 | feeder2_line71 | 3 | 99 | 4.9612e-08 | 7.041e-07 | 5.0113e-08 | 7.1121e-07
360 | feeder2_line72 | 1 | 354.6 | 96.9548 | 96.9488 | 27.342 | 27.3403
360 | feeder2_line72 | 2 | 354.6 | 101.3658 | 101.3678 | 28.586 | 28.5865
360 | feeder2_line72 | 3 | 354.6 | 98.6293 | 98.6326 | 27.8142 | 27.8152
360 | feeder2_line73 | 1 | 99 | 5.9229e-07 | 1.5196e-06 | 5.9827e-07 | 1.535e-06
360 | feeder2_line73 | 2 | 99 | 0.25725 | 0.25725 | 0.25984 | 0.25985
360 | feeder2_line73 | 3 | 99 | 5.8952e-07 | 1.5113e-06 | 5.9548e-07 | 1.5265e-06
360 | feeder2_line74 | 1 | 99 | 4.8829e-08 | 4.5323e-07 | 4.9322e-08 | 4.5781e-07
360 | feeder2_line74 | 2 | 99 | 0.29117 | 0.29118 | 0.29411 | 0.29412
360 | feeder2_line74 | 3 | 99 | 4.962e-08 | 4.5074e-07 | 5.0121e-08 | 4.5529e-07
360 | feeder2_line75 | 1 | 266.4 | 0.086407 | 0.086435 | 0.032435 | 0.032446
360 | feeder2_line75 | 2 | 266.4 | 1.4721 | 1.4721 | 0.55258 | 0.55258
360 | feeder2_line75 | 3 | 266.4 | 0.29106 | 0.29111 | 0.10926 | 0.10927
360 | feeder2_line76 | 1 | 99 | 0.086439 | 0.086435 | 0.087312 | 0.087308
360 | feeder2_line76 | 2 | 99 | 8.3719e-07 | 1.5634e-06 | 8.4564e-07 | 1.5792e-06
360 | feeder2_line76 | 3 | 99 | 8.3467e-07 | 1.5589e-06 | 8.431e-07 | 1.5747e-06
360 | feeder2_line77 | 1 | 99 | 2.4408e-08 | 5.6956e-07 | 2.4655e-08 | 5.7532e-07
360 | feeder2_line77 | 2 | 99 | 2.4646e-08 | 5.6805e-07 | 2.4895e-08 | 5.7379e-07
360 | feeder2_line77 | 3 | 99 | 0.29109 | 0.29111 | 0.29403 | 0.29405
360 | feeder2_line78 | 1 | 266.4 | 9.6018e-12 | 9.4425e-07 | 3.6043e-12 | 3.5445e-07
360 | feeder2_line78 | 2 | 266.4 | 1.4721 | 1.4721 | 0.55259 | 0.55259
360 | feeder2_line78 | 3 | 266.4 | 2.7056e-12 | 9.3974e-07 | 1.0156e-12 | 3.5275e-07
360 | feeder2_line79 | 1 | 354.6 | 0.37407 | 0.3736 | 0.10549 | 0.10536
360 | feeder2_line79 | 2 | 354.6 | 5.1484 | 5.1483 | 1.4519 | 1.4519
360 | feeder2_line79 | 3 | 354.6 | 5.02 | 5.0197 | 1.4157 | 1.4156
360 | feeder2_line80 | 1 | 354.6 | 97.131 | 97.1246 | 27.3917 | 27.3899
360 | feeder2_line80 | 2 | 354.6 | 99.0716 | 99.0734 | 27.939 | 27.9395
360 | feeder2_line80 | 3 | 354.6 | 97.3995 | 97.4025 | 27.4674 | 27.4683
360 | feeder2_line81 | 1 | 354.6 | 97.1309 | 97.1246 | 27.3917 | 27.3899
360 | feeder2_line81 | 2 | 354.6 | 99.0715 | 99.0734 | 27.9389 | 27.9395
360 | feeder2_line81 | 3 | 354.6 | 97.5083 | 97.5115 | 27.4981 | 27.499
360 | feeder2_line82 | 1 | 354.6 | 2.5818e-11 | 7.2578e-07 | 7.2808e-12 | 2.0468e-07
360 | feeder2_line82 | 2 | 354.6 | 3.0519e-11 | 7.2378e-07 | 8.6066e-12 | 2.0411e-07
360 | feeder2_line82 | 3 | 354.6 | 0.2494 | 0.2494 | 0.070331 | 0.070332
360 | feeder2_line83 | 1 | 354.6 | 97.131 | 97.1246 | 27.3917 | 27.3899
360 | feeder2_line83 | 2 | 354.6 | 98.6083 | 98.61 | 27.8083 | 27.8088
360 | feeder2_line83 | 3 | 354.6 | 97.5084 | 97.5115 | 27.4982 | 27.499
360 | feeder2_line84 | 1 | 354.6 | 1.3127e-11 | 1.2825e-06 | 3.7018e-12 | 3.6167e-07
360 | feeder2_line84 | 2 | 354.6 | 1.05 | 1.05 | 0.2961 | 0.29611
360 | feeder2_line84 | 3 | 354.6 | 1.2734e-11 | 1.2758e-06 | 3.5912e-12 | 3.5979e-07
360 | feeder2_line85 | 1 | 99 | 0.077826 | 0.077821 | 0.078612 | 0.078607
360 | feeder2_line85 | 2 | 99 | 4.927e-08 | 4.5645e-07 | 4.9768e-08 | 4.6106e-07
360 | feeder2_line85 | 3 | 99 | 4.9598e-08 | 4.5521e-07 | 5.0099e-08 | 4.5981e-07
360 | feeder2_line86 | 1 | 354.6 | 97.1689 | 97.1625 | 27.4024 | 27.4006
360 | feeder2_line86 | 2 | 354.6 | 98.6083 | 98.61 | 27.8083 | 27.8088
360 | feeder2_line86 | 3 | 354.6 | 97.5085 | 97.5115 | 27.4982 | 27.499
360 | feeder2_line87 | 1 | 354.6 | 97.169 | 97.1625 | 27.4024 | 27.4006
360 | feeder2_line87 | 2 | 354.6 | 98.1092 | 98.1109 | 27.6676 | 27.668
360 | feeder2_line87 | 3 | 354.6 | 97.6249 | 97.6279 | 27.531 | 27.5318
360 | feeder2_line88 | 1 | 354.6 | 0.00011435 | 3.3242e-06 | 3.2246e-05 | 9.3744e-07
360 | feeder2_line88 | 2 | 354.6 | 1.125 | 1.1251 | 0.31727 | 0.31727
360 | feeder2_line88 | 3 | 354.6 | 0.26178 | 0.2617 | 0.073824 | 0.073802
360 | feeder2_line89 | 1 | 354.6 | 97.1678 | 97.1625 | 27.4021 | 27.4006
360 | feeder2_line89 | 2 | 354.6 | 97.7506 | 97.7534 | 27.5664 | 27.5672
360 | feeder2_line89 | 3 | 354.6 | 97.6237 | 97.6279 | 27.5306 | 27.5318
360 | feeder2_line90 | 1 | 354.6 | 0.00071705 | 2.0064e-06 | 0.00020221 | 5.6581e-07
360 | feeder2_line90 | 2 | 354.6 | 1.1827 | 1.1828 | 0.33353 | 0.33355
360 | feeder2_line90 | 3 | 354.6 | 0.00070977 | 1.9938e-06 | 0.00020016 | 5.6228e-07
360 | feeder2_line91 | 1 | 354.6 | 97.1679 | 97.1625 | 27.4021 | 27.4006
360 | feeder2_line91 | 2 | 354.6 | 97.7507 | 97.7534 | 27.5665 | 27.5672
360 | feeder2_line91 | 3 | 354.6 | 97.655 | 97.6591 | 27.5395 | 27.5406
360 | feeder2_line92 | 1 | 354.6 | 1.0613e-11 | 1.0116e-06 | 2.993e-12 | 2.8527e-07
360 | feeder2_line92 | 2 | 354.6 | 1.5342e-11 | 1.0087e-06 | 4.3265e-12 | 2.8447e-07
360 | feeder2_line92 | 3 | 354.6 | 0.062509 | 0.06251 | 0.017628 | 0.017628
360 | feeder2_line93 | 1 | 99 | 2.4366e-08 | 3.3778e-07 | 2.4612e-08 | 3.4119e-07
360 | feeder2_line93 | 2 | 99 | 1.0499 | 1.0499 | 1.0605 | 1.0606
360 | feeder2_line93 | 3 | 99 | 2.4793e-08 | 3.3582e-07 | 2.5044e-08 | 3.3922e-07
360 | feeder2_line94 | 1 | 354.6 | 2.4372e-06 | 1.6439e-06 | 6.8731e-07 | 4.636e-07
360 | feeder2_line94 | 2 | 354.6 | 0.19464 | 0.19464 | 0.054889 | 0.054891
360 | feeder2_line94 | 3 | 354.6 | 2.4792e-06 | 1.6354e-06 | 6.9916e-07 | 4.612e-07
360 | feeder2_line95 | 1 | 99 | 3.5268e-06 | 2.5778e-06 | 3.5624e-06 | 2.6038e-06
360 | feeder2_line95 | 2 | 99 | 1.125 | 1.1251 | 1.1364 | 1.1364
360 | feeder2_line95 | 3 | 99 | 3.4991e-06 | 2.563e-06 | 3.5345e-06 | 2.5889e-06
360 | feeder2_line96 | 1 | 354.6 | 0.00011971 | 6.144e-07 | 3.3759e-05 | 1.7327e-07
360 | feeder2_line96 | 2 | 354.6 | 0.00011923 | 6.1253e-07 | 3.3624e-05 | 1.7274e-07
360 | feeder2_line96 | 3 | 354.6 | 0.26176 | 0.2617 | 0.073818 | 0.073802
360 | feeder2_line97 | 1 | 354.6 | 97.2559 | 97.2502 | 27.4269 | 27.4253
360 | feeder2_line97 | 2 | 354.6 | 97.7511 | 97.7534 | 27.5666 | 27.5672
360 | feeder2_line97 | 3 | 354.6 | 97.6553 | 97.6591 | 27.5396 | 27.5406
360 | feeder2_line98 | 1 | 354.6 | 0.15783 | 0.1561 | 0.044509 | 0.044022
360 | feeder2_line98 | 2 | 354.6 | 0.0016673 | 6.0839e-07 | 0.00047019 | 1.7157e-07
360 | feeder2_line98 | 3 | 354.6 | 0.0016692 | 6.1006e-07 | 0.00047072 | 1.7204e-07
360 | feeder2_line99 | 1 | 99 | 2.4377e-08 | 4.4175e-07 | 2.4623e-08 | 4.4621e-07
360 | feeder2_line99 | 2 | 99 | 2.4636e-08 | 4.4037e-07 | 2.4885e-08 | 4.4482e-07
360 | feeder2_line99 | 3 | 99 | 0.26168 | 0.2617 | 0.26432 | 0.26435
360 | feeder2_line100 | 1 | 99 | 0.15614 | 0.1561 | 0.15772 | 0.15768
360 | feeder2_line100 | 2 | 99 | 2.4628e-08 | 6.0431e-07 | 2.4877e-08 | 6.1041e-07
360 | feeder2_line100 | 3 | 99 | 2.4791e-08 | 6.0273e-07 | 2.5041e-08 | 6.0882e-07
360 | feeder2_line101 | 1 | 354.6 | 0.19503 | 0.1946 | 0.054999 | 0.054878
360 | feeder2_line101 | 2 | 354.6 | 5.1484 | 5.1483 | 1.4519 | 1.4519
360 | feeder2_line101 | 3 | 354.6 | 5.02 | 5.0197 | 1.4157 | 1.4156
360 | feeder2_line102 | 1 | 99 | 0.17942 | 0.17939 | 0.18123 | 0.1812
360 | feeder2_line102 | 2 | 99 | 2.2967e-06 | 8.6544e-07 | 2.3199e-06 | 8.7418e-07
360 | feeder2_line102 | 3 | 99 | 2.2916e-06 | 8.6301e-07 | 2.3147e-06 | 8.7172e-07
360 | feeder2_line103 | 1 | 99 | 5.433e-07 | 7.9459e-07 | 5.4878e-07 | 8.0262e-07
360 | feeder2_line103 | 2 | 99 | 0.097391 | 0.097394 | 0.098375 | 0.098378
360 | feeder2_line103 | 3 | 99 | 5.3947e-07 | 7.8989e-07 | 5.4492e-07 | 7.9787e-07
360 | feeder2_line104 | 1 | 354.6 | 0.19493 | 0.1946 | 0.054971 | 0.054878
360 | feeder2_line104 | 2 | 354.6 | 5.0953 | 5.0952 | 1.4369 | 1.4369
360 | feeder2_line104 | 3 | 354.6 | 5.02 | 5.0197 | 1.4157 | 1.4156
360 | feeder2_line105 | 1 | 99 | 2.5215e-06 | 7.3113e-07 | 2.547e-06 | 7.3852e-07
360 | feeder2_line105 | 2 | 99 | 2.5092e-06 | 7.2886e-07 | 2.5345e-06 | 7.3622e-07
360 | feeder2_line105 | 3 | 99 | 0.48808 | 0.4881 | 0.49301 | 0.49303
360 | feeder2_line106 | 1 | 354.6 | 0.19487 | 0.1946 | 0.054955 | 0.054878
360 | feeder2_line106 | 2 | 354.6 | 5.0953 | 5.0952 | 1.4369 | 1.4369
360 | feeder2_line106 | 3 | 354.6 | 4.6423 | 4.6421 | 1.3092 | 1.3091
360 | feeder2_line107 | 1 | 99 | 3.204e-07 | 8.91e-07 | 3.2363e-07 | 9e-07
360 | feeder2_line107 | 2 | 99 | 2.1907 | 2.1908 | 2.2129 | 2.2129
360 | feeder2_line107 | 3 | 99 | 3.1933e-07 | 8.8565e-07 | 3.2256e-07 | 8.946e-07
360 | feeder2_line108 | 1 | 354.6 | 0.19486 | 0.1946 | 0.054952 | 0.054878
360 | feeder2_line108 | 2 | 354.6 | 2.9121 | 2.912 | 0.82124 | 0.82121
360 | feeder2_line108 | 3 | 354.6 | 4.6423 | 4.6421 | 1.3092 | 1.3091
360 | feeder2_line109 | 1 | 354.6 | 96.7355 | 96.7294 | 27.2802 | 27.2785
360 | feeder2_line109 | 2 | 354.6 | 97.7514 | 97.7534 | 27.5667 | 27.5672
360 | feeder2_line109 | 3 | 354.6 | 97.6557 | 97.6591 | 27.5397 | 27.5406
360 | feeder2_line110 | 1 | 99 | 1.4065 | 1.406 | 1.4207 | 1.4202
360 | feeder2_line110 | 2 | 99 | 0.00079108 | 8.951e-07 | 0.00079907 | 9.0414e-07
360 | feeder2_line110 | 3 | 99 | 0.00078783 | 8.9171e-07 | 0.00079578 | 9.0071e-07
360 | feeder2_line111 | 1 | 99 | 2.4374e-08 | 3.7729e-07 | 2.462e-08 | 3.811e-07
360 | feeder2_line111 | 2 | 99 | 0.073143 | 0.073145 | 0.073882 | 0.073884
360 | feeder2_line111 | 3 | 99 | 2.4796e-08 | 3.7513e-07 | 2.5047e-08 | 3.7892e-07
360 | feeder2_line112 | 1 | 99 | 3.2032e-07 | 9.0666e-07 | 3.2355e-07 | 9.1582e-07
360 | feeder2_line112 | 2 | 99 | 1.0909 | 1.091 | 1.102 | 1.102
360 | feeder2_line112 | 3 | 99 | 3.193e-07 | 9.0145e-07 | 3.2253e-07 | 9.1056e-07
360 | feeder2_line113 | 1 | 99 | 1.3468 | 1.3468 | 1.3604 | 1.3604
360 | feeder2_line113 | 2 | 99 | 3.197e-07 | 8.9085e-07 | 3.2293e-07 | 8.9985e-07
360 | feeder2_line113 | 3 | 99 | 3.192e-07 | 8.8855e-07 | 3.2243e-07 | 8.9752e-07
360 | feeder2_line114 | 1 | 99 | 0.097102 | 0.097099 | 0.098083 | 0.09808
360 | feeder2_line114 | 2 | 99 | 2.4641e-08 | 4.3034e-07 | 2.489e-08 | 4.3469e-07
360 | feeder2_line114 | 3 | 99 | 2.4807e-08 | 4.2914e-07 | 2.5057e-08 | 4.3347e-07
360 | feeder2_line115 | 1 | 99 | 2.4374e-08 | 5.5603e-07 | 2.462e-08 | 5.6165e-07
360 | feeder2_line115 | 2 | 99 | 1.4941 | 1.4941 | 1.5092 | 1.5092
360 | feeder2_line115 | 3 | 99 | 2.4812e-08 | 5.5266e-07 | 2.5063e-08 | 5.5824e-07
360 | feeder2_line116 | 1 | 354.6 | 0.19487 | 0.1946 | 0.054954 | 0.054878
360 | feeder2_line116 | 2 | 354.6 | 1.4189 | 1.4188 | 0.40015 | 0.40012
360 | feeder2_line116 | 3 | 354.6 | 4.6423 | 4.6421 | 1.3092 | 1.3091
360 | feeder2_line117 | 1 | 99 | 4.8728e-08 | 6.3424e-07 | 4.922e-08 | 6.4064e-07
360 | feeder2_line117 | 2 | 99 | 0.16293 | 0.16293 | 0.16457 | 0.16458
360 | feeder2_line117 | 3 | 99 | 4.9565e-08 | 6.3061e-07 | 5.0066e-08 | 6.3698e-07
360 | feeder2_line118 | 1 | 354.6 | 96.7356 | 96.7294 | 27.2802 | 27.2785
360 | feeder2_line118 | 2 | 354.6 | 97.8219 | 97.8239 | 27.5865 | 27.5871
360 | feeder2_line118 | 3 | 354.6 | 97.6557 | 97.6591 | 27.5397 | 27.5406
360 | feeder2_line119 | 1 | 99 | 2.437e-08 | 5.9831e-07 | 2.4616e-08 | 6.0436e-07
360 | feeder2_line119 | 2 | 99 | 2.4628e-08 | 5.9643e-07 | 2.4877e-08 | 6.0245e-07
360 | feeder2_line119 | 3 | 99 | 0.54217 | 0.54217 | 0.54765 | 0.54765
360 | feeder2_line120 | 1 | 354.6 | 0.19487 | 0.1946 | 0.054955 | 0.054878
360 | feeder2_line120 | 2 | 354.6 | 1.4189 | 1.4188 | 0.40015 | 0.40012
360 | feeder2_line120 | 3 | 354.6 | 4.2523 | 4.2521 | 1.1992 | 1.1991
360 | feeder2_line121 | 1 | 99 | 3.204e-07 | 9.2651e-07 | 3.2364e-07 | 9.3587e-07
360 | feeder2_line121 | 2 | 99 | 1.3087 | 1.3087 | 1.3219 | 1.322
360 | feeder2_line121 | 3 | 99 | 3.1929e-07 | 9.2078e-07 | 3.2251e-07 | 9.3008e-07
360 | feeder2_line122 | 1 | 354.6 | 0.19486 | 0.1946 | 0.054951 | 0.054878
360 | feeder2_line122 | 2 | 354.6 | 0.18005 | 0.17982 | 0.050775 | 0.05071
360 | feeder2_line122 | 3 | 354.6 | 4.2523 | 4.2521 | 1.1992 | 1.1991
360 | feeder2_line123 | 1 | 99 | 5.6769e-07 | 9.6008e-07 | 5.7342e-07 | 9.6978e-07
360 | feeder2_line123 | 2 | 99 | 5.6588e-07 | 9.5707e-07 | 5.716e-07 | 9.6674e-07
360 | feeder2_line123 | 3 | 99 | 0.10996 | 0.10996 | 0.11107 | 0.11107
360 | feeder2_line124 | 1 | 354.6 | 0.19477 | 0.1946 | 0.054926 | 0.054878
360 | feeder2_line124 | 2 | 354.6 | 0.17996 | 0.17982 | 0.05075 | 0.05071
360 | feeder2_line124 | 3 | 354.6 | 4.1915 | 4.1913 | 1.182 | 1.182
360 | feeder2_line125 | 1 | 99 | 5.6768e-07 | 8.9249e-07 | 5.7342e-07 | 9.015e-07
360 | feeder2_line125 | 2 | 99 | 5.6589e-07 | 8.897e-07 | 5.716e-07 | 8.9868e-07
360 | feeder2_line125 | 3 | 99 | 0.1571 | 0.15713 | 0.15869 | 0.15872
360 | feeder2_line126 | 1 | 354.6 | 0.19492 | 0.1946 | 0.05497 | 0.054878
360 | feeder2_line126 | 2 | 354.6 | 0.18012 | 0.17982 | 0.050794 | 0.05071
360 | feeder2_line126 | 3 | 354.6 | 4.1099 | 4.1095 | 1.159 | 1.1589
360 | feeder2_line127 | 1 | 99 | 5.6769e-07 | 1.0684e-06 | 5.7342e-07 | 1.0792e-06
360 | feeder2_line127 | 2 | 99 | 5.6589e-07 | 1.0651e-06 | 5.7161e-07 | 1.0759e-06
360 | feeder2_line127 | 3 | 99 | 1.5486 | 1.5486 | 1.5643 | 1.5643
360 | feeder2_line128 | 1 | 354.6 | 0.19484 | 0.1946 | 0.054946 | 0.054878
360 | feeder2_line128 | 2 | 354.6 | 0.18003 | 0.17982 | 0.050771 | 0.05071
360 | feeder2_line128 | 3 | 354.6 | 2.5619 | 2.5616 | 0.72248 | 0.7224
360 | feeder2_line129 | 1 | 99 | 5.4331e-07 | 8.6636e-07 | 5.488e-07 | 8.7511e-07
360 | feeder2_line129 | 2 | 99 | 0.17981 | 0.17982 | 0.18163 | 0.18163
360 | feeder2_line129 | 3 | 99 | 5.3927e-07 | 8.6093e-07 | 5.4471e-07 | 8.6963e-07
360 | feeder2_line130 | 1 | 354.6 | 0.19486 | 0.1946 | 0.054951 | 0.054878
360 | feeder2_line130 | 2 | 354.6 | 0.00030455 | 4.5706e-06 | 8.5886e-05 | 1.2889e-06
360 | feeder2_line130 | 3 | 354.6 | 2.562 | 2.5616 | 0.72249 | 0.7224
360 | feeder2_line131 | 1 | 99 | 5.6768e-07 | 9.6021e-07 | 5.7342e-07 | 9.6991e-07
360 | feeder2_line131 | 2 | 99 | 5.6589e-07 | 9.5724e-07 | 5.7161e-07 | 9.6691e-07
360 | feeder2_line131 | 3 | 99 | 2.5181 | 2.5181 | 2.5436 | 2.5435
360 | feeder2_line132 | 1 | 354.6 | 0.19469 | 0.1946 | 0.054905 | 0.054878
360 | feeder2_line132 | 2 | 354.6 | 0.00012385 | 2.8736e-06 | 3.4927e-05 | 8.1037e-07
360 | feeder2_line132 | 3 | 354.6 | 0.078589 | 0.078523 | 0.022163 | 0.022144
360 | feeder2_line133 | 1 | 99 | 0.19462 | 0.1946 | 0.19659 | 0.19656
360 | feeder2_line133 | 2 | 99 | 2.9526e-07 | 9.6489e-07 | 2.9824e-07 | 9.7464e-07
360 | feeder2_line133 | 3 | 99 | 2.9445e-07 | 9.6181e-07 | 2.9742e-07 | 9.7153e-07
360 | feeder2_line134 | 1 | 354.6 | 5.9905e-12 | 1.7645e-06 | 1.6894e-12 | 4.9761e-07
360 | feeder2_line134 | 2 | 354.6 | 5.2599e-12 | 1.7596e-06 | 1.4833e-12 | 4.9623e-07
360 | feeder2_line134 | 3 | 354.6 | 0.078522 | 0.078523 | 0.022144 | 0.022144
360 | feeder2_line135 | 1 | 99 | 1.4226 | 1.4226 | 1.437 | 1.4369
360 | feeder2_line135 | 2 | 99 | 4.9236e-08 | 5.7592e-07 | 4.9734e-08 | 5.8174e-07
360 | feeder2_line135 | 3 | 99 | 4.9556e-08 | 5.7445e-07 | 5.0056e-08 | 5.8026e-07
360 | feeder2_line136 | 1 | 354.6 | 96.2744 | 96.2682 | 27.1501 | 27.1484
360 | feeder2_line136 | 2 | 354.6 | 97.8219 | 97.8239 | 27.5865 | 27.5871
360 | feeder2_line136 | 3 | 354.6 | 97.6557 | 97.6591 | 27.5397 | 27.5406
360 | feeder2_line137 | 1 | 99 | 0.086477 | 0.086438 | 0.087351 | 0.087311
360 | feeder2_line137 | 2 | 99 | 8.3567e-07 | 1.551e-06 | 8.4411e-07 | 1.5667e-06
360 | feeder2_line137 | 3 | 99 | 8.3342e-07 | 1.5471e-06 | 8.4184e-07 | 1.5627e-06
360 | feeder2_line138 | 1 | 354.6 | 96.3179 | 96.3116 | 27.1624 | 27.1606
360 | feeder2_line138 | 2 | 354.6 | 97.822 | 97.8239 | 27.5866 | 27.5871
360 | feeder2_line138 | 3 | 354.6 | 97.6558 | 97.6591 | 27.5397 | 27.5406
360 | feeder2_line139 | 1 | 99 | 4.8721e-08 | 4.8477e-07 | 4.9214e-08 | 4.8967e-07
360 | feeder2_line139 | 2 | 99 | 4.9241e-08 | 4.8323e-07 | 4.9738e-08 | 4.8811e-07
360 | feeder2_line139 | 3 | 99 | 0.97261 | 0.97237 | 0.98243 | 0.98219
360 | feeder2_line140 | 1 | 354.6 | 96.3179 | 96.3116 | 27.1624 | 27.1606
360 | feeder2_line140 | 2 | 354.6 | 97.8219 | 97.8239 | 27.5866 | 27.5871
360 | feeder2_line140 | 3 | 354.6 | 97.3097 | 97.3134 | 27.4421 | 27.4432
360 | feeder2_line141 | 1 | 99 | 2.4946e-06 | 4.7948e-07 | 2.5198e-06 | 4.8432e-07
360 | feeder2_line141 | 2 | 99 | 0.19002 | 0.19002 | 0.19194 | 0.19194
360 | feeder2_line141 | 3 | 99 | 2.4723e-06 | 4.7674e-07 | 2.4972e-06 | 4.8155e-07
360 | feeder2_line142 | 1 | 354.6 | 96.3179 | 96.3116 | 27.1624 | 27.1606
360 | feeder2_line142 | 2 | 354.6 | 97.9064 | 97.9084 | 27.6104 | 27.6109
360 | feeder2_line142 | 3 | 354.6 | 97.3097 | 97.3134 | 27.4421 | 27.4432
360 | feeder2_line143 | 1 | 99 | 8.3845e-07 | 1.7037e-06 | 8.4692e-07 | 1.7209e-06
360 | feeder2_line143 | 2 | 99 | 2.1899 | 2.1899 | 2.212 | 2.2121
360 | feeder2_line143 | 3 | 99 | 8.3333e-07 | 1.694e-06 | 8.4175e-07 | 1.7111e-06
360 | feeder2_line144 | 1 | 354.6 | 96.3177 | 96.3116 | 27.1624 | 27.1606
360 | feeder2_line144 | 2 | 354.6 | 96.9204 | 96.9226 | 27.3323 | 27.3329
360 | feeder2_line144 | 3 | 354.6 | 97.3095 | 97.3134 | 27.4421 | 27.4432
360 | feeder2_line145 | 1 | 99 | 2.4357e-08 | 4.777e-07 | 2.4603e-08 | 4.8253e-07
360 | feeder2_line145 | 2 | 99 | 0.24953 | 0.24954 | 0.25206 | 0.25206
360 | feeder2_line145 | 3 | 99 | 2.4774e-08 | 4.7497e-07 | 2.5024e-08 | 4.7977e-07
360 | feeder2_line146 | 1 | 354.6 | 96.3177 | 96.3116 | 27.1624 | 27.1606
360 | feeder2_line146 | 2 | 354.6 | 97.0325 | 97.0347 | 27.3639 | 27.3645
360 | feeder2_line146 | 3 | 354.6 | 97.3095 | 97.3134 | 27.442 | 27.4432
360 | feeder2_line147 | 1 | 99 | 0.10889 | 0.10888 | 0.10999 | 0.10998
360 | feeder2_line147 | 2 | 99 | 1.1304e-06 | 2.1961e-06 | 1.1419e-06 | 2.2183e-06
360 | feeder2_line147 | 3 | 99 | 1.1276e-06 | 2.1906e-06 | 1.139e-06 | 2.2128e-06
360 | feeder2_line148 | 1 | 99 | 0.22051 | 0.22051 | 0.22274 | 0.22274
360 | feeder2_line148 | 2 | 99 | 5.8983e-07 | 1.4716e-06 | 5.9579e-07 | 1.4864e-06
360 | feeder2_line148 | 3 | 99 | 5.8856e-07 | 1.4679e-06 | 5.945e-07 | 1.4827e-06
360 | feeder2_line149 | 1 | 354.6 | 96.4815 | 96.4752 | 27.2085 | 27.2068
360 | feeder2_line149 | 2 | 354.6 | 97.0326 | 97.0347 | 27.364 | 27.3645
360 | feeder2_line149 | 3 | 354.6 | 97.3096 | 97.3134 | 27.4421 | 27.4432
360 | feeder2_line150 | 1 | 354.6 | 96.4815 | 96.4752 | 27.2086 | 27.2068
360 | feeder2_line150 | 2 | 354.6 | 96.461 | 96.4631 | 27.2028 | 27.2034
360 | feeder2_line150 | 3 | 354.6 | 97.3097 | 97.3134 | 27.4421 | 27.4432
360 | feeder2_line151 | 1 | 99 | 9.6394e-06 | 1.7528e-06 | 9.7368e-06 | 1.7705e-06
360 | feeder2_line151 | 2 | 99 | 1.5213 | 1.5213 | 1.5366 | 1.5366
360 | feeder2_line151 | 3 | 99 | 9.5452e-06 | 1.7428e-06 | 9.6416e-06 | 1.7604e-06
360 | feeder2_line152 | 1 | 354.6 | 1.7795e-11 | 1.1674e-06 | 5.0184e-12 | 3.2921e-07
360 | feeder2_line152 | 2 | 354.6 | 2.9199e-12 | 1.1641e-06 | 8.2344e-13 | 3.2827e-07
360 | feeder2_line152 | 3 | 354.6 | 1.1783 | 1.1783 | 0.33228 | 0.33228
360 | feeder2_line153 | 1 | 99 | 1.3105 | 1.3105 | 1.3237 | 1.3237
360 | feeder2_line153 | 2 | 99 | 4.9221e-08 | 5.8238e-07 | 4.9718e-08 | 5.8826e-07
360 | feeder2_line153 | 3 | 99 | 4.9536e-08 | 5.8091e-07 | 5.0036e-08 | 5.8678e-07
360 | feeder2_line154 | 1 | 99 | 5.6694e-07 | 8.6939e-07 | 5.7267e-07 | 8.7818e-07
360 | feeder2_line154 | 2 | 99 | 5.651e-07 | 8.666e-07 | 5.708e-07 | 8.7535e-07
360 | feeder2_line154 | 3 | 99 | 0.041428 | 0.041463 | 0.041846 | 0.041882
360 | feeder2_line155 | 1 | 99 | 95.8877 | 95.8814 | 96.8562 | 96.8499
360 | feeder2_line155 | 2 | 99 | 96.461 | 96.4631 | 97.4353 | 97.4375
360 | feeder2_line155 | 3 | 99 | 96.8367 | 96.8405 | 97.8148 | 97.8187
360 | feeder2_line156 | 1 | 99 | 5.9135e-07 | 1.1446e-06 | 5.9733e-07 | 1.1561e-06
360 | feeder2_line156 | 2 | 99 | 0.09747 | 0.097474 | 0.098455 | 0.098458
360 | feeder2_line156 | 3 | 99 | 5.8849e-07 | 1.138e-06 | 5.9443e-07 | 1.1495e-06
360 | feeder2_line157 | 1 | 99 | 2.4348e-08 | 2.4847e-07 | 2.4594e-08 | 2.5098e-07
360 | feeder2_line157 | 2 | 99 | 1.4711 | 1.4711 | 1.486 | 1.486
360 | feeder2_line157 | 3 | 99 | 2.4771e-08 | 2.4706e-07 | 2.5022e-08 | 2.4955e-07
390 | feeder2_line1 | 1 | 354.6 | 78.0912 | 78.0987 | 22.0223 | 22.0244
390 | feeder2_line1 | 2 | 354.6 | 93.2015 | 93.1966 | 26.2836 | 26.2822
390 | feeder2_line1 | 3 | 354.6 | 93.3758 | 93.3748 | 26.3327 | 26.3324
390 | feeder2_line2 | 1 | 354.6 | 78.4495 | 78.4569 | 22.1234 | 22.1255
390 | feeder2_line2 | 2 | 354.6 | 93.2017 | 93.1966 | 26.2836 | 26.2822
390 | feeder2_line2 | 3 | 354.6 | 93.376 | 93.3748 | 26.3328 | 26.3324
390 | feeder2_line3 | 1 | 80.1 | 1.6379 | 1.6379 | 2.0448 | 2.0448
390 | feeder2_line3 | 2 | 80.1 | 5.7096e-07 | 1.0551e-06 | 7.1281e-07 | 1.3172e-06
390 | feeder2_line3 | 3 | 80.1 | 5.7117e-07 | 1.0555e-06 | 7.1307e-07 | 1.3178e-06
390 | feeder2_line4 | 1 | 354.6 | 78.4496 | 78.4569 | 22.1234 | 22.1255
390 | feeder2_line4 | 2 | 354.6 | 93.4333 | 93.4281 | 26.3489 | 26.3475
390 | feeder2_line4 | 3 | 354.6 | 93.3761 | 93.3748 | 26.3328 | 26.3324
390 | feeder2_line5 | 1 | 80.1 | 5.7041e-07 | 9.9532e-07 | 7.1212e-07 | 1.2426e-06
390 | feeder2_line5 | 2 | 80.1 | 0.27924 | 0.27924 | 0.34862 | 0.34861
390 | feeder2_line5 | 3 | 80.1 | 5.7121e-07 | 9.967e-07 | 7.1312e-07 | 1.2443e-06
390 | feeder2_line6 | 1 | 80.1 | 5.7042e-07 | 1.1709e-06 | 7.1214e-07 | 1.4618e-06
390 | feeder2_line6 | 2 | 80.1 | 5.7103e-07 | 1.1721e-06 | 7.129e-07 | 1.4633e-06
390 | feeder2_line6 | 3 | 80.1 | 0.08547 | 0.085461 | 0.1067 | 0.10669
390 | feeder2_line7 | 1 | 354.6 | 78.4497 | 78.4569 | 22.1234 | 22.1255
390 | feeder2_line7 | 2 | 354.6 | 93.4334 | 93.4281 | 26.349 | 26.3475
390 | feeder2_line7 | 3 | 354.6 | 93.4511 | 93.4497 | 26.3539 | 26.3536
390 | feeder2_line8 | 1 | 80.1 | 0.072889 | 0.07289 | 0.090998 | 0.090999
390 | feeder2_line8 | 2 | 80.1 | 5.7116e-07 | 1.1305e-06 | 7.1306e-07 | 1.4113e-06
390 | feeder2_line8 | 3 | 80.1 | 5.7139e-07 | 1.1309e-06 | 7.1335e-07 | 1.4119e-06
390 | feeder2_line9 | 1 | 354.6 | 78.5095 | 78.5167 | 22.1403 | 22.1423
390 | feeder2_line9 | 2 | 354.6 | 93.4334 | 93.4281 | 26.349 | 26.3475
390 | feeder2_line9 | 3 | 354.6 | 93.4511 | 93.4497 | 26.3539 | 26.3536
390 | feeder2_line10 | 1 | 80.1 | 8.4325e-07 | 1.4908e-06 | 1.0527e-06 | 1.8612e-06
390 | feeder2_line10 | 2 | 80.1 | 0.072734 | 0.072733 | 0.090803 | 0.090802
390 | feeder2_line10 | 3 | 80.1 | 8.447e-07 | 1.4933e-06 | 1.0546e-06 | 1.8643e-06
390 | feeder2_line11 | 1 | 354.6 | 78.5096 | 78.5167 | 22.1403 | 22.1423
390 | feeder2_line11 | 2 | 354.6 | 93.4961 | 93.4908 | 26.3666 | 26.3651
390 | feeder2_line11 | 3 | 354.6 | 93.4511 | 93.4497 | 26.354 | 26.3536
390 | feeder2_line12 | 1 | 80.1 | 5.4559e-07 | 9.8893e-07 | 6.8114e-07 | 1.2346e-06
390 | feeder2_line12 | 2 | 80.1 | 5.4646e-07 | 9.9023e-07 | 6.8223e-07 | 1.2362e-06
390 | feeder2_line12 | 3 | 80.1 | 0.061852 | 0.061852 | 0.077219 | 0.077219
390 | feeder2_line13 | 1 | 354.6 | 78.5096 | 78.5167 | 22.1403 | 22.1423
390 | feeder2_line13 | 2 | 354.6 | 93.4961 | 93.4908 | 26.3666 | 26.3651
390 | feeder2_line13 | 3 | 354.6 | 93.5054 | 93.504 | 26.3693 | 26.3689
390 | feeder2_line14 | 1 | 80.1 | 1.1738 | 1.1738 | 1.4655 | 1.4654
390 | feeder2_line14 | 2 | 80.1 | 2.9802e-07 | 6.4576e-07 | 3.7207e-07 | 8.0619e-07
390 | feeder2_line14 | 3 | 80.1 | 2.9817e-07 | 6.4603e-07 | 3.7225e-07 | 8.0653e-07
390 | feeder2_line15 | 1 | 354.6 | 78.6558 | 78.663 | 22.1816 | 22.1836
390 | feeder2_line15 | 2 | 354.6 | 93.4961 | 93.4908 | 26.3666 | 26.3651
390 | feeder2_line15 | 3 | 354.6 | 93.5054 | 93.504 | 26.3693 | 26.3689
390 | feeder2_line16 | 1 | 80.1 | 5.7051e-07 | 1.0278e-06 | 7.1225e-07 | 1.2832e-06
390 | feeder2_line16 | 2 | 80.1 | 0.25425 | 0.25424 | 0.31741 | 0.31741
390 | feeder2_line16 | 3 | 80.1 | 5.7159e-07 | 1.0298e-06 | 7.136e-07 | 1.2856e-06
390 | feeder2_line17 | 1 | 354.6 | 78.6558 | 78.663 | 22.1816 | 22.1836
390 | feeder2_line17 | 2 | 354.6 | 93.7047 | 93.6993 | 26.4255 | 26.4239
390 | feeder2_line17 | 3 | 354.6 | 93.5054 | 93.504 | 26.3693 | 26.3689
390 | feeder2_line18 | 1 | 80.1 | 5.4569e-07 | 7.3586e-07 | 6.8126e-07 | 9.1868e-07
390 | feeder2_line18 | 2 | 80.1 | 5.4691e-07 | 7.3722e-07 | 6.8279e-07 | 9.2037e-07
390 | feeder2_line18 | 3 | 80.1 | 1.4137 | 1.4137 | 1.765 | 1.7649
390 | feeder2_line19 | 1 | 354.6 | 78.6558 | 78.663 | 22.1816 | 22.1836
390 | feeder2_line19 | 2 | 354.6 | 93.7047 | 93.6993 | 26.4255 | 26.4239
390 | feeder2_line19 | 3 | 354.6 | 93.9594 | 93.9579 | 26.4973 | 26.4969
390 | feeder2_line20 | 1 | 99 | 5.4572e-07 | 8.8232e-07 | 5.5124e-07 | 8.9123e-07
390 | feeder2_line20 | 2 | 99 | 5.4704e-07 | 8.8407e-07 | 5.5256e-07 | 8.93e-07
390 | feeder2_line20 | 3 | 99 | 0.086077 | 0.086062 | 0.086947 | 0.086932
390 | feeder2_line21 | 1 | 354.6 | 78.656 | 78.663 | 22.1816 | 22.1836
390 | feeder2_line21 | 2 | 354.6 | 93.7049 | 93.6993 | 26.4255 | 26.4239
390 | feeder2_line21 | 3 | 354.6 | 94.0362 | 94.0345 | 26.5189 | 26.5185
390 | feeder2_line22 | 1 | 99 | 5.7068e-07 | 1.0115e-06 | 5.7645e-07 | 1.0217e-06
390 | feeder2_line22 | 2 | 99 | 0.093985 | 0.093983 | 0.094934 | 0.094933
390 | feeder2_line22 | 3 | 99 | 5.7215e-07 | 1.0141e-06 | 5.7793e-07 | 1.0243e-06
390 | feeder2_line23 | 1 | 99 | 5.7068e-07 | 9.4686e-07 | 5.7644e-07 | 9.5642e-07
390 | feeder2_line23 | 2 | 99 | 5.7188e-07 | 9.4882e-07 | 5.7765e-07 | 9.584e-07
390 | feeder2_line23 | 3 | 99 | 0.84035 | 0.84036 | 0.84884 | 0.84885
390 | feeder2_line24 | 1 | 354.6 | 78.656 | 78.663 | 22.1816 | 22.1836
390 | feeder2_line24 | 2 | 354.6 | 93.7854 | 93.7798 | 26.4482 | 26.4466
390 | feeder2_line24 | 3 | 354.6 | 94.1998 | 94.1981 | 26.5651 | 26.5646
390 | feeder2_line25 | 1 | 99 | 0.094247 | 0.094249 | 0.095199 | 0.095201
390 | feeder2_line25 | 2 | 99 | 4.953e-08 | 6.8996e-07 | 5.003e-08 | 6.9693e-07
390 | feeder2_line25 | 3 | 99 | 4.9704e-08 | 6.9032e-07 | 5.0206e-08 | 6.973e-07
390 | feeder2_line26 | 1 | 99 | 0.22051 | 0.22051 | 0.22273 | 0.22274
390 | feeder2_line26 | 2 | 99 | 5.4724e-07 | 8.5482e-07 | 5.5276e-07 | 8.6346e-07
390 | feeder2_line26 | 3 | 99 | 5.4744e-07 | 8.5527e-07 | 5.5297e-07 | 8.6391e-07
390 | feeder2_line27 | 1 | 354.6 | 78.9097 | 78.9167 | 22.2532 | 22.2551
390 | feeder2_line27 | 2 | 354.6 | 93.7854 | 93.7798 | 26.4482 | 26.4466
390 | feeder2_line27 | 3 | 354.6 | 94.1998 | 94.1981 | 26.5651 | 26.5646
390 | feeder2_line28 | 1 | 99 | 2.5294e-06 | 7.0811e-07 | 2.555e-06 | 7.1526e-07
390 | feeder2_line28 | 2 | 99 | 0.76376 | 0.76374 | 0.77147 | 0.77145
390 | feeder2_line28 | 3 | 99 | 2.5396e-06 | 7.1025e-07 | 2.5652e-06 | 7.1743e-07
390 | feeder2_line29 | 1 | 354.6 | 78.9097 | 78.9167 | 22.2532 | 22.2551
390 | feeder2_line29 | 2 | 354.6 | 93.8894 | 93.8838 | 26.4776 | 26.476
390 | feeder2_line29 | 3 | 354.6 | 94.1998 | 94.1981 | 26.5651 | 26.5646
390 | feeder2_line30 | 1 | 266.4 | 20.6872 | 20.6869 | 7.7655 | 7.7654
390 | feeder2_line30 | 2 | 266.4 | 1.5497 | 1.5499 | 0.58174 | 0.5818
390 | feeder2_line30 | 3 | 266.4 | 1.7598 | 1.7599 | 0.66058 | 0.66063
390 | feeder2_line31 | 1 | 354.6 | 95.4865 | 95.4929 | 26.9279 | 26.9298
390 | feeder2_line31 | 2 | 354.6 | 94.0953 | 94.0891 | 26.5356 | 26.5339
390 | feeder2_line31 | 3 | 354.6 | 94.7592 | 94.7569 | 26.7228 | 26.7222
390 | feeder2_line32 | 1 | 354.6 | 95.4865 | 95.4929 | 26.9279 | 26.9298
390 | feeder2_line32 | 2 | 354.6 | 94.3136 | 94.3074 | 26.5972 | 26.5954
390 | feeder2_line32 | 3 | 354.6 | 94.7592 | 94.7569 | 26.7228 | 26.7222
390 | feeder2_line33 | 1 | 99 | 4.9989e-08 | 6.8348e-07 | 5.0494e-08 | 6.9038e-07
390 | feeder2_line33 | 2 | 99 | 0.25761 | 0.25761 | 0.26021 | 0.26021
390 | feeder2_line33 | 3 | 99 | 4.9746e-08 | 6.8581e-07 | 5.0248e-08 | 6.9274e-07
390 | feeder2_line34 | 1 | 354.6 | 95.4865 | 95.4929 | 26.9279 | 26.9298
390 | feeder2_line34 | 2 | 354.6 | 94.3136 | 94.3074 | 26.5972 | 26.5954
390 | feeder2_line34 | 3 | 354.6 | 94.9979 | 94.9957 | 26.7902 | 26.7895
390 | feeder2_line35 | 1 | 99 | 2.9808e-07 | 7.5698e-07 | 3.0109e-07 | 7.6463e-07
390 | feeder2_line35 | 2 | 99 | 2.9876e-07 | 7.5902e-07 | 3.0177e-07 | 7.6669e-07
390 | feeder2_line35 | 3 | 99 | 0.27527 | 0.27527 | 0.27805 | 0.27805
390 | feeder2_line36 | 1 | 354.6 | 95.6219 | 95.6286 | 26.9661 | 26.968
390 | feeder2_line36 | 2 | 354.6 | 94.3136 | 94.3074 | 26.5972 | 26.5954
390 | feeder2_line36 | 3 | 354.6 | 94.9979 | 94.9957 | 26.7902 | 26.7895
390 | feeder2_line37 | 1 | 99 | 1.2315 | 1.2314 | 1.2439 | 1.2439
390 | feeder2_line37 | 2 | 99 | 2.9879e-07 | 8.3994e-07 | 3.0181e-07 | 8.4842e-07
390 | feeder2_line37 | 3 | 99 | 2.9904e-07 | 8.4054e-07 | 3.0206e-07 | 8.4903e-07
390 | feeder2_line38 | 1 | 99 | 3.229e-07 | 7.7247e-07 | 3.2616e-07 | 7.8027e-07
390 | feeder2_line38 | 2 | 99 | 0.077286 | 0.077282 | 0.078067 | 0.078063
390 | feeder2_line38 | 3 | 99 | 3.2374e-07 | 7.7526e-07 | 3.2701e-07 | 7.8309e-07
390 | feeder2_line39 | 1 | 266.4 | 20.6872 | 20.6869 | 7.7655 | 7.7654
390 | feeder2_line39 | 2 | 266.4 | 1.5053 | 1.5055 | 0.56507 | 0.56514
390 | feeder2_line39 | 3 | 266.4 | 1.7598 | 1.7599 | 0.66059 | 0.66063
390 | feeder2_line40 | 1 | 354.6 | 95.707 | 95.7137 | 26.9901 | 26.992
390 | feeder2_line40 | 2 | 354.6 | 94.3136 | 94.3074 | 26.5972 | 26.5954
390 | feeder2_line40 | 3 | 354.6 | 94.9979 | 94.9957 | 26.7902 | 26.7895
390 | feeder2_line41 | 1 | 99 | 0.094178 | 0.094181 | 0.095129 | 0.095133
390 | feeder2_line41 | 2 | 99 | 4.9575e-08 | 7.34e-07 | 5.0076e-08 | 7.4141e-07
390 | feeder2_line41 | 3 | 99 | 4.9767e-08 | 7.3454e-07 | 5.027e-08 | 7.4196e-07
390 | feeder2_line42 | 1 | 99 | 2.9784e-07 | 7.4544e-07 | 3.0085e-07 | 7.5297e-07
390 | feeder2_line42 | 2 | 99 | 2.9865e-07 | 7.4784e-07 | 3.0167e-07 | 7.5539e-07
390 | feeder2_line42 | 3 | 99 | 0.18992 | 0.18992 | 0.19184 | 0.19184
390 | feeder2_line43 | 1 | 266.4 | 20.6872 | 20.6869 | 7.7654 | 7.7654
390 | feeder2_line43 | 2 | 266.4 | 1.5054 | 1.5055 | 0.5651 | 0.56514
390 | feeder2_line43 | 3 | 266.4 | 1.6246 | 1.6247 | 0.60983 | 0.60986
390 | feeder2_line44 | 1 | 354.6 | 95.707 | 95.7137 | 26.9901 | 26.992
390 | feeder2_line44 | 2 | 354.6 | 94.3137 | 94.3074 | 26.5972 | 26.5954
390 | feeder2_line44 | 3 | 354.6 | 95.0757 | 95.0733 | 26.8121 | 26.8114
390 | feeder2_line45 | 1 | 99 | 5.0002e-08 | 5.774e-07 | 5.0507e-08 | 5.8323e-07
390 | feeder2_line45 | 2 | 99 | 4.9579e-08 | 5.7889e-07 | 5.008e-08 | 5.8474e-07
390 | feeder2_line45 | 3 | 99 | 0.085921 | 0.085896 | 0.086789 | 0.086764
390 | feeder2_line46 | 1 | 99 | 5.7068e-07 | 1.3513e-06 | 5.7644e-07 | 1.365e-06
390 | feeder2_line46 | 2 | 99 | 5.7254e-07 | 1.3557e-06 | 5.7833e-07 | 1.3694e-06
390 | feeder2_line46 | 3 | 99 | 1.5275 | 1.5275 | 1.5429 | 1.5429
390 | feeder2_line47 | 1 | 266.4 | 20.6872 | 20.6869 | 7.7655 | 7.7654
390 | feeder2_line47 | 2 | 266.4 | 1.5056 | 1.5055 | 0.56517 | 0.56514
390 | feeder2_line47 | 3 | 266.4 | 0.17015 | 0.16988 | 0.06387 | 0.063769
390 | feeder2_line48 | 1 | 99 | 1.1978 | 1.1978 | 1.2099 | 1.2099
390 | feeder2_line48 | 2 | 99 | 4.9504e-08 | 7.2994e-07 | 5.0004e-08 | 7.3731e-07
390 | feeder2_line48 | 3 | 99 | 4.9713e-08 | 7.3042e-07 | 5.0215e-08 | 7.378e-07
390 | feeder2_line49 | 1 | 266.4 | 19.8749 | 19.8747 | 7.4605 | 7.4605
390 | feeder2_line49 | 2 | 266.4 | 1.5056 | 1.5055 | 0.56516 | 0.56514
390 | feeder2_line49 | 3 | 266.4 | 0.17013 | 0.16988 | 0.063863 | 0.063769
390 | feeder2_line50 | 1 | 99 | 5.7057e-07 | 1.2296e-06 | 5.7633e-07 | 1.242e-06
390 | feeder2_line50 | 2 | 99 | 0.08523 | 0.085217 | 0.086091 | 0.086078
390 | feeder2_line50 | 3 | 99 | 5.7293e-07 | 1.2346e-06 | 5.7872e-07 | 1.2471e-06
390 | feeder2_line51 | 1 | 99 | 19.0403 | 19.0403 | 19.2326 | 19.2326
390 | feeder2_line51 | 2 | 99 | 5.7251e-07 | 1.3394e-06 | 5.783e-07 | 1.3529e-06
390 | feeder2_line51 | 3 | 99 | 5.729e-07 | 1.3403e-06 | 5.7868e-07 | 1.3538e-06
390 | feeder2_line52 | 1 | 266.4 | 0.83452 | 0.83443 | 0.31326 | 0.31323
390 | feeder2_line52 | 2 | 266.4 | 1.4587 | 1.4587 | 0.54755 | 0.54756
390 | feeder2_line52 | 3 | 266.4 | 0.16999 | 0.16988 | 0.063812 | 0.063769
390 | feeder2_line53 | 1 | 99 | 5.4556e-07 | 7.5044e-07 | 5.5107e-07 | 7.5802e-07
390 | feeder2_line53 | 2 | 99 | 1.4587 | 1.4587 | 1.4735 | 1.4734
390 | feeder2_line53 | 3 | 99 | 5.4808e-07 | 7.5352e-07 | 5.5361e-07 | 7.6113e-07
390 | feeder2_line54 | 1 | 266.4 | 0.83435 | 0.83443 | 0.31319 | 0.31323
390 | feeder2_line54 | 2 | 266.4 | 8.5388e-05 | 4.6191e-06 | 3.2053e-05 | 1.7339e-06
390 | feeder2_line54 | 3 | 266.4 | 0.1698 | 0.16988 | 0.06374 | 0.063769
390 | feeder2_line55 | 1 | 99 | 0.18077 | 0.18077 | 0.1826 | 0.1826
390 | feeder2_line55 | 2 | 99 | 4.9603e-08 | 7.2954e-07 | 5.0104e-08 | 7.3691e-07
390 | feeder2_line55 | 3 | 99 | 4.9797e-08 | 7.3012e-07 | 5.03e-08 | 7.3749e-07
390 | feeder2_line56 | 1 | 354.6 | 95.8657 | 95.8723 | 27.0349 | 27.0367
390 | feeder2_line56 | 2 | 354.6 | 94.3137 | 94.3074 | 26.5972 | 26.5954
390 | feeder2_line56 | 3 | 354.6 | 95.0757 | 95.0733 | 26.8121 | 26.8114
390 | feeder2_line57 | 1 | 99 | 7.5023e-07 | 1.5371e-06 | 7.5781e-07 | 1.5527e-06
390 | feeder2_line57 | 2 | 99 | 7.4242e-07 | 1.5424e-06 | 7.4992e-07 | 1.558e-06
390 | feeder2_line57 | 3 | 99 | 0.16988 | 0.16988 | 0.17159 | 0.1716
390 | feeder2_line58 | 1 | 266.4 | 0.83441 | 0.83443 | 0.31322 | 0.31323
390 | feeder2_line58 | 2 | 266.4 | 1.8924e-05 | 2.6817e-06 | 7.1037e-06 | 1.0066e-06
390 | feeder2_line58 | 3 | 266.4 | 1.8946e-05 | 2.6836e-06 | 7.112e-06 | 1.0074e-06
390 | feeder2_line59 | 1 | 99 | 5.0015e-08 | 5.3431e-07 | 5.052e-08 | 5.3971e-07
390 | feeder2_line59 | 2 | 99 | 4.9494e-08 | 5.3615e-07 | 4.9994e-08 | 5.4157e-07
390 | feeder2_line59 | 3 | 99 | 0.10829 | 0.10829 | 0.10938 | 0.10938
390 | feeder2_line60 | 1 | 99 | 2.9778e-07 | 8.0752e-07 | 3.0079e-07 | 8.1567e-07
390 | feeder2_line60 | 2 | 99 | 2.9865e-07 | 8.103e-07 | 3.0167e-07 | 8.1848e-07
390 | feeder2_line60 | 3 | 99 | 0.061729 | 0.061729 | 0.062352 | 0.062352
390 | feeder2_line61 | 1 | 266.4 | 1.4733 | 1.4734 | 0.55304 | 0.5531
390 | feeder2_line61 | 2 | 266.4 | 0.63862 | 0.63877 | 0.23972 | 0.23978
390 | feeder2_line61 | 3 | 266.4 | 0.38497 | 0.38512 | 0.14451 | 0.14457
390 | feeder2_line62 | 1 | 354.6 | 96.0996 | 96.1064 | 27.1008 | 27.1028
390 | feeder2_line62 | 2 | 354.6 | 94.8594 | 94.8533 | 26.7511 | 26.7494
390 | feeder2_line62 | 3 | 354.6 | 95.4151 | 95.4129 | 26.9078 | 26.9072
390 | feeder2_line63 | 1 | 99 | 0.53954 | 0.53954 | 0.54499 | 0.54499
390 | feeder2_line63 | 2 | 99 | 5.7256e-07 | 1.2183e-06 | 5.7834e-07 | 1.2306e-06
390 | feeder2_line63 | 3 | 99 | 5.7293e-07 | 1.2191e-06 | 5.7872e-07 | 1.2314e-06
390 | feeder2_line64 | 1 | 99 | 0.29489 | 0.2949 | 0.29787 | 0.29788
390 | feeder2_line64 | 2 | 99 | 1.1882e-11 | 3.2091e-07 | 1.2002e-11 | 3.2415e-07
390 | feeder2_line64 | 3 | 99 | 6.4235e-13 | 3.2113e-07 | 6.4884e-13 | 3.2437e-07
390 | feeder2_line65 | 1 | 99 | 5.0024e-08 | 6.3964e-07 | 5.0529e-08 | 6.461e-07
390 | feeder2_line65 | 2 | 99 | 0.27939 | 0.27938 | 0.28221 | 0.28221
390 | feeder2_line65 | 3 | 99 | 4.9838e-08 | 6.416e-07 | 5.0342e-08 | 6.4808e-07
390 | feeder2_line66 | 1 | 354.6 | 96.0995 | 96.1064 | 27.1008 | 27.1028
390 | feeder2_line66 | 2 | 354.6 | 95.0975 | 95.0914 | 26.8182 | 26.8165
390 | feeder2_line66 | 3 | 354.6 | 95.4151 | 95.4129 | 26.9078 | 26.9072
390 | feeder2_line67 | 1 | 99 | 2.5012e-08 | 3.6147e-07 | 2.5265e-08 | 3.6512e-07
390 | feeder2_line67 | 2 | 99 | 2.4811e-08 | 3.6232e-07 | 2.5062e-08 | 3.6598e-07
390 | feeder2_line67 | 3 | 99 | 0.093771 | 0.093772 | 0.094719 | 0.094719
390 | feeder2_line68 | 1 | 266.4 | 1.4733 | 1.4734 | 0.55305 | 0.5531
390 | feeder2_line68 | 2 | 266.4 | 0.63866 | 0.63877 | 0.23974 | 0.23978
390 | feeder2_line68 | 3 | 266.4 | 0.2913 | 0.29142 | 0.10935 | 0.10939
390 | feeder2_line69 | 1 | 99 | 0.21404 | 0.21408 | 0.2162 | 0.21625
390 | feeder2_line69 | 2 | 99 | 2.5446e-06 | 6.6559e-07 | 2.5703e-06 | 6.7232e-07
390 | feeder2_line69 | 3 | 99 | 2.5456e-06 | 6.6614e-07 | 2.5714e-06 | 6.7287e-07
390 | feeder2_line70 | 1 | 354.6 | 96.2907 | 96.2976 | 27.1547 | 27.1567
390 | feeder2_line70 | 2 | 354.6 | 95.0975 | 95.0914 | 26.8182 | 26.8165
390 | feeder2_line70 | 3 | 354.6 | 95.415 | 95.4129 | 26.9078 | 26.9072
390 | feeder2_line71 | 1 | 99 | 5.0025e-08 | 7.1379e-07 | 5.053e-08 | 7.21e-07
390 | feeder2_line71 | 2 | 99 | 2.6352 | 2.6351 | 2.6618 | 2.6617
390 | feeder2_line71 | 3 | 99 | 4.9857e-08 | 7.1593e-07 | 5.0361e-08 | 7.2316e-07
390 | feeder2_line72 | 1 | 354.6 | 96.2908 | 96.2976 | 27.1548 | 27.1567
390 | feeder2_line72 | 2 | 354.6 | 95.4876 | 95.4814 | 26.9283 | 26.9265
390 | feeder2_line72 | 3 | 354.6 | 95.4151 | 95.4129 | 26.9078 | 26.9072
390 | feeder2_line73 | 1 | 99 | 5.9686e-07 | 1.5303e-06 | 6.0289e-07 | 1.5458e-06
390 | feeder2_line73 | 2 | 99 | 0.25764 | 0.25763 | 0.26024 | 0.26024
390 | feeder2_line73 | 3 | 99 | 5.9859e-07 | 1.5352e-06 | 6.0464e-07 | 1.5507e-06
390 | feeder2_line74 | 1 | 99 | 5.0021e-08 | 4.5643e-07 | 5.0527e-08 | 4.6104e-07
390 | feeder2_line74 | 2 | 99 | 0.29142 | 0.29141 | 0.29437 | 0.29435
390 | feeder2_line74 | 3 | 99 | 4.9814e-08 | 4.5788e-07 | 5.0317e-08 | 4.6251e-07
390 | feeder2_line75 | 1 | 266.4 | 1.4734 | 1.4734 | 0.55308 | 0.5531
390 | feeder2_line75 | 2 | 266.4 | 0.089805 | 0.089834 | 0.03371 | 0.033722
390 | feeder2_line75 | 3 | 266.4 | 0.2914 | 0.29142 | 0.10938 | 0.10939
390 | feeder2_line76 | 1 | 99 | 1.4734 | 1.4735 | 1.4883 | 1.4883
390 | feeder2_line76 | 2 | 99 | 8.4743e-07 | 1.5823e-06 | 8.5599e-07 | 1.5983e-06
390 | feeder2_line76 | 3 | 99 | 8.4807e-07 | 1.5836e-06 | 8.5664e-07 | 1.5996e-06
390 | feeder2_line77 | 1 | 99 | 2.5009e-08 | 5.7357e-07 | 2.5261e-08 | 5.7937e-07
390 | feeder2_line77 | 2 | 99 | 2.4817e-08 | 5.7494e-07 | 2.5067e-08 | 5.8075e-07
390 | feeder2_line77 | 3 | 99 | 0.29143 | 0.29142 | 0.29438 | 0.29436
390 | feeder2_line78 | 1 | 266.4 | 3.4776e-12 | 9.5145e-07 | 1.3054e-12 | 3.5715e-07
390 | feeder2_line78 | 2 | 266.4 | 0.089837 | 0.089834 | 0.033723 | 0.033722
390 | feeder2_line78 | 3 | 266.4 | 1.0493e-11 | 9.5425e-07 | 3.9389e-12 | 3.582e-07
390 | feeder2_line79 | 1 | 354.6 | 0.37335 | 0.37299 | 0.10529 | 0.10519
390 | feeder2_line79 | 2 | 354.6 | 3.0509 | 3.0506 | 0.86037 | 0.8603
390 | feeder2_line79 | 3 | 354.6 | 2.9849 | 2.9845 | 0.84176 | 0.84166
390 | feeder2_line80 | 1 | 354.6 | 96.633 | 96.6394 | 27.2513 | 27.2531
390 | feeder2_line80 | 2 | 354.6 | 96.3717 | 96.3648 | 27.1776 | 27.1756
390 | feeder2_line80 | 3 | 354.6 | 97.0278 | 97.0251 | 27.3626 | 27.3618
390 | feeder2_line81 | 1 | 354.6 | 96.6329 | 96.6394 | 27.2512 | 27.2531
390 | feeder2_line81 | 2 | 354.6 | 96.3716 | 96.3648 | 27.1776 | 27.1756
390 | feeder2_line81 | 3 | 354.6 | 97.3657 | 97.3631 | 27.4579 | 27.4572
390 | feeder2_line82 | 1 | 354.6 | 7.5833e-12 | 7.3242e-07 | 2.1385e-12 | 2.0655e-07
390 | feeder2_line82 | 2 | 354.6 | 5.6896e-11 | 7.3375e-07 | 1.6045e-11 | 2.0692e-07
390 | feeder2_line82 | 3 | 354.6 | 1.1601 | 1.16 | 0.32715 | 0.32714
390 | feeder2_line83 | 1 | 354.6 | 96.6331 | 96.6394 | 27.2513 | 27.2531
390 | feeder2_line83 | 2 | 354.6 | 96.7147 | 96.7077 | 27.2743 | 27.2723
390 | feeder2_line83 | 3 | 354.6 | 97.3659 | 97.3631 | 27.4579 | 27.4572
390 | feeder2_line84 | 1 | 354.6 | 1.2833e-11 | 1.2946e-06 | 3.619e-12 | 3.6508e-07
390 | feeder2_line84 | 2 | 354.6 | 2.271 | 2.2709 | 0.64044 | 0.64042
390 | feeder2_line84 | 3 | 354.6 | 3.2026e-12 | 1.2981e-06 | 9.0316e-13 | 3.6608e-07
390 | feeder2_line85 | 1 | 99 | 0.077375 | 0.077381 | 0.078156 | 0.078163
390 | feeder2_line85 | 2 | 99 | 4.9688e-08 | 4.6297e-07 | 5.019e-08 | 4.6764e-07
390 | feeder2_line85 | 3 | 99 | 4.9897e-08 | 4.6336e-07 | 5.0401e-08 | 4.6804e-07
390 | feeder2_line86 | 1 | 354.6 | 96.7045 | 96.7108 | 27.2714 | 27.2732
390 | feeder2_line86 | 2 | 354.6 | 96.7148 | 96.7077 | 27.2743 | 27.2723
390 | feeder2_line86 | 3 | 354.6 | 97.3659 | 97.3631 | 27.458 | 27.4572
390 | feeder2_line87 | 1 | 354.6 | 96.7047 | 96.7108 | 27.2715 | 27.2732
390 | feeder2_line87 | 2 | 354.6 | 96.8216 | 96.8144 | 27.3045 | 27.3024
390 | feeder2_line87 | 3 | 354.6 | 97.9063 | 97.9033 | 27.6104 | 27.6095
390 | feeder2_line88 | 1 | 354.6 | 0.00011324 | 3.3556e-06 | 3.1934e-05 | 9.463e-07
390 | feeder2_line88 | 2 | 354.6 | 0.11338 | 0.11323 | 0.031973 | 0.031931
390 | feeder2_line88 | 3 | 354.6 | 2.4481 | 2.4481 | 0.69038 | 0.69037
390 | feeder2_line89 | 1 | 354.6 | 96.7025 | 96.7108 | 27.2709 | 27.2732
390 | feeder2_line89 | 2 | 354.6 | 97.3935 | 97.3884 | 27.4657 | 27.4643
390 | feeder2_line89 | 3 | 354.6 | 97.9041 | 97.9033 | 27.6097 | 27.6095
390 | feeder2_line90 | 1 | 354.6 | 0.00072145 | 2.0252e-06 | 0.00020345 | 5.7111e-07
390 | feeder2_line90 | 2 | 354.6 | 2.3896 | 2.3895 | 0.67388 | 0.67384
390 | feeder2_line90 | 3 | 354.6 | 0.00072422 | 2.0312e-06 | 0.00020424 | 5.7281e-07
390 | feeder2_line91 | 1 | 354.6 | 96.7025 | 96.7108 | 27.2709 | 27.2732
390 | feeder2_line91 | 2 | 354.6 | 97.3935 | 97.3884 | 27.4657 | 27.4643
390 | feeder2_line91 | 3 | 354.6 | 97.9613 | 97.9605 | 27.6259 | 27.6256
390 | feeder2_line92 | 1 | 354.6 | 1.5177e-11 | 1.0219e-06 | 4.2801e-12 | 2.8819e-07
390 | feeder2_line92 | 2 | 354.6 | 2.8527e-11 | 1.0238e-06 | 8.0449e-12 | 2.8871e-07
390 | feeder2_line92 | 3 | 354.6 | 0.061601 | 0.061601 | 0.017372 | 0.017372
390 | feeder2_line93 | 1 | 99 | 2.5038e-08 | 3.4107e-07 | 2.5291e-08 | 3.4452e-07
390 | feeder2_line93 | 2 | 99 | 2.2714 | 2.2713 | 2.2943 | 2.2943
390 | feeder2_line93 | 3 | 99 | 2.4958e-08 | 3.4206e-07 | 2.521e-08 | 3.4552e-07
390 | feeder2_line94 | 1 | 354.6 | 2.5041e-06 | 1.6607e-06 | 7.0619e-07 | 4.6834e-07
390 | feeder2_line94 | 2 | 354.6 | 0.1946 | 0.19458 | 0.054879 | 0.054874
390 | feeder2_line94 | 3 | 354.6 | 2.4959e-06 | 1.6653e-06 | 7.0385e-07 | 4.6964e-07
390 | feeder2_line95 | 1 | 99 | 3.5555e-06 | 2.602e-06 | 3.5914e-06 | 2.6283e-06
390 | feeder2_line95 | 2 | 99 | 0.11327 | 0.11323 | 0.11441 | 0.11437
390 | feeder2_line95 | 3 | 99 | 3.5695e-06 | 2.6096e-06 | 3.6056e-06 | 2.6359e-06
390 | feeder2_line96 | 1 | 354.6 | 0.00012073 | 6.2022e-07 | 3.4048e-05 | 1.7491e-07
390 | feeder2_line96 | 2 | 354.6 | 0.00012104 | 6.2174e-07 | 3.4133e-05 | 1.7534e-07
390 | feeder2_line96 | 3 | 354.6 | 2.4481 | 2.4481 | 0.69037 | 0.69037
390 | feeder2_line97 | 1 | 354.6 | 96.8509 | 96.8589 | 27.3127 | 27.315
390 | feeder2_line97 | 2 | 354.6 | 97.3938 | 97.3884 | 27.4658 | 27.4643
390 | feeder2_line97 | 3 | 354.6 | 97.9616 | 97.9605 | 27.6259 | 27.6256
390 | feeder2_line98 | 1 | 354.6 | 0.1571 | 0.15545 | 0.044303 | 0.043838
390 | feeder2_line98 | 2 | 354.6 | 0.0017048 | 6.2283e-07 | 0.00048078 | 1.7564e-07
390 | feeder2_line98 | 3 | 354.6 | 0.0016999 | 6.2222e-07 | 0.00047939 | 1.7547e-07
390 | feeder2_line99 | 1 | 99 | 2.5032e-08 | 4.459e-07 | 2.5285e-08 | 4.504e-07
390 | feeder2_line99 | 2 | 99 | 2.4851e-08 | 4.4682e-07 | 2.5102e-08 | 4.5134e-07
390 | feeder2_line99 | 3 | 99 | 2.4481 | 2.4481 | 2.4728 | 2.4728
390 | feeder2_line100 | 1 | 99 | 0.1554 | 0.15545 | 0.15697 | 0.15702
390 | feeder2_line100 | 2 | 99 | 2.4869e-08 | 6.1356e-07 | 2.512e-08 | 6.1976e-07
390 | feeder2_line100 | 3 | 99 | 2.4963e-08 | 6.1411e-07 | 2.5215e-08 | 6.2031e-07
390 | feeder2_line101 | 1 | 354.6 | 0.19502 | 0.19464 | 0.054996 | 0.054889
390 | feeder2_line101 | 2 | 354.6 | 3.0509 | 3.0506 | 0.86037 | 0.8603
390 | feeder2_line101 | 3 | 354.6 | 2.9849 | 2.9845 | 0.84175 | 0.84166
390 | feeder2_line102 | 1 | 99 | 0.1787 | 0.17874 | 0.18051 | 0.18054
390 | feeder2_line102 | 2 | 99 | 2.3364e-06 | 8.7736e-07 | 2.36e-06 | 8.8622e-07
390 | feeder2_line102 | 3 | 99 | 2.3338e-06 | 8.7805e-07 | 2.3573e-06 | 8.8692e-07
390 | feeder2_line103 | 1 | 99 | 5.475e-07 | 8.0141e-07 | 5.5303e-07 | 8.0951e-07
390 | feeder2_line103 | 2 | 99 | 0.096581 | 0.096578 | 0.097557 | 0.097553
390 | feeder2_line103 | 3 | 99 | 5.492e-07 | 8.0367e-07 | 5.5475e-07 | 8.1179e-07
390 | feeder2_line104 | 1 | 354.6 | 0.19491 | 0.19464 | 0.054967 | 0.054889
390 | feeder2_line104 | 2 | 354.6 | 2.9922 | 2.992 | 0.84382 | 0.84377
390 | feeder2_line104 | 3 | 354.6 | 2.9848 | 2.9845 | 0.84174 | 0.84166
390 | feeder2_line105 | 1 | 99 | 2.5374e-06 | 7.3741e-07 | 2.563e-06 | 7.4486e-07
390 | feeder2_line105 | 2 | 99 | 2.5456e-06 | 7.389e-07 | 2.5713e-06 | 7.4636e-07
390 | feeder2_line105 | 3 | 99 | 1.4151 | 1.4151 | 1.4294 | 1.4294
390 | feeder2_line106 | 1 | 354.6 | 0.19486 | 0.19464 | 0.054952 | 0.054889
390 | feeder2_line106 | 2 | 354.6 | 2.9922 | 2.992 | 0.84382 | 0.84377
390 | feeder2_line106 | 3 | 354.6 | 1.6153 | 1.6151 | 0.45553 | 0.45546
390 | feeder2_line107 | 1 | 99 | 3.2379e-07 | 8.9865e-07 | 3.2706e-07 | 9.0773e-07
390 | feeder2_line107 | 2 | 99 | 0.1163 | 0.11628 | 0.11748 | 0.11745
390 | feeder2_line107 | 3 | 99 | 3.2448e-07 | 9.0114e-07 | 3.2775e-07 | 9.1024e-07
390 | feeder2_line108 | 1 | 354.6 | 0.19485 | 0.19464 | 0.054949 | 0.054889
390 | feeder2_line108 | 2 | 354.6 | 2.9232 | 2.923 | 0.82436 | 0.82432
390 | feeder2_line108 | 3 | 354.6 | 1.6153 | 1.6151 | 0.45553 | 0.45546
390 | feeder2_line109 | 1 | 354.6 | 97.0748 | 97.0818 | 27.3759 | 27.3778
390 | feeder2_line109 | 2 | 354.6 | 97.3948 | 97.3884 | 27.4661 | 27.4643
390 | feeder2_line109 | 3 | 354.6 | 97.9626 | 97.9605 | 27.6262 | 27.6256
390 | feeder2_line110 | 1 | 99 | 0.23788 | 0.2371 | 0.24029 | 0.23949
390 | feeder2_line110 | 2 | 99 | 0.00080426 | 9.0781e-07 | 0.00081238 | 9.1698e-07
390 | feeder2_line110 | 3 | 99 | 0.00080459 | 9.0899e-07 | 0.00081271 | 9.1817e-07
390 | feeder2_line111 | 1 | 99 | 2.503e-08 | 3.8084e-07 | 2.5282e-08 | 3.8469e-07
390 | feeder2_line111 | 2 | 99 | 0.072665 | 0.072653 | 0.073399 | 0.073387
390 | feeder2_line111 | 3 | 99 | 2.4952e-08 | 3.8194e-07 | 2.5204e-08 | 3.858e-07
390 | feeder2_line112 | 1 | 99 | 3.2396e-07 | 9.1518e-07 | 3.2723e-07 | 9.2442e-07
390 | feeder2_line112 | 2 | 99 | 0.040816 | 0.040786 | 0.041229 | 0.041198
390 | feeder2_line112 | 3 | 99 | 3.2467e-07 | 9.1783e-07 | 3.2795e-07 | 9.271e-07
390 | feeder2_line113 | 1 | 99 | 0.12887 | 0.12887 | 0.13017 | 0.13018
390 | feeder2_line113 | 2 | 99 | 3.2451e-07 | 9.0483e-07 | 3.2779e-07 | 9.1397e-07
390 | feeder2_line113 | 3 | 99 | 3.2492e-07 | 9.0565e-07 | 3.282e-07 | 9.148e-07
390 | feeder2_line114 | 1 | 99 | 0.096773 | 0.096777 | 0.097751 | 0.097754
390 | feeder2_line114 | 2 | 99 | 2.4839e-08 | 4.3628e-07 | 2.509e-08 | 4.4068e-07
390 | feeder2_line114 | 3 | 99 | 2.4942e-08 | 4.3662e-07 | 2.5194e-08 | 4.4103e-07
390 | feeder2_line115 | 1 | 99 | 2.5009e-08 | 5.6081e-07 | 2.5261e-08 | 5.6647e-07
390 | feeder2_line115 | 2 | 99 | 0.33197 | 0.33197 | 0.33532 | 0.33532
390 | feeder2_line115 | 3 | 99 | 2.4943e-08 | 5.6234e-07 | 2.5195e-08 | 5.6802e-07
390 | feeder2_line116 | 1 | 354.6 | 0.19486 | 0.19464 | 0.054951 | 0.054889
390 | feeder2_line116 | 2 | 354.6 | 2.707 | 2.7069 | 0.7634 | 0.76337
390 | feeder2_line116 | 3 | 354.6 | 1.6153 | 1.6151 | 0.45553 | 0.45546
390 | feeder2_line117 | 1 | 99 | 5.0127e-08 | 6.4113e-07 | 5.0633e-08 | 6.476e-07
390 | feeder2_line117 | 2 | 99 | 1.5291 | 1.529 | 1.5445 | 1.5445
390 | feeder2_line117 | 3 | 99 | 4.995e-08 | 6.4307e-07 | 5.0455e-08 | 6.4956e-07
390 | feeder2_line118 | 1 | 354.6 | 97.0748 | 97.0818 | 27.3759 | 27.3778
390 | feeder2_line118 | 2 | 354.6 | 97.7562 | 97.7496 | 27.568 | 27.5662
390 | feeder2_line118 | 3 | 354.6 | 97.9626 | 97.9605 | 27.6262 | 27.6256
390 | feeder2_line119 | 1 | 99 | 2.5014e-08 | 6.0346e-07 | 2.5266e-08 | 6.0956e-07
390 | feeder2_line119 | 2 | 99 | 2.4838e-08 | 6.0462e-07 | 2.5089e-08 | 6.1072e-07
390 | feeder2_line119 | 3 | 99 | 0.54549 | 0.54548 | 0.551 | 0.55099
390 | feeder2_line120 | 1 | 354.6 | 0.19486 | 0.19464 | 0.054951 | 0.054889
390 | feeder2_line120 | 2 | 354.6 | 2.707 | 2.7069 | 0.7634 | 0.76337
390 | feeder2_line120 | 3 | 354.6 | 1.1142 | 1.114 | 0.31423 | 0.31416
390 | feeder2_line121 | 1 | 99 | 3.2379e-07 | 9.345e-07 | 3.2706e-07 | 9.4394e-07
390 | feeder2_line121 | 2 | 99 | 0.044095 | 0.044093 | 0.04454 | 0.044538
390 | feeder2_line121 | 3 | 99 | 3.2446e-07 | 9.3698e-07 | 3.2774e-07 | 9.4644e-07
390 | feeder2_line122 | 1 | 354.6 | 0.19484 | 0.19464 | 0.054948 | 0.054889
390 | feeder2_line122 | 2 | 354.6 | 2.6805 | 2.6804 | 0.75591 | 0.75589
390 | feeder2_line122 | 3 | 354.6 | 1.1142 | 1.114 | 0.31422 | 0.31416
390 | feeder2_line123 | 1 | 99 | 5.7256e-07 | 9.6837e-07 | 5.7834e-07 | 9.7815e-07
390 | feeder2_line123 | 2 | 99 | 5.7363e-07 | 9.7015e-07 | 5.7942e-07 | 9.7995e-07
390 | feeder2_line123 | 3 | 99 | 0.7641 | 0.76408 | 0.77182 | 0.7718
390 | feeder2_line124 | 1 | 354.6 | 0.19475 | 0.19464 | 0.054922 | 0.054889
390 | feeder2_line124 | 2 | 354.6 | 2.6805 | 2.6804 | 0.75593 | 0.75589
390 | feeder2_line124 | 3 | 354.6 | 0.47073 | 0.47056 | 0.13275 | 0.1327
390 | feeder2_line125 | 1 | 99 | 5.7255e-07 | 9.002e-07 | 5.7834e-07 | 9.0929e-07
390 | feeder2_line125 | 2 | 99 | 5.7363e-07 | 9.0185e-07 | 5.7942e-07 | 9.1096e-07
390 | feeder2_line125 | 3 | 99 | 0.15514 | 0.15511 | 0.15671 | 0.15668
390 | feeder2_line126 | 1 | 354.6 | 0.19491 | 0.19464 | 0.054967 | 0.054889
390 | feeder2_line126 | 2 | 354.6 | 2.6806 | 2.6804 | 0.75596 | 0.75589
390 | feeder2_line126 | 3 | 354.6 | 0.31668 | 0.31638 | 0.089307 | 0.089221
390 | feeder2_line127 | 1 | 99 | 5.7257e-07 | 1.0777e-06 | 5.7835e-07 | 1.0886e-06
390 | feeder2_line127 | 2 | 99 | 5.7362e-07 | 1.0796e-06 | 5.7941e-07 | 1.0905e-06
390 | feeder2_line127 | 3 | 99 | 0.077149 | 0.077148 | 0.077928 | 0.077927
390 | feeder2_line128 | 1 | 354.6 | 0.19483 | 0.19464 | 0.054943 | 0.054889
390 | feeder2_line128 | 2 | 354.6 | 2.6806 | 2.6804 | 0.75596 | 0.75589
390 | feeder2_line128 | 3 | 354.6 | 0.23957 | 0.23934 | 0.067559 | 0.067496
390 | feeder2_line129 | 1 | 99 | 5.4755e-07 | 8.7385e-07 | 5.5308e-07 | 8.8268e-07
390 | feeder2_line129 | 2 | 99 | 2.6804 | 2.6804 | 2.7074 | 2.7075
390 | feeder2_line129 | 3 | 99 | 5.4912e-07 | 8.7614e-07 | 5.5467e-07 | 8.8499e-07
390 | feeder2_line130 | 1 | 354.6 | 0.19484 | 0.19464 | 0.054948 | 0.054889
390 | feeder2_line130 | 2 | 354.6 | 0.00030785 | 4.6324e-06 | 8.6816e-05 | 1.3064e-06
390 | feeder2_line130 | 3 | 354.6 | 0.23958 | 0.23934 | 0.067564 | 0.067496
390 | feeder2_line131 | 1 | 99 | 5.7256e-07 | 9.6853e-07 | 5.7835e-07 | 9.7832e-07
390 | feeder2_line131 | 2 | 99 | 5.7361e-07 | 9.7027e-07 | 5.794e-07 | 9.8007e-07
390 | feeder2_line131 | 3 | 99 | 0.16241 | 0.16241 | 0.16405 | 0.16405
390 | feeder2_line132 | 1 | 354.6 | 0.19468 | 0.19464 | 0.054901 | 0.054889
390 | feeder2_line132 | 2 | 354.6 | 0.00012558 | 2.9124e-06 | 3.5415e-05 | 8.2133e-07
390 | feeder2_line132 | 3 | 354.6 | 0.077218 | 0.077148 | 0.021776 | 0.021756
390 | feeder2_line133 | 1 | 99 | 0.19461 | 0.19464 | 0.19657 | 0.1966
390 | feeder2_line133 | 2 | 99 | 2.9923e-07 | 9.7801e-07 | 3.0225e-07 | 9.8789e-07
390 | feeder2_line133 | 3 | 99 | 2.9951e-07 | 9.7881e-07 | 3.0253e-07 | 9.887e-07
390 | feeder2_line134 | 1 | 354.6 | 2.2312e-12 | 1.7806e-06 | 6.2923e-13 | 5.0213e-07
390 | feeder2_line134 | 2 | 354.6 | 7.3423e-12 | 1.7834e-06 | 2.0706e-12 | 5.0293e-07
390 | feeder2_line134 | 3 | 354.6 | 0.077149 | 0.077148 | 0.021757 | 0.021756
390 | feeder2_line135 | 1 | 99 | 2.634 | 2.6339 | 2.6606 | 2.6605
390 | feeder2_line135 | 2 | 99 | 4.9784e-08 | 5.8557e-07 | 5.0287e-08 | 5.9148e-07
390 | feeder2_line135 | 3 | 99 | 4.9961e-08 | 5.8612e-07 | 5.0465e-08 | 5.9204e-07
390 | feeder2_line136 | 1 | 354.6 | 97.694 | 97.7011 | 27.5505 | 27.5525
390 | feeder2_line136 | 2 | 354.6 | 97.7562 | 97.7496 | 27.568 | 27.5662
390 | feeder2_line136 | 3 | 354.6 | 97.9626 | 97.9605 | 27.6262 | 27.6256
390 | feeder2_line137 | 1 | 99 | 1.9774 | 1.9774 | 1.9974 | 1.9974
390 | feeder2_line137 | 2 | 99 | 8.499e-07 | 1.5772e-06 | 8.5849e-07 | 1.5932e-06
390 | feeder2_line137 | 3 | 99 | 8.5064e-07 | 1.5787e-06 | 8.5923e-07 | 1.5947e-06
390 | feeder2_line138 | 1 | 354.6 | 98.0821 | 98.0892 | 27.6599 | 27.6619
390 | feeder2_line138 | 2 | 354.6 | 97.7562 | 97.7496 | 27.568 | 27.5662
390 | feeder2_line138 | 3 | 354.6 | 97.9627 | 97.9605 | 27.6262 | 27.6256
390 | feeder2_line139 | 1 | 99 | 5.0161e-08 | 4.9043e-07 | 5.0667e-08 | 4.9539e-07
390 | feeder2_line139 | 2 | 99 | 4.9791e-08 | 4.9147e-07 | 5.0294e-08 | 4.9644e-07
390 | feeder2_line139 | 3 | 99 | 2.2647 | 2.265 | 2.2875 | 2.2878
390 | feeder2_line140 | 1 | 354.6 | 98.0822 | 98.0892 | 27.66 | 27.6619
390 | feeder2_line140 | 2 | 354.6 | 97.7563 | 97.7496 | 27.568 | 27.5662
390 | feeder2_line140 | 3 | 354.6 | 98.4516 | 98.4491 | 27.7641 | 27.7634
390 | feeder2_line141 | 1 | 99 | 2.5178e-06 | 4.8516e-07 | 2.5432e-06 | 4.9006e-07
390 | feeder2_line141 | 2 | 99 | 0.1899 | 0.18989 | 0.19182 | 0.19181
390 | feeder2_line141 | 3 | 99 | 2.528e-06 | 4.8665e-07 | 2.5535e-06 | 4.9157e-07
390 | feeder2_line142 | 1 | 354.6 | 98.0821 | 98.0892 | 27.6599 | 27.6619
390 | feeder2_line142 | 2 | 354.6 | 97.93 | 97.9235 | 27.617 | 27.6152
390 | feeder2_line142 | 3 | 354.6 | 98.4514 | 98.4491 | 27.7641 | 27.7634
390 | feeder2_line143 | 1 | 99 | 8.4819e-07 | 1.724e-06 | 8.5676e-07 | 1.7414e-06
390 | feeder2_line143 | 2 | 99 | 0.11611 | 0.11608 | 0.11728 | 0.11725
390 | feeder2_line143 | 3 | 99 | 8.5091e-07 | 1.7293e-06 | 8.595e-07 | 1.7468e-06
390 | feeder2_line144 | 1 | 354.6 | 98.0819 | 98.0892 | 27.6599 | 27.6619
390 | feeder2_line144 | 2 | 354.6 | 98.0408 | 98.0344 | 27.6483 | 27.6465
390 | feeder2_line144 | 3 | 354.6 | 98.4512 | 98.4491 | 27.764 | 27.7634
390 | feeder2_line145 | 1 | 99 | 2.5087e-08 | 4.8344e-07 | 2.5341e-08 | 4.8832e-07
390 | feeder2_line145 | 2 | 99 | 1.1607 | 1.1606 | 1.1724 | 1.1724
390 | feeder2_line145 | 3 | 99 | 2.4994e-08 | 4.8492e-07 | 2.5246e-08 | 4.8982e-07
390 | feeder2_line146 | 1 | 354.6 | 98.0818 | 98.0892 | 27.6598 | 27.6619
390 | feeder2_line146 | 2 | 354.6 | 98.4343 | 98.428 | 27.7592 | 27.7575
390 | feeder2_line146 | 3 | 354.6 | 98.4511 | 98.4491 | 27.764 | 27.7634
390 | feeder2_line147 | 1 | 99 | 0.10817 | 0.10818 | 0.10926 | 0.10927
390 | feeder2_line147 | 2 | 99 | 1.1503e-06 | 2.2346e-06 | 1.1619e-06 | 2.2572e-06
390 | feeder2_line147 | 3 | 99 | 1.1513e-06 | 2.2367e-06 | 1.163e-06 | 2.2593e-06
390 | feeder2_line148 | 1 | 99 | 0.22049 | 0.2205 | 0.22272 | 0.22273
390 | feeder2_line148 | 2 | 99 | 6.0004e-07 | 1.4974e-06 | 6.061e-07 | 1.5125e-06
390 | feeder2_line148 | 3 | 99 | 6.0067e-07 | 1.4988e-06 | 6.0673e-07 | 1.5139e-06
390 | feeder2_line149 | 1 | 354.6 | 98.3882 | 98.3955 | 27.7462 | 27.7483
390 | feeder2_line149 | 2 | 354.6 | 98.4345 | 98.428 | 27.7593 | 27.7575
390 | feeder2_line149 | 3 | 354.6 | 98.4513 | 98.4491 | 27.764 | 27.7634
390 | feeder2_line150 | 1 | 354.6 | 98.3883 | 98.3955 | 27.7463 | 27.7483
390 | feeder2_line150 | 2 | 354.6 | 98.6113 | 98.6047 | 27.8092 | 27.8073
390 | feeder2_line150 | 3 | 354.6 | 98.4514 | 98.4491 | 27.7641 | 27.7634
390 | feeder2_line151 | 1 | 99 | 9.7279e-06 | 1.7748e-06 | 9.8262e-06 | 1.7927e-06
390 | feeder2_line151 | 2 | 99 | 0.18584 | 0.18584 | 0.18771 | 0.18771
390 | feeder2_line151 | 3 | 99 | 9.7682e-06 | 1.7803e-06 | 9.8669e-06 | 1.7983e-06
390 | feeder2_line152 | 1 | 354.6 | 9.4728e-12 | 1.183e-06 | 2.6714e-12 | 3.3363e-07
390 | feeder2_line152 | 2 | 354.6 | 1.0837e-11 | 1.1853e-06 | 3.0561e-12 | 3.3426e-07
390 | feeder2_line152 | 3 | 354.6 | 0.076803 | 0.076802 | 0.021659 | 0.021659
390 | feeder2_line153 | 1 | 99 | 0.044111 | 0.044114 | 0.044557 | 0.04456
390 | feeder2_line153 | 2 | 99 | 4.9839e-08 | 5.9308e-07 | 5.0343e-08 | 5.9907e-07
390 | feeder2_line153 | 3 | 99 | 5.0022e-08 | 5.9363e-07 | 5.0527e-08 | 5.9963e-07
390 | feeder2_line154 | 1 | 99 | 5.7425e-07 | 8.8064e-07 | 5.8005e-07 | 8.8954e-07
390 | feeder2_line154 | 2 | 99 | 5.7549e-07 | 8.8252e-07 | 5.8131e-07 | 8.9143e-07
390 | feeder2_line154 | 3 | 99 | 0.040676 | 0.040636 | 0.041087 | 0.041047
390 | feeder2_line155 | 1 | 99 | 98.4286 | 98.4359 | 99.4229 | 99.4302
390 | feeder2_line155 | 2 | 99 | 98.6112 | 98.6047 | 99.6072 | 99.6007
390 | feeder2_line155 | 3 | 99 | 98.561 | 98.5587 | 99.5565 | 99.5543
390 | feeder2_line156 | 1 | 99 | 5.9918e-07 | 1.1589e-06 | 6.0523e-07 | 1.1706e-06
390 | feeder2_line156 | 2 | 99 | 0.096426 | 0.096421 | 0.0974 | 0.097395
390 | feeder2_line156 | 3 | 99 | 6.0087e-07 | 1.1625e-06 | 6.0694e-07 | 1.1742e-06
390 | feeder2_line157 | 1 | 99 | 2.5092e-08 | 2.516e-07 | 2.5345e-08 | 2.5415e-07
390 | feeder2_line157 | 2 | 99 | 0.089574 | 0.08957 | 0.090479 | 0.090474
390 | feeder2_line157 | 3 | 99 | 2.5004e-08 | 2.5237e-07 | 2.5256e-08 | 2.5492e-07
420 | feeder2_line1 | 1 | 354.6 | 71.8922 | 71.8997 | 20.2742 | 20.2763
420 | feeder2_line1 | 2 | 354.6 | 83.9888 | 83.9849 | 23.6855 | 23.6844
420 | feeder2_line1 | 3 | 354.6 | 90.4573 | 90.4568 | 25.5097 | 25.5095
420 | feeder2_line2 | 1 | 354.6 | 73.244 | 73.2513 | 20.6554 | 20.6575
420 | feeder2_line2 | 2 | 354.6 | 83.9889 | 83.9849 | 23.6855 | 23.6844
420 | feeder2_line2 | 3 | 354.6 | 90.4575 | 90.4568 | 25.5097 | 25.5095
420 | feeder2_line3 | 1 | 80.1 | 2.218 | 2.2181 | 2.7691 | 2.7691
420 | feeder2_line3 | 2 | 80.1 | 5.7156e-07 | 1.0562e-06 | 7.1355e-07 | 1.3186e-06
420 | feeder2_line3 | 3 | 80.1 | 5.7222e-07 | 1.0574e-06 | 7.1438e-07 | 1.3202e-06
420 | feeder2_line4 | 1 | 354.6 | 73.2441 | 73.2513 | 20.6554 | 20.6575
420 | feeder2_line4 | 2 | 354.6 | 84.2486 | 84.2444 | 23.7588 | 23.7576
420 | feeder2_line4 | 3 | 354.6 | 90.4577 | 90.4568 | 25.5098 | 25.5095
420 | feeder2_line5 | 1 | 80.1 | 5.713e-07 | 9.9687e-07 | 7.1323e-07 | 1.2445e-06
420 | feeder2_line5 | 2 | 80.1 | 0.27927 | 0.27927 | 0.34865 | 0.34865
420 | feeder2_line5 | 3 | 80.1 | 5.7227e-07 | 9.9855e-07 | 7.1444e-07 | 1.2466e-06
420 | feeder2_line6 | 1 | 80.1 | 5.7134e-07 | 1.1728e-06 | 7.1328e-07 | 1.4641e-06
420 | feeder2_line6 | 2 | 80.1 | 5.7164e-07 | 1.1734e-06 | 7.1366e-07 | 1.4649e-06
420 | feeder2_line6 | 3 | 80.1 | 0.085304 | 0.085297 | 0.1065 | 0.10649
420 | feeder2_line7 | 1 | 354.6 | 73.2442 | 73.2513 | 20.6554 | 20.6575
420 | feeder2_line7 | 2 | 354.6 | 84.2487 | 84.2444 | 23.7588 | 23.7576
420 | feeder2_line7 | 3 | 354.6 | 90.5409 | 90.5399 | 25.5333 | 25.533
420 | feeder2_line8 | 1 | 80.1 | 0.072758 | 0.072759 | 0.090834 | 0.090835
420 | feeder2_line8 | 2 | 80.1 | 5.7179e-07 | 1.1317e-06 | 7.1385e-07 | 1.4129e-06
420 | feeder2_line8 | 3 | 80.1 | 5.7257e-07 | 1.1333e-06 | 7.1482e-07 | 1.4148e-06
420 | feeder2_line9 | 1 | 354.6 | 73.3129 | 73.32 | 20.6748 | 20.6768
420 | feeder2_line9 | 2 | 354.6 | 84.2487 | 84.2444 | 23.7588 | 23.7576
420 | feeder2_line9 | 3 | 354.6 | 90.541 | 90.5399 | 25.5333 | 25.533
420 | feeder2_line10 | 1 | 80.1 | 8.4473e-07 | 1.4935e-06 | 1.0546e-06 | 1.8645e-06
420 | feeder2_line10 | 2 | 80.1 | 0.072672 | 0.072671 | 0.090726 | 0.090725
420 | feeder2_line10 | 3 | 80.1 | 8.4649e-07 | 1.4964e-06 | 1.0568e-06 | 1.8682e-06
420 | feeder2_line11 | 1 | 354.6 | 73.3129 | 73.32 | 20.6748 | 20.6768
420 | feeder2_line11 | 2 | 354.6 | 84.3177 | 84.3134 | 23.7783 | 23.777
420 | feeder2_line11 | 3 | 354.6 | 90.541 | 90.5399 | 25.5333 | 25.533
420 | feeder2_line12 | 1 | 80.1 | 5.4658e-07 | 9.9072e-07 | 6.8237e-07 | 1.2369e-06
420 | feeder2_line12 | 2 | 80.1 | 5.4703e-07 | 9.9135e-07 | 6.8293e-07 | 1.2376e-06
420 | feeder2_line12 | 3 | 80.1 | 0.061745 | 0.061745 | 0.077086 | 0.077085
420 | feeder2_line13 | 1 | 354.6 | 73.3129 | 73.32 | 20.6748 | 20.6768
420 | feeder2_line13 | 2 | 354.6 | 84.3177 | 84.3134 | 23.7783 | 23.777
420 | feeder2_line13 | 3 | 354.6 | 90.6012 | 90.6002 | 25.5502 | 25.55
420 | feeder2_line14 | 1 | 80.1 | 0.2752 | 0.2752 | 0.34357 | 0.34357
420 | feeder2_line14 | 2 | 80.1 | 2.9839e-07 | 6.465e-07 | 3.7252e-07 | 8.0712e-07
420 | feeder2_line14 | 3 | 80.1 | 2.9881e-07 | 6.4745e-07 | 3.7305e-07 | 8.0831e-07
420 | feeder2_line15 | 1 | 354.6 | 73.5667 | 73.5737 | 20.7464 | 20.7484
420 | feeder2_line15 | 2 | 354.6 | 84.3177 | 84.3134 | 23.7783 | 23.777
420 | feeder2_line15 | 3 | 354.6 | 90.6012 | 90.6002 | 25.5502 | 25.55
420 | feeder2_line16 | 1 | 80.1 | 5.7161e-07 | 1.0298e-06 | 7.1362e-07 | 1.2856e-06
420 | feeder2_line16 | 2 | 80.1 | 0.25433 | 0.25433 | 0.31752 | 0.31752
420 | feeder2_line16 | 3 | 80.1 | 5.729e-07 | 1.0321e-06 | 7.1524e-07 | 1.2885e-06
420 | feeder2_line17 | 1 | 354.6 | 73.5667 | 73.5737 | 20.7464 | 20.7484
420 | feeder2_line17 | 2 | 354.6 | 84.5525 | 84.5482 | 23.8445 | 23.8432
420 | feeder2_line17 | 3 | 354.6 | 90.6012 | 90.6002 | 25.5503 | 25.55
420 | feeder2_line18 | 1 | 80.1 | 5.4692e-07 | 7.3749e-07 | 6.828e-07 | 9.2072e-07
420 | feeder2_line18 | 2 | 80.1 | 5.4754e-07 | 7.3816e-07 | 6.8357e-07 | 9.2155e-07
420 | feeder2_line18 | 3 | 80.1 | 0.5179 | 0.51789 | 0.64657 | 0.64656
420 | feeder2_line19 | 1 | 354.6 | 73.5667 | 73.5737 | 20.7464 | 20.7484
420 | feeder2_line19 | 2 | 354.6 | 84.5526 | 84.5482 | 23.8445 | 23.8432
420 | feeder2_line19 | 3 | 354.6 | 91.0991 | 91.098 | 25.6907 | 25.6904
420 | feeder2_line20 | 1 | 99 | 5.4701e-07 | 8.8437e-07 | 5.5253e-07 | 8.933e-07
420 | feeder2_line20 | 2 | 99 | 5.4768e-07 | 8.8524e-07 | 5.5321e-07 | 8.9418e-07
420 | feeder2_line20 | 3 | 99 | 0.085855 | 0.085842 | 0.086722 | 0.086709
420 | feeder2_line21 | 1 | 354.6 | 73.5668 | 73.5737 | 20.7464 | 20.7484
420 | feeder2_line21 | 2 | 354.6 | 84.5527 | 84.5482 | 23.8445 | 23.8432
420 | feeder2_line21 | 3 | 354.6 | 91.1831 | 91.1819 | 25.7144 | 25.714
420 | feeder2_line22 | 1 | 99 | 5.7205e-07 | 1.0139e-06 | 5.7783e-07 | 1.0242e-06
420 | feeder2_line22 | 2 | 99 | 0.3418 | 0.3418 | 0.34526 | 0.34525
420 | feeder2_line22 | 3 | 99 | 5.7382e-07 | 1.017e-06 | 5.7961e-07 | 1.0273e-06
420 | feeder2_line23 | 1 | 99 | 5.7205e-07 | 9.4913e-07 | 5.7783e-07 | 9.5872e-07
420 | feeder2_line23 | 2 | 99 | 5.7264e-07 | 9.501e-07 | 5.7843e-07 | 9.5969e-07
420 | feeder2_line23 | 3 | 99 | 0.8408 | 0.84081 | 0.84929 | 0.8493
420 | feeder2_line24 | 1 | 354.6 | 73.5669 | 73.5737 | 20.7464 | 20.7484
420 | feeder2_line24 | 2 | 354.6 | 84.8867 | 84.8821 | 23.9387 | 23.9374
420 | feeder2_line24 | 3 | 354.6 | 91.5543 | 91.553 | 25.819 | 25.8187
420 | feeder2_line25 | 1 | 99 | 0.34185 | 0.34185 | 0.34531 | 0.34531
420 | feeder2_line25 | 2 | 99 | 4.9771e-08 | 6.9093e-07 | 5.0274e-08 | 6.9791e-07
420 | feeder2_line25 | 3 | 99 | 4.9716e-08 | 6.9243e-07 | 5.0218e-08 | 6.9942e-07
420 | feeder2_line26 | 1 | 99 | 0.085389 | 0.085392 | 0.086251 | 0.086255
420 | feeder2_line26 | 2 | 99 | 5.4791e-07 | 8.5601e-07 | 5.5344e-07 | 8.6466e-07
420 | feeder2_line26 | 3 | 99 | 5.4919e-07 | 8.5788e-07 | 5.5474e-07 | 8.6655e-07
420 | feeder2_line27 | 1 | 354.6 | 73.9802 | 73.987 | 20.863 | 20.8649
420 | feeder2_line27 | 2 | 354.6 | 84.8867 | 84.8821 | 23.9387 | 23.9374
420 | feeder2_line27 | 3 | 354.6 | 91.5543 | 91.553 | 25.819 | 25.8187
420 | feeder2_line28 | 1 | 99 | 2.5365e-06 | 7.1002e-07 | 2.5621e-06 | 7.172e-07
420 | feeder2_line28 | 2 | 99 | 0.76387 | 0.76385 | 0.77159 | 0.77156
420 | feeder2_line28 | 3 | 99 | 2.549e-06 | 7.126e-07 | 2.5747e-06 | 7.1979e-07
420 | feeder2_line29 | 1 | 354.6 | 73.9802 | 73.987 | 20.863 | 20.8649
420 | feeder2_line29 | 2 | 354.6 | 85.1483 | 85.1437 | 24.0125 | 24.0112
420 | feeder2_line29 | 3 | 354.6 | 91.5543 | 91.553 | 25.819 | 25.8187
420 | feeder2_line30 | 1 | 266.4 | 2.1233 | 2.1233 | 0.79704 | 0.79703
420 | feeder2_line30 | 2 | 266.4 | 1.8179 | 1.818 | 0.68239 | 0.68242
420 | feeder2_line30 | 3 | 266.4 | 1.7931 | 1.7932 | 0.6731 | 0.67312
420 | feeder2_line31 | 1 | 354.6 | 75.4846 | 75.4911 | 21.2872 | 21.2891
420 | feeder2_line31 | 2 | 354.6 | 86.0199 | 86.0148 | 24.2583 | 24.2569
420 | feeder2_line31 | 3 | 354.6 | 92.735 | 92.7333 | 26.152 | 26.1515
420 | feeder2_line32 | 1 | 354.6 | 75.4846 | 75.4911 | 21.2872 | 21.2891
420 | feeder2_line32 | 2 | 354.6 | 86.5429 | 86.5378 | 24.4058 | 24.4043
420 | feeder2_line32 | 3 | 354.6 | 92.735 | 92.7333 | 26.152 | 26.1515
420 | feeder2_line33 | 1 | 99 | 5.0121e-08 | 6.8547e-07 | 5.0627e-08 | 6.9239e-07
420 | feeder2_line33 | 2 | 99 | 1.3038 | 1.3038 | 1.317 | 1.317
420 | feeder2_line33 | 3 | 99 | 4.9745e-08 | 6.8847e-07 | 5.0247e-08 | 6.9542e-07
420 | feeder2_line34 | 1 | 354.6 | 75.4846 | 75.4911 | 21.2872 | 21.2891
420 | feeder2_line34 | 2 | 354.6 | 86.5429 | 86.5378 | 24.4058 | 24.4043
420 | feeder2_line34 | 3 | 354.6 | 93.0011 | 92.9994 | 26.227 | 26.2266
420 | feeder2_line35 | 1 | 99 | 2.9894e-07 | 7.5916e-07 | 3.0196e-07 | 7.6683e-07
420 | feeder2_line35 | 2 | 99 | 2.9932e-07 | 7.6034e-07 | 3.0234e-07 | 7.6802e-07
420 | feeder2_line35 | 3 | 99 | 0.27544 | 0.27544 | 0.27823 | 0.27823
420 | feeder2_line36 | 1 | 354.6 | 75.5111 | 75.5178 | 21.2947 | 21.2966
420 | feeder2_line36 | 2 | 354.6 | 86.5429 | 86.5378 | 24.4058 | 24.4043
420 | feeder2_line36 | 3 | 354.6 | 93.001 | 92.9994 | 26.227 | 26.2266
420 | feeder2_line37 | 1 | 99 | 0.028177 | 0.028324 | 0.028461 | 0.02861
420 | feeder2_line37 | 2 | 99 | 2.9937e-07 | 8.4144e-07 | 3.024e-07 | 8.4994e-07
420 | feeder2_line37 | 3 | 99 | 3.0022e-07 | 8.4399e-07 | 3.0325e-07 | 8.5251e-07
420 | feeder2_line38 | 1 | 99 | 3.2387e-07 | 7.7488e-07 | 3.2714e-07 | 7.827e-07
420 | feeder2_line38 | 2 | 99 | 0.077226 | 0.077222 | 0.078006 | 0.078002
420 | feeder2_line38 | 3 | 99 | 3.2479e-07 | 7.7807e-07 | 3.2807e-07 | 7.8593e-07
420 | feeder2_line39 | 1 | 266.4 | 2.1233 | 2.1233 | 0.79704 | 0.79703
420 | feeder2_line39 | 2 | 266.4 | 1.7641 | 1.7642 | 0.66222 | 0.66225
420 | feeder2_line39 | 3 | 266.4 | 1.7932 | 1.7932 | 0.67311 | 0.67312
420 | feeder2_line40 | 1 | 354.6 | 75.8457 | 75.8524 | 21.3891 | 21.391
420 | feeder2_line40 | 2 | 354.6 | 86.5429 | 86.5378 | 24.4058 | 24.4043
420 | feeder2_line40 | 3 | 354.6 | 93.0011 | 92.9994 | 26.227 | 26.2266
420 | feeder2_line41 | 1 | 99 | 0.34182 | 0.34182 | 0.34528 | 0.34528
420 | feeder2_line41 | 2 | 99 | 4.9868e-08 | 7.3534e-07 | 5.0372e-08 | 7.4277e-07
420 | feeder2_line41 | 3 | 99 | 4.9753e-08 | 7.376e-07 | 5.0255e-08 | 7.4505e-07
420 | feeder2_line42 | 1 | 99 | 2.9882e-07 | 7.4792e-07 | 3.0183e-07 | 7.5548e-07
420 | feeder2_line42 | 2 | 99 | 2.9916e-07 | 7.4898e-07 | 3.0218e-07 | 7.5655e-07
420 | feeder2_line42 | 3 | 99 | 0.1899 | 0.18989 | 0.19181 | 0.19181
420 | feeder2_line43 | 1 | 266.4 | 2.1233 | 2.1233 | 0.79703 | 0.79703
420 | feeder2_line43 | 2 | 266.4 | 1.7642 | 1.7642 | 0.66224 | 0.66225
420 | feeder2_line43 | 3 | 266.4 | 1.6405 | 1.6405 | 0.6158 | 0.61581
420 | feeder2_line44 | 1 | 354.6 | 75.8457 | 75.8524 | 21.3891 | 21.391
420 | feeder2_line44 | 2 | 354.6 | 86.5429 | 86.5378 | 24.4058 | 24.4043
420 | feeder2_line44 | 3 | 354.6 | 93.0853 | 93.0835 | 26.2508 | 26.2503
420 | feeder2_line45 | 1 | 99 | 5.0176e-08 | 5.7901e-07 | 5.0683e-08 | 5.8486e-07
420 | feeder2_line45 | 2 | 99 | 4.9867e-08 | 5.7998e-07 | 5.0371e-08 | 5.8583e-07
420 | feeder2_line45 | 3 | 99 | 0.08558 | 0.085558 | 0.086445 | 0.086422
420 | feeder2_line46 | 1 | 99 | 5.7259e-07 | 1.3559e-06 | 5.7837e-07 | 1.3696e-06
420 | feeder2_line46 | 2 | 99 | 5.7341e-07 | 1.3578e-06 | 5.792e-07 | 1.3715e-06
420 | feeder2_line46 | 3 | 99 | 1.2575 | 1.2576 | 1.2702 | 1.2703
420 | feeder2_line47 | 1 | 266.4 | 2.1234 | 2.1233 | 0.79707 | 0.79703
420 | feeder2_line47 | 2 | 266.4 | 1.7644 | 1.7642 | 0.6623 | 0.66225
420 | feeder2_line47 | 3 | 266.4 | 0.55321 | 0.55296 | 0.20766 | 0.20757
420 | feeder2_line48 | 1 | 99 | 0.13653 | 0.13653 | 0.13791 | 0.13791
420 | feeder2_line48 | 2 | 99 | 4.9824e-08 | 7.3104e-07 | 5.0327e-08 | 7.3843e-07
420 | feeder2_line48 | 3 | 99 | 4.9736e-08 | 7.3303e-07 | 5.0239e-08 | 7.4043e-07
420 | feeder2_line49 | 1 | 266.4 | 2.0114 | 2.0114 | 0.75504 | 0.75502
420 | feeder2_line49 | 2 | 266.4 | 1.7643 | 1.7642 | 0.66229 | 0.66225
420 | feeder2_line49 | 3 | 266.4 | 0.5532 | 0.55296 | 0.20766 | 0.20757
420 | feeder2_line50 | 1 | 99 | 5.7258e-07 | 1.2339e-06 | 5.7837e-07 | 1.2464e-06
420 | feeder2_line50 | 2 | 99 | 0.085175 | 0.085169 | 0.086036 | 0.086029
420 | feeder2_line50 | 3 | 99 | 5.7497e-07 | 1.239e-06 | 5.8078e-07 | 1.2515e-06
420 | feeder2_line51 | 1 | 99 | 0.0449 | 0.045039 | 0.045353 | 0.045494
420 | feeder2_line51 | 2 | 99 | 5.734e-07 | 1.3414e-06 | 5.792e-07 | 1.355e-06
420 | feeder2_line51 | 3 | 99 | 5.7497e-07 | 1.3451e-06 | 5.8078e-07 | 1.3587e-06
420 | feeder2_line52 | 1 | 266.4 | 1.971 | 1.971 | 0.73987 | 0.73986
420 | feeder2_line52 | 2 | 266.4 | 1.7062 | 1.7062 | 0.64045 | 0.64045
420 | feeder2_line52 | 3 | 266.4 | 0.55306 | 0.55296 | 0.2076 | 0.20757
420 | feeder2_line53 | 1 | 99 | 5.4753e-07 | 7.5307e-07 | 5.5306e-07 | 7.6068e-07
420 | feeder2_line53 | 2 | 99 | 1.7062 | 1.7062 | 1.7234 | 1.7234
420 | feeder2_line53 | 3 | 99 | 5.5011e-07 | 7.562e-07 | 5.5566e-07 | 7.6383e-07
420 | feeder2_line54 | 1 | 266.4 | 1.9709 | 1.971 | 0.73983 | 0.73986
420 | feeder2_line54 | 2 | 266.4 | 8.5542e-05 | 4.6262e-06 | 3.211e-05 | 1.7366e-06
420 | feeder2_line54 | 3 | 266.4 | 0.55288 | 0.55296 | 0.20754 | 0.20757
420 | feeder2_line55 | 1 | 99 | 0.18089 | 0.18089 | 0.18271 | 0.18272
420 | feeder2_line55 | 2 | 99 | 4.9891e-08 | 7.3102e-07 | 5.0395e-08 | 7.384e-07
420 | feeder2_line55 | 3 | 99 | 4.9764e-08 | 7.3345e-07 | 5.0267e-08 | 7.4086e-07
420 | feeder2_line56 | 1 | 354.6 | 76.0139 | 76.0205 | 21.4365 | 21.4384
420 | feeder2_line56 | 2 | 354.6 | 86.543 | 86.5378 | 24.4058 | 24.4043
420 | feeder2_line56 | 3 | 354.6 | 93.0853 | 93.0835 | 26.2508 | 26.2503
420 | feeder2_line57 | 1 | 99 | 7.5132e-07 | 1.5425e-06 | 7.589e-07 | 1.5581e-06
420 | feeder2_line57 | 2 | 99 | 7.4734e-07 | 1.5447e-06 | 7.5489e-07 | 1.5603e-06
420 | feeder2_line57 | 3 | 99 | 0.55296 | 0.55296 | 0.55854 | 0.55854
420 | feeder2_line58 | 1 | 266.4 | 1.971 | 1.971 | 0.73985 | 0.73986
420 | feeder2_line58 | 2 | 266.4 | 1.8946e-05 | 2.6859e-06 | 7.1117e-06 | 1.0082e-06
420 | feeder2_line58 | 3 | 266.4 | 1.9014e-05 | 2.693e-06 | 7.1372e-06 | 1.0109e-06
420 | feeder2_line59 | 1 | 99 | 5.0091e-08 | 5.362e-07 | 5.0597e-08 | 5.4161e-07
420 | feeder2_line59 | 2 | 99 | 4.9829e-08 | 5.3695e-07 | 5.0332e-08 | 5.4237e-07
420 | feeder2_line59 | 3 | 99 | 0.49146 | 0.49146 | 0.49643 | 0.49643
420 | feeder2_line60 | 1 | 99 | 2.9881e-07 | 8.1036e-07 | 3.0182e-07 | 8.1854e-07
420 | feeder2_line60 | 2 | 99 | 2.9916e-07 | 8.1151e-07 | 3.0218e-07 | 8.197e-07
420 | feeder2_line60 | 3 | 99 | 0.061552 | 0.061552 | 0.062173 | 0.062173
420 | feeder2_line61 | 1 | 266.4 | 0.221 | 0.22118 | 0.082958 | 0.083024
420 | feeder2_line61 | 2 | 266.4 | 1.4344 | 1.4346 | 0.53845 | 0.53851
420 | feeder2_line61 | 3 | 266.4 | 0.44239 | 0.44254 | 0.16606 | 0.16612
420 | feeder2_line62 | 1 | 354.6 | 76.2209 | 76.2277 | 21.4949 | 21.4968
420 | feeder2_line62 | 2 | 354.6 | 87.2682 | 87.2632 | 24.6103 | 24.6089
420 | feeder2_line62 | 3 | 354.6 | 93.525 | 93.5233 | 26.3748 | 26.3743
420 | feeder2_line63 | 1 | 99 | 0.92354 | 0.92354 | 0.93287 | 0.93287
420 | feeder2_line63 | 2 | 99 | 5.734e-07 | 1.2201e-06 | 5.7919e-07 | 1.2324e-06
420 | feeder2_line63 | 3 | 99 | 5.7498e-07 | 1.2234e-06 | 5.8078e-07 | 1.2358e-06
420 | feeder2_line64 | 1 | 99 | 1.1962 | 1.1962 | 1.2083 | 1.2083
420 | feeder2_line64 | 2 | 99 | 5.4793e-13 | 3.214e-07 | 5.5347e-13 | 3.2465e-07
420 | feeder2_line64 | 3 | 99 | 7.6926e-12 | 3.2227e-07 | 7.7703e-12 | 3.2553e-07
420 | feeder2_line65 | 1 | 99 | 5.0293e-08 | 6.412e-07 | 5.0801e-08 | 6.4768e-07
420 | feeder2_line65 | 2 | 99 | 0.27945 | 0.27944 | 0.28227 | 0.28227
420 | feeder2_line65 | 3 | 99 | 4.9778e-08 | 6.4488e-07 | 5.0281e-08 | 6.5139e-07
420 | feeder2_line66 | 1 | 354.6 | 76.2209 | 76.2277 | 21.4949 | 21.4968
420 | feeder2_line66 | 2 | 354.6 | 87.5339 | 87.5289 | 24.6853 | 24.6839
420 | feeder2_line66 | 3 | 354.6 | 93.5249 | 93.5233 | 26.3748 | 26.3743
420 | feeder2_line67 | 1 | 99 | 2.5123e-08 | 3.6242e-07 | 2.5377e-08 | 3.6608e-07
420 | feeder2_line67 | 2 | 99 | 2.4958e-08 | 3.631e-07 | 2.521e-08 | 3.6677e-07
420 | feeder2_line67 | 3 | 99 | 0.34158 | 0.34158 | 0.34503 | 0.34503
420 | feeder2_line68 | 1 | 266.4 | 0.22104 | 0.22118 | 0.082973 | 0.083024
420 | feeder2_line68 | 2 | 266.4 | 1.4345 | 1.4346 | 0.53847 | 0.53851
420 | feeder2_line68 | 3 | 266.4 | 0.10128 | 0.10139 | 0.038017 | 0.038061
420 | feeder2_line69 | 1 | 99 | 2.8441 | 2.8441 | 2.8728 | 2.8728
420 | feeder2_line69 | 2 | 99 | 2.5493e-06 | 6.6713e-07 | 2.5751e-06 | 6.7387e-07
420 | feeder2_line69 | 3 | 99 | 2.5611e-06 | 6.6961e-07 | 2.587e-06 | 6.7638e-07
420 | feeder2_line70 | 1 | 354.6 | 77.0703 | 77.0773 | 21.7344 | 21.7364
420 | feeder2_line70 | 2 | 354.6 | 87.5339 | 87.5289 | 24.6852 | 24.6839
420 | feeder2_line70 | 3 | 354.6 | 93.5248 | 93.5233 | 26.3747 | 26.3743
420 | feeder2_line71 | 1 | 99 | 5.0317e-08 | 7.1547e-07 | 5.0826e-08 | 7.227e-07
420 | feeder2_line71 | 2 | 99 | 0.05279 | 0.052778 | 0.053323 | 0.053311
420 | feeder2_line71 | 3 | 99 | 4.9785e-08 | 7.1973e-07 | 5.0288e-08 | 7.27e-07
420 | feeder2_line72 | 1 | 354.6 | 77.0704 | 77.0773 | 21.7345 | 21.7364
420 | feeder2_line72 | 2 | 354.6 | 87.5847 | 87.5797 | 24.6996 | 24.6982
420 | feeder2_line72 | 3 | 354.6 | 93.5249 | 93.5233 | 26.3748 | 26.3743
420 | feeder2_line73 | 1 | 99 | 5.9844e-07 | 1.5343e-06 | 6.0449e-07 | 1.5498e-06
420 | feeder2_line73 | 2 | 99 | 1.3043 | 1.3043 | 1.3175 | 1.3175
420 | feeder2_line73 | 3 | 99 | 6.0135e-07 | 1.5426e-06 | 6.0742e-07 | 1.5582e-06
420 | feeder2_line74 | 1 | 99 | 5.0249e-08 | 4.5761e-07 | 5.0756e-08 | 4.6223e-07
420 | feeder2_line74 | 2 | 99 | 0.10179 | 0.10178 | 0.10282 | 0.10281
420 | feeder2_line74 | 3 | 99 | 4.9771e-08 | 4.6009e-07 | 5.0273e-08 | 4.6474e-07
420 | feeder2_line75 | 1 | 266.4 | 0.22114 | 0.22118 | 0.08301 | 0.083024
420 | feeder2_line75 | 2 | 266.4 | 0.089691 | 0.089721 | 0.033668 | 0.033679
420 | feeder2_line75 | 3 | 266.4 | 0.10138 | 0.10139 | 0.038054 | 0.038061
420 | feeder2_line76 | 1 | 99 | 0.22117 | 0.22118 | 0.22341 | 0.22341
420 | feeder2_line76 | 2 | 99 | 8.4917e-07 | 1.5857e-06 | 8.5775e-07 | 1.6017e-06
420 | feeder2_line76 | 3 | 99 | 8.5225e-07 | 1.5913e-06 | 8.6086e-07 | 1.6074e-06
420 | feeder2_line77 | 1 | 99 | 2.5126e-08 | 5.7506e-07 | 2.538e-08 | 5.8087e-07
420 | feeder2_line77 | 2 | 99 | 2.4952e-08 | 5.7616e-07 | 2.5204e-08 | 5.8198e-07
420 | feeder2_line77 | 3 | 99 | 0.10141 | 0.10139 | 0.10243 | 0.10242
420 | feeder2_line78 | 1 | 266.4 | 1.2342e-12 | 9.5399e-07 | 4.633e-13 | 3.5811e-07
420 | feeder2_line78 | 2 | 266.4 | 0.089723 | 0.089721 | 0.03368 | 0.033679
420 | feeder2_line78 | 3 | 266.4 | 2.4055e-12 | 9.5866e-07 | 9.0298e-13 | 3.5986e-07
420 | feeder2_line79 | 1 | 354.6 | 2.4566 | 2.4564 | 0.69277 | 0.69271
420 | feeder2_line79 | 2 | 354.6 | 8.2206 | 8.2202 | 2.3183 | 2.3182
420 | feeder2_line79 | 3 | 354.6 | 4.5803 | 4.58 | 1.2917 | 1.2916
420 | feeder2_line80 | 1 | 354.6 | 78.2931 | 78.2995 | 22.0793 | 22.0811
420 | feeder2_line80 | 2 | 354.6 | 95.0457 | 95.0401 | 26.8036 | 26.8021
420 | feeder2_line80 | 3 | 354.6 | 96.4564 | 96.4543 | 27.2015 | 27.2009
420 | feeder2_line81 | 1 | 354.6 | 78.293 | 78.2995 | 22.0792 | 22.0811
420 | feeder2_line81 | 2 | 354.6 | 95.0456 | 95.0401 | 26.8036 | 26.8021
420 | feeder2_line81 | 3 | 354.6 | 96.5247 | 96.5226 | 27.2207 | 27.2201
420 | feeder2_line82 | 1 | 354.6 | 3.4292e-11 | 7.3412e-07 | 9.6707e-12 | 2.0703e-07
420 | feeder2_line82 | 2 | 354.6 | 4.1526e-11 | 7.3568e-07 | 1.1711e-11 | 2.0747e-07
420 | feeder2_line82 | 3 | 354.6 | 0.069271 | 0.06927 | 0.019535 | 0.019535
420 | feeder2_line83 | 1 | 354.6 | 78.2932 | 78.2995 | 22.0793 | 22.0811
420 | feeder2_line83 | 2 | 354.6 | 95.532 | 95.5262 | 26.9408 | 26.9392
420 | feeder2_line83 | 3 | 354.6 | 96.5249 | 96.5226 | 27.2208 | 27.2201
420 | feeder2_line84 | 1 | 354.6 | 7.3445e-12 | 1.2976e-06 | 2.0712e-12 | 3.6593e-07
420 | feeder2_line84 | 2 | 354.6 | 1.3348 | 1.3348 | 0.37643 | 0.37642
420 | feeder2_line84 | 3 | 354.6 | 1.6544e-11 | 1.3054e-06 | 4.6655e-12 | 3.6813e-07
420 | feeder2_line85 | 1 | 99 | 0.077268 | 0.077275 | 0.078049 | 0.078055
420 | feeder2_line85 | 2 | 99 | 4.9982e-08 | 4.642e-07 | 5.0487e-08 | 4.6889e-07
420 | feeder2_line85 | 3 | 99 | 4.9814e-08 | 4.6605e-07 | 5.0317e-08 | 4.7075e-07
420 | feeder2_line86 | 1 | 354.6 | 78.3686 | 78.3748 | 22.1006 | 22.1023
420 | feeder2_line86 | 2 | 354.6 | 95.5321 | 95.5262 | 26.9408 | 26.9392
420 | feeder2_line86 | 3 | 354.6 | 96.525 | 96.5226 | 27.2208 | 27.2201
420 | feeder2_line87 | 1 | 354.6 | 78.3687 | 78.3748 | 22.1006 | 22.1023
420 | feeder2_line87 | 2 | 354.6 | 96.4398 | 96.4337 | 27.1968 | 27.1951
420 | feeder2_line87 | 3 | 354.6 | 98.1745 | 98.172 | 27.686 | 27.6853
420 | feeder2_line88 | 1 | 354.6 | 0.00011253 | 3.3627e-06 | 3.1734e-05 | 9.483e-07
420 | feeder2_line88 | 2 | 354.6 | 2.4921 | 2.492 | 0.70278 | 0.70277
420 | feeder2_line88 | 3 | 354.6 | 1.6821 | 1.6819 | 0.47436 | 0.47432
420 | feeder2_line89 | 1 | 354.6 | 78.3665 | 78.3748 | 22.1 | 22.1023
420 | feeder2_line89 | 2 | 354.6 | 97.1597 | 97.1559 | 27.3998 | 27.3987
420 | feeder2_line89 | 3 | 354.6 | 98.1722 | 98.172 | 27.6853 | 27.6853
420 | feeder2_line90 | 1 | 354.6 | 0.00072202 | 2.0299e-06 | 0.00020362 | 5.7245e-07
420 | feeder2_line90 | 2 | 354.6 | 1.4583 | 1.4582 | 0.41124 | 0.41122
420 | feeder2_line90 | 3 | 354.6 | 0.00072971 | 2.0432e-06 | 0.00020578 | 5.762e-07
420 | feeder2_line91 | 1 | 354.6 | 78.3664 | 78.3748 | 22.1 | 22.1023
420 | feeder2_line91 | 2 | 354.6 | 97.1596 | 97.1559 | 27.3998 | 27.3987
420 | feeder2_line91 | 3 | 354.6 | 98.2328 | 98.2326 | 27.7024 | 27.7024
420 | feeder2_line92 | 1 | 354.6 | 1.1724e-11 | 1.0242e-06 | 3.3062e-12 | 2.8884e-07
420 | feeder2_line92 | 2 | 354.6 | 1.1386e-11 | 1.0268e-06 | 3.2111e-12 | 2.8956e-07
420 | feeder2_line92 | 3 | 354.6 | 0.061283 | 0.061282 | 0.017282 | 0.017282
420 | feeder2_line93 | 1 | 99 | 2.5225e-08 | 3.418e-07 | 2.548e-08 | 3.4525e-07
420 | feeder2_line93 | 2 | 99 | 1.3352 | 1.3351 | 1.3487 | 1.3486
420 | feeder2_line93 | 3 | 99 | 2.4917e-08 | 3.4415e-07 | 2.5169e-08 | 3.4763e-07
420 | feeder2_line94 | 1 | 354.6 | 2.5226e-06 | 1.6645e-06 | 7.1138e-07 | 4.694e-07
420 | feeder2_line94 | 2 | 354.6 | 0.1946 | 0.19459 | 0.054878 | 0.054875
420 | feeder2_line94 | 3 | 354.6 | 2.4917e-06 | 1.6752e-06 | 7.0267e-07 | 4.7241e-07
420 | feeder2_line95 | 1 | 99 | 3.5634e-06 | 2.6077e-06 | 3.5993e-06 | 2.634e-06
420 | feeder2_line95 | 2 | 99 | 2.492 | 2.492 | 2.5172 | 2.5172
420 | feeder2_line95 | 3 | 99 | 3.5931e-06 | 2.625e-06 | 3.6294e-06 | 2.6515e-06
420 | feeder2_line96 | 1 | 354.6 | 0.00012096 | 6.217e-07 | 3.4112e-05 | 1.7532e-07
420 | feeder2_line96 | 2 | 354.6 | 0.00012136 | 6.2346e-07 | 3.4226e-05 | 1.7582e-07
420 | feeder2_line96 | 3 | 354.6 | 1.6821 | 1.6819 | 0.47435 | 0.47432
420 | feeder2_line97 | 1 | 354.6 | 78.8985 | 78.9067 | 22.25 | 22.2523
420 | feeder2_line97 | 2 | 354.6 | 97.1599 | 97.1559 | 27.3999 | 27.3987
420 | feeder2_line97 | 3 | 354.6 | 98.233 | 98.2326 | 27.7025 | 27.7024
420 | feeder2_line98 | 1 | 354.6 | 1.3553 | 1.3545 | 0.38221 | 0.38197
420 | feeder2_line98 | 2 | 354.6 | 0.0017128 | 6.2235e-07 | 0.00048303 | 1.7551e-07
420 | feeder2_line98 | 3 | 354.6 | 0.0017138 | 6.2592e-07 | 0.00048329 | 1.7651e-07
420 | feeder2_line99 | 1 | 99 | 2.5207e-08 | 4.4687e-07 | 2.5462e-08 | 4.5139e-07
420 | feeder2_line99 | 2 | 99 | 2.4988e-08 | 4.4804e-07 | 2.5241e-08 | 4.5256e-07
420 | feeder2_line99 | 3 | 99 | 1.682 | 1.6819 | 1.699 | 1.6989
420 | feeder2_line100 | 1 | 99 | 1.3545 | 1.3545 | 1.3681 | 1.3682
420 | feeder2_line100 | 2 | 99 | 2.5002e-08 | 6.1539e-07 | 2.5255e-08 | 6.2161e-07
420 | feeder2_line100 | 3 | 99 | 2.4919e-08 | 6.1791e-07 | 2.5171e-08 | 6.2415e-07
420 | feeder2_line101 | 1 | 354.6 | 0.19501 | 0.19463 | 0.054995 | 0.054888
420 | feeder2_line101 | 2 | 354.6 | 8.2205 | 8.2202 | 2.3183 | 2.3182
420 | feeder2_line101 | 3 | 354.6 | 4.5803 | 4.58 | 1.2917 | 1.2916
420 | feeder2_line102 | 1 | 99 | 2.3177 | 2.3177 | 2.3411 | 2.3411
420 | feeder2_line102 | 2 | 99 | 2.3423e-06 | 8.7946e-07 | 2.3659e-06 | 8.8834e-07
420 | feeder2_line102 | 3 | 99 | 2.3507e-06 | 8.8297e-07 | 2.3744e-06 | 8.9188e-07
420 | feeder2_line103 | 1 | 99 | 5.4862e-07 | 8.0322e-07 | 5.5416e-07 | 8.1134e-07
420 | feeder2_line103 | 2 | 99 | 1.4975 | 1.4975 | 1.5126 | 1.5126
420 | feeder2_line103 | 3 | 99 | 5.5248e-07 | 8.0818e-07 | 5.5806e-07 | 8.1634e-07
420 | feeder2_line104 | 1 | 354.6 | 0.19491 | 0.19463 | 0.054967 | 0.054888
420 | feeder2_line104 | 2 | 354.6 | 7.0367 | 7.0364 | 1.9844 | 1.9843
420 | feeder2_line104 | 3 | 354.6 | 4.5803 | 4.58 | 1.2917 | 1.2916
420 | feeder2_line105 | 1 | 99 | 2.5418e-06 | 7.3908e-07 | 2.5674e-06 | 7.4654e-07
420 | feeder2_line105 | 2 | 99 | 2.5504e-06 | 7.4065e-07 | 2.5762e-06 | 7.4813e-07
420 | feeder2_line105 | 3 | 99 | 0.51947 | 0.51944 | 0.52471 | 0.52469
420 | feeder2_line106 | 1 | 354.6 | 0.19486 | 0.19463 | 0.054951 | 0.054888
420 | feeder2_line106 | 2 | 354.6 | 7.0366 | 7.0364 | 1.9844 | 1.9843
420 | feeder2_line106 | 3 | 354.6 | 4.1782 | 4.178 | 1.1783 | 1.1782
420 | feeder2_line107 | 1 | 99 | 3.2466e-07 | 9.0068e-07 | 3.2794e-07 | 9.0978e-07
420 | feeder2_line107 | 2 | 99 | 0.11616 | 0.11614 | 0.11733 | 0.11731
420 | feeder2_line107 | 3 | 99 | 3.2601e-07 | 9.0618e-07 | 3.2931e-07 | 9.1534e-07
420 | feeder2_line108 | 1 | 354.6 | 0.19485 | 0.19463 | 0.054948 | 0.054888
420 | feeder2_line108 | 2 | 354.6 | 6.9216 | 6.9215 | 1.952 | 1.9519
420 | feeder2_line108 | 3 | 354.6 | 4.1782 | 4.178 | 1.1783 | 1.1782
420 | feeder2_line109 | 1 | 354.6 | 79.0728 | 79.0798 | 22.2991 | 22.3011
420 | feeder2_line109 | 2 | 354.6 | 97.161 | 97.1559 | 27.4002 | 27.3987
420 | feeder2_line109 | 3 | 354.6 | 98.2342 | 98.2326 | 27.7028 | 27.7024
420 | feeder2_line110 | 1 | 99 | 0.17955 | 0.17876 | 0.18137 | 0.18057
420 | feeder2_line110 | 2 | 99 | 0.00080648 | 9.1065e-07 | 0.00081462 | 9.1985e-07
420 | feeder2_line110 | 3 | 99 | 0.00081077 | 9.1481e-07 | 0.00081896 | 9.2405e-07
420 | feeder2_line111 | 1 | 99 | 2.52e-08 | 3.8167e-07 | 2.5454e-08 | 3.8553e-07
420 | feeder2_line111 | 2 | 99 | 2.4699 | 2.47 | 2.4949 | 2.4949
420 | feeder2_line111 | 3 | 99 | 2.4913e-08 | 3.842e-07 | 2.5165e-08 | 3.8809e-07
420 | feeder2_line112 | 1 | 99 | 3.2483e-07 | 9.1716e-07 | 3.2811e-07 | 9.2643e-07
420 | feeder2_line112 | 2 | 99 | 0.040746 | 0.040732 | 0.041158 | 0.041143
420 | feeder2_line112 | 3 | 99 | 3.2632e-07 | 9.2327e-07 | 3.2962e-07 | 9.3259e-07
420 | feeder2_line113 | 1 | 99 | 0.09766 | 0.097664 | 0.098646 | 0.098651
420 | feeder2_line113 | 2 | 99 | 3.256e-07 | 9.0764e-07 | 3.2889e-07 | 9.1681e-07
420 | feeder2_line113 | 3 | 99 | 3.2668e-07 | 9.1138e-07 | 3.2998e-07 | 9.2059e-07
420 | feeder2_line114 | 1 | 99 | 1.4962 | 1.4962 | 1.5113 | 1.5113
420 | feeder2_line114 | 2 | 99 | 2.4988e-08 | 4.3733e-07 | 2.524e-08 | 4.4175e-07
420 | feeder2_line114 | 3 | 99 | 2.4894e-08 | 4.3906e-07 | 2.5146e-08 | 4.435e-07
420 | feeder2_line115 | 1 | 99 | 2.5178e-08 | 5.6207e-07 | 2.5432e-08 | 5.6775e-07
420 | feeder2_line115 | 2 | 99 | 0.33214 | 0.33214 | 0.3355 | 0.33549
420 | feeder2_line115 | 3 | 99 | 2.4892e-08 | 5.6549e-07 | 2.5143e-08 | 5.712e-07
420 | feeder2_line116 | 1 | 354.6 | 0.19485 | 0.19463 | 0.05495 | 0.054888
420 | feeder2_line116 | 2 | 354.6 | 6.5895 | 6.5894 | 1.8583 | 1.8583
420 | feeder2_line116 | 3 | 354.6 | 4.1782 | 4.178 | 1.1783 | 1.1782
420 | feeder2_line117 | 1 | 99 | 5.0549e-08 | 6.424e-07 | 5.1059e-08 | 6.4889e-07
420 | feeder2_line117 | 2 | 99 | 1.2585 | 1.2585 | 1.2712 | 1.2712
420 | feeder2_line117 | 3 | 99 | 4.9867e-08 | 6.4726e-07 | 5.037e-08 | 6.538e-07
420 | feeder2_line118 | 1 | 354.6 | 79.0728 | 79.0798 | 22.2991 | 22.3011
420 | feeder2_line118 | 2 | 354.6 | 97.6655 | 97.6603 | 27.5424 | 27.541
420 | feeder2_line118 | 3 | 354.6 | 98.2342 | 98.2326 | 27.7028 | 27.7024
420 | feeder2_line119 | 1 | 99 | 2.5168e-08 | 6.0483e-07 | 2.5422e-08 | 6.1094e-07
420 | feeder2_line119 | 2 | 99 | 2.4988e-08 | 6.06e-07 | 2.524e-08 | 6.1212e-07
420 | feeder2_line119 | 3 | 99 | 1.4137 | 1.4137 | 1.428 | 1.428
420 | feeder2_line120 | 1 | 354.6 | 0.19486 | 0.19463 | 0.054951 | 0.054888
420 | feeder2_line120 | 2 | 354.6 | 6.5895 | 6.5894 | 1.8583 | 1.8583
420 | feeder2_line120 | 3 | 354.6 | 2.8103 | 2.8101 | 0.79254 | 0.79248
420 | feeder2_line121 | 1 | 99 | 3.2467e-07 | 9.3661e-07 | 3.2795e-07 | 9.4607e-07
420 | feeder2_line121 | 2 | 99 | 0.044022 | 0.04402 | 0.044467 | 0.044465
420 | feeder2_line121 | 3 | 99 | 3.2598e-07 | 9.4221e-07 | 3.2928e-07 | 9.5173e-07
420 | feeder2_line122 | 1 | 354.6 | 0.19484 | 0.19463 | 0.054947 | 0.054888
420 | feeder2_line122 | 2 | 354.6 | 6.5455 | 6.5453 | 1.8459 | 1.8458
420 | feeder2_line122 | 3 | 354.6 | 2.8103 | 2.8101 | 0.79253 | 0.79248
420 | feeder2_line123 | 1 | 99 | 5.7384e-07 | 9.7056e-07 | 5.7964e-07 | 9.8036e-07
420 | feeder2_line123 | 2 | 99 | 5.7489e-07 | 9.7229e-07 | 5.8069e-07 | 9.8211e-07
420 | feeder2_line123 | 3 | 99 | 0.76502 | 0.765 | 0.77275 | 0.77272
420 | feeder2_line124 | 1 | 354.6 | 0.19475 | 0.19463 | 0.054921 | 0.054888
420 | feeder2_line124 | 2 | 354.6 | 6.5454 | 6.5453 | 1.8459 | 1.8458
420 | feeder2_line124 | 3 | 354.6 | 2.0743 | 2.0741 | 0.58496 | 0.58491
420 | feeder2_line125 | 1 | 99 | 5.7384e-07 | 9.0223e-07 | 5.7964e-07 | 9.1135e-07
420 | feeder2_line125 | 2 | 99 | 5.7487e-07 | 9.0383e-07 | 5.8068e-07 | 9.1296e-07
420 | feeder2_line125 | 3 | 99 | 1.357 | 1.357 | 1.3707 | 1.3707
420 | feeder2_line126 | 1 | 354.6 | 0.19491 | 0.19463 | 0.054966 | 0.054888
420 | feeder2_line126 | 2 | 354.6 | 6.5456 | 6.5453 | 1.8459 | 1.8458
420 | feeder2_line126 | 3 | 354.6 | 0.92362 | 0.92331 | 0.26047 | 0.26038
420 | feeder2_line127 | 1 | 99 | 5.7385e-07 | 1.0801e-06 | 5.7964e-07 | 1.091e-06
420 | feeder2_line127 | 2 | 99 | 5.7485e-07 | 1.082e-06 | 5.8066e-07 | 1.0929e-06
420 | feeder2_line127 | 3 | 99 | 0.076676 | 0.076674 | 0.07745 | 0.077449
420 | feeder2_line128 | 1 | 354.6 | 0.19483 | 0.19463 | 0.054943 | 0.054888
420 | feeder2_line128 | 2 | 354.6 | 6.5455 | 6.5453 | 1.8459 | 1.8458
420 | feeder2_line128 | 3 | 354.6 | 0.84712 | 0.84689 | 0.23889 | 0.23883
420 | feeder2_line129 | 1 | 99 | 5.4868e-07 | 8.7583e-07 | 5.5422e-07 | 8.8467e-07
420 | feeder2_line129 | 2 | 99 | 6.5453 | 6.5453 | 6.6114 | 6.6115
420 | feeder2_line129 | 3 | 99 | 5.5241e-07 | 8.8103e-07 | 5.5799e-07 | 8.8993e-07
420 | feeder2_line130 | 1 | 354.6 | 0.19484 | 0.19463 | 0.054947 | 0.054888
420 | feeder2_line130 | 2 | 354.6 | 0.0003083 | 4.6427e-06 | 8.6942e-05 | 1.3093e-06
420 | feeder2_line130 | 3 | 354.6 | 0.84714 | 0.84689 | 0.2389 | 0.23883
420 | feeder2_line131 | 1 | 99 | 5.7385e-07 | 9.7073e-07 | 5.7965e-07 | 9.8053e-07
420 | feeder2_line131 | 2 | 99 | 5.7484e-07 | 9.7236e-07 | 5.8065e-07 | 9.8219e-07
420 | feeder2_line131 | 3 | 99 | 0.77052 | 0.77052 | 0.77831 | 0.77831
420 | feeder2_line132 | 1 | 354.6 | 0.19468 | 0.19463 | 0.054901 | 0.054888
420 | feeder2_line132 | 2 | 354.6 | 0.00012579 | 2.9189e-06 | 3.5474e-05 | 8.2314e-07
420 | feeder2_line132 | 3 | 354.6 | 0.076745 | 0.076674 | 0.021643 | 0.021623
420 | feeder2_line133 | 1 | 99 | 0.1946 | 0.19463 | 0.19657 | 0.1966
420 | feeder2_line133 | 2 | 99 | 2.9992e-07 | 9.8013e-07 | 3.0295e-07 | 9.9003e-07
420 | feeder2_line133 | 3 | 99 | 3.0109e-07 | 9.8429e-07 | 3.0413e-07 | 9.9423e-07
420 | feeder2_line134 | 1 | 354.6 | 2.0737e-12 | 1.7848e-06 | 5.848e-13 | 5.0332e-07
420 | feeder2_line134 | 2 | 354.6 | 1.0308e-11 | 1.7874e-06 | 2.907e-12 | 5.0406e-07
420 | feeder2_line134 | 3 | 354.6 | 0.076675 | 0.076674 | 0.021623 | 0.021623
420 | feeder2_line135 | 1 | 99 | 0.052893 | 0.052941 | 0.053427 | 0.053476
420 | feeder2_line135 | 2 | 99 | 5.0017e-08 | 5.876e-07 | 5.0522e-08 | 5.9354e-07
420 | feeder2_line135 | 3 | 99 | 4.9882e-08 | 5.9007e-07 | 5.0386e-08 | 5.9603e-07
420 | feeder2_line136 | 1 | 354.6 | 79.1241 | 79.1312 | 22.3136 | 22.3156
420 | feeder2_line136 | 2 | 354.6 | 97.6655 | 97.6603 | 27.5424 | 27.541
420 | feeder2_line136 | 3 | 354.6 | 98.2342 | 98.2326 | 27.7028 | 27.7024
420 | feeder2_line137 | 1 | 99 | 0.83166 | 0.83168 | 0.84006 | 0.84009
420 | feeder2_line137 | 2 | 99 | 8.5286e-07 | 1.5828e-06 | 8.6148e-07 | 1.5988e-06
420 | feeder2_line137 | 3 | 99 | 8.5655e-07 | 1.5894e-06 | 8.6521e-07 | 1.6055e-06
420 | feeder2_line138 | 1 | 354.6 | 79.4494 | 79.4565 | 22.4054 | 22.4074
420 | feeder2_line138 | 2 | 354.6 | 97.6656 | 97.6603 | 27.5425 | 27.541
420 | feeder2_line138 | 3 | 354.6 | 98.2343 | 98.2326 | 27.7028 | 27.7024
420 | feeder2_line139 | 1 | 99 | 5.0622e-08 | 4.9136e-07 | 5.1133e-08 | 4.9633e-07
420 | feeder2_line139 | 2 | 99 | 5.0032e-08 | 4.9323e-07 | 5.0537e-08 | 4.9821e-07
420 | feeder2_line139 | 3 | 99 | 0.13648 | 0.13628 | 0.13786 | 0.13766
420 | feeder2_line140 | 1 | 354.6 | 79.4495 | 79.4565 | 22.4054 | 22.4074
420 | feeder2_line140 | 2 | 354.6 | 97.6656 | 97.6603 | 27.5425 | 27.541
420 | feeder2_line140 | 3 | 354.6 | 98.3705 | 98.3685 | 27.7413 | 27.7407
420 | feeder2_line141 | 1 | 99 | 2.5197e-06 | 4.8605e-07 | 2.5451e-06 | 4.9096e-07
420 | feeder2_line141 | 2 | 99 | 0.18988 | 0.18987 | 0.1918 | 0.19179
420 | feeder2_line141 | 3 | 99 | 2.5486e-06 | 4.9002e-07 | 2.5743e-06 | 4.9497e-07
420 | feeder2_line142 | 1 | 354.6 | 79.4494 | 79.4565 | 22.4054 | 22.4074
420 | feeder2_line142 | 2 | 354.6 | 97.8515 | 97.8464 | 27.5949 | 27.5934
420 | feeder2_line142 | 3 | 354.6 | 98.3703 | 98.3685 | 27.7412 | 27.7407
420 | feeder2_line143 | 1 | 99 | 8.4963e-07 | 1.7272e-06 | 8.5821e-07 | 1.7446e-06
420 | feeder2_line143 | 2 | 99 | 0.11583 | 0.11581 | 0.117 | 0.11698
420 | feeder2_line143 | 3 | 99 | 8.5696e-07 | 1.7413e-06 | 8.6561e-07 | 1.7589e-06
420 | feeder2_line144 | 1 | 354.6 | 79.4492 | 79.4565 | 22.4053 | 22.4074
420 | feeder2_line144 | 2 | 354.6 | 97.9667 | 97.9617 | 27.6274 | 27.626
420 | feeder2_line144 | 3 | 354.6 | 98.3701 | 98.3685 | 27.7412 | 27.7407
420 | feeder2_line145 | 1 | 99 | 2.5322e-08 | 4.8432e-07 | 2.5577e-08 | 4.8921e-07
420 | feeder2_line145 | 2 | 99 | 0.069337 | 0.06933 | 0.070037 | 0.07003
420 | feeder2_line145 | 3 | 99 | 2.4951e-08 | 4.8831e-07 | 2.5203e-08 | 4.9324e-07
420 | feeder2_line146 | 1 | 354.6 | 79.4491 | 79.4565 | 22.4053 | 22.4074
420 | feeder2_line146 | 2 | 354.6 | 98.035 | 98.0301 | 27.6467 | 27.6453
420 | feeder2_line146 | 3 | 354.6 | 98.37 | 98.3685 | 27.7411 | 27.7407
420 | feeder2_line147 | 1 | 99 | 0.081086 | 0.08109 | 0.081905 | 0.08191
420 | feeder2_line147 | 2 | 99 | 1.1545e-06 | 2.2429e-06 | 1.1662e-06 | 2.2656e-06
420 | feeder2_line147 | 3 | 99 | 1.1595e-06 | 2.2524e-06 | 1.1712e-06 | 2.2752e-06
420 | feeder2_line148 | 1 | 99 | 0.085118 | 0.085127 | 0.085978 | 0.085987
420 | feeder2_line148 | 2 | 99 | 6.0229e-07 | 1.5029e-06 | 6.0837e-07 | 1.5181e-06
420 | feeder2_line148 | 3 | 99 | 6.0468e-07 | 1.5093e-06 | 6.1079e-07 | 1.5245e-06
420 | feeder2_line149 | 1 | 354.6 | 79.6116 | 79.6189 | 22.4511 | 22.4531
420 | feeder2_line149 | 2 | 354.6 | 98.0352 | 98.0301 | 27.6467 | 27.6453
420 | feeder2_line149 | 3 | 354.6 | 98.3702 | 98.3685 | 27.7412 | 27.7407
420 | feeder2_line150 | 1 | 354.6 | 79.6116 | 79.6189 | 22.4511 | 22.4531
420 | feeder2_line150 | 2 | 354.6 | 99.0001 | 98.9949 | 27.9188 | 27.9173
420 | feeder2_line150 | 3 | 354.6 | 98.3703 | 98.3685 | 27.7412 | 27.7407
420 | feeder2_line151 | 1 | 99 | 9.7281e-06 | 1.7778e-06 | 9.8264e-06 | 1.7958e-06
420 | feeder2_line151 | 2 | 99 | 1.5629 | 1.5629 | 1.5787 | 1.5787
420 | feeder2_line151 | 3 | 99 | 9.8532e-06 | 1.7931e-06 | 9.9527e-06 | 1.8112e-06
420 | feeder2_line152 | 1 | 354.6 | 1.2277e-11 | 1.1852e-06 | 3.4621e-12 | 3.3423e-07
420 | feeder2_line152 | 2 | 354.6 | 5.4987e-12 | 1.19e-06 | 1.5507e-12 | 3.3559e-07
420 | feeder2_line152 | 3 | 354.6 | 0.076209 | 0.076208 | 0.021492 | 0.021491
420 | feeder2_line153 | 1 | 99 | 0.0441 | 0.044103 | 0.044545 | 0.044548
420 | feeder2_line153 | 2 | 99 | 5.0055e-08 | 5.9544e-07 | 5.056e-08 | 6.0146e-07
420 | feeder2_line153 | 3 | 99 | 4.993e-08 | 5.9798e-07 | 5.0434e-08 | 6.0402e-07
420 | feeder2_line154 | 1 | 99 | 5.7517e-07 | 8.8208e-07 | 5.8098e-07 | 8.9099e-07
420 | feeder2_line154 | 2 | 99 | 5.7779e-07 | 8.8605e-07 | 5.8363e-07 | 8.95e-07
420 | feeder2_line154 | 3 | 99 | 0.040403 | 0.040369 | 0.040811 | 0.040776
420 | feeder2_line155 | 1 | 99 | 79.6541 | 79.6614 | 80.4587 | 80.4661
420 | feeder2_line155 | 2 | 99 | 99 | 98.9949 | 100 | 99.9948
420 | feeder2_line155 | 3 | 99 | 98.4854 | 98.4837 | 99.4802 | 99.4785
420 | feeder2_line156 | 1 | 99 | 6.0039e-07 | 1.1609e-06 | 6.0645e-07 | 1.1726e-06
420 | feeder2_line156 | 2 | 99 | 1.4991 | 1.4991 | 1.5143 | 1.5143
420 | feeder2_line156 | 3 | 99 | 6.0497e-07 | 1.1708e-06 | 6.1109e-07 | 1.1827e-06
420 | feeder2_line157 | 1 | 99 | 2.5349e-08 | 2.5202e-07 | 2.5605e-08 | 2.5456e-07
420 | feeder2_line157 | 2 | 99 | 0.089304 | 0.089301 | 0.090207 | 0.090203
420 | feeder2_line157 | 3 | 99 | 2.4958e-08 | 2.5419e-07 | 2.521e-08 | 2.5675e-07
450 | feeder2_line1 | 1 | 354.6 | 84.3828 | 84.3687 | 23.7966 | 23.7926
450 | feeder2_line1 | 2 | 354.6 | 85.3085 | 85.3188 | 24.0577 | 24.0606
450 | feeder2_line1 | 3 | 354.6 | 59.3477 | 59.3553 | 16.7365 | 16.7387
450 | feeder2_line2 | 1 | 354.6 | 85.633 | 85.6187 | 24.1492 | 24.1451
450 | feeder2_line2 | 2 | 354.6 | 85.3087 | 85.3188 | 24.0577 | 24.0606
450 | feeder2_line2 | 3 | 354.6 | 59.3479 | 59.3553 | 16.7366 | 16.7387
450 | feeder2_line3 | 1 | 80.1 | 1.2964 | 1.2964 | 1.6185 | 1.6185
450 | feeder2_line3 | 2 | 80.1 | 5.7204e-07 | 1.0571e-06 | 7.1416e-07 | 1.3197e-06
450 | feeder2_line3 | 3 | 80.1 | 5.7074e-07 | 1.0547e-06 | 7.1253e-07 | 1.3168e-06
450 | feeder2_line4 | 1 | 354.6 | 85.6332 | 85.6187 | 24.1492 | 24.1451
450 | feeder2_line4 | 2 | 354.6 | 85.9007 | 85.9107 | 24.2247 | 24.2275
450 | feeder2_line4 | 3 | 354.6 | 59.348 | 59.3553 | 16.7366 | 16.7387
450 | feeder2_line5 | 1 | 80.1 | 5.7215e-07 | 9.9834e-07 | 7.1429e-07 | 1.2464e-06
450 | feeder2_line5 | 2 | 80.1 | 1.5293 | 1.5293 | 1.9092 | 1.9092
450 | feeder2_line5 | 3 | 80.1 | 5.7074e-07 | 9.9591e-07 | 7.1254e-07 | 1.2433e-06
450 | feeder2_line6 | 1 | 80.1 | 5.7224e-07 | 1.1746e-06 | 7.144e-07 | 1.4664e-06
450 | feeder2_line6 | 2 | 80.1 | 5.7216e-07 | 1.1744e-06 | 7.143e-07 | 1.4662e-06
450 | feeder2_line6 | 3 | 80.1 | 1.2584 | 1.2584 | 1.571 | 1.571
450 | feeder2_line7 | 1 | 354.6 | 85.6333 | 85.6187 | 24.1493 | 24.1451
450 | feeder2_line7 | 2 | 354.6 | 85.9008 | 85.9107 | 24.2247 | 24.2275
450 | feeder2_line7 | 3 | 354.6 | 59.5686 | 59.5757 | 16.7988 | 16.8008
450 | feeder2_line8 | 1 | 80.1 | 0.072536 | 0.072534 | 0.090557 | 0.090554
450 | feeder2_line8 | 2 | 80.1 | 5.7238e-07 | 1.1329e-06 | 7.1458e-07 | 1.4143e-06
450 | feeder2_line8 | 3 | 80.1 | 5.7076e-07 | 1.1297e-06 | 7.1255e-07 | 1.4103e-06
450 | feeder2_line9 | 1 | 354.6 | 85.7042 | 85.6895 | 24.1693 | 24.1651
450 | feeder2_line9 | 2 | 354.6 | 85.9008 | 85.9107 | 24.2247 | 24.2275
450 | feeder2_line9 | 3 | 354.6 | 59.5686 | 59.5757 | 16.7988 | 16.8008
450 | feeder2_line10 | 1 | 80.1 | 8.4636e-07 | 1.4961e-06 | 1.0566e-06 | 1.8678e-06
450 | feeder2_line10 | 2 | 80.1 | 0.072588 | 0.07259 | 0.090622 | 0.090624
450 | feeder2_line10 | 3 | 80.1 | 8.4365e-07 | 1.4916e-06 | 1.0532e-06 | 1.8622e-06
450 | feeder2_line11 | 1 | 354.6 | 85.7042 | 85.6895 | 24.1693 | 24.1651
450 | feeder2_line11 | 2 | 354.6 | 85.9707 | 85.9806 | 24.2444 | 24.2472
450 | feeder2_line11 | 3 | 354.6 | 59.5686 | 59.5757 | 16.7988 | 16.8008
450 | feeder2_line12 | 1 | 80.1 | 5.4783e-07 | 9.9256e-07 | 6.8393e-07 | 1.2392e-06
450 | feeder2_line12 | 2 | 80.1 | 5.4763e-07 | 9.9241e-07 | 6.8369e-07 | 1.239e-06
450 | feeder2_line12 | 3 | 80.1 | 0.17762 | 0.17762 | 0.22174 | 0.22174
450 | feeder2_line13 | 1 | 354.6 | 85.7042 | 85.6895 | 24.1693 | 24.1651
450 | feeder2_line13 | 2 | 354.6 | 85.9707 | 85.9806 | 24.2444 | 24.2472
450 | feeder2_line13 | 3 | 354.6 | 59.7432 | 59.7503 | 16.8481 | 16.8501
450 | feeder2_line14 | 1 | 80.1 | 2.6805 | 2.6805 | 3.3464 | 3.3464
450 | feeder2_line14 | 2 | 80.1 | 2.9871e-07 | 6.4722e-07 | 3.7292e-07 | 8.0801e-07
450 | feeder2_line14 | 3 | 80.1 | 2.9788e-07 | 6.452e-07 | 3.7189e-07 | 8.0549e-07
450 | feeder2_line15 | 1 | 354.6 | 87.7205 | 87.7058 | 24.7379 | 24.7337
450 | feeder2_line15 | 2 | 354.6 | 85.9707 | 85.9806 | 24.2444 | 24.2472
450 | feeder2_line15 | 3 | 354.6 | 59.7432 | 59.7503 | 16.8481 | 16.8501
450 | feeder2_line16 | 1 | 80.1 | 5.728e-07 | 1.0319e-06 | 7.1511e-07 | 1.2883e-06
450 | feeder2_line16 | 2 | 80.1 | 0.25447 | 0.25447 | 0.31769 | 0.31769
450 | feeder2_line16 | 3 | 80.1 | 5.7077e-07 | 1.0283e-06 | 7.1258e-07 | 1.2838e-06
450 | feeder2_line17 | 1 | 354.6 | 87.7205 | 87.7058 | 24.7379 | 24.7337
450 | feeder2_line17 | 2 | 354.6 | 86.2099 | 86.2197 | 24.3119 | 24.3146
450 | feeder2_line17 | 3 | 354.6 | 59.7433 | 59.7503 | 16.8481 | 16.8501
450 | feeder2_line18 | 1 | 80.1 | 5.4868e-07 | 7.3944e-07 | 6.8499e-07 | 9.2314e-07
450 | feeder2_line18 | 2 | 80.1 | 5.4836e-07 | 7.3921e-07 | 6.8459e-07 | 9.2286e-07
450 | feeder2_line18 | 3 | 80.1 | 0.47533 | 0.47536 | 0.59342 | 0.59346
450 | feeder2_line19 | 1 | 354.6 | 87.7206 | 87.7058 | 24.7379 | 24.7337
450 | feeder2_line19 | 2 | 354.6 | 86.2099 | 86.2197 | 24.3119 | 24.3146
450 | feeder2_line19 | 3 | 354.6 | 60.1745 | 60.1816 | 16.9697 | 16.9717
450 | feeder2_line20 | 1 | 99 | 5.4891e-07 | 8.869e-07 | 5.5446e-07 | 8.9585e-07
450 | feeder2_line20 | 2 | 99 | 5.4855e-07 | 8.8658e-07 | 5.5409e-07 | 8.9554e-07
450 | feeder2_line20 | 3 | 99 | 1.4001 | 1.4001 | 1.4142 | 1.4143
450 | feeder2_line21 | 1 | 354.6 | 87.7207 | 87.7058 | 24.7379 | 24.7337
450 | feeder2_line21 | 2 | 354.6 | 86.21 | 86.2197 | 24.3119 | 24.3146
450 | feeder2_line21 | 3 | 354.6 | 60.4513 | 60.4582 | 17.0477 | 17.0497
450 | feeder2_line22 | 1 | 99 | 5.7378e-07 | 1.017e-06 | 5.7958e-07 | 1.0272e-06
450 | feeder2_line22 | 2 | 99 | 1.8486 | 1.8486 | 1.8673 | 1.8673
450 | feeder2_line22 | 3 | 99 | 5.7082e-07 | 1.0118e-06 | 5.7658e-07 | 1.022e-06
450 | feeder2_line23 | 1 | 99 | 5.7375e-07 | 9.5194e-07 | 5.7954e-07 | 9.6156e-07
450 | feeder2_line23 | 2 | 99 | 5.7352e-07 | 9.5158e-07 | 5.7932e-07 | 9.6119e-07
450 | feeder2_line23 | 3 | 99 | 18.9638 | 18.9637 | 19.1554 | 19.1552
450 | feeder2_line24 | 1 | 354.6 | 87.7207 | 87.7058 | 24.7379 | 24.7337
450 | feeder2_line24 | 2 | 354.6 | 87.9123 | 87.922 | 24.792 | 24.7947
450 | feeder2_line24 | 3 | 354.6 | 77.9012 | 77.9075 | 21.9687 | 21.9705
450 | feeder2_line25 | 1 | 99 | 1.8477 | 1.8477 | 1.8663 | 1.8663
450 | feeder2_line25 | 2 | 99 | 4.9752e-08 | 6.9206e-07 | 5.0255e-08 | 6.9905e-07
450 | feeder2_line25 | 3 | 99 | 5.0236e-08 | 6.8871e-07 | 5.0743e-08 | 6.9567e-07
450 | feeder2_line26 | 1 | 99 | 0.08498 | 0.084971 | 0.085838 | 0.08583
450 | feeder2_line26 | 2 | 99 | 5.4887e-07 | 8.5743e-07 | 5.5441e-07 | 8.6609e-07
450 | feeder2_line26 | 3 | 99 | 5.4582e-07 | 8.5328e-07 | 5.5133e-07 | 8.619e-07
450 | feeder2_line27 | 1 | 354.6 | 89.5538 | 89.5388 | 25.2549 | 25.2507
450 | feeder2_line27 | 2 | 354.6 | 87.9123 | 87.922 | 24.792 | 24.7947
450 | feeder2_line27 | 3 | 354.6 | 77.9012 | 77.9075 | 21.9688 | 21.9705
450 | feeder2_line28 | 1 | 99 | 2.5504e-06 | 7.1251e-07 | 2.5762e-06 | 7.1971e-07
450 | feeder2_line28 | 2 | 99 | 1.264 | 1.264 | 1.2767 | 1.2767
450 | feeder2_line28 | 3 | 99 | 2.5288e-06 | 7.0854e-07 | 2.5543e-06 | 7.157e-07
450 | feeder2_line29 | 1 | 354.6 | 89.5538 | 89.5388 | 25.2549 | 25.2507
450 | feeder2_line29 | 2 | 354.6 | 88.3477 | 88.3574 | 24.9148 | 24.9175
450 | feeder2_line29 | 3 | 354.6 | 77.9012 | 77.9075 | 21.9688 | 21.9705
450 | feeder2_line30 | 1 | 266.4 | 1.5655 | 1.5647 | 0.58763 | 0.58737
450 | feeder2_line30 | 2 | 266.4 | 1.6536 | 1.6537 | 0.62072 | 0.62077
450 | feeder2_line30 | 3 | 266.4 | 3.6743 | 3.6744 | 1.3792 | 1.3793
450 | feeder2_line31 | 1 | 354.6 | 91.0749 | 91.0591 | 25.6838 | 25.6794
450 | feeder2_line31 | 2 | 354.6 | 89.3014 | 89.3107 | 25.1837 | 25.1863
450 | feeder2_line31 | 3 | 354.6 | 79.7522 | 79.758 | 22.4908 | 22.4924
450 | feeder2_line32 | 1 | 354.6 | 91.0749 | 91.0591 | 25.6838 | 25.6794
450 | feeder2_line32 | 2 | 354.6 | 89.5486 | 89.5579 | 25.2534 | 25.256
450 | feeder2_line32 | 3 | 354.6 | 79.7523 | 79.758 | 22.4908 | 22.4924
450 | feeder2_line33 | 1 | 99 | 4.9481e-08 | 6.8837e-07 | 4.9981e-08 | 6.9532e-07
450 | feeder2_line33 | 2 | 99 | 0.25772 | 0.25773 | 0.26032 | 0.26033
450 | feeder2_line33 | 3 | 99 | 5.0395e-08 | 6.8409e-07 | 5.0904e-08 | 6.91e-07
450 | feeder2_line34 | 1 | 354.6 | 91.0749 | 91.0591 | 25.6838 | 25.6794
450 | feeder2_line34 | 2 | 354.6 | 89.5486 | 89.5579 | 25.2534 | 25.256
450 | feeder2_line34 | 3 | 354.6 | 79.8352 | 79.841 | 22.5142 | 22.5158
450 | feeder2_line35 | 1 | 99 | 3.0004e-07 | 7.6246e-07 | 3.0307e-07 | 7.7016e-07
450 | feeder2_line35 | 2 | 99 | 2.999e-07 | 7.619e-07 | 3.0293e-07 | 7.696e-07
450 | feeder2_line35 | 3 | 99 | 0.085994 | 0.085999 | 0.086863 | 0.086867
450 | feeder2_line36 | 1 | 354.6 | 91.1022 | 91.0861 | 25.6915 | 25.687
450 | feeder2_line36 | 2 | 354.6 | 89.5485 | 89.5579 | 25.2534 | 25.256
450 | feeder2_line36 | 3 | 354.6 | 79.8352 | 79.841 | 22.5142 | 22.5158
450 | feeder2_line37 | 1 | 99 | 0.027973 | 0.027598 | 0.028256 | 0.027876
450 | feeder2_line37 | 2 | 99 | 2.9997e-07 | 8.432e-07 | 3.03e-07 | 8.5171e-07
450 | feeder2_line37 | 3 | 99 | 2.9848e-07 | 8.3844e-07 | 3.0149e-07 | 8.4691e-07
450 | feeder2_line38 | 1 | 99 | 3.2456e-07 | 7.7797e-07 | 3.2784e-07 | 7.8583e-07
450 | feeder2_line38 | 2 | 99 | 0.077064 | 0.07707 | 0.077842 | 0.077849
450 | feeder2_line38 | 3 | 99 | 3.2347e-07 | 7.7327e-07 | 3.2674e-07 | 7.8109e-07
450 | feeder2_line39 | 1 | 266.4 | 1.5655 | 1.5647 | 0.58764 | 0.58737
450 | feeder2_line39 | 2 | 266.4 | 1.597 | 1.5971 | 0.59946 | 0.59952
450 | feeder2_line39 | 3 | 266.4 | 3.6743 | 3.6744 | 1.3792 | 1.3793
450 | feeder2_line40 | 1 | 354.6 | 92.858 | 92.8418 | 26.1867 | 26.1821
450 | feeder2_line40 | 2 | 354.6 | 89.5486 | 89.5579 | 25.2534 | 25.256
450 | feeder2_line40 | 3 | 354.6 | 79.8353 | 79.841 | 22.5142 | 22.5158
450 | feeder2_line41 | 1 | 99 | 1.8461 | 1.846 | 1.8647 | 1.8647
450 | feeder2_line41 | 2 | 99 | 4.9854e-08 | 7.3689e-07 | 5.0357e-08 | 7.4434e-07
450 | feeder2_line41 | 3 | 99 | 5.044e-08 | 7.327e-07 | 5.0949e-08 | 7.401e-07
450 | feeder2_line42 | 1 | 99 | 2.9982e-07 | 7.5091e-07 | 3.0285e-07 | 7.585e-07
450 | feeder2_line42 | 2 | 99 | 2.9972e-07 | 7.5045e-07 | 3.0275e-07 | 7.5803e-07
450 | feeder2_line42 | 3 | 99 | 1.2552 | 1.2552 | 1.2679 | 1.2678
450 | feeder2_line43 | 1 | 266.4 | 1.5654 | 1.5647 | 0.5876 | 0.58737
450 | feeder2_line43 | 2 | 266.4 | 1.597 | 1.5971 | 0.59948 | 0.59952
450 | feeder2_line43 | 3 | 266.4 | 2.4315 | 2.4316 | 0.91272 | 0.91275
450 | feeder2_line44 | 1 | 354.6 | 92.8581 | 92.8418 | 26.1867 | 26.1821
450 | feeder2_line44 | 2 | 354.6 | 89.5486 | 89.5579 | 25.2534 | 25.256
450 | feeder2_line44 | 3 | 354.6 | 80.341 | 80.3467 | 22.6568 | 22.6584
450 | feeder2_line45 | 1 | 99 | 4.9488e-08 | 5.8168e-07 | 4.9988e-08 | 5.8756e-07
450 | feeder2_line45 | 2 | 99 | 4.9858e-08 | 5.8121e-07 | 5.0362e-08 | 5.8708e-07
450 | feeder2_line45 | 3 | 99 | 1.4007 | 1.4007 | 1.4148 | 1.4148
450 | feeder2_line46 | 1 | 99 | 5.7491e-07 | 1.3613e-06 | 5.8072e-07 | 1.375e-06
450 | feeder2_line46 | 2 | 99 | 5.7453e-07 | 1.3604e-06 | 5.8034e-07 | 1.3742e-06
450 | feeder2_line46 | 3 | 99 | 1.2539 | 1.2539 | 1.2665 | 1.2665
450 | feeder2_line47 | 1 | 266.4 | 1.5654 | 1.5647 | 0.5876 | 0.58737
450 | feeder2_line47 | 2 | 266.4 | 1.5972 | 1.5971 | 0.59953 | 0.59952
450 | feeder2_line47 | 3 | 266.4 | 1.2563 | 1.2561 | 0.47159 | 0.47153
450 | feeder2_line48 | 1 | 99 | 0.13606 | 0.13605 | 0.13744 | 0.13743
450 | feeder2_line48 | 2 | 99 | 4.9805e-08 | 7.3248e-07 | 5.0308e-08 | 7.3988e-07
450 | feeder2_line48 | 3 | 99 | 5.0365e-08 | 7.2849e-07 | 5.0874e-08 | 7.3585e-07
450 | feeder2_line49 | 1 | 266.4 | 1.4317 | 1.4311 | 0.53743 | 0.5372
450 | feeder2_line49 | 2 | 266.4 | 1.5971 | 1.5971 | 0.59953 | 0.59952
450 | feeder2_line49 | 3 | 266.4 | 1.2563 | 1.2561 | 0.47158 | 0.47153
450 | feeder2_line50 | 1 | 99 | 5.749e-07 | 1.2388e-06 | 5.8071e-07 | 1.2514e-06
450 | feeder2_line50 | 2 | 99 | 1.2614 | 1.2615 | 1.2742 | 1.2742
450 | feeder2_line50 | 3 | 99 | 5.7137e-07 | 1.2313e-06 | 5.7715e-07 | 1.2438e-06
450 | feeder2_line51 | 1 | 99 | 0.044668 | 0.044301 | 0.045119 | 0.044748
450 | feeder2_line51 | 2 | 99 | 5.7454e-07 | 1.3441e-06 | 5.8034e-07 | 1.3577e-06
450 | feeder2_line51 | 3 | 99 | 5.7137e-07 | 1.3368e-06 | 5.7714e-07 | 1.3503e-06
450 | feeder2_line52 | 1 | 266.4 | 1.3869 | 1.3868 | 0.52061 | 0.52058
450 | feeder2_line52 | 2 | 266.4 | 0.47393 | 0.47383 | 0.1779 | 0.17786
450 | feeder2_line52 | 3 | 266.4 | 1.2562 | 1.2562 | 0.47154 | 0.47153
450 | feeder2_line53 | 1 | 99 | 5.5016e-07 | 7.5609e-07 | 5.5572e-07 | 7.6373e-07
450 | feeder2_line53 | 2 | 99 | 0.47383 | 0.47383 | 0.47862 | 0.47862
450 | feeder2_line53 | 3 | 99 | 5.4619e-07 | 7.5151e-07 | 5.5171e-07 | 7.591e-07
450 | feeder2_line54 | 1 | 266.4 | 1.3867 | 1.3868 | 0.52054 | 0.52058
450 | feeder2_line54 | 2 | 266.4 | 8.5654e-05 | 4.6352e-06 | 3.2153e-05 | 1.7399e-06
450 | feeder2_line54 | 3 | 266.4 | 1.2561 | 1.2562 | 0.4715 | 0.47153
450 | feeder2_line55 | 1 | 99 | 0.045346 | 0.045336 | 0.045804 | 0.045794
450 | feeder2_line55 | 2 | 99 | 4.9894e-08 | 7.3263e-07 | 5.0398e-08 | 7.4003e-07
450 | feeder2_line55 | 3 | 99 | 5.05e-08 | 7.2832e-07 | 5.101e-08 | 7.3568e-07
450 | feeder2_line56 | 1 | 354.6 | 92.9025 | 92.8862 | 26.1992 | 26.1946
450 | feeder2_line56 | 2 | 354.6 | 89.5487 | 89.5579 | 25.2534 | 25.256
450 | feeder2_line56 | 3 | 354.6 | 80.341 | 80.3467 | 22.6568 | 22.6584
450 | feeder2_line57 | 1 | 99 | 7.4212e-07 | 1.5487e-06 | 7.4962e-07 | 1.5644e-06
450 | feeder2_line57 | 2 | 99 | 7.47e-07 | 1.5478e-06 | 7.5454e-07 | 1.5634e-06
450 | feeder2_line57 | 3 | 99 | 1.2562 | 1.2562 | 1.2688 | 1.2688
450 | feeder2_line58 | 1 | 266.4 | 1.3868 | 1.3868 | 0.52057 | 0.52058
450 | feeder2_line58 | 2 | 266.4 | 1.9007e-05 | 2.6911e-06 | 7.1347e-06 | 1.0102e-06
450 | feeder2_line58 | 3 | 266.4 | 1.8865e-05 | 2.677e-06 | 7.0813e-06 | 1.0049e-06
450 | feeder2_line59 | 1 | 99 | 4.9473e-08 | 5.3834e-07 | 4.9973e-08 | 5.4378e-07
450 | feeder2_line59 | 2 | 99 | 4.9799e-08 | 5.3802e-07 | 5.0302e-08 | 5.4346e-07
450 | feeder2_line59 | 3 | 99 | 1.127 | 1.127 | 1.1384 | 1.1384
450 | feeder2_line60 | 1 | 99 | 2.9982e-07 | 8.136e-07 | 3.0285e-07 | 8.2182e-07
450 | feeder2_line60 | 2 | 99 | 2.9972e-07 | 8.1311e-07 | 3.0275e-07 | 8.2133e-07
450 | feeder2_line60 | 3 | 99 | 0.17761 | 0.17761 | 0.17941 | 0.17941
450 | feeder2_line61 | 1 | 266.4 | 0.085229 | 0.085386 | 0.031993 | 0.032052
450 | feeder2_line61 | 2 | 266.4 | 1.092 | 1.0923 | 0.40992 | 0.41001
450 | feeder2_line61 | 3 | 266.4 | 2.5099 | 2.5101 | 0.94216 | 0.94225
450 | feeder2_line62 | 1 | 354.6 | 92.9864 | 92.9703 | 26.2229 | 26.2183
450 | feeder2_line62 | 2 | 354.6 | 90.2185 | 90.228 | 25.4423 | 25.445
450 | feeder2_line62 | 3 | 354.6 | 82.4489 | 82.4547 | 23.2512 | 23.2529
450 | feeder2_line63 | 1 | 99 | 1.0906 | 1.0906 | 1.1016 | 1.1016
450 | feeder2_line63 | 2 | 99 | 5.7454e-07 | 1.2225e-06 | 5.8034e-07 | 1.2348e-06
450 | feeder2_line63 | 3 | 99 | 5.7137e-07 | 1.2158e-06 | 5.7714e-07 | 1.2281e-06
450 | feeder2_line64 | 1 | 99 | 0.29628 | 0.29627 | 0.29927 | 0.29926
450 | feeder2_line64 | 2 | 99 | 6.64e-12 | 3.2203e-07 | 6.707e-12 | 3.2529e-07
450 | feeder2_line64 | 3 | 99 | 1.0567e-11 | 3.2027e-07 | 1.0674e-11 | 3.2351e-07
450 | feeder2_line65 | 1 | 99 | 4.9499e-08 | 6.4477e-07 | 4.9999e-08 | 6.5129e-07
450 | feeder2_line65 | 2 | 99 | 1.5322 | 1.5322 | 1.5477 | 1.5477
450 | feeder2_line65 | 3 | 99 | 5.0577e-08 | 6.401e-07 | 5.1088e-08 | 6.4656e-07
450 | feeder2_line66 | 1 | 354.6 | 92.9863 | 92.9703 | 26.2229 | 26.2183
450 | feeder2_line66 | 2 | 354.6 | 90.9107 | 90.9203 | 25.6375 | 25.6403
450 | feeder2_line66 | 3 | 354.6 | 82.4488 | 82.4547 | 23.2512 | 23.2529
450 | feeder2_line67 | 1 | 99 | 2.4744e-08 | 3.6431e-07 | 2.4994e-08 | 3.6799e-07
450 | feeder2_line67 | 2 | 99 | 2.496e-08 | 3.6392e-07 | 2.5212e-08 | 3.6759e-07
450 | feeder2_line67 | 3 | 99 | 1.8513 | 1.8513 | 1.87 | 1.87
450 | feeder2_line68 | 1 | 266.4 | 0.085268 | 0.085386 | 0.032007 | 0.032052
450 | feeder2_line68 | 2 | 266.4 | 1.0921 | 1.0923 | 0.40994 | 0.41001
450 | feeder2_line68 | 3 | 266.4 | 0.83921 | 0.83935 | 0.31502 | 0.31507
450 | feeder2_line69 | 1 | 99 | 1.5617 | 1.5616 | 1.5775 | 1.5774
450 | feeder2_line69 | 2 | 99 | 2.556e-06 | 6.687e-07 | 2.5818e-06 | 6.7545e-07
450 | feeder2_line69 | 3 | 99 | 2.534e-06 | 6.6459e-07 | 2.5596e-06 | 6.7131e-07
450 | feeder2_line70 | 1 | 354.6 | 93.6931 | 93.677 | 26.4222 | 26.4177
450 | feeder2_line70 | 2 | 354.6 | 90.9107 | 90.9203 | 25.6375 | 25.6403
450 | feeder2_line70 | 3 | 354.6 | 82.4487 | 82.4547 | 23.2512 | 23.2529
450 | feeder2_line71 | 1 | 99 | 4.9507e-08 | 7.1961e-07 | 5.0007e-08 | 7.2688e-07
450 | feeder2_line71 | 2 | 99 | 0.052673 | 0.052686 | 0.053205 | 0.053219
450 | feeder2_line71 | 3 | 99 | 5.0606e-08 | 7.1428e-07 | 5.1117e-08 | 7.2149e-07
450 | feeder2_line72 | 1 | 354.6 | 93.6932 | 93.677 | 26.4222 | 26.4177
450 | feeder2_line72 | 2 | 354.6 | 90.9621 | 90.9717 | 25.652 | 25.6547
450 | feeder2_line72 | 3 | 354.6 | 82.4488 | 82.4547 | 23.2512 | 23.2529
450 | feeder2_line73 | 1 | 99 | 6.0114e-07 | 1.5424e-06 | 6.0721e-07 | 1.558e-06
450 | feeder2_line73 | 2 | 99 | 0.25777 | 0.25778 | 0.26038 | 0.26038
450 | feeder2_line73 | 3 | 99 | 5.9752e-07 | 1.5314e-06 | 6.0355e-07 | 1.5469e-06
450 | feeder2_line74 | 1 | 99 | 4.9493e-08 | 4.6002e-07 | 4.9993e-08 | 4.6467e-07
450 | feeder2_line74 | 2 | 99 | 0.84092 | 0.84097 | 0.84941 | 0.84947
450 | feeder2_line74 | 3 | 99 | 5.0541e-08 | 4.5676e-07 | 5.1051e-08 | 4.6138e-07
450 | feeder2_line75 | 1 | 266.4 | 0.085366 | 0.085386 | 0.032044 | 0.032052
450 | feeder2_line75 | 2 | 266.4 | 0.0895 | 0.089539 | 0.033596 | 0.033611
450 | feeder2_line75 | 3 | 266.4 | 0.83929 | 0.83936 | 0.31505 | 0.31507
450 | feeder2_line76 | 1 | 99 | 0.085399 | 0.085386 | 0.086261 | 0.086248
450 | feeder2_line76 | 2 | 99 | 8.5114e-07 | 1.5893e-06 | 8.5974e-07 | 1.6054e-06
450 | feeder2_line76 | 3 | 99 | 8.4573e-07 | 1.5798e-06 | 8.5428e-07 | 1.5957e-06
450 | feeder2_line77 | 1 | 99 | 2.4747e-08 | 5.781e-07 | 2.4997e-08 | 5.8394e-07
450 | feeder2_line77 | 2 | 99 | 2.4959e-08 | 5.7746e-07 | 2.5211e-08 | 5.833e-07
450 | feeder2_line77 | 3 | 99 | 0.83933 | 0.83936 | 0.84781 | 0.84784
450 | feeder2_line78 | 1 | 266.4 | 2.767e-12 | 9.5836e-07 | 1.0387e-12 | 3.5974e-07
450 | feeder2_line78 | 2 | 266.4 | 0.089533 | 0.089538 | 0.033609 | 0.033611
450 | feeder2_line78 | 3 | 266.4 | 1.8131e-11 | 9.5245e-07 | 6.806e-12 | 3.5752e-07
450 | feeder2_line79 | 1 | 354.6 | 3.4703 | 3.4699 | 0.97864 | 0.97854
450 | feeder2_line79 | 2 | 354.6 | 3.6672 | 3.667 | 1.0342 | 1.0341
450 | feeder2_line79 | 3 | 354.6 | 15.1107 | 15.1103 | 4.2613 | 4.2612
450 | feeder2_line80 | 1 | 354.6 | 96.2237 | 96.2069 | 27.1358 | 27.1311
450 | feeder2_line80 | 2 | 354.6 | 93.597 | 93.6062 | 26.3951 | 26.3977
450 | feeder2_line80 | 3 | 354.6 | 96.5003 | 96.5053 | 27.2138 | 27.2153
450 | feeder2_line81 | 1 | 354.6 | 96.2236 | 96.2069 | 27.1358 | 27.1311
450 | feeder2_line81 | 2 | 354.6 | 93.597 | 93.6062 | 26.3951 | 26.3977
450 | feeder2_line81 | 3 | 354.6 | 96.5694 | 96.5746 | 27.2333 | 27.2348
450 | feeder2_line82 | 1 | 354.6 | 5.1262e-11 | 7.3824e-07 | 1.4456e-11 | 2.0819e-07
450 | feeder2_line82 | 2 | 354.6 | 1.4166e-12 | 7.3743e-07 | 3.995e-13 | 2.0796e-07
450 | feeder2_line82 | 3 | 354.6 | 0.069876 | 0.069882 | 0.019706 | 0.019707
450 | feeder2_line83 | 1 | 354.6 | 96.2238 | 96.2069 | 27.1359 | 27.1311
450 | feeder2_line83 | 2 | 354.6 | 93.6846 | 93.6937 | 26.4198 | 26.4224
450 | feeder2_line83 | 3 | 354.6 | 96.5696 | 96.5746 | 27.2334 | 27.2348
450 | feeder2_line84 | 1 | 354.6 | 1.4556e-11 | 1.305e-06 | 4.1049e-12 | 3.6803e-07
450 | feeder2_line84 | 2 | 354.6 | 0.088752 | 0.088759 | 0.025029 | 0.025031
450 | feeder2_line84 | 3 | 354.6 | 5.9877e-12 | 1.296e-06 | 1.6886e-12 | 3.6548e-07
450 | feeder2_line85 | 1 | 99 | 0.076578 | 0.076561 | 0.077351 | 0.077335
450 | feeder2_line85 | 2 | 99 | 5.0027e-08 | 4.6531e-07 | 5.0532e-08 | 4.7001e-07
450 | feeder2_line85 | 3 | 99 | 5.0674e-08 | 4.624e-07 | 5.1186e-08 | 4.6707e-07
450 | feeder2_line86 | 1 | 354.6 | 96.2999 | 96.2829 | 27.1573 | 27.1525
450 | feeder2_line86 | 2 | 354.6 | 93.6847 | 93.6937 | 26.4198 | 26.4224
450 | feeder2_line86 | 3 | 354.6 | 96.5697 | 96.5746 | 27.2334 | 27.2348
450 | feeder2_line87 | 1 | 354.6 | 96.3001 | 96.2829 | 27.1574 | 27.1525
450 | feeder2_line87 | 2 | 354.6 | 94.6129 | 94.6218 | 26.6816 | 26.6841
450 | feeder2_line87 | 3 | 354.6 | 97.3292 | 97.3339 | 27.4476 | 27.4489
450 | feeder2_line88 | 1 | 354.6 | 0.00011703 | 3.3843e-06 | 3.3004e-05 | 9.544e-07
450 | feeder2_line88 | 2 | 354.6 | 2.3487 | 2.3488 | 0.66236 | 0.66239
450 | feeder2_line88 | 3 | 354.6 | 0.76387 | 0.76384 | 0.21542 | 0.21541
450 | feeder2_line89 | 1 | 354.6 | 96.2978 | 96.2829 | 27.1567 | 27.1525
450 | feeder2_line89 | 2 | 354.6 | 95.3307 | 95.3419 | 26.884 | 26.8872
450 | feeder2_line89 | 3 | 354.6 | 97.3269 | 97.3339 | 27.447 | 27.4489
450 | feeder2_line90 | 1 | 354.6 | 0.00073093 | 2.0416e-06 | 0.00020613 | 5.7576e-07
450 | feeder2_line90 | 2 | 354.6 | 0.73584 | 0.73636 | 0.20751 | 0.20766
450 | feeder2_line90 | 3 | 354.6 | 0.00072073 | 2.0282e-06 | 0.00020325 | 5.7196e-07
450 | feeder2_line91 | 1 | 354.6 | 96.2977 | 96.2829 | 27.1567 | 27.1525
450 | feeder2_line91 | 2 | 354.6 | 95.3307 | 95.3419 | 26.884 | 26.8872
450 | feeder2_line91 | 3 | 354.6 | 97.5035 | 97.5105 | 27.4967 | 27.4987
450 | feeder2_line92 | 1 | 354.6 | 1.2342e-11 | 1.0305e-06 | 3.4805e-12 | 2.906e-07
450 | feeder2_line92 | 2 | 354.6 | 2.116e-11 | 1.0292e-06 | 5.9672e-12 | 2.9024e-07
450 | feeder2_line92 | 3 | 354.6 | 0.17741 | 0.17741 | 0.05003 | 0.050031
450 | feeder2_line93 | 1 | 99 | 2.4779e-08 | 3.4408e-07 | 2.503e-08 | 3.4755e-07
450 | feeder2_line93 | 2 | 99 | 0.088695 | 0.088703 | 0.089591 | 0.089599
450 | feeder2_line93 | 3 | 99 | 2.5354e-08 | 3.4144e-07 | 2.561e-08 | 3.4489e-07
450 | feeder2_line94 | 1 | 354.6 | 2.4782e-06 | 1.6746e-06 | 6.9887e-07 | 4.7225e-07
450 | feeder2_line94 | 2 | 354.6 | 0.64788 | 0.64788 | 0.18271 | 0.18271
450 | feeder2_line94 | 3 | 354.6 | 2.5354e-06 | 1.663e-06 | 7.15e-07 | 4.6898e-07
450 | feeder2_line95 | 1 | 99 | 3.59e-06 | 2.6245e-06 | 3.6262e-06 | 2.6511e-06
450 | feeder2_line95 | 2 | 99 | 2.3487 | 2.3488 | 2.3724 | 2.3726
450 | feeder2_line95 | 3 | 99 | 3.5542e-06 | 2.6044e-06 | 3.5901e-06 | 2.6307e-06
450 | feeder2_line96 | 1 | 354.6 | 0.0001219 | 6.256e-07 | 3.4377e-05 | 1.7642e-07
450 | feeder2_line96 | 2 | 354.6 | 0.0001216 | 6.2491e-07 | 3.4293e-05 | 1.7623e-07
450 | feeder2_line96 | 3 | 354.6 | 0.76385 | 0.76384 | 0.21541 | 0.21541
450 | feeder2_line97 | 1 | 354.6 | 96.3969 | 96.3817 | 27.1847 | 27.1804
450 | feeder2_line97 | 2 | 354.6 | 95.3309 | 95.3419 | 26.8841 | 26.8872
450 | feeder2_line97 | 3 | 354.6 | 97.5036 | 97.5106 | 27.4968 | 27.4987
450 | feeder2_line98 | 1 | 354.6 | 0.10188 | 0.10007 | 0.02873 | 0.02822
450 | feeder2_line98 | 2 | 354.6 | 0.0017016 | 6.2299e-07 | 0.00047987 | 1.7569e-07
450 | feeder2_line98 | 3 | 354.6 | 0.0016939 | 6.212e-07 | 0.00047769 | 1.7518e-07
450 | feeder2_line99 | 1 | 99 | 2.4768e-08 | 4.4977e-07 | 2.5018e-08 | 4.5431e-07
450 | feeder2_line99 | 2 | 99 | 2.5018e-08 | 4.491e-07 | 2.5271e-08 | 4.5364e-07
450 | feeder2_line99 | 3 | 99 | 0.76376 | 0.76384 | 0.77148 | 0.77156
450 | feeder2_line100 | 1 | 99 | 0.10016 | 0.10007 | 0.10118 | 0.10108
450 | feeder2_line100 | 2 | 99 | 2.504e-08 | 6.1682e-07 | 2.5293e-08 | 6.2305e-07
450 | feeder2_line100 | 3 | 99 | 2.5361e-08 | 6.1303e-07 | 2.5617e-08 | 6.1922e-07
450 | feeder2_line101 | 1 | 354.6 | 0.64891 | 0.64845 | 0.183 | 0.18287
450 | feeder2_line101 | 2 | 354.6 | 3.6672 | 3.667 | 1.0342 | 1.0341
450 | feeder2_line101 | 3 | 354.6 | 15.1107 | 15.1103 | 4.2613 | 4.2612
450 | feeder2_line102 | 1 | 99 | 2.9301 | 2.9301 | 2.9597 | 2.9597
450 | feeder2_line102 | 2 | 99 | 2.3408e-06 | 8.817e-07 | 2.3644e-06 | 8.9061e-07
450 | feeder2_line102 | 3 | 99 | 2.3223e-06 | 8.7595e-07 | 2.3458e-06 | 8.848e-07
450 | feeder2_line103 | 1 | 99 | 5.526e-07 | 8.0812e-07 | 5.5818e-07 | 8.1628e-07
450 | feeder2_line103 | 2 | 99 | 1.0502 | 1.0502 | 1.0608 | 1.0608
450 | feeder2_line103 | 3 | 99 | 5.4736e-07 | 8.017e-07 | 5.5289e-07 | 8.098e-07
450 | feeder2_line104 | 1 | 354.6 | 0.64881 | 0.64845 | 0.18297 | 0.18287
450 | feeder2_line104 | 2 | 354.6 | 2.808 | 2.8079 | 0.79189 | 0.79186
450 | feeder2_line104 | 3 | 354.6 | 15.1106 | 15.1103 | 4.2613 | 4.2612
450 | feeder2_line105 | 1 | 99 | 2.5651e-06 | 7.4358e-07 | 2.591e-06 | 7.5109e-07
450 | feeder2_line105 | 2 | 99 | 2.5579e-06 | 7.4258e-07 | 2.5838e-06 | 7.5008e-07
450 | feeder2_line105 | 3 | 99 | 0.47569 | 0.47576 | 0.48049 | 0.48056
450 | feeder2_line106 | 1 | 354.6 | 0.64875 | 0.64845 | 0.18295 | 0.18287
450 | feeder2_line106 | 2 | 354.6 | 2.808 | 2.8079 | 0.79188 | 0.79186
450 | feeder2_line106 | 3 | 354.6 | 14.6434 | 14.6431 | 4.1296 | 4.1295
450 | feeder2_line107 | 1 | 99 | 3.2579e-07 | 9.0618e-07 | 3.2908e-07 | 9.1533e-07
450 | feeder2_line107 | 2 | 99 | 0.97799 | 0.97805 | 0.98787 | 0.98793
450 | feeder2_line107 | 3 | 99 | 3.243e-07 | 8.9877e-07 | 3.2758e-07 | 9.0785e-07
450 | feeder2_line108 | 1 | 354.6 | 0.64874 | 0.64845 | 0.18295 | 0.18287
450 | feeder2_line108 | 2 | 354.6 | 1.8599 | 1.8597 | 0.5245 | 0.52446
450 | feeder2_line108 | 3 | 354.6 | 14.6434 | 14.6431 | 4.1296 | 4.1295
450 | feeder2_line109 | 1 | 354.6 | 96.5729 | 96.5565 | 27.2343 | 27.2297
450 | feeder2_line109 | 2 | 354.6 | 95.332 | 95.3419 | 26.8844 | 26.8872
450 | feeder2_line109 | 3 | 354.6 | 97.5048 | 97.5106 | 27.4971 | 27.4987
450 | feeder2_line110 | 1 | 99 | 0.17792 | 0.17709 | 0.17972 | 0.17888
450 | feeder2_line110 | 2 | 99 | 0.00080837 | 9.1151e-07 | 0.00081654 | 9.2072e-07
450 | feeder2_line110 | 3 | 99 | 0.00080084 | 9.0741e-07 | 0.00080893 | 9.1658e-07
450 | feeder2_line111 | 1 | 99 | 2.477e-08 | 3.8414e-07 | 2.502e-08 | 3.8802e-07
450 | feeder2_line111 | 2 | 99 | 1.0345 | 1.0345 | 1.0449 | 1.0449
450 | feeder2_line111 | 3 | 99 | 2.5347e-08 | 3.812e-07 | 2.5603e-08 | 3.8505e-07
450 | feeder2_line112 | 1 | 99 | 3.2606e-07 | 9.231e-07 | 3.2935e-07 | 9.3243e-07
450 | feeder2_line112 | 2 | 99 | 1.3147 | 1.3148 | 1.328 | 1.3281
450 | feeder2_line112 | 3 | 99 | 3.2468e-07 | 9.1603e-07 | 3.2796e-07 | 9.2529e-07
450 | feeder2_line113 | 1 | 99 | 0.096805 | 0.096792 | 0.097783 | 0.09777
450 | feeder2_line113 | 2 | 99 | 3.2632e-07 | 9.0971e-07 | 3.2962e-07 | 9.189e-07
450 | feeder2_line113 | 3 | 99 | 3.2503e-07 | 9.0415e-07 | 3.2831e-07 | 9.1328e-07
450 | feeder2_line114 | 1 | 99 | 1.0515 | 1.0515 | 1.0621 | 1.0622
450 | feeder2_line114 | 2 | 99 | 2.4996e-08 | 4.3843e-07 | 2.5249e-08 | 4.4286e-07
450 | feeder2_line114 | 3 | 99 | 2.5331e-08 | 4.3557e-07 | 2.5586e-08 | 4.3997e-07
450 | feeder2_line115 | 1 | 99 | 2.474e-08 | 5.6551e-07 | 2.499e-08 | 5.7123e-07
450 | feeder2_line115 | 2 | 99 | 0.33246 | 0.33247 | 0.33582 | 0.33583
450 | feeder2_line115 | 3 | 99 | 2.5349e-08 | 5.6078e-07 | 2.5605e-08 | 5.6645e-07
450 | feeder2_line116 | 1 | 354.6 | 0.64875 | 0.64845 | 0.18295 | 0.18287
450 | feeder2_line116 | 2 | 354.6 | 1.5965 | 1.5963 | 0.45022 | 0.45018
450 | feeder2_line116 | 3 | 354.6 | 14.6434 | 14.6431 | 4.1296 | 4.1295
450 | feeder2_line117 | 1 | 99 | 4.9614e-08 | 6.4705e-07 | 5.0115e-08 | 6.5358e-07
450 | feeder2_line117 | 2 | 99 | 1.2594 | 1.2595 | 1.2721 | 1.2722
450 | feeder2_line117 | 3 | 99 | 5.0764e-08 | 6.4209e-07 | 5.1277e-08 | 6.4857e-07
450 | feeder2_line118 | 1 | 354.6 | 96.5729 | 96.5565 | 27.2343 | 27.2297
450 | feeder2_line118 | 2 | 354.6 | 95.8587 | 95.8686 | 27.0329 | 27.0357
450 | feeder2_line118 | 3 | 354.6 | 97.5048 | 97.5106 | 27.4971 | 27.4987
450 | feeder2_line119 | 1 | 99 | 2.4723e-08 | 6.0853e-07 | 2.4973e-08 | 6.1468e-07
450 | feeder2_line119 | 2 | 99 | 2.4973e-08 | 6.0772e-07 | 2.5226e-08 | 6.1386e-07
450 | feeder2_line119 | 3 | 99 | 0.54445 | 0.54446 | 0.54995 | 0.54996
450 | feeder2_line120 | 1 | 354.6 | 0.64875 | 0.64845 | 0.18295 | 0.18287
450 | feeder2_line120 | 2 | 354.6 | 1.5965 | 1.5963 | 0.45022 | 0.45018
450 | feeder2_line120 | 3 | 354.6 | 14.1055 | 14.1052 | 3.9779 | 3.9778
450 | feeder2_line121 | 1 | 99 | 3.2578e-07 | 9.4237e-07 | 3.2907e-07 | 9.5189e-07
450 | feeder2_line121 | 2 | 99 | 1.318 | 1.318 | 1.3313 | 1.3313
450 | feeder2_line121 | 3 | 99 | 3.2417e-07 | 9.3405e-07 | 3.2745e-07 | 9.4349e-07
450 | feeder2_line122 | 1 | 354.6 | 0.64874 | 0.64845 | 0.18295 | 0.18287
450 | feeder2_line122 | 2 | 354.6 | 0.44042 | 0.44019 | 0.1242 | 0.12414
450 | feeder2_line122 | 3 | 354.6 | 14.1055 | 14.1052 | 3.9779 | 3.9778
450 | feeder2_line123 | 1 | 99 | 5.7742e-07 | 9.7653e-07 | 5.8326e-07 | 9.864e-07
450 | feeder2_line123 | 2 | 99 | 5.7663e-07 | 9.7524e-07 | 5.8245e-07 | 9.8509e-07
450 | feeder2_line123 | 3 | 99 | 1.2617 | 1.2617 | 1.2745 | 1.2744
450 | feeder2_line124 | 1 | 354.6 | 0.64865 | 0.64845 | 0.18292 | 0.18287
450 | feeder2_line124 | 2 | 354.6 | 0.44033 | 0.44019 | 0.12418 | 0.12414
450 | feeder2_line124 | 3 | 354.6 | 13.19 | 13.1897 | 3.7197 | 3.7196
450 | feeder2_line125 | 1 | 99 | 5.7743e-07 | 9.0779e-07 | 5.8326e-07 | 9.1696e-07
450 | feeder2_line125 | 2 | 99 | 5.7664e-07 | 9.066e-07 | 5.8247e-07 | 9.1575e-07
450 | feeder2_line125 | 3 | 99 | 0.10161 | 0.10168 | 0.10263 | 0.10271
450 | feeder2_line126 | 1 | 354.6 | 0.64881 | 0.64845 | 0.18297 | 0.18287
450 | feeder2_line126 | 2 | 354.6 | 0.44049 | 0.44019 | 0.12422 | 0.12414
450 | feeder2_line126 | 3 | 354.6 | 13.0896 | 13.0891 | 3.6914 | 3.6912
450 | feeder2_line127 | 1 | 99 | 5.7744e-07 | 1.0868e-06 | 5.8327e-07 | 1.0978e-06
450 | feeder2_line127 | 2 | 99 | 5.7665e-07 | 1.0854e-06 | 5.8248e-07 | 1.0963e-06
450 | feeder2_line127 | 3 | 99 | 1.4673 | 1.4673 | 1.4821 | 1.4821
450 | feeder2_line128 | 1 | 354.6 | 0.64873 | 0.64845 | 0.18295 | 0.18287
450 | feeder2_line128 | 2 | 354.6 | 0.4404 | 0.44019 | 0.1242 | 0.12414
450 | feeder2_line128 | 3 | 354.6 | 12.1401 | 12.1397 | 3.4236 | 3.4235
450 | feeder2_line129 | 1 | 99 | 5.5273e-07 | 8.8124e-07 | 5.5831e-07 | 8.9014e-07
450 | feeder2_line129 | 2 | 99 | 0.44018 | 0.44019 | 0.44463 | 0.44463
450 | feeder2_line129 | 3 | 99 | 5.4671e-07 | 8.7317e-07 | 5.5223e-07 | 8.8199e-07
450 | feeder2_line130 | 1 | 354.6 | 0.64874 | 0.64845 | 0.18295 | 0.18287
450 | feeder2_line130 | 2 | 354.6 | 0.00031052 | 4.6572e-06 | 8.757e-05 | 1.3134e-06
450 | feeder2_line130 | 3 | 354.6 | 12.1401 | 12.1397 | 3.4236 | 3.4235
450 | feeder2_line131 | 1 | 99 | 5.7743e-07 | 9.7671e-07 | 5.8326e-07 | 9.8657e-07
450 | feeder2_line131 | 2 | 99 | 5.7666e-07 | 9.7544e-07 | 5.8248e-07 | 9.8529e-07
450 | feeder2_line131 | 3 | 99 | 12.0626 | 12.0624 | 12.1845 | 12.1843
450 | feeder2_line132 | 1 | 354.6 | 0.64858 | 0.64845 | 0.1829 | 0.18287
450 | feeder2_line132 | 2 | 354.6 | 0.00012629 | 2.9279e-06 | 3.5614e-05 | 8.257e-07
450 | feeder2_line132 | 3 | 354.6 | 0.077687 | 0.077624 | 0.021908 | 0.021891
450 | feeder2_line133 | 1 | 99 | 0.6485 | 0.64845 | 0.65505 | 0.655
450 | feeder2_line133 | 2 | 99 | 3.0081e-07 | 9.8324e-07 | 3.0385e-07 | 9.9317e-07
450 | feeder2_line133 | 3 | 99 | 2.9871e-07 | 9.7542e-07 | 3.0172e-07 | 9.8527e-07
450 | feeder2_line134 | 1 | 354.6 | 3.4953e-12 | 1.7947e-06 | 9.857e-13 | 5.0612e-07
450 | feeder2_line134 | 2 | 354.6 | 8.3058e-12 | 1.7929e-06 | 2.3423e-12 | 5.056e-07
450 | feeder2_line134 | 3 | 354.6 | 0.077618 | 0.077624 | 0.021889 | 0.021891
450 | feeder2_line135 | 1 | 99 | 0.052387 | 0.052275 | 0.052916 | 0.052803
450 | feeder2_line135 | 2 | 99 | 5.0155e-08 | 5.8888e-07 | 5.0662e-08 | 5.9483e-07
450 | feeder2_line135 | 3 | 99 | 5.079e-08 | 5.8532e-07 | 5.1303e-08 | 5.9124e-07
450 | feeder2_line136 | 1 | 354.6 | 96.6246 | 96.6081 | 27.2489 | 27.2443
450 | feeder2_line136 | 2 | 354.6 | 95.8586 | 95.8686 | 27.0329 | 27.0357
450 | feeder2_line136 | 3 | 354.6 | 97.5048 | 97.5106 | 27.4971 | 27.4987
450 | feeder2_line137 | 1 | 99 | 0.8342 | 0.83412 | 0.84262 | 0.84254
450 | feeder2_line137 | 2 | 99 | 8.547e-07 | 1.5862e-06 | 8.6333e-07 | 1.6022e-06
450 | feeder2_line137 | 3 | 99 | 8.4925e-07 | 1.5766e-06 | 8.5783e-07 | 1.5926e-06
450 | feeder2_line138 | 1 | 354.6 | 97.0122 | 96.9955 | 27.3582 | 27.3535
450 | feeder2_line138 | 2 | 354.6 | 95.8587 | 95.8686 | 27.0329 | 27.0357
450 | feeder2_line138 | 3 | 354.6 | 97.5049 | 97.5106 | 27.4971 | 27.4987
450 | feeder2_line139 | 1 | 99 | 4.9651e-08 | 4.9511e-07 | 5.0153e-08 | 5.0011e-07
450 | feeder2_line139 | 2 | 99 | 5.0172e-08 | 4.9429e-07 | 5.0679e-08 | 4.9928e-07
450 | feeder2_line139 | 3 | 99 | 0.89796 | 0.89843 | 0.90703 | 0.90751
450 | feeder2_line140 | 1 | 354.6 | 97.0123 | 96.9955 | 27.3582 | 27.3535
450 | feeder2_line140 | 2 | 354.6 | 95.8588 | 95.8686 | 27.0329 | 27.0357
450 | feeder2_line140 | 3 | 354.6 | 98.3957 | 98.4018 | 27.7484 | 27.7501
450 | feeder2_line141 | 1 | 99 | 2.549e-06 | 4.8981e-07 | 2.5748e-06 | 4.9476e-07
450 | feeder2_line141 | 2 | 99 | 1.2602 | 1.2602 | 1.2729 | 1.2729
450 | feeder2_line141 | 3 | 99 | 2.5185e-06 | 4.8606e-07 | 2.5439e-06 | 4.9097e-07
450 | feeder2_line142 | 1 | 354.6 | 97.0121 | 96.9955 | 27.3582 | 27.3535
450 | feeder2_line142 | 2 | 354.6 | 96.4881 | 96.4981 | 27.2104 | 27.2132
450 | feeder2_line142 | 3 | 354.6 | 98.3955 | 98.4018 | 27.7483 | 27.7501
450 | feeder2_line143 | 1 | 99 | 8.5665e-07 | 1.7406e-06 | 8.653e-07 | 1.7582e-06
450 | feeder2_line143 | 2 | 99 | 0.97882 | 0.97889 | 0.9887 | 0.98878
450 | feeder2_line143 | 3 | 99 | 8.4962e-07 | 1.7273e-06 | 8.582e-07 | 1.7447e-06
450 | feeder2_line144 | 1 | 354.6 | 97.0119 | 96.9955 | 27.3581 | 27.3535
450 | feeder2_line144 | 2 | 354.6 | 96.9397 | 96.95 | 27.3378 | 27.3407
450 | feeder2_line144 | 3 | 354.6 | 98.3953 | 98.4018 | 27.7483 | 27.7501
450 | feeder2_line145 | 1 | 99 | 2.4834e-08 | 4.8808e-07 | 2.5085e-08 | 4.9301e-07
450 | feeder2_line145 | 2 | 99 | 0.069235 | 0.069249 | 0.069934 | 0.069949
450 | feeder2_line145 | 3 | 99 | 2.541e-08 | 4.8435e-07 | 2.5666e-08 | 4.8924e-07
450 | feeder2_line146 | 1 | 354.6 | 97.0118 | 96.9955 | 27.3581 | 27.3535
450 | feeder2_line146 | 2 | 354.6 | 97.0083 | 97.0187 | 27.3571 | 27.36
450 | feeder2_line146 | 3 | 354.6 | 98.3952 | 98.4018 | 27.7482 | 27.7501
450 | feeder2_line147 | 1 | 99 | 0.080214 | 0.080201 | 0.081024 | 0.081011
450 | feeder2_line147 | 2 | 99 | 1.157e-06 | 2.2477e-06 | 1.1687e-06 | 2.2704e-06
450 | feeder2_line147 | 3 | 99 | 1.15e-06 | 2.2342e-06 | 1.1616e-06 | 2.2567e-06
450 | feeder2_line148 | 1 | 99 | 0.084196 | 0.084175 | 0.085047 | 0.085025
450 | feeder2_line148 | 2 | 99 | 6.0358e-07 | 1.5061e-06 | 6.0967e-07 | 1.5213e-06
450 | feeder2_line148 | 3 | 99 | 6.0039e-07 | 1.4971e-06 | 6.0646e-07 | 1.5122e-06
450 | feeder2_line149 | 1 | 354.6 | 97.175 | 97.1585 | 27.4041 | 27.3995
450 | feeder2_line149 | 2 | 354.6 | 97.0085 | 97.0187 | 27.3572 | 27.36
450 | feeder2_line149 | 3 | 354.6 | 98.3954 | 98.4018 | 27.7483 | 27.7501
450 | feeder2_line150 | 1 | 354.6 | 97.1751 | 97.1585 | 27.4041 | 27.3995
450 | feeder2_line150 | 2 | 354.6 | 98.1341 | 98.1443 | 27.6746 | 27.6775
450 | feeder2_line150 | 3 | 354.6 | 98.3955 | 98.4018 | 27.7483 | 27.7501
450 | feeder2_line151 | 1 | 99 | 9.8606e-06 | 1.7921e-06 | 9.9602e-06 | 1.8102e-06
450 | feeder2_line151 | 2 | 99 | 1.1409 | 1.1409 | 1.1524 | 1.1524
450 | feeder2_line151 | 3 | 99 | 9.73e-06 | 1.7785e-06 | 9.8282e-06 | 1.7964e-06
450 | feeder2_line152 | 1 | 354.6 | 1.0495e-11 | 1.1941e-06 | 2.9597e-12 | 3.3676e-07
450 | feeder2_line152 | 2 | 354.6 | 1.416e-11 | 1.1925e-06 | 3.9934e-12 | 3.363e-07
450 | feeder2_line152 | 3 | 354.6 | 0.077053 | 0.077056 | 0.021729 | 0.02173
450 | feeder2_line153 | 1 | 99 | 1.3217 | 1.3218 | 1.3351 | 1.3352
450 | feeder2_line153 | 2 | 99 | 5.0237e-08 | 5.9667e-07 | 5.0744e-08 | 6.027e-07
450 | feeder2_line153 | 3 | 99 | 5.0864e-08 | 5.931e-07 | 5.1378e-08 | 5.9909e-07
450 | feeder2_line154 | 1 | 99 | 5.7996e-07 | 8.8933e-07 | 5.8581e-07 | 8.9831e-07
450 | feeder2_line154 | 2 | 99 | 5.7897e-07 | 8.8787e-07 | 5.8482e-07 | 8.9684e-07
450 | feeder2_line154 | 3 | 99 | 1.241 | 1.241 | 1.2536 | 1.2536
450 | feeder2_line155 | 1 | 99 | 97.7254 | 97.7089 | 98.7125 | 98.6958
450 | feeder2_line155 | 2 | 99 | 98.134 | 98.1443 | 99.1253 | 99.1356
450 | feeder2_line155 | 3 | 99 | 99 | 99.0065 | 100 | 100.0065
450 | feeder2_line156 | 1 | 99 | 6.0458e-07 | 1.1702e-06 | 6.1069e-07 | 1.1821e-06
450 | feeder2_line156 | 2 | 99 | 1.0518 | 1.0518 | 1.0625 | 1.0625
450 | feeder2_line156 | 3 | 99 | 6.0067e-07 | 1.1613e-06 | 6.0674e-07 | 1.1731e-06
450 | feeder2_line157 | 1 | 99 | 2.4857e-08 | 2.5406e-07 | 2.5108e-08 | 2.5663e-07
450 | feeder2_line157 | 2 | 99 | 0.089169 | 0.089177 | 0.090069 | 0.090078
450 | feeder2_line157 | 3 | 99 | 2.5422e-08 | 2.5212e-07 | 2.5679e-08 | 2.5467e-07
480 | feeder2_line1 | 1 | 354.6 | 64.6192 | 64.6162 | 18.2231 | 18.2223
480 | feeder2_line1 | 2 | 354.6 | 70.3039 | 70.3031 | 19.8262 | 19.826
480 | feeder2_line1 | 3 | 354.6 | 38.0419 | 38.0477 | 10.7281 | 10.7298
480 | feeder2_line2 | 1 | 354.6 | 65.8834 | 65.8802 | 18.5796 | 18.5788
480 | feeder2_line2 | 2 | 354.6 | 70.3041 | 70.3031 | 19.8263 | 19.826
480 | feeder2_line2 | 3 | 354.6 | 38.0421 | 38.0477 | 10.7282 | 10.7298
480 | feeder2_line3 | 1 | 80.1 | 1.2963 | 1.2963 | 1.6184 | 1.6184
480 | feeder2_line3 | 2 | 80.1 | 5.7227e-07 | 1.0575e-06 | 7.1444e-07 | 1.3203e-06
480 | feeder2_line3 | 3 | 80.1 | 5.7021e-07 | 1.0538e-06 | 7.1187e-07 | 1.3156e-06
480 | feeder2_line4 | 1 | 354.6 | 65.8835 | 65.8802 | 18.5797 | 18.5788
480 | feeder2_line4 | 2 | 354.6 | 70.3918 | 70.3907 | 19.851 | 19.8507
480 | feeder2_line4 | 3 | 354.6 | 38.0422 | 38.0477 | 10.7282 | 10.7298
480 | feeder2_line5 | 1 | 80.1 | 5.7191e-07 | 9.9792e-07 | 7.14e-07 | 1.2458e-06
480 | feeder2_line5 | 2 | 80.1 | 0.090005 | 0.090005 | 0.11237 | 0.11237
480 | feeder2_line5 | 3 | 80.1 | 5.7019e-07 | 9.9496e-07 | 7.1185e-07 | 1.2421e-06
480 | feeder2_line6 | 1 | 80.1 | 5.7198e-07 | 1.1741e-06 | 7.1408e-07 | 1.4657e-06
480 | feeder2_line6 | 2 | 80.1 | 5.7239e-07 | 1.1749e-06 | 7.146e-07 | 1.4668e-06
480 | feeder2_line6 | 3 | 80.1 | 0.90109 | 0.90107 | 1.125 | 1.1249
480 | feeder2_line7 | 1 | 354.6 | 65.8837 | 65.8802 | 18.5797 | 18.5788
480 | feeder2_line7 | 2 | 354.6 | 70.3919 | 70.3907 | 19.8511 | 19.8507
480 | feeder2_line7 | 3 | 354.6 | 38.0005 | 38.0061 | 10.7164 | 10.718
480 | feeder2_line8 | 1 | 80.1 | 0.072577 | 0.072577 | 0.090608 | 0.090607
480 | feeder2_line8 | 2 | 80.1 | 5.7262e-07 | 1.1333e-06 | 7.1488e-07 | 1.4149e-06
480 | feeder2_line8 | 3 | 80.1 | 5.7009e-07 | 1.1284e-06 | 7.1172e-07 | 1.4087e-06
480 | feeder2_line9 | 1 | 354.6 | 65.9552 | 65.9518 | 18.5999 | 18.5989
480 | feeder2_line9 | 2 | 354.6 | 70.3919 | 70.3907 | 19.8511 | 19.8507
480 | feeder2_line9 | 3 | 354.6 | 38.0005 | 38.0061 | 10.7164 | 10.718
480 | feeder2_line10 | 1 | 80.1 | 8.459e-07 | 1.4953e-06 | 1.0561e-06 | 1.8668e-06
480 | feeder2_line10 | 2 | 80.1 | 0.072526 | 0.072526 | 0.090545 | 0.090544
480 | feeder2_line10 | 3 | 80.1 | 8.4261e-07 | 1.4899e-06 | 1.052e-06 | 1.86e-06
480 | feeder2_line11 | 1 | 354.6 | 65.9552 | 65.9518 | 18.5999 | 18.5989
480 | feeder2_line11 | 2 | 354.6 | 70.4625 | 70.4613 | 19.871 | 19.8706
480 | feeder2_line11 | 3 | 354.6 | 38.0006 | 38.0061 | 10.7165 | 10.718
480 | feeder2_line12 | 1 | 80.1 | 5.4751e-07 | 9.9199e-07 | 6.8353e-07 | 1.2384e-06
480 | feeder2_line12 | 2 | 80.1 | 5.4794e-07 | 9.9283e-07 | 6.8407e-07 | 1.2395e-06
480 | feeder2_line12 | 3 | 80.1 | 4.0404 | 4.0404 | 5.0441 | 5.0442
480 | feeder2_line13 | 1 | 354.6 | 65.9552 | 65.9518 | 18.5999 | 18.5989
480 | feeder2_line13 | 2 | 354.6 | 70.4625 | 70.4613 | 19.871 | 19.8706
480 | feeder2_line13 | 3 | 354.6 | 40.1043 | 40.11 | 11.3097 | 11.3113
480 | feeder2_line14 | 1 | 80.1 | 1.7452 | 1.7452 | 2.1787 | 2.1787
480 | feeder2_line14 | 2 | 80.1 | 2.9881e-07 | 6.475e-07 | 3.7304e-07 | 8.0836e-07
480 | feeder2_line14 | 3 | 80.1 | 2.9753e-07 | 6.4438e-07 | 3.7145e-07 | 8.0446e-07
480 | feeder2_line15 | 1 | 354.6 | 67.6221 | 67.6186 | 19.07 | 19.069
480 | feeder2_line15 | 2 | 354.6 | 70.4625 | 70.4613 | 19.871 | 19.8706
480 | feeder2_line15 | 3 | 354.6 | 40.1043 | 40.11 | 11.3097 | 11.3113
480 | feeder2_line16 | 1 | 80.1 | 5.7243e-07 | 1.0312e-06 | 7.1464e-07 | 1.2874e-06
480 | feeder2_line16 | 2 | 80.1 | 0.8902 | 0.89019 | 1.1114 | 1.1114
480 | feeder2_line16 | 3 | 80.1 | 5.7e-07 | 1.0269e-06 | 7.1161e-07 | 1.2821e-06
480 | feeder2_line17 | 1 | 354.6 | 67.6221 | 67.6186 | 19.07 | 19.069
480 | feeder2_line17 | 2 | 354.6 | 71.3133 | 71.312 | 20.1109 | 20.1106
480 | feeder2_line17 | 3 | 354.6 | 40.1044 | 40.11 | 11.3097 | 11.3113
480 | feeder2_line18 | 1 | 80.1 | 5.4818e-07 | 7.3879e-07 | 6.8437e-07 | 9.2233e-07
480 | feeder2_line18 | 2 | 80.1 | 5.4871e-07 | 7.3954e-07 | 6.8503e-07 | 9.2328e-07
480 | feeder2_line18 | 3 | 80.1 | 1.0941 | 1.0941 | 1.3659 | 1.3659
480 | feeder2_line19 | 1 | 354.6 | 67.6221 | 67.6186 | 19.07 | 19.069
480 | feeder2_line19 | 2 | 354.6 | 71.3133 | 71.312 | 20.1109 | 20.1106
480 | feeder2_line19 | 3 | 354.6 | 40.1222 | 40.1278 | 11.3148 | 11.3164
480 | feeder2_line20 | 1 | 99 | 5.4835e-07 | 8.8603e-07 | 5.5389e-07 | 8.9498e-07
480 | feeder2_line20 | 2 | 99 | 5.4891e-07 | 8.8698e-07 | 5.5446e-07 | 8.9594e-07
480 | feeder2_line20 | 3 | 99 | 10.1426 | 10.1426 | 10.245 | 10.245
480 | feeder2_line21 | 1 | 354.6 | 67.6223 | 67.6186 | 19.07 | 19.069
480 | feeder2_line21 | 2 | 354.6 | 71.3134 | 71.312 | 20.111 | 20.1106
480 | feeder2_line21 | 3 | 354.6 | 48.7495 | 48.755 | 13.7477 | 13.7493
480 | feeder2_line22 | 1 | 99 | 5.7317e-07 | 1.0159e-06 | 5.7896e-07 | 1.0262e-06
480 | feeder2_line22 | 2 | 99 | 11.461 | 11.461 | 11.5768 | 11.5768
480 | feeder2_line22 | 3 | 99 | 5.698e-07 | 1.01e-06 | 5.7556e-07 | 1.0202e-06
480 | feeder2_line23 | 1 | 99 | 5.7318e-07 | 9.5098e-07 | 5.7897e-07 | 9.6058e-07
480 | feeder2_line23 | 2 | 99 | 5.7381e-07 | 9.5203e-07 | 5.7961e-07 | 9.6164e-07
480 | feeder2_line23 | 3 | 99 | 1.9286 | 1.9286 | 1.948 | 1.9481
480 | feeder2_line24 | 1 | 354.6 | 67.6223 | 67.6186 | 19.07 | 19.069
480 | feeder2_line24 | 2 | 354.6 | 82.2664 | 82.265 | 23.1998 | 23.1994
480 | feeder2_line24 | 3 | 354.6 | 49.6515 | 49.657 | 14.0021 | 14.0037
480 | feeder2_line25 | 1 | 99 | 11.4573 | 11.4573 | 11.573 | 11.573
480 | feeder2_line25 | 2 | 99 | 4.9548e-08 | 6.9245e-07 | 5.0048e-08 | 6.9945e-07
480 | feeder2_line25 | 3 | 99 | 5.0317e-08 | 6.8738e-07 | 5.0825e-08 | 6.9432e-07
480 | feeder2_line26 | 1 | 99 | 0.085077 | 0.085075 | 0.085937 | 0.085935
480 | feeder2_line26 | 2 | 99 | 5.493e-07 | 8.5791e-07 | 5.5485e-07 | 8.6658e-07
480 | feeder2_line26 | 3 | 99 | 5.4466e-07 | 8.5163e-07 | 5.5017e-07 | 8.6023e-07
480 | feeder2_line27 | 1 | 354.6 | 78.8288 | 78.8251 | 22.2304 | 22.2293
480 | feeder2_line27 | 2 | 354.6 | 82.2664 | 82.265 | 23.1998 | 23.1994
480 | feeder2_line27 | 3 | 354.6 | 49.6515 | 49.657 | 14.0021 | 14.0037
480 | feeder2_line28 | 1 | 99 | 2.5473e-06 | 7.117e-07 | 2.5731e-06 | 7.1889e-07
480 | feeder2_line28 | 2 | 99 | 0.10839 | 0.10839 | 0.10949 | 0.10949
480 | feeder2_line28 | 3 | 99 | 2.5214e-06 | 7.0691e-07 | 2.5468e-06 | 7.1405e-07
480 | feeder2_line29 | 1 | 354.6 | 78.8288 | 78.8251 | 22.2304 | 22.2293
480 | feeder2_line29 | 2 | 354.6 | 82.3744 | 82.3729 | 23.2302 | 23.2298
480 | feeder2_line29 | 3 | 354.6 | 49.6515 | 49.657 | 14.0021 | 14.0037
480 | feeder2_line30 | 1 | 266.4 | 1.0632 | 1.0628 | 0.3991 | 0.39894
480 | feeder2_line30 | 2 | 266.4 | 3.2956 | 3.2955 | 1.2371 | 1.2371
480 | feeder2_line30 | 3 | 266.4 | 5.8601 | 5.86 | 2.1997 | 2.1997
480 | feeder2_line31 | 1 | 354.6 | 79.8715 | 79.8673 | 22.5244 | 22.5232
480 | feeder2_line31 | 2 | 354.6 | 84.7402 | 84.7383 | 23.8974 | 23.8969
480 | feeder2_line31 | 3 | 354.6 | 53.9665 | 53.9716 | 15.219 | 15.2204
480 | feeder2_line32 | 1 | 354.6 | 79.8715 | 79.8673 | 22.5244 | 22.5232
480 | feeder2_line32 | 2 | 354.6 | 84.8162 | 84.8144 | 23.9189 | 23.9183
480 | feeder2_line32 | 3 | 354.6 | 53.9665 | 53.9716 | 15.219 | 15.2204
480 | feeder2_line33 | 1 | 99 | 4.9419e-08 | 6.8757e-07 | 4.9918e-08 | 6.9451e-07
480 | feeder2_line33 | 2 | 99 | 0.07685 | 0.076849 | 0.077627 | 0.077625
480 | feeder2_line33 | 3 | 99 | 5.0582e-08 | 6.8199e-07 | 5.1093e-08 | 6.8888e-07
480 | feeder2_line34 | 1 | 354.6 | 79.8715 | 79.8673 | 22.5244 | 22.5232
480 | feeder2_line34 | 2 | 354.6 | 84.8162 | 84.8144 | 23.9188 | 23.9183
480 | feeder2_line34 | 3 | 354.6 | 54.0479 | 54.053 | 15.2419 | 15.2434
480 | feeder2_line35 | 1 | 99 | 2.9968e-07 | 7.6156e-07 | 3.0271e-07 | 7.6925e-07
480 | feeder2_line35 | 2 | 99 | 3.0015e-07 | 7.6273e-07 | 3.0318e-07 | 7.7043e-07
480 | feeder2_line35 | 3 | 99 | 0.086287 | 0.086292 | 0.087158 | 0.087163
480 | feeder2_line36 | 1 | 354.6 | 80.0005 | 79.9963 | 22.5608 | 22.5596
480 | feeder2_line36 | 2 | 354.6 | 84.8162 | 84.8144 | 23.9188 | 23.9183
480 | feeder2_line36 | 3 | 354.6 | 54.0479 | 54.053 | 15.2419 | 15.2434
480 | feeder2_line37 | 1 | 99 | 0.13008 | 0.13001 | 0.1314 | 0.13132
480 | feeder2_line37 | 2 | 99 | 3.0023e-07 | 8.4417e-07 | 3.0326e-07 | 8.527e-07
480 | feeder2_line37 | 3 | 99 | 2.9758e-07 | 8.3566e-07 | 3.0058e-07 | 8.441e-07
480 | feeder2_line38 | 1 | 99 | 3.2419e-07 | 7.7708e-07 | 3.2746e-07 | 7.8493e-07
480 | feeder2_line38 | 2 | 99 | 1.3284 | 1.3284 | 1.3418 | 1.3418
480 | feeder2_line38 | 3 | 99 | 3.2278e-07 | 7.7107e-07 | 3.2604e-07 | 7.7885e-07
480 | feeder2_line39 | 1 | 266.4 | 1.0632 | 1.0628 | 0.39911 | 0.39894
480 | feeder2_line39 | 2 | 266.4 | 2.1276 | 2.1274 | 0.79864 | 0.79857
480 | feeder2_line39 | 3 | 266.4 | 5.8601 | 5.86 | 2.1997 | 2.1997
480 | feeder2_line40 | 1 | 354.6 | 91.2415 | 91.2372 | 25.7308 | 25.7296
480 | feeder2_line40 | 2 | 354.6 | 84.8162 | 84.8144 | 23.9189 | 23.9183
480 | feeder2_line40 | 3 | 354.6 | 54.0479 | 54.053 | 15.2419 | 15.2434
480 | feeder2_line41 | 1 | 99 | 11.4858 | 11.4858 | 11.6018 | 11.6019
480 | feeder2_line41 | 2 | 99 | 4.9537e-08 | 7.3775e-07 | 5.0037e-08 | 7.452e-07
480 | feeder2_line41 | 3 | 99 | 5.0646e-08 | 7.3022e-07 | 5.1158e-08 | 7.3759e-07
480 | feeder2_line42 | 1 | 99 | 2.9948e-07 | 7.5006e-07 | 3.0251e-07 | 7.5764e-07
480 | feeder2_line42 | 2 | 99 | 2.9992e-07 | 7.5113e-07 | 3.0295e-07 | 7.5872e-07
480 | feeder2_line42 | 3 | 99 | 0.077854 | 0.077857 | 0.07864 | 0.078643
480 | feeder2_line43 | 1 | 266.4 | 1.0631 | 1.0628 | 0.39907 | 0.39894
480 | feeder2_line43 | 2 | 266.4 | 2.1275 | 2.1274 | 0.79862 | 0.79857
480 | feeder2_line43 | 3 | 266.4 | 5.7889 | 5.7889 | 2.173 | 2.173
480 | feeder2_line44 | 1 | 354.6 | 91.2415 | 91.2372 | 25.7308 | 25.7296
480 | feeder2_line44 | 2 | 354.6 | 84.8163 | 84.8144 | 23.9189 | 23.9183
480 | feeder2_line44 | 3 | 354.6 | 63.5629 | 63.5679 | 17.9252 | 17.9267
480 | feeder2_line45 | 1 | 99 | 4.9404e-08 | 5.8099e-07 | 4.9903e-08 | 5.8686e-07
480 | feeder2_line45 | 2 | 99 | 4.9547e-08 | 5.8191e-07 | 5.0048e-08 | 5.8779e-07
480 | feeder2_line45 | 3 | 99 | 10.1322 | 10.1322 | 10.2345 | 10.2345
480 | feeder2_line46 | 1 | 99 | 5.7426e-07 | 1.3597e-06 | 5.8006e-07 | 1.3735e-06
480 | feeder2_line46 | 2 | 99 | 5.7507e-07 | 1.3617e-06 | 5.8088e-07 | 1.3754e-06
480 | feeder2_line46 | 3 | 99 | 0.073029 | 0.073049 | 0.073767 | 0.073787
480 | feeder2_line47 | 1 | 266.4 | 1.0631 | 1.0628 | 0.39907 | 0.39894
480 | feeder2_line47 | 2 | 266.4 | 2.1276 | 2.1274 | 0.79865 | 0.79857
480 | feeder2_line47 | 3 | 266.4 | 5.7215 | 5.7214 | 2.1477 | 2.1477
480 | feeder2_line48 | 1 | 99 | 0.081593 | 0.081591 | 0.082417 | 0.082415
480 | feeder2_line48 | 2 | 99 | 4.9543e-08 | 7.3314e-07 | 5.0043e-08 | 7.4055e-07
480 | feeder2_line48 | 3 | 99 | 5.0534e-08 | 7.2637e-07 | 5.1045e-08 | 7.337e-07
480 | feeder2_line49 | 1 | 266.4 | 0.98169 | 0.98135 | 0.3685 | 0.36837
480 | feeder2_line49 | 2 | 266.4 | 2.1276 | 2.1274 | 0.79864 | 0.79857
480 | feeder2_line49 | 3 | 266.4 | 5.7215 | 5.7214 | 2.1477 | 2.1477
480 | feeder2_line50 | 1 | 99 | 5.7426e-07 | 1.2375e-06 | 5.8006e-07 | 1.25e-06
480 | feeder2_line50 | 2 | 99 | 0.90366 | 0.90363 | 0.91278 | 0.91275
480 | feeder2_line50 | 3 | 99 | 5.6969e-07 | 1.2277e-06 | 5.7544e-07 | 1.2401e-06
480 | feeder2_line51 | 1 | 99 | 0.044707 | 0.044607 | 0.045158 | 0.045057
480 | feeder2_line51 | 2 | 99 | 5.7507e-07 | 1.3453e-06 | 5.8088e-07 | 1.3589e-06
480 | feeder2_line51 | 3 | 99 | 5.6969e-07 | 1.3328e-06 | 5.7544e-07 | 1.3463e-06
480 | feeder2_line52 | 1 | 266.4 | 0.93686 | 0.93676 | 0.35167 | 0.35164
480 | feeder2_line52 | 2 | 266.4 | 1.4708 | 1.4707 | 0.55209 | 0.55205
480 | feeder2_line52 | 3 | 266.4 | 5.7213 | 5.7214 | 2.1477 | 2.1477
480 | feeder2_line53 | 1 | 99 | 5.4956e-07 | 7.5524e-07 | 5.5511e-07 | 7.6287e-07
480 | feeder2_line53 | 2 | 99 | 1.4707 | 1.4707 | 1.4855 | 1.4855
480 | feeder2_line53 | 3 | 99 | 5.4441e-07 | 7.493e-07 | 5.4991e-07 | 7.5687e-07
480 | feeder2_line54 | 1 | 266.4 | 0.93668 | 0.93676 | 0.35161 | 0.35164
480 | feeder2_line54 | 2 | 266.4 | 8.5694e-05 | 4.6391e-06 | 3.2167e-05 | 1.7414e-06
480 | feeder2_line54 | 3 | 266.4 | 5.7212 | 5.7214 | 2.1476 | 2.1477
480 | feeder2_line55 | 1 | 99 | 0.045372 | 0.045369 | 0.04583 | 0.045827
480 | feeder2_line55 | 2 | 99 | 4.9574e-08 | 7.3359e-07 | 5.0074e-08 | 7.41e-07
480 | feeder2_line55 | 3 | 99 | 5.0745e-08 | 7.2563e-07 | 5.1257e-08 | 7.3296e-07
480 | feeder2_line56 | 1 | 354.6 | 91.2866 | 91.2822 | 25.7435 | 25.7423
480 | feeder2_line56 | 2 | 354.6 | 84.8163 | 84.8144 | 23.9189 | 23.9183
480 | feeder2_line56 | 3 | 354.6 | 63.563 | 63.5679 | 17.9253 | 17.9267
480 | feeder2_line57 | 1 | 99 | 7.4117e-07 | 1.547e-06 | 7.4865e-07 | 1.5626e-06
480 | feeder2_line57 | 2 | 99 | 7.4302e-07 | 1.5492e-06 | 7.5053e-07 | 1.5648e-06
480 | feeder2_line57 | 3 | 99 | 5.7213 | 5.7214 | 5.7791 | 5.7791
480 | feeder2_line58 | 1 | 266.4 | 0.93675 | 0.93676 | 0.35163 | 0.35164
480 | feeder2_line58 | 2 | 266.4 | 1.9035e-05 | 2.6933e-06 | 7.1455e-06 | 1.011e-06
480 | feeder2_line58 | 3 | 266.4 | 1.8804e-05 | 2.6694e-06 | 7.0587e-06 | 1.002e-06
480 | feeder2_line59 | 1 | 99 | 4.9406e-08 | 5.3774e-07 | 4.9905e-08 | 5.4317e-07
480 | feeder2_line59 | 2 | 99 | 4.9539e-08 | 5.385e-07 | 5.0039e-08 | 5.4394e-07
480 | feeder2_line59 | 3 | 99 | 1.6833 | 1.6833 | 1.7003 | 1.7004
480 | feeder2_line60 | 1 | 99 | 2.9947e-07 | 8.1269e-07 | 3.025e-07 | 8.209e-07
480 | feeder2_line60 | 2 | 99 | 2.9991e-07 | 8.1385e-07 | 3.0294e-07 | 8.2207e-07
480 | feeder2_line60 | 3 | 99 | 4.038 | 4.038 | 4.0788 | 4.0788
480 | feeder2_line61 | 1 | 266.4 | 0.085283 | 0.08545 | 0.032013 | 0.032076
480 | feeder2_line61 | 2 | 266.4 | 3.4756 | 3.4757 | 1.3046 | 1.3047
480 | feeder2_line61 | 3 | 266.4 | 12.1879 | 12.188 | 4.575 | 4.5751
480 | feeder2_line62 | 1 | 354.6 | 91.3714 | 91.3673 | 25.7675 | 25.7663
480 | feeder2_line62 | 2 | 354.6 | 87.3448 | 87.3432 | 24.6319 | 24.6315
480 | feeder2_line62 | 3 | 354.6 | 75.0049 | 75.0099 | 21.152 | 21.1534
480 | feeder2_line63 | 1 | 99 | 0.088834 | 0.08883 | 0.089731 | 0.089727
480 | feeder2_line63 | 2 | 99 | 5.7508e-07 | 1.2236e-06 | 5.8089e-07 | 1.236e-06
480 | feeder2_line63 | 3 | 99 | 5.6967e-07 | 1.2122e-06 | 5.7542e-07 | 1.2245e-06
480 | feeder2_line64 | 1 | 99 | 0.84808 | 0.84807 | 0.85664 | 0.85664
480 | feeder2_line64 | 2 | 99 | 6.7007e-12 | 3.2232e-07 | 6.7684e-12 | 3.2557e-07
480 | feeder2_line64 | 3 | 99 | 4.8658e-12 | 3.1932e-07 | 4.9149e-12 | 3.2255e-07
480 | feeder2_line65 | 1 | 99 | 4.9402e-08 | 6.4414e-07 | 4.9901e-08 | 6.5064e-07
480 | feeder2_line65 | 2 | 99 | 0.089339 | 0.089338 | 0.090242 | 0.09024
480 | feeder2_line65 | 3 | 99 | 5.0846e-08 | 6.3757e-07 | 5.1359e-08 | 6.4401e-07
480 | feeder2_line66 | 1 | 354.6 | 91.3714 | 91.3673 | 25.7674 | 25.7663
480 | feeder2_line66 | 2 | 354.6 | 87.4335 | 87.4319 | 24.6569 | 24.6565
480 | feeder2_line66 | 3 | 354.6 | 75.0048 | 75.0099 | 21.1519 | 21.1534
480 | feeder2_line67 | 1 | 99 | 2.4697e-08 | 3.6394e-07 | 2.4947e-08 | 3.6762e-07
480 | feeder2_line67 | 2 | 99 | 2.4789e-08 | 3.6443e-07 | 2.5039e-08 | 3.6811e-07
480 | feeder2_line67 | 3 | 99 | 11.3609 | 11.3608 | 11.4757 | 11.4756
480 | feeder2_line68 | 1 | 266.4 | 0.085322 | 0.08545 | 0.032028 | 0.032076
480 | feeder2_line68 | 2 | 266.4 | 3.4756 | 3.4757 | 1.3047 | 1.3047
480 | feeder2_line68 | 3 | 266.4 | 1.0104 | 1.0106 | 0.3793 | 0.37934
480 | feeder2_line69 | 1 | 99 | 0.10049 | 0.10048 | 0.1015 | 0.1015
480 | feeder2_line69 | 2 | 99 | 2.5626e-06 | 6.697e-07 | 2.5885e-06 | 6.7646e-07
480 | feeder2_line69 | 3 | 99 | 2.5207e-06 | 6.6195e-07 | 2.5462e-06 | 6.6864e-07
480 | feeder2_line70 | 1 | 354.6 | 91.4711 | 91.4671 | 25.7956 | 25.7944
480 | feeder2_line70 | 2 | 354.6 | 87.4334 | 87.4319 | 24.6569 | 24.6565
480 | feeder2_line70 | 3 | 354.6 | 75.0047 | 75.0099 | 21.1519 | 21.1534
480 | feeder2_line71 | 1 | 99 | 4.9409e-08 | 7.1891e-07 | 4.9908e-08 | 7.2617e-07
480 | feeder2_line71 | 2 | 99 | 1.25 | 1.25 | 1.2627 | 1.2627
480 | feeder2_line71 | 3 | 99 | 5.0881e-08 | 7.1142e-07 | 5.1395e-08 | 7.1861e-07
480 | feeder2_line72 | 1 | 354.6 | 91.4712 | 91.4671 | 25.7956 | 25.7944
480 | feeder2_line72 | 2 | 354.6 | 87.9718 | 87.9702 | 24.8087 | 24.8083
480 | feeder2_line72 | 3 | 354.6 | 75.0048 | 75.0099 | 21.152 | 21.1534
480 | feeder2_line73 | 1 | 99 | 6.005e-07 | 1.5408e-06 | 6.0657e-07 | 1.5564e-06
480 | feeder2_line73 | 2 | 99 | 0.076698 | 0.076697 | 0.077473 | 0.077471
480 | feeder2_line73 | 3 | 99 | 5.9537e-07 | 1.5254e-06 | 6.0138e-07 | 1.5408e-06
480 | feeder2_line74 | 1 | 99 | 4.9387e-08 | 4.5956e-07 | 4.9885e-08 | 4.642e-07
480 | feeder2_line74 | 2 | 99 | 1.0104 | 1.0104 | 1.0206 | 1.0206
480 | feeder2_line74 | 3 | 99 | 5.0806e-08 | 4.5496e-07 | 5.1319e-08 | 4.5955e-07
480 | feeder2_line75 | 1 | 266.4 | 0.08542 | 0.08545 | 0.032065 | 0.032076
480 | feeder2_line75 | 2 | 266.4 | 2.4119 | 2.412 | 0.90538 | 0.90539
480 | feeder2_line75 | 3 | 266.4 | 1.0105 | 1.0106 | 0.37933 | 0.37934
480 | feeder2_line76 | 1 | 99 | 0.085453 | 0.08545 | 0.086316 | 0.086313
480 | feeder2_line76 | 2 | 99 | 8.5241e-07 | 1.5915e-06 | 8.6102e-07 | 1.6075e-06
480 | feeder2_line76 | 3 | 99 | 8.4225e-07 | 1.5735e-06 | 8.5075e-07 | 1.5894e-06
480 | feeder2_line77 | 1 | 99 | 2.4694e-08 | 5.7752e-07 | 2.4943e-08 | 5.8335e-07
480 | feeder2_line77 | 2 | 99 | 2.4792e-08 | 5.7825e-07 | 2.5042e-08 | 5.8409e-07
480 | feeder2_line77 | 3 | 99 | 1.0106 | 1.0106 | 1.0208 | 1.0208
480 | feeder2_line78 | 1 | 266.4 | 1.1241e-11 | 9.5736e-07 | 4.2196e-12 | 3.5937e-07
480 | feeder2_line78 | 2 | 266.4 | 2.412 | 2.412 | 0.90539 | 0.90539
480 | feeder2_line78 | 3 | 266.4 | 7.3002e-12 | 9.4899e-07 | 2.7403e-12 | 3.5623e-07
480 | feeder2_line79 | 1 | 354.6 | 1.2935 | 1.2931 | 0.36478 | 0.36465
480 | feeder2_line79 | 2 | 354.6 | 5.0303 | 5.03 | 1.4186 | 1.4185
480 | feeder2_line79 | 3 | 354.6 | 13.002 | 13.0019 | 3.6667 | 3.6666
480 | feeder2_line80 | 1 | 354.6 | 92.7591 | 92.7545 | 26.1588 | 26.1575
480 | feeder2_line80 | 2 | 354.6 | 91.3751 | 91.373 | 25.7685 | 25.7679
480 | feeder2_line80 | 3 | 354.6 | 85.2317 | 85.2364 | 24.036 | 24.0373
480 | feeder2_line81 | 1 | 354.6 | 92.7591 | 92.7545 | 26.1588 | 26.1575
480 | feeder2_line81 | 2 | 354.6 | 91.3751 | 91.373 | 25.7685 | 25.7679
480 | feeder2_line81 | 3 | 354.6 | 85.3016 | 85.3063 | 24.0557 | 24.0571
480 | feeder2_line82 | 1 | 354.6 | 1.3457e-11 | 7.3751e-07 | 3.7951e-12 | 2.0799e-07
480 | feeder2_line82 | 2 | 354.6 | 1.8129e-11 | 7.3843e-07 | 5.1124e-12 | 2.0824e-07
480 | feeder2_line82 | 3 | 354.6 | 0.070171 | 0.070177 | 0.019789 | 0.01979
480 | feeder2_line83 | 1 | 354.6 | 92.7593 | 92.7545 | 26.1588 | 26.1575
480 | feeder2_line83 | 2 | 354.6 | 91.4636 | 91.4613 | 25.7935 | 25.7928
480 | feeder2_line83 | 3 | 354.6 | 85.3018 | 85.3063 | 24.0558 | 24.0571
480 | feeder2_line84 | 1 | 354.6 | 9.5942e-12 | 1.3037e-06 | 2.7056e-12 | 3.6766e-07
480 | feeder2_line84 | 2 | 354.6 | 0.088508 | 0.088489 | 0.02496 | 0.024955
480 | feeder2_line84 | 3 | 354.6 | 1.0958e-11 | 1.291e-06 | 3.0902e-12 | 3.6407e-07
480 | feeder2_line85 | 1 | 99 | 1.3303 | 1.3303 | 1.3438 | 1.3438
480 | feeder2_line85 | 2 | 99 | 4.9676e-08 | 4.6609e-07 | 5.0178e-08 | 4.708e-07
480 | feeder2_line85 | 3 | 99 | 5.0959e-08 | 4.605e-07 | 5.1473e-08 | 4.6515e-07
480 | feeder2_line86 | 1 | 354.6 | 93.3793 | 93.3744 | 26.3337 | 26.3323
480 | feeder2_line86 | 2 | 354.6 | 91.4637 | 91.4613 | 25.7935 | 25.7928
480 | feeder2_line86 | 3 | 354.6 | 85.3019 | 85.3063 | 24.0558 | 24.0571
480 | feeder2_line87 | 1 | 354.6 | 93.3795 | 93.3744 | 26.3338 | 26.3323
480 | feeder2_line87 | 2 | 354.6 | 93.1861 | 93.1835 | 26.2792 | 26.2785
480 | feeder2_line87 | 3 | 354.6 | 92.9049 | 92.9091 | 26.1999 | 26.2011
480 | feeder2_line88 | 1 | 354.6 | 0.00011783 | 3.3812e-06 | 3.3229e-05 | 9.5351e-07
480 | feeder2_line88 | 2 | 354.6 | 2.7654 | 2.7653 | 0.77988 | 0.77985
480 | feeder2_line88 | 3 | 354.6 | 7.8053 | 7.8051 | 2.2012 | 2.2011
480 | feeder2_line89 | 1 | 354.6 | 93.3772 | 93.3744 | 26.3331 | 26.3323
480 | feeder2_line89 | 2 | 354.6 | 94.0709 | 94.0706 | 26.5287 | 26.5287
480 | feeder2_line89 | 3 | 354.6 | 92.9027 | 92.9091 | 26.1993 | 26.2011
480 | feeder2_line90 | 1 | 354.6 | 0.00073075 | 2.0408e-06 | 0.00020608 | 5.7551e-07
480 | feeder2_line90 | 2 | 354.6 | 0.88793 | 0.88842 | 0.2504 | 0.25054
480 | feeder2_line90 | 3 | 354.6 | 0.00071615 | 2.0206e-06 | 0.00020196 | 5.6983e-07
480 | feeder2_line91 | 1 | 354.6 | 93.3771 | 93.3744 | 26.3331 | 26.3323
480 | feeder2_line91 | 2 | 354.6 | 94.0709 | 94.0706 | 26.5287 | 26.5287
480 | feeder2_line91 | 3 | 354.6 | 96.5184 | 96.5249 | 27.2189 | 27.2208
480 | feeder2_line92 | 1 | 354.6 | 1.742e-11 | 1.0294e-06 | 4.9126e-12 | 2.9031e-07
480 | feeder2_line92 | 2 | 354.6 | 2.3224e-11 | 1.0307e-06 | 6.5494e-12 | 2.9068e-07
480 | feeder2_line92 | 3 | 354.6 | 4.04 | 4.04 | 1.1393 | 1.1393
480 | feeder2_line93 | 1 | 99 | 2.4742e-08 | 3.4375e-07 | 2.4991e-08 | 3.4722e-07
480 | feeder2_line93 | 2 | 99 | 0.088442 | 0.088421 | 0.089335 | 0.089315
480 | feeder2_line93 | 3 | 99 | 2.5499e-08 | 3.4003e-07 | 2.5756e-08 | 3.4346e-07
480 | feeder2_line94 | 1 | 354.6 | 2.4737e-06 | 1.6729e-06 | 6.976e-07 | 4.7178e-07
480 | feeder2_line94 | 2 | 354.6 | 0.80004 | 0.80001 | 0.22562 | 0.22561
480 | feeder2_line94 | 3 | 354.6 | 2.5498e-06 | 1.6566e-06 | 7.1907e-07 | 4.6716e-07
480 | feeder2_line95 | 1 | 99 | 3.5842e-06 | 2.622e-06 | 3.6205e-06 | 2.6485e-06
480 | feeder2_line95 | 2 | 99 | 2.7654 | 2.7653 | 2.7933 | 2.7933
480 | feeder2_line95 | 3 | 99 | 3.5375e-06 | 2.5936e-06 | 3.5732e-06 | 2.6198e-06
480 | feeder2_line96 | 1 | 354.6 | 0.00012181 | 6.2477e-07 | 3.4352e-05 | 1.7619e-07
480 | feeder2_line96 | 2 | 354.6 | 0.00012185 | 6.2583e-07 | 3.4362e-05 | 1.7649e-07
480 | feeder2_line96 | 3 | 354.6 | 7.8053 | 7.8051 | 2.2011 | 2.2011
480 | feeder2_line97 | 1 | 354.6 | 93.477 | 93.4741 | 26.3613 | 26.3604
480 | feeder2_line97 | 2 | 354.6 | 94.071 | 94.0706 | 26.5288 | 26.5287
480 | feeder2_line97 | 3 | 354.6 | 96.5185 | 96.5249 | 27.219 | 27.2208
480 | feeder2_line98 | 1 | 354.6 | 0.10196 | 0.10023 | 0.028752 | 0.028266
480 | feeder2_line98 | 2 | 354.6 | 0.0017063 | 6.278e-07 | 0.00048119 | 1.7704e-07
480 | feeder2_line98 | 3 | 354.6 | 0.0016792 | 6.1844e-07 | 0.00047353 | 1.7441e-07
480 | feeder2_line99 | 1 | 99 | 2.4725e-08 | 4.4935e-07 | 2.4975e-08 | 4.5388e-07
480 | feeder2_line99 | 2 | 99 | 2.484e-08 | 4.4988e-07 | 2.5091e-08 | 4.5442e-07
480 | feeder2_line99 | 3 | 99 | 7.8052 | 7.8051 | 7.884 | 7.884
480 | feeder2_line100 | 1 | 99 | 0.10024 | 0.10023 | 0.10125 | 0.10124
480 | feeder2_line100 | 2 | 99 | 2.4866e-08 | 6.1791e-07 | 2.5117e-08 | 6.2415e-07
480 | feeder2_line100 | 3 | 99 | 2.5504e-08 | 6.1052e-07 | 2.5762e-08 | 6.1668e-07
480 | feeder2_line101 | 1 | 354.6 | 0.80015 | 0.79972 | 0.22565 | 0.22553
480 | feeder2_line101 | 2 | 354.6 | 5.0303 | 5.03 | 1.4186 | 1.4185
480 | feeder2_line101 | 3 | 354.6 | 13.002 | 13.0019 | 3.6667 | 3.6666
480 | feeder2_line102 | 1 | 99 | 0.49379 | 0.49378 | 0.49878 | 0.49877
480 | feeder2_line102 | 2 | 99 | 2.3473e-06 | 8.831e-07 | 2.371e-06 | 8.9202e-07
480 | feeder2_line102 | 3 | 99 | 2.3064e-06 | 8.7241e-07 | 2.3297e-06 | 8.8122e-07
480 | feeder2_line103 | 1 | 99 | 5.5209e-07 | 8.0734e-07 | 5.5767e-07 | 8.155e-07
480 | feeder2_line103 | 2 | 99 | 0.4122 | 0.41219 | 0.41636 | 0.41636
480 | feeder2_line103 | 3 | 99 | 5.4489e-07 | 7.9846e-07 | 5.5039e-07 | 8.0652e-07
480 | feeder2_line104 | 1 | 354.6 | 0.80004 | 0.79972 | 0.22562 | 0.22553
480 | feeder2_line104 | 2 | 354.6 | 4.7476 | 4.7474 | 1.3389 | 1.3388
480 | feeder2_line104 | 3 | 354.6 | 13.002 | 13.0019 | 3.6667 | 3.6666
480 | feeder2_line105 | 1 | 99 | 2.563e-06 | 7.4287e-07 | 2.5888e-06 | 7.5037e-07
480 | feeder2_line105 | 2 | 99 | 2.5649e-06 | 7.4375e-07 | 2.5908e-06 | 7.5127e-07
480 | feeder2_line105 | 3 | 99 | 1.0936 | 1.0936 | 1.1047 | 1.1047
480 | feeder2_line106 | 1 | 354.6 | 0.79999 | 0.79972 | 0.2256 | 0.22553
480 | feeder2_line106 | 2 | 354.6 | 4.7475 | 4.7474 | 1.3388 | 1.3388
480 | feeder2_line106 | 3 | 354.6 | 12.0342 | 12.0342 | 3.3937 | 3.3937
480 | feeder2_line107 | 1 | 99 | 3.2544e-07 | 9.053e-07 | 3.2872e-07 | 9.1445e-07
480 | feeder2_line107 | 2 | 99 | 1.1944 | 1.1944 | 1.2064 | 1.2065
480 | feeder2_line107 | 3 | 99 | 3.2335e-07 | 8.9516e-07 | 3.2662e-07 | 9.042e-07
480 | feeder2_line108 | 1 | 354.6 | 0.79998 | 0.79972 | 0.2256 | 0.22553
480 | feeder2_line108 | 2 | 354.6 | 3.5797 | 3.5795 | 1.0095 | 1.0095
480 | feeder2_line108 | 3 | 354.6 | 12.0342 | 12.0342 | 3.3937 | 3.3937
480 | feeder2_line109 | 1 | 354.6 | 94.7227 | 94.7185 | 26.7126 | 26.7114
480 | feeder2_line109 | 2 | 354.6 | 94.0723 | 94.0706 | 26.5291 | 26.5287
480 | feeder2_line109 | 3 | 354.6 | 96.5197 | 96.5249 | 27.2193 | 27.2208
480 | feeder2_line110 | 1 | 99 | 2.5388 | 2.5383 | 2.5645 | 2.5639
480 | feeder2_line110 | 2 | 99 | 0.00081106 | 9.1454e-07 | 0.00081925 | 9.2378e-07
480 | feeder2_line110 | 3 | 99 | 0.00079626 | 9.0368e-07 | 0.00080431 | 9.1281e-07
480 | feeder2_line111 | 1 | 99 | 2.4713e-08 | 3.8377e-07 | 2.4963e-08 | 3.8765e-07
480 | feeder2_line111 | 2 | 99 | 0.60944 | 0.60942 | 0.6156 | 0.61558
480 | feeder2_line111 | 3 | 99 | 2.5491e-08 | 3.7961e-07 | 2.5748e-08 | 3.8345e-07
480 | feeder2_line112 | 1 | 99 | 3.257e-07 | 9.2222e-07 | 3.2899e-07 | 9.3153e-07
480 | feeder2_line112 | 2 | 99 | 2.3972 | 2.3971 | 2.4214 | 2.4213
480 | feeder2_line112 | 3 | 99 | 3.237e-07 | 9.1222e-07 | 3.2697e-07 | 9.2144e-07
480 | feeder2_line113 | 1 | 99 | 1.4193 | 1.4193 | 1.4337 | 1.4336
480 | feeder2_line113 | 2 | 99 | 3.2659e-07 | 9.1136e-07 | 3.2989e-07 | 9.2056e-07
480 | feeder2_line113 | 3 | 99 | 3.2406e-07 | 9.0049e-07 | 3.2734e-07 | 9.0958e-07
480 | feeder2_line114 | 1 | 99 | 0.41247 | 0.41247 | 0.41664 | 0.41663
480 | feeder2_line114 | 2 | 99 | 2.4819e-08 | 4.3912e-07 | 2.507e-08 | 4.4356e-07
480 | feeder2_line114 | 3 | 99 | 2.5471e-08 | 4.3381e-07 | 2.5728e-08 | 4.382e-07
480 | feeder2_line115 | 1 | 99 | 2.4693e-08 | 5.6496e-07 | 2.4942e-08 | 5.7067e-07
480 | feeder2_line115 | 2 | 99 | 1.3236 | 1.3236 | 1.337 | 1.337
480 | feeder2_line115 | 3 | 99 | 2.5486e-08 | 5.5854e-07 | 2.5744e-08 | 5.6419e-07
480 | feeder2_line116 | 1 | 354.6 | 0.79999 | 0.79972 | 0.2256 | 0.22553
480 | feeder2_line116 | 2 | 354.6 | 2.328 | 2.3278 | 0.65652 | 0.65646
480 | feeder2_line116 | 3 | 354.6 | 12.0342 | 12.0342 | 3.3937 | 3.3937
480 | feeder2_line117 | 1 | 99 | 4.9541e-08 | 6.4644e-07 | 5.0041e-08 | 6.5297e-07
480 | feeder2_line117 | 2 | 99 | 0.071523 | 0.071495 | 0.072245 | 0.072217
480 | feeder2_line117 | 3 | 99 | 5.1046e-08 | 6.3953e-07 | 5.1562e-08 | 6.4599e-07
480 | feeder2_line118 | 1 | 354.6 | 94.7228 | 94.7185 | 26.7126 | 26.7114
480 | feeder2_line118 | 2 | 354.6 | 94.1437 | 94.142 | 26.5493 | 26.5488
480 | feeder2_line118 | 3 | 354.6 | 96.5197 | 96.5249 | 27.2193 | 27.2208
480 | feeder2_line119 | 1 | 99 | 2.469e-08 | 6.0792e-07 | 2.4939e-08 | 6.1406e-07
480 | feeder2_line119 | 2 | 99 | 2.4804e-08 | 6.0866e-07 | 2.5054e-08 | 6.148e-07
480 | feeder2_line119 | 3 | 99 | 1.5689 | 1.5689 | 1.5847 | 1.5848
480 | feeder2_line120 | 1 | 354.6 | 0.79999 | 0.79972 | 0.2256 | 0.22553
480 | feeder2_line120 | 2 | 354.6 | 2.328 | 2.3278 | 0.65652 | 0.65646
480 | feeder2_line120 | 3 | 354.6 | 10.6347 | 10.6346 | 2.9991 | 2.999
480 | feeder2_line121 | 1 | 99 | 3.2543e-07 | 9.414e-07 | 3.2872e-07 | 9.5091e-07
480 | feeder2_line121 | 2 | 99 | 0.04374 | 0.04374 | 0.044182 | 0.044182
480 | feeder2_line121 | 3 | 99 | 3.2324e-07 | 9.304e-07 | 3.2651e-07 | 9.398e-07
480 | feeder2_line122 | 1 | 354.6 | 0.79997 | 0.79972 | 0.2256 | 0.22553
480 | feeder2_line122 | 2 | 354.6 | 2.2906 | 2.2904 | 0.64596 | 0.64591
480 | feeder2_line122 | 3 | 354.6 | 10.6346 | 10.6346 | 2.9991 | 2.999
480 | feeder2_line123 | 1 | 99 | 5.7682e-07 | 9.7551e-07 | 5.8265e-07 | 9.8537e-07
480 | feeder2_line123 | 2 | 99 | 5.7753e-07 | 9.7672e-07 | 5.8336e-07 | 9.8659e-07
480 | feeder2_line123 | 3 | 99 | 0.10939 | 0.10939 | 0.11049 | 0.1105
480 | feeder2_line124 | 1 | 354.6 | 0.79988 | 0.79972 | 0.22557 | 0.22553
480 | feeder2_line124 | 2 | 354.6 | 2.2906 | 2.2904 | 0.64596 | 0.64591
480 | feeder2_line124 | 3 | 354.6 | 10.5478 | 10.5478 | 2.9746 | 2.9746
480 | feeder2_line125 | 1 | 99 | 5.7682e-07 | 9.0684e-07 | 5.8265e-07 | 9.16e-07
480 | feeder2_line125 | 2 | 99 | 5.7753e-07 | 9.0797e-07 | 5.8336e-07 | 9.1714e-07
480 | feeder2_line125 | 3 | 99 | 0.1021 | 0.10214 | 0.10314 | 0.10317
480 | feeder2_line126 | 1 | 354.6 | 0.80004 | 0.79972 | 0.22562 | 0.22553
480 | feeder2_line126 | 2 | 354.6 | 2.2907 | 2.2904 | 0.64601 | 0.64591
480 | feeder2_line126 | 3 | 354.6 | 10.461 | 10.4608 | 2.9501 | 2.95
480 | feeder2_line127 | 1 | 99 | 5.7682e-07 | 1.0856e-06 | 5.8265e-07 | 1.0966e-06
480 | feeder2_line127 | 2 | 99 | 5.7754e-07 | 1.087e-06 | 5.8337e-07 | 1.098e-06
480 | feeder2_line127 | 3 | 99 | 0.96566 | 0.96564 | 0.97542 | 0.9754
480 | feeder2_line128 | 1 | 354.6 | 0.79995 | 0.79972 | 0.22559 | 0.22553
480 | feeder2_line128 | 2 | 354.6 | 2.2907 | 2.2904 | 0.64599 | 0.64591
480 | feeder2_line128 | 3 | 354.6 | 9.5744 | 9.5742 | 2.7 | 2.7
480 | feeder2_line129 | 1 | 99 | 5.5214e-07 | 8.8029e-07 | 5.5772e-07 | 8.8918e-07
480 | feeder2_line129 | 2 | 99 | 2.2904 | 2.2904 | 2.3136 | 2.3136
480 | feeder2_line129 | 3 | 99 | 5.4436e-07 | 8.698e-07 | 5.4985e-07 | 8.7859e-07
480 | feeder2_line130 | 1 | 354.6 | 0.79997 | 0.79972 | 0.2256 | 0.22553
480 | feeder2_line130 | 2 | 354.6 | 0.00031101 | 4.6636e-06 | 8.7708e-05 | 1.3152e-06
480 | feeder2_line130 | 3 | 354.6 | 9.5744 | 9.5742 | 2.7001 | 2.7
480 | feeder2_line131 | 1 | 99 | 5.7681e-07 | 9.7565e-07 | 5.8264e-07 | 9.8551e-07
480 | feeder2_line131 | 2 | 99 | 5.7754e-07 | 9.769e-07 | 5.8337e-07 | 9.8677e-07
480 | feeder2_line131 | 3 | 99 | 8.4012 | 8.4013 | 8.4861 | 8.4862
480 | feeder2_line132 | 1 | 354.6 | 0.7998 | 0.79972 | 0.22555 | 0.22553
480 | feeder2_line132 | 2 | 354.6 | 0.0001266 | 2.9319e-06 | 3.5704e-05 | 8.2682e-07
480 | feeder2_line132 | 3 | 354.6 | 1.3223 | 1.3221 | 0.37289 | 0.37285
480 | feeder2_line133 | 1 | 99 | 0.79973 | 0.79972 | 0.80781 | 0.8078
480 | feeder2_line133 | 2 | 99 | 3.0117e-07 | 9.8472e-07 | 3.0421e-07 | 9.9467e-07
480 | feeder2_line133 | 3 | 99 | 2.9766e-07 | 9.7167e-07 | 3.0067e-07 | 9.8148e-07
480 | feeder2_line134 | 1 | 354.6 | 3.7257e-12 | 1.7927e-06 | 1.0507e-12 | 5.0556e-07
480 | feeder2_line134 | 2 | 354.6 | 5.858e-12 | 1.7952e-06 | 1.652e-12 | 5.0626e-07
480 | feeder2_line134 | 3 | 354.6 | 1.3221 | 1.3221 | 0.37285 | 0.37285
480 | feeder2_line135 | 1 | 99 | 1.2514 | 1.2514 | 1.2641 | 1.264
480 | feeder2_line135 | 2 | 99 | 4.9816e-08 | 5.8999e-07 | 5.0319e-08 | 5.9595e-07
480 | feeder2_line135 | 3 | 99 | 5.1071e-08 | 5.8302e-07 | 5.1587e-08 | 5.8891e-07
480 | feeder2_line136 | 1 | 354.6 | 95.3284 | 95.3241 | 26.8833 | 26.8822
480 | feeder2_line136 | 2 | 354.6 | 94.1436 | 94.142 | 26.5493 | 26.5488
480 | feeder2_line136 | 3 | 354.6 | 96.5197 | 96.5249 | 27.2193 | 27.2208
480 | feeder2_line137 | 1 | 99 | 1.1935 | 1.1935 | 1.2056 | 1.2055
480 | feeder2_line137 | 2 | 99 | 8.5647e-07 | 1.5892e-06 | 8.6512e-07 | 1.6053e-06
480 | feeder2_line137 | 3 | 99 | 8.4577e-07 | 1.5705e-06 | 8.5431e-07 | 1.5863e-06
480 | feeder2_line138 | 1 | 354.6 | 95.9461 | 95.9418 | 27.0576 | 27.0564
480 | feeder2_line138 | 2 | 354.6 | 94.1437 | 94.142 | 26.5493 | 26.5488
480 | feeder2_line138 | 3 | 354.6 | 96.5198 | 96.5249 | 27.2193 | 27.2208
480 | feeder2_line139 | 1 | 99 | 4.9588e-08 | 4.9467e-07 | 5.0089e-08 | 4.9966e-07
480 | feeder2_line139 | 2 | 99 | 4.9828e-08 | 4.9523e-07 | 5.0331e-08 | 5.0023e-07
480 | feeder2_line139 | 3 | 99 | 2.1852 | 2.1854 | 2.2072 | 2.2075
480 | feeder2_line140 | 1 | 354.6 | 95.9462 | 95.9418 | 27.0576 | 27.0564
480 | feeder2_line140 | 2 | 354.6 | 94.1438 | 94.142 | 26.5493 | 26.5488
480 | feeder2_line140 | 3 | 354.6 | 98.3177 | 98.3231 | 27.7264 | 27.7279
480 | feeder2_line141 | 1 | 99 | 2.5471e-06 | 4.8938e-07 | 2.5728e-06 | 4.9433e-07
480 | feeder2_line141 | 2 | 99 | 0.076348 | 0.076345 | 0.077119 | 0.077117
480 | feeder2_line141 | 3 | 99 | 2.5052e-06 | 4.8418e-07 | 2.5306e-06 | 4.8907e-07
480 | feeder2_line142 | 1 | 354.6 | 95.9461 | 95.9418 | 27.0575 | 27.0564
480 | feeder2_line142 | 2 | 354.6 | 94.2199 | 94.2183 | 26.5708 | 26.5703
480 | feeder2_line142 | 3 | 354.6 | 98.3175 | 98.3231 | 27.7263 | 27.7279
480 | feeder2_line143 | 1 | 99 | 8.5591e-07 | 1.7391e-06 | 8.6455e-07 | 1.7566e-06
480 | feeder2_line143 | 2 | 99 | 1.1957 | 1.1957 | 1.2077 | 1.2078
480 | feeder2_line143 | 3 | 99 | 8.4618e-07 | 1.7206e-06 | 8.5473e-07 | 1.738e-06
480 | feeder2_line144 | 1 | 354.6 | 95.9459 | 95.9418 | 27.0575 | 27.0564
480 | feeder2_line144 | 2 | 354.6 | 94.8438 | 94.8423 | 26.7467 | 26.7463
480 | feeder2_line144 | 3 | 354.6 | 98.3173 | 98.3231 | 27.7263 | 27.7279
480 | feeder2_line145 | 1 | 99 | 2.4808e-08 | 4.8766e-07 | 2.5058e-08 | 4.9259e-07
480 | feeder2_line145 | 2 | 99 | 0.069066 | 0.069063 | 0.069763 | 0.069761
480 | feeder2_line145 | 3 | 99 | 2.5552e-08 | 4.8248e-07 | 2.581e-08 | 4.8735e-07
480 | feeder2_line146 | 1 | 354.6 | 95.9458 | 95.9418 | 27.0575 | 27.0564
480 | feeder2_line146 | 2 | 354.6 | 94.9127 | 94.9113 | 26.7661 | 26.7657
480 | feeder2_line146 | 3 | 354.6 | 98.3172 | 98.3231 | 27.7262 | 27.7279
480 | feeder2_line147 | 1 | 99 | 1.1197 | 1.1196 | 1.131 | 1.1309
480 | feeder2_line147 | 2 | 99 | 1.1593e-06 | 2.252e-06 | 1.171e-06 | 2.2748e-06
480 | feeder2_line147 | 3 | 99 | 1.1455e-06 | 2.2255e-06 | 1.157e-06 | 2.248e-06
480 | feeder2_line148 | 1 | 99 | 0.084253 | 0.084248 | 0.085104 | 0.085099
480 | feeder2_line148 | 2 | 99 | 6.0454e-07 | 1.509e-06 | 6.1065e-07 | 1.5243e-06
480 | feeder2_line148 | 3 | 99 | 5.983e-07 | 1.4913e-06 | 6.0434e-07 | 1.5064e-06
480 | feeder2_line149 | 1 | 354.6 | 96.6199 | 96.6158 | 27.2476 | 27.2464
480 | feeder2_line149 | 2 | 354.6 | 94.9128 | 94.9113 | 26.7662 | 26.7657
480 | feeder2_line149 | 3 | 354.6 | 98.3174 | 98.3231 | 27.7263 | 27.7279
480 | feeder2_line150 | 1 | 354.6 | 96.62 | 96.6158 | 27.2476 | 27.2464
480 | feeder2_line150 | 2 | 354.6 | 97.303 | 97.3014 | 27.4402 | 27.4398
480 | feeder2_line150 | 3 | 354.6 | 98.3175 | 98.3231 | 27.7263 | 27.7279
480 | feeder2_line151 | 1 | 99 | 9.8569e-06 | 1.7907e-06 | 9.9565e-06 | 1.8088e-06
480 | feeder2_line151 | 2 | 99 | 2.7572 | 2.7573 | 2.7851 | 2.7851
480 | feeder2_line151 | 3 | 99 | 9.6745e-06 | 1.7717e-06 | 9.7723e-06 | 1.7896e-06
480 | feeder2_line152 | 1 | 354.6 | 1.1574e-11 | 1.1932e-06 | 3.2641e-12 | 3.3649e-07
480 | feeder2_line152 | 2 | 354.6 | 4.1983e-12 | 1.1946e-06 | 1.184e-12 | 3.3689e-07
480 | feeder2_line152 | 3 | 354.6 | 1.1832 | 1.1832 | 0.33367 | 0.33366
480 | feeder2_line153 | 1 | 99 | 0.043577 | 0.043575 | 0.044017 | 0.044015
480 | feeder2_line153 | 2 | 99 | 4.9897e-08 | 5.9786e-07 | 5.0401e-08 | 6.039e-07
480 | feeder2_line153 | 3 | 99 | 5.1152e-08 | 5.9087e-07 | 5.1669e-08 | 5.9684e-07
480 | feeder2_line154 | 1 | 99 | 5.7951e-07 | 8.8865e-07 | 5.8536e-07 | 8.9763e-07
480 | feeder2_line154 | 2 | 99 | 5.8014e-07 | 8.8964e-07 | 5.86e-07 | 8.9862e-07
480 | feeder2_line154 | 3 | 99 | 0.040957 | 0.040994 | 0.041371 | 0.041408
480 | feeder2_line155 | 1 | 99 | 96.6633 | 96.6592 | 97.6397 | 97.6356
480 | feeder2_line155 | 2 | 99 | 97.3029 | 97.3014 | 98.2857 | 98.2842
480 | feeder2_line155 | 3 | 99 | 99 | 99.0058 | 100 | 100.0058
480 | feeder2_line156 | 1 | 99 | 6.0408e-07 | 1.1693e-06 | 6.1018e-07 | 1.1811e-06
480 | feeder2_line156 | 2 | 99 | 0.41067 | 0.41066 | 0.41482 | 0.41481
480 | feeder2_line156 | 3 | 99 | 5.9861e-07 | 1.1569e-06 | 6.0465e-07 | 1.1686e-06
480 | feeder2_line157 | 1 | 99 | 2.4821e-08 | 2.5385e-07 | 2.5072e-08 | 2.5642e-07
480 | feeder2_line157 | 2 | 99 | 2.4154 | 2.4154 | 2.4398 | 2.4398
480 | feeder2_line157 | 3 | 99 | 2.5564e-08 | 2.5116e-07 | 2.5822e-08 | 2.537e-07
510 | feeder2_line1 | 1 | 354.6 | 64.5866 | 64.5945 | 18.2139 | 18.2162
510 | feeder2_line1 | 2 | 354.6 | 75.0416 | 75.0405 | 21.1623 | 21.162
510 | feeder2_line1 | 3 | 354.6 | 55.2125 | 55.2076 | 15.5704 | 15.569
510 | feeder2_line2 | 1 | 354.6 | 67.7006 | 67.7084 | 19.0921 | 19.0943
510 | feeder2_line2 | 2 | 354.6 | 75.0418 | 75.0405 | 21.1624 | 21.162
510 | feeder2_line2 | 3 | 354.6 | 55.2127 | 55.2076 | 15.5704 | 15.569
510 | feeder2_line3 | 1 | 80.1 | 3.4594 | 3.4595 | 4.3189 | 4.319
510 | feeder2_line3 | 2 | 80.1 | 5.7249e-07 | 1.058e-06 | 7.1472e-07 | 1.3208e-06
510 | feeder2_line3 | 3 | 80.1 | 5.7163e-07 | 1.0564e-06 | 7.1365e-07 | 1.3188e-06
510 | feeder2_line4 | 1 | 354.6 | 67.7007 | 67.7084 | 19.0921 | 19.0943
510 | feeder2_line4 | 2 | 354.6 | 75.1316 | 75.1302 | 21.1877 | 21.1873
510 | feeder2_line4 | 3 | 354.6 | 55.2128 | 55.2076 | 15.5705 | 15.569
510 | feeder2_line5 | 1 | 80.1 | 5.7203e-07 | 9.9813e-07 | 7.1414e-07 | 1.2461e-06
510 | feeder2_line5 | 2 | 80.1 | 0.089988 | 0.089988 | 0.11234 | 0.11234
510 | feeder2_line5 | 3 | 80.1 | 5.7166e-07 | 9.9751e-07 | 7.1368e-07 | 1.2453e-06
510 | feeder2_line6 | 1 | 80.1 | 5.7209e-07 | 1.1743e-06 | 7.1422e-07 | 1.4661e-06
510 | feeder2_line6 | 2 | 80.1 | 5.7262e-07 | 1.1754e-06 | 7.1489e-07 | 1.4674e-06
510 | feeder2_line6 | 3 | 80.1 | 0.90184 | 0.90181 | 1.1259 | 1.1259
510 | feeder2_line7 | 1 | 354.6 | 67.7009 | 67.7084 | 19.0922 | 19.0943
510 | feeder2_line7 | 2 | 354.6 | 75.1318 | 75.1302 | 21.1878 | 21.1873
510 | feeder2_line7 | 3 | 354.6 | 55.6415 | 55.6361 | 15.6913 | 15.6898
510 | feeder2_line8 | 1 | 80.1 | 0.072605 | 0.072606 | 0.090643 | 0.090644
510 | feeder2_line8 | 2 | 80.1 | 5.7286e-07 | 1.1338e-06 | 7.1518e-07 | 1.4155e-06
510 | feeder2_line8 | 3 | 80.1 | 5.7179e-07 | 1.1317e-06 | 7.1384e-07 | 1.4129e-06
510 | feeder2_line9 | 1 | 354.6 | 67.7733 | 67.7808 | 19.1126 | 19.1147
510 | feeder2_line9 | 2 | 354.6 | 75.1318 | 75.1302 | 21.1878 | 21.1873
510 | feeder2_line9 | 3 | 354.6 | 55.6415 | 55.6361 | 15.6914 | 15.6898
510 | feeder2_line10 | 1 | 80.1 | 8.4602e-07 | 1.4956e-06 | 1.0562e-06 | 1.8672e-06
510 | feeder2_line10 | 2 | 80.1 | 0.072513 | 0.072513 | 0.090528 | 0.090528
510 | feeder2_line10 | 3 | 80.1 | 8.4522e-07 | 1.4943e-06 | 1.0552e-06 | 1.8656e-06
510 | feeder2_line11 | 1 | 354.6 | 67.7733 | 67.7808 | 19.1126 | 19.1147
510 | feeder2_line11 | 2 | 354.6 | 75.2041 | 75.2025 | 21.2082 | 21.2077
510 | feeder2_line11 | 3 | 354.6 | 55.6415 | 55.6361 | 15.6913 | 15.6898
510 | feeder2_line12 | 1 | 80.1 | 5.4752e-07 | 9.9221e-07 | 6.8355e-07 | 1.2387e-06
510 | feeder2_line12 | 2 | 80.1 | 5.4813e-07 | 9.9325e-07 | 6.8431e-07 | 1.24e-06
510 | feeder2_line12 | 3 | 80.1 | 2.3974 | 2.3974 | 2.993 | 2.993
510 | feeder2_line13 | 1 | 354.6 | 67.7733 | 67.7808 | 19.1126 | 19.1147
510 | feeder2_line13 | 2 | 354.6 | 75.2041 | 75.2025 | 21.2081 | 21.2077
510 | feeder2_line13 | 3 | 354.6 | 57.3567 | 57.3513 | 16.175 | 16.1735
510 | feeder2_line14 | 1 | 80.1 | 1.3083 | 1.3083 | 1.6334 | 1.6333
510 | feeder2_line14 | 2 | 80.1 | 2.9895e-07 | 6.4777e-07 | 3.7322e-07 | 8.087e-07
510 | feeder2_line14 | 3 | 80.1 | 2.9842e-07 | 6.4645e-07 | 3.7256e-07 | 8.0705e-07
510 | feeder2_line15 | 1 | 354.6 | 69.0455 | 69.053 | 19.4714 | 19.4735
510 | feeder2_line15 | 2 | 354.6 | 75.2041 | 75.2025 | 21.2082 | 21.2077
510 | feeder2_line15 | 3 | 354.6 | 57.3567 | 57.3513 | 16.175 | 16.1735
510 | feeder2_line16 | 1 | 80.1 | 5.7254e-07 | 1.0315e-06 | 7.1479e-07 | 1.2877e-06
510 | feeder2_line16 | 2 | 80.1 | 0.99466 | 0.99466 | 1.2418 | 1.2418
510 | feeder2_line16 | 3 | 80.1 | 5.7193e-07 | 1.0304e-06 | 7.1403e-07 | 1.2864e-06
510 | feeder2_line17 | 1 | 354.6 | 69.0455 | 69.053 | 19.4714 | 19.4735
510 | feeder2_line17 | 2 | 354.6 | 76.1986 | 76.1969 | 21.4886 | 21.4881
510 | feeder2_line17 | 3 | 354.6 | 57.3567 | 57.3513 | 16.1751 | 16.1735
510 | feeder2_line18 | 1 | 80.1 | 5.4816e-07 | 7.3895e-07 | 6.8434e-07 | 9.2253e-07
510 | feeder2_line18 | 2 | 80.1 | 5.489e-07 | 7.399e-07 | 6.8527e-07 | 9.2372e-07
510 | feeder2_line18 | 3 | 80.1 | 0.040261 | 0.040241 | 0.050263 | 0.050239
510 | feeder2_line19 | 1 | 354.6 | 69.0456 | 69.053 | 19.4714 | 19.4735
510 | feeder2_line19 | 2 | 354.6 | 76.1986 | 76.1969 | 21.4886 | 21.4881
510 | feeder2_line19 | 3 | 354.6 | 57.3967 | 57.3912 | 16.1863 | 16.1848
510 | feeder2_line20 | 1 | 99 | 5.4833e-07 | 8.8623e-07 | 5.5387e-07 | 8.9518e-07
510 | feeder2_line20 | 2 | 99 | 5.491e-07 | 8.8741e-07 | 5.5465e-07 | 8.9638e-07
510 | feeder2_line20 | 3 | 99 | 0.086122 | 0.086098 | 0.086992 | 0.086968
510 | feeder2_line21 | 1 | 354.6 | 69.0457 | 69.053 | 19.4714 | 19.4735
510 | feeder2_line21 | 2 | 354.6 | 76.1987 | 76.1969 | 21.4886 | 21.4881
510 | feeder2_line21 | 3 | 354.6 | 57.4827 | 57.4771 | 16.2106 | 16.209
510 | feeder2_line22 | 1 | 99 | 5.733e-07 | 1.0161e-06 | 5.7909e-07 | 1.0264e-06
510 | feeder2_line22 | 2 | 99 | 9.455 | 9.455 | 9.5505 | 9.5505
510 | feeder2_line22 | 3 | 99 | 5.7234e-07 | 1.0145e-06 | 5.7812e-07 | 1.0247e-06
510 | feeder2_line23 | 1 | 99 | 5.7331e-07 | 9.512e-07 | 5.791e-07 | 9.6081e-07
510 | feeder2_line23 | 2 | 99 | 5.7409e-07 | 9.5251e-07 | 5.7989e-07 | 9.6213e-07
510 | feeder2_line23 | 3 | 99 | 2.2411 | 2.2412 | 2.2638 | 2.2638
510 | feeder2_line24 | 1 | 354.6 | 69.0457 | 69.053 | 19.4714 | 19.4735
510 | feeder2_line24 | 2 | 354.6 | 85.5511 | 85.5493 | 24.1261 | 24.1256
510 | feeder2_line24 | 3 | 354.6 | 59.2597 | 59.2541 | 16.7117 | 16.7101
510 | feeder2_line25 | 1 | 99 | 9.4445 | 9.4444 | 9.5399 | 9.5398
510 | feeder2_line25 | 2 | 99 | 4.972e-08 | 6.9282e-07 | 5.0222e-08 | 6.9982e-07
510 | feeder2_line25 | 3 | 99 | 5.0111e-08 | 6.9054e-07 | 5.0618e-08 | 6.9752e-07
510 | feeder2_line26 | 1 | 99 | 0.085125 | 0.085129 | 0.085985 | 0.085989
510 | feeder2_line26 | 2 | 99 | 5.4951e-07 | 8.5837e-07 | 5.5506e-07 | 8.6704e-07
510 | feeder2_line26 | 3 | 99 | 5.4741e-07 | 8.5555e-07 | 5.5294e-07 | 8.6419e-07
510 | feeder2_line27 | 1 | 354.6 | 78.4838 | 78.4909 | 22.133 | 22.1351
510 | feeder2_line27 | 2 | 354.6 | 85.5511 | 85.5493 | 24.1261 | 24.1256
510 | feeder2_line27 | 3 | 354.6 | 59.2597 | 59.2541 | 16.7117 | 16.7101
510 | feeder2_line28 | 1 | 99 | 2.546e-06 | 7.1189e-07 | 2.5717e-06 | 7.1908e-07
510 | feeder2_line28 | 2 | 99 | 0.076857 | 0.076856 | 0.077633 | 0.077632
510 | feeder2_line28 | 3 | 99 | 2.5369e-06 | 7.1038e-07 | 2.5625e-06 | 7.1755e-07
510 | feeder2_line29 | 1 | 354.6 | 78.4838 | 78.4909 | 22.133 | 22.1351
510 | feeder2_line29 | 2 | 354.6 | 85.6278 | 85.626 | 24.1477 | 24.1472
510 | feeder2_line29 | 3 | 354.6 | 59.2598 | 59.2541 | 16.7117 | 16.7101
510 | feeder2_line30 | 1 | 266.4 | 4.7041 | 4.7043 | 1.7658 | 1.7659
510 | feeder2_line30 | 2 | 266.4 | 2.3454 | 2.3453 | 0.88042 | 0.88035
510 | feeder2_line30 | 3 | 266.4 | 22.0478 | 22.0478 | 8.2762 | 8.2762
510 | feeder2_line31 | 1 | 354.6 | 81.8651 | 81.8721 | 23.0866 | 23.0886
510 | feeder2_line31 | 2 | 354.6 | 87.8059 | 87.8037 | 24.762 | 24.7613
510 | feeder2_line31 | 3 | 354.6 | 80.6894 | 80.6837 | 22.7551 | 22.7534
510 | feeder2_line32 | 1 | 354.6 | 81.8651 | 81.8721 | 23.0866 | 23.0886
510 | feeder2_line32 | 2 | 354.6 | 87.8828 | 87.8805 | 24.7836 | 24.783
510 | feeder2_line32 | 3 | 354.6 | 80.6895 | 80.6837 | 22.7551 | 22.7534
510 | feeder2_line33 | 1 | 99 | 4.9774e-08 | 6.8776e-07 | 5.0277e-08 | 6.9471e-07
510 | feeder2_line33 | 2 | 99 | 0.076854 | 0.076853 | 0.077631 | 0.077629
510 | feeder2_line33 | 3 | 99 | 5.0313e-08 | 6.859e-07 | 5.0822e-08 | 6.9282e-07
510 | feeder2_line34 | 1 | 354.6 | 81.8651 | 81.8721 | 23.0866 | 23.0886
510 | feeder2_line34 | 2 | 354.6 | 87.8827 | 87.8805 | 24.7836 | 24.783
510 | feeder2_line34 | 3 | 354.6 | 80.7752 | 80.7695 | 22.7792 | 22.7776
510 | feeder2_line35 | 1 | 99 | 2.9985e-07 | 7.6179e-07 | 3.0288e-07 | 7.6949e-07
510 | feeder2_line35 | 2 | 99 | 3.0038e-07 | 7.6317e-07 | 3.0341e-07 | 7.7088e-07
510 | feeder2_line35 | 3 | 99 | 0.085765 | 0.08576 | 0.086632 | 0.086627
510 | feeder2_line36 | 1 | 354.6 | 82.9443 | 82.9515 | 23.3909 | 23.393
510 | feeder2_line36 | 2 | 354.6 | 87.8827 | 87.8805 | 24.7836 | 24.783
510 | feeder2_line36 | 3 | 354.6 | 80.7751 | 80.7695 | 22.7792 | 22.7776
510 | feeder2_line37 | 1 | 99 | 1.4224 | 1.4226 | 1.4368 | 1.437
510 | feeder2_line37 | 2 | 99 | 3.0046e-07 | 8.4465e-07 | 3.0349e-07 | 8.5318e-07
510 | feeder2_line37 | 3 | 99 | 2.9926e-07 | 8.4077e-07 | 3.0228e-07 | 8.4927e-07
510 | feeder2_line38 | 1 | 99 | 3.2451e-07 | 7.7729e-07 | 3.2779e-07 | 7.8514e-07
510 | feeder2_line38 | 2 | 99 | 0.076929 | 0.076928 | 0.077706 | 0.077705
510 | feeder2_line38 | 3 | 99 | 3.241e-07 | 7.7511e-07 | 3.2737e-07 | 7.8294e-07
510 | feeder2_line39 | 1 | 266.4 | 4.7041 | 4.7043 | 1.7658 | 1.7659
510 | feeder2_line39 | 2 | 266.4 | 2.2732 | 2.273 | 0.85329 | 0.85322
510 | feeder2_line39 | 3 | 266.4 | 22.0478 | 22.0478 | 8.2762 | 8.2762
510 | feeder2_line40 | 1 | 354.6 | 92.391 | 92.3979 | 26.055 | 26.0569
510 | feeder2_line40 | 2 | 354.6 | 87.8828 | 87.8805 | 24.7836 | 24.783
510 | feeder2_line40 | 3 | 354.6 | 80.7752 | 80.7695 | 22.7792 | 22.7776
510 | feeder2_line41 | 1 | 99 | 9.4719 | 9.4718 | 9.5676 | 9.5675
510 | feeder2_line41 | 2 | 99 | 4.98e-08 | 7.3817e-07 | 5.0303e-08 | 7.4562e-07
510 | feeder2_line41 | 3 | 99 | 5.035e-08 | 7.3477e-07 | 5.0859e-08 | 7.4219e-07
510 | feeder2_line42 | 1 | 99 | 2.9963e-07 | 7.5025e-07 | 3.0266e-07 | 7.5783e-07
510 | feeder2_line42 | 2 | 99 | 3.0016e-07 | 7.5164e-07 | 3.032e-07 | 7.5923e-07
510 | feeder2_line42 | 3 | 99 | 0.077392 | 0.077388 | 0.078174 | 0.07817
510 | feeder2_line43 | 1 | 266.4 | 4.7042 | 4.7043 | 1.7658 | 1.7659
510 | feeder2_line43 | 2 | 266.4 | 2.2731 | 2.273 | 0.85327 | 0.85322
510 | feeder2_line43 | 3 | 266.4 | 21.9724 | 21.9724 | 8.2479 | 8.2479
510 | feeder2_line44 | 1 | 354.6 | 92.391 | 92.3979 | 26.055 | 26.0569
510 | feeder2_line44 | 2 | 354.6 | 87.8828 | 87.8805 | 24.7836 | 24.783
510 | feeder2_line44 | 3 | 354.6 | 80.8612 | 80.8554 | 22.8035 | 22.8019
510 | feeder2_line45 | 1 | 99 | 4.9801e-08 | 5.812e-07 | 5.0304e-08 | 5.8708e-07
510 | feeder2_line45 | 2 | 99 | 4.9818e-08 | 5.8224e-07 | 5.0322e-08 | 5.8812e-07
510 | feeder2_line45 | 3 | 99 | 0.08602 | 0.085981 | 0.086889 | 0.086849
510 | feeder2_line46 | 1 | 99 | 5.744e-07 | 1.3601e-06 | 5.802e-07 | 1.3738e-06
510 | feeder2_line46 | 2 | 99 | 5.7545e-07 | 1.3626e-06 | 5.8126e-07 | 1.3763e-06
510 | feeder2_line46 | 3 | 99 | 1.4697 | 1.4697 | 1.4846 | 1.4845
510 | feeder2_line47 | 1 | 266.4 | 4.7043 | 4.7043 | 1.7659 | 1.7659
510 | feeder2_line47 | 2 | 266.4 | 2.2732 | 2.273 | 0.8533 | 0.85322
510 | feeder2_line47 | 3 | 266.4 | 20.9485 | 20.9485 | 7.8635 | 7.8635
510 | feeder2_line48 | 1 | 99 | 2.2649 | 2.2649 | 2.2878 | 2.2878
510 | feeder2_line48 | 2 | 99 | 4.9744e-08 | 7.3364e-07 | 5.0247e-08 | 7.4105e-07
510 | feeder2_line48 | 3 | 99 | 5.03e-08 | 7.2999e-07 | 5.0808e-08 | 7.3736e-07
510 | feeder2_line49 | 1 | 266.4 | 2.5948 | 2.5948 | 0.97402 | 0.97404
510 | feeder2_line49 | 2 | 266.4 | 2.2732 | 2.273 | 0.85329 | 0.85322
510 | feeder2_line49 | 3 | 266.4 | 20.9484 | 20.9485 | 7.8635 | 7.8635
510 | feeder2_line50 | 1 | 99 | 5.7439e-07 | 1.2378e-06 | 5.8019e-07 | 1.2503e-06
510 | feeder2_line50 | 2 | 99 | 0.9037 | 0.90366 | 0.91282 | 0.91279
510 | feeder2_line50 | 3 | 99 | 5.7252e-07 | 1.2338e-06 | 5.783e-07 | 1.2462e-06
510 | feeder2_line51 | 1 | 99 | 0.044731 | 0.044906 | 0.045183 | 0.045359
510 | feeder2_line51 | 2 | 99 | 5.7546e-07 | 1.3462e-06 | 5.8127e-07 | 1.3598e-06
510 | feeder2_line51 | 3 | 99 | 5.7251e-07 | 1.3394e-06 | 5.783e-07 | 1.3529e-06
510 | feeder2_line52 | 1 | 266.4 | 2.5546 | 2.5546 | 0.95894 | 0.95894
510 | feeder2_line52 | 2 | 266.4 | 1.6244 | 1.6243 | 0.60975 | 0.60971
510 | feeder2_line52 | 3 | 266.4 | 20.9483 | 20.9485 | 7.8635 | 7.8635
510 | feeder2_line53 | 1 | 99 | 5.4953e-07 | 7.5543e-07 | 5.5508e-07 | 7.6306e-07
510 | feeder2_line53 | 2 | 99 | 1.6243 | 1.6243 | 1.6407 | 1.6407
510 | feeder2_line53 | 3 | 99 | 5.4734e-07 | 7.5298e-07 | 5.5287e-07 | 7.6058e-07
510 | feeder2_line54 | 1 | 266.4 | 2.5545 | 2.5546 | 0.9589 | 0.95894
510 | feeder2_line54 | 2 | 266.4 | 8.579e-05 | 4.6426e-06 | 3.2203e-05 | 1.7427e-06
510 | feeder2_line54 | 3 | 266.4 | 20.9482 | 20.9485 | 7.8634 | 7.8635
510 | feeder2_line55 | 1 | 99 | 0.045394 | 0.045399 | 0.045853 | 0.045857
510 | feeder2_line55 | 2 | 99 | 4.9859e-08 | 7.34e-07 | 5.0362e-08 | 7.4141e-07
510 | feeder2_line55 | 3 | 99 | 5.0423e-08 | 7.3052e-07 | 5.0932e-08 | 7.3789e-07
510 | feeder2_line56 | 1 | 354.6 | 92.4364 | 92.4433 | 26.0678 | 26.0697
510 | feeder2_line56 | 2 | 354.6 | 87.8828 | 87.8805 | 24.7837 | 24.783
510 | feeder2_line56 | 3 | 354.6 | 80.8613 | 80.8554 | 22.8035 | 22.8019
510 | feeder2_line57 | 1 | 99 | 7.457e-07 | 1.5473e-06 | 7.5324e-07 | 1.563e-06
510 | feeder2_line57 | 2 | 99 | 7.4589e-07 | 1.5503e-06 | 7.5343e-07 | 1.5659e-06
510 | feeder2_line57 | 3 | 99 | 20.9482 | 20.9485 | 21.1598 | 21.1601
510 | feeder2_line58 | 1 | 266.4 | 2.5546 | 2.5546 | 0.95892 | 0.95894
510 | feeder2_line58 | 2 | 266.4 | 1.9036e-05 | 2.6954e-06 | 7.1457e-06 | 1.0118e-06
510 | feeder2_line58 | 3 | 266.4 | 1.8908e-05 | 2.6819e-06 | 7.0977e-06 | 1.0067e-06
510 | feeder2_line59 | 1 | 99 | 4.9703e-08 | 5.3787e-07 | 5.0205e-08 | 5.433e-07
510 | feeder2_line59 | 2 | 99 | 4.9716e-08 | 5.3888e-07 | 5.0218e-08 | 5.4432e-07
510 | feeder2_line59 | 3 | 99 | 18.8834 | 18.8836 | 19.0741 | 19.0743
510 | feeder2_line60 | 1 | 99 | 2.9962e-07 | 8.1289e-07 | 3.0265e-07 | 8.211e-07
510 | feeder2_line60 | 2 | 99 | 3.0016e-07 | 8.1442e-07 | 3.032e-07 | 8.2265e-07
510 | feeder2_line60 | 3 | 99 | 2.3973 | 2.3973 | 2.4216 | 2.4216
510 | feeder2_line61 | 1 | 266.4 | 1.4776 | 1.4778 | 0.55467 | 0.55473
510 | feeder2_line61 | 2 | 266.4 | 1.282 | 1.2822 | 0.48122 | 0.48129
510 | feeder2_line61 | 3 | 266.4 | 10.452 | 10.4523 | 3.9234 | 3.9235
510 | feeder2_line62 | 1 | 354.6 | 93.2659 | 93.2731 | 26.3017 | 26.3037
510 | feeder2_line62 | 2 | 354.6 | 88.9751 | 88.973 | 25.0917 | 25.0911
510 | feeder2_line62 | 3 | 354.6 | 91.2532 | 91.2477 | 25.7341 | 25.7326
510 | feeder2_line63 | 1 | 99 | 1.4088 | 1.4088 | 1.423 | 1.4231
510 | feeder2_line63 | 2 | 99 | 5.7548e-07 | 1.2245e-06 | 5.8129e-07 | 1.2368e-06
510 | feeder2_line63 | 3 | 99 | 5.7244e-07 | 1.2181e-06 | 5.7822e-07 | 1.2304e-06
510 | feeder2_line64 | 1 | 99 | 1.4547 | 1.4547 | 1.4694 | 1.4694
510 | feeder2_line64 | 2 | 99 | 2.7245e-12 | 3.2256e-07 | 2.752e-12 | 3.2582e-07
510 | feeder2_line64 | 3 | 99 | 9.0419e-12 | 3.2087e-07 | 9.1333e-12 | 3.2411e-07
510 | feeder2_line65 | 1 | 99 | 4.9832e-08 | 6.4445e-07 | 5.0336e-08 | 6.5096e-07
510 | feeder2_line65 | 2 | 99 | 0.089365 | 0.089363 | 0.090268 | 0.090266
510 | feeder2_line65 | 3 | 99 | 5.05e-08 | 6.4223e-07 | 5.101e-08 | 6.4872e-07
510 | feeder2_line66 | 1 | 354.6 | 93.2659 | 93.2731 | 26.3017 | 26.3037
510 | feeder2_line66 | 2 | 354.6 | 89.0644 | 89.0624 | 25.1169 | 25.1163
510 | feeder2_line66 | 3 | 354.6 | 91.2532 | 91.2477 | 25.7341 | 25.7326
510 | feeder2_line67 | 1 | 99 | 2.4902e-08 | 3.641e-07 | 2.5154e-08 | 3.6778e-07
510 | feeder2_line67 | 2 | 99 | 2.4945e-08 | 3.6465e-07 | 2.5197e-08 | 3.6833e-07
510 | feeder2_line67 | 3 | 99 | 9.4356 | 9.4358 | 9.531 | 9.5311
510 | feeder2_line68 | 1 | 266.4 | 1.4777 | 1.4778 | 0.55469 | 0.55473
510 | feeder2_line68 | 2 | 266.4 | 1.282 | 1.2822 | 0.48124 | 0.48129
510 | feeder2_line68 | 3 | 266.4 | 1.1414 | 1.1415 | 0.42846 | 0.4285
510 | feeder2_line69 | 1 | 99 | 0.10056 | 0.10059 | 0.10157 | 0.1016
510 | feeder2_line69 | 2 | 99 | 2.562e-06 | 6.7007e-07 | 2.5879e-06 | 6.7683e-07
510 | feeder2_line69 | 3 | 99 | 2.5443e-06 | 6.6687e-07 | 2.57e-06 | 6.736e-07
510 | feeder2_line70 | 1 | 354.6 | 93.3663 | 93.3736 | 26.33 | 26.3321
510 | feeder2_line70 | 2 | 354.6 | 89.0643 | 89.0624 | 25.1168 | 25.1163
510 | feeder2_line70 | 3 | 354.6 | 91.2531 | 91.2477 | 25.7341 | 25.7326
510 | feeder2_line71 | 1 | 99 | 4.9851e-08 | 7.193e-07 | 5.0355e-08 | 7.2657e-07
510 | feeder2_line71 | 2 | 99 | 0.052568 | 0.052581 | 0.053099 | 0.053112
510 | feeder2_line71 | 3 | 99 | 5.0527e-08 | 7.1678e-07 | 5.1038e-08 | 7.2402e-07
510 | feeder2_line72 | 1 | 354.6 | 93.3664 | 93.3736 | 26.3301 | 26.3321
510 | feeder2_line72 | 2 | 354.6 | 89.1169 | 89.1149 | 25.1317 | 25.1311
510 | feeder2_line72 | 3 | 354.6 | 91.2532 | 91.2477 | 25.7341 | 25.7326
510 | feeder2_line73 | 1 | 99 | 6.0092e-07 | 1.5414e-06 | 6.0699e-07 | 1.557e-06
510 | feeder2_line73 | 2 | 99 | 0.076716 | 0.076714 | 0.077491 | 0.077489
510 | feeder2_line73 | 3 | 99 | 5.9925e-07 | 1.5362e-06 | 6.0531e-07 | 1.5517e-06
510 | feeder2_line74 | 1 | 99 | 4.9809e-08 | 4.5975e-07 | 5.0312e-08 | 4.6439e-07
510 | feeder2_line74 | 2 | 99 | 1.1405 | 1.1405 | 1.152 | 1.152
510 | feeder2_line74 | 3 | 99 | 5.0468e-08 | 4.5817e-07 | 5.0977e-08 | 4.6279e-07
510 | feeder2_line75 | 1 | 266.4 | 1.4778 | 1.4778 | 0.55472 | 0.55473
510 | feeder2_line75 | 2 | 266.4 | 0.089332 | 0.089364 | 0.033533 | 0.033545
510 | feeder2_line75 | 3 | 266.4 | 1.1415 | 1.1415 | 0.4285 | 0.42851
510 | feeder2_line76 | 1 | 99 | 1.4778 | 1.4778 | 1.4927 | 1.4927
510 | feeder2_line76 | 2 | 99 | 8.5285e-07 | 1.5924e-06 | 8.6147e-07 | 1.6085e-06
510 | feeder2_line76 | 3 | 99 | 8.484e-07 | 1.5846e-06 | 8.5697e-07 | 1.6006e-06
510 | feeder2_line77 | 1 | 99 | 2.4908e-08 | 5.7774e-07 | 2.516e-08 | 5.8357e-07
510 | feeder2_line77 | 2 | 99 | 2.4944e-08 | 5.786e-07 | 2.5195e-08 | 5.8445e-07
510 | feeder2_line77 | 3 | 99 | 1.1416 | 1.1415 | 1.1531 | 1.1531
510 | feeder2_line78 | 1 | 266.4 | 9.2897e-12 | 9.5799e-07 | 3.4871e-12 | 3.5961e-07
510 | feeder2_line78 | 2 | 266.4 | 0.089365 | 0.089364 | 0.033545 | 0.033545
510 | feeder2_line78 | 3 | 266.4 | 1.0906e-11 | 9.5522e-07 | 4.0938e-12 | 3.5857e-07
510 | feeder2_line79 | 1 | 354.6 | 2.5202 | 2.5199 | 0.71071 | 0.71062
510 | feeder2_line79 | 2 | 354.6 | 3.2591 | 3.2589 | 0.9191 | 0.91905
510 | feeder2_line79 | 3 | 354.6 | 4.4036 | 4.4032 | 1.2419 | 1.2417
510 | feeder2_line80 | 1 | 354.6 | 95.7735 | 95.7802 | 27.0089 | 27.0108
510 | feeder2_line80 | 2 | 354.6 | 91.1964 | 91.1937 | 25.7181 | 25.7174
510 | feeder2_line80 | 3 | 354.6 | 95.2837 | 95.2776 | 26.8707 | 26.869
510 | feeder2_line81 | 1 | 354.6 | 95.7734 | 95.7802 | 27.0089 | 27.0108
510 | feeder2_line81 | 2 | 354.6 | 91.1964 | 91.1937 | 25.7181 | 25.7174
510 | feeder2_line81 | 3 | 354.6 | 95.3532 | 95.3471 | 26.8904 | 26.8886
510 | feeder2_line82 | 1 | 354.6 | 1.1429e-11 | 7.3819e-07 | 3.2231e-12 | 2.0818e-07
510 | feeder2_line82 | 2 | 354.6 | 4.8002e-11 | 7.3899e-07 | 1.3537e-11 | 2.084e-07
510 | feeder2_line82 | 3 | 354.6 | 0.069637 | 0.06963 | 0.019638 | 0.019636
510 | feeder2_line83 | 1 | 354.6 | 95.7736 | 95.7802 | 27.0089 | 27.0108
510 | feeder2_line83 | 2 | 354.6 | 92.4088 | 92.406 | 26.06 | 26.0592
510 | feeder2_line83 | 3 | 354.6 | 95.3534 | 95.3471 | 26.8904 | 26.8886
510 | feeder2_line84 | 1 | 354.6 | 1.7047e-11 | 1.305e-06 | 4.8075e-12 | 3.6801e-07
510 | feeder2_line84 | 2 | 354.6 | 2.2725 | 2.2725 | 0.64086 | 0.64086
510 | feeder2_line84 | 3 | 354.6 | 9.8396e-12 | 1.3008e-06 | 2.7748e-12 | 3.6683e-07
510 | feeder2_line85 | 1 | 99 | 0.076672 | 0.07668 | 0.077446 | 0.077454
510 | feeder2_line85 | 2 | 99 | 5.0037e-08 | 4.6633e-07 | 5.0543e-08 | 4.7104e-07
510 | feeder2_line85 | 3 | 99 | 5.0595e-08 | 4.6417e-07 | 5.1106e-08 | 4.6886e-07
510 | feeder2_line86 | 1 | 354.6 | 95.8503 | 95.8568 | 27.0305 | 27.0324
510 | feeder2_line86 | 2 | 354.6 | 92.409 | 92.406 | 26.0601 | 26.0592
510 | feeder2_line86 | 3 | 354.6 | 95.3535 | 95.3471 | 26.8904 | 26.8886
510 | feeder2_line87 | 1 | 354.6 | 95.8505 | 95.8568 | 27.0306 | 27.0324
510 | feeder2_line87 | 2 | 354.6 | 93.0364 | 93.0333 | 26.237 | 26.2361
510 | feeder2_line87 | 3 | 354.6 | 96.2282 | 96.2217 | 27.1371 | 27.1353
510 | feeder2_line88 | 1 | 354.6 | 0.00011605 | 3.384e-06 | 3.2726e-05 | 9.5431e-07
510 | feeder2_line88 | 2 | 354.6 | 0.62738 | 0.62733 | 0.17693 | 0.17691
510 | feeder2_line88 | 3 | 354.6 | 0.90145 | 0.90129 | 0.25422 | 0.25417
510 | feeder2_line89 | 1 | 354.6 | 95.8482 | 95.8568 | 27.03 | 27.0324
510 | feeder2_line89 | 2 | 354.6 | 96.2081 | 96.2073 | 27.1314 | 27.1312
510 | feeder2_line89 | 3 | 354.6 | 96.226 | 96.2217 | 27.1365 | 27.1353
510 | feeder2_line90 | 1 | 354.6 | 0.00072971 | 2.0426e-06 | 0.00020579 | 5.7602e-07
510 | feeder2_line90 | 2 | 354.6 | 4.1505 | 4.1506 | 1.1705 | 1.1705
510 | feeder2_line90 | 3 | 354.6 | 0.00072417 | 2.0374e-06 | 0.00020422 | 5.7456e-07
510 | feeder2_line91 | 1 | 354.6 | 95.8481 | 95.8568 | 27.0299 | 27.0324
510 | feeder2_line91 | 2 | 354.6 | 96.208 | 96.2073 | 27.1314 | 27.1312
510 | feeder2_line91 | 3 | 354.6 | 98.1799 | 98.1758 | 27.6875 | 27.6863
510 | feeder2_line92 | 1 | 354.6 | 1.2497e-11 | 1.0305e-06 | 3.5242e-12 | 2.9062e-07
510 | feeder2_line92 | 2 | 354.6 | 7.7309e-12 | 1.0315e-06 | 2.1802e-12 | 2.909e-07
510 | feeder2_line92 | 3 | 354.6 | 2.4003 | 2.4003 | 0.67689 | 0.67689
510 | feeder2_line93 | 1 | 99 | 2.4962e-08 | 3.4405e-07 | 2.5214e-08 | 3.4752e-07
510 | feeder2_line93 | 2 | 99 | 2.2732 | 2.2732 | 2.2962 | 2.2961
510 | feeder2_line93 | 3 | 99 | 2.5319e-08 | 3.4278e-07 | 2.5575e-08 | 3.4624e-07
510 | feeder2_line94 | 1 | 354.6 | 2.496e-06 | 1.6747e-06 | 7.039e-07 | 4.7228e-07
510 | feeder2_line94 | 2 | 354.6 | 2.0678 | 2.0678 | 0.58314 | 0.58314
510 | feeder2_line94 | 3 | 354.6 | 2.5317e-06 | 1.6693e-06 | 7.1395e-07 | 4.7076e-07
510 | feeder2_line95 | 1 | 99 | 3.5876e-06 | 2.6241e-06 | 3.6238e-06 | 2.6506e-06
510 | feeder2_line95 | 2 | 99 | 0.62728 | 0.62733 | 0.63361 | 0.63366
510 | feeder2_line95 | 3 | 99 | 3.5709e-06 | 2.6145e-06 | 3.607e-06 | 2.6409e-06
510 | feeder2_line96 | 1 | 354.6 | 0.00012183 | 6.2549e-07 | 3.4358e-05 | 1.7639e-07
510 | feeder2_line96 | 2 | 354.6 | 0.0001219 | 6.262e-07 | 3.4377e-05 | 1.7659e-07
510 | feeder2_line96 | 3 | 354.6 | 0.90144 | 0.90129 | 0.25421 | 0.25417
510 | feeder2_line97 | 1 | 354.6 | 95.9486 | 95.9571 | 27.0583 | 27.0607
510 | feeder2_line97 | 2 | 354.6 | 96.2082 | 96.2073 | 27.1315 | 27.1312
510 | feeder2_line97 | 3 | 354.6 | 98.1801 | 98.1758 | 27.6876 | 27.6863
510 | feeder2_line98 | 1 | 354.6 | 0.10198 | 0.1003 | 0.028759 | 0.028287
510 | feeder2_line98 | 2 | 354.6 | 0.0017106 | 6.2291e-07 | 0.00048241 | 1.7567e-07
510 | feeder2_line98 | 3 | 354.6 | 0.0017007 | 6.2403e-07 | 0.0004796 | 1.7598e-07
510 | feeder2_line99 | 1 | 99 | 2.4953e-08 | 4.4969e-07 | 2.5205e-08 | 4.5423e-07
510 | feeder2_line99 | 2 | 99 | 2.5025e-08 | 4.5011e-07 | 2.5277e-08 | 4.5466e-07
510 | feeder2_line99 | 3 | 99 | 0.90134 | 0.90129 | 0.91044 | 0.91039
510 | feeder2_line100 | 1 | 99 | 0.10027 | 0.1003 | 0.10129 | 0.10132
510 | feeder2_line100 | 2 | 99 | 2.5049e-08 | 6.1828e-07 | 2.5302e-08 | 6.2452e-07
510 | feeder2_line100 | 3 | 99 | 2.5325e-08 | 6.1547e-07 | 2.5581e-08 | 6.2169e-07
510 | feeder2_line101 | 1 | 354.6 | 2.0671 | 2.0668 | 0.58294 | 0.58285
510 | feeder2_line101 | 2 | 354.6 | 3.2591 | 3.2589 | 0.9191 | 0.91905
510 | feeder2_line101 | 3 | 354.6 | 4.4036 | 4.4032 | 1.2419 | 1.2417
510 | feeder2_line102 | 1 | 99 | 0.49412 | 0.49415 | 0.49911 | 0.49915
510 | feeder2_line102 | 2 | 99 | 2.3491e-06 | 8.8356e-07 | 2.3728e-06 | 8.9249e-07
510 | feeder2_line102 | 3 | 99 | 2.3326e-06 | 8.7935e-07 | 2.3562e-06 | 8.8823e-07
510 | feeder2_line103 | 1 | 99 | 5.5219e-07 | 8.0782e-07 | 5.5776e-07 | 8.1598e-07
510 | feeder2_line103 | 2 | 99 | 0.41241 | 0.41241 | 0.41658 | 0.41658
510 | feeder2_line103 | 3 | 99 | 5.4968e-07 | 8.0485e-07 | 5.5523e-07 | 8.1298e-07
510 | feeder2_line104 | 1 | 354.6 | 2.0671 | 2.0668 | 0.58293 | 0.58285
510 | feeder2_line104 | 2 | 354.6 | 3.0211 | 3.0209 | 0.85197 | 0.85193
510 | feeder2_line104 | 3 | 354.6 | 4.4036 | 4.4032 | 1.2418 | 1.2417
510 | feeder2_line105 | 1 | 99 | 2.5615e-06 | 7.433e-07 | 2.5874e-06 | 7.5081e-07
510 | feeder2_line105 | 2 | 99 | 2.5638e-06 | 7.4412e-07 | 2.5897e-06 | 7.5163e-07
510 | feeder2_line105 | 3 | 99 | 0.040103 | 0.040059 | 0.040509 | 0.040463
510 | feeder2_line106 | 1 | 354.6 | 2.067 | 2.0668 | 0.58291 | 0.58285
510 | feeder2_line106 | 2 | 354.6 | 3.0211 | 3.0209 | 0.85196 | 0.85193
510 | feeder2_line106 | 3 | 354.6 | 4.3668 | 4.3666 | 1.2315 | 1.2314
510 | feeder2_line107 | 1 | 99 | 3.2595e-07 | 9.0581e-07 | 3.2924e-07 | 9.1496e-07
510 | feeder2_line107 | 2 | 99 | 1.0504 | 1.0504 | 1.061 | 1.061
510 | feeder2_line107 | 3 | 99 | 3.254e-07 | 9.0244e-07 | 3.2868e-07 | 9.1156e-07
510 | feeder2_line108 | 1 | 354.6 | 2.067 | 2.0668 | 0.58291 | 0.58285
510 | feeder2_line108 | 2 | 354.6 | 1.9707 | 1.9706 | 0.55576 | 0.55572
510 | feeder2_line108 | 3 | 354.6 | 4.3668 | 4.3666 | 1.2315 | 1.2314
510 | feeder2_line109 | 1 | 354.6 | 97.5647 | 97.572 | 27.514 | 27.5161
510 | feeder2_line109 | 2 | 354.6 | 96.2094 | 96.2073 | 27.1318 | 27.1312
510 | feeder2_line109 | 3 | 354.6 | 98.1813 | 98.1758 | 27.6879 | 27.6863
510 | feeder2_line110 | 1 | 99 | 2.7592 | 2.7586 | 2.787 | 2.7865
510 | feeder2_line110 | 2 | 99 | 0.0008106 | 9.1542e-07 | 0.00081878 | 9.2467e-07
510 | feeder2_line110 | 3 | 99 | 0.00080484 | 9.1125e-07 | 0.00081297 | 9.2046e-07
510 | feeder2_line111 | 1 | 99 | 2.4951e-08 | 3.8407e-07 | 2.5203e-08 | 3.8795e-07
510 | feeder2_line111 | 2 | 99 | 0.58669 | 0.58671 | 0.59262 | 0.59264
510 | feeder2_line111 | 3 | 99 | 2.5305e-08 | 3.8267e-07 | 2.5561e-08 | 3.8653e-07
510 | feeder2_line112 | 1 | 99 | 3.2628e-07 | 9.2294e-07 | 3.2957e-07 | 9.3226e-07
510 | feeder2_line112 | 2 | 99 | 0.040582 | 0.040616 | 0.040991 | 0.041026
510 | feeder2_line112 | 3 | 99 | 3.2573e-07 | 9.1956e-07 | 3.2902e-07 | 9.2885e-07
510 | feeder2_line113 | 1 | 99 | 2.7153 | 2.7152 | 2.7427 | 2.7426
510 | feeder2_line113 | 2 | 99 | 3.2705e-07 | 9.1192e-07 | 3.3035e-07 | 9.2113e-07
510 | feeder2_line113 | 3 | 99 | 3.2614e-07 | 9.0781e-07 | 3.2943e-07 | 9.1698e-07
510 | feeder2_line114 | 1 | 99 | 0.41275 | 0.41277 | 0.41692 | 0.41693
510 | feeder2_line114 | 2 | 99 | 2.4996e-08 | 4.3935e-07 | 2.5249e-08 | 4.4379e-07
510 | feeder2_line114 | 3 | 99 | 2.5285e-08 | 4.3726e-07 | 2.554e-08 | 4.4168e-07
510 | feeder2_line115 | 1 | 99 | 2.4923e-08 | 5.6527e-07 | 2.5174e-08 | 5.7098e-07
510 | feeder2_line115 | 2 | 99 | 0.060647 | 0.060645 | 0.06126 | 0.061258
510 | feeder2_line115 | 3 | 99 | 2.5288e-08 | 5.6314e-07 | 2.5544e-08 | 5.6883e-07
510 | feeder2_line116 | 1 | 354.6 | 2.067 | 2.0668 | 0.58291 | 0.58285
510 | feeder2_line116 | 2 | 354.6 | 1.9371 | 1.937 | 0.54627 | 0.54624
510 | feeder2_line116 | 3 | 354.6 | 4.3669 | 4.3666 | 1.2315 | 1.2314
510 | feeder2_line117 | 1 | 99 | 4.9982e-08 | 6.4711e-07 | 5.0487e-08 | 6.5365e-07
510 | feeder2_line117 | 2 | 99 | 1.4768 | 1.4767 | 1.4917 | 1.4916
510 | feeder2_line117 | 3 | 99 | 5.0699e-08 | 6.4476e-07 | 5.1212e-08 | 6.5127e-07
510 | feeder2_line118 | 1 | 354.6 | 97.5647 | 97.572 | 27.514 | 27.5161
510 | feeder2_line118 | 2 | 354.6 | 97.0619 | 97.0597 | 27.3722 | 27.3716
510 | feeder2_line118 | 3 | 354.6 | 98.1813 | 98.1758 | 27.6879 | 27.6863
510 | feeder2_line119 | 1 | 99 | 2.4926e-08 | 6.0824e-07 | 2.5178e-08 | 6.1438e-07
510 | feeder2_line119 | 2 | 99 | 2.4994e-08 | 6.0893e-07 | 2.5246e-08 | 6.1508e-07
510 | feeder2_line119 | 3 | 99 | 1.3922 | 1.3922 | 1.4063 | 1.4063
510 | feeder2_line120 | 1 | 354.6 | 2.067 | 2.0668 | 0.58291 | 0.58286
510 | feeder2_line120 | 2 | 354.6 | 1.9371 | 1.937 | 0.54627 | 0.54624
510 | feeder2_line120 | 3 | 354.6 | 3.1347 | 3.1344 | 0.88401 | 0.88393
510 | feeder2_line121 | 1 | 99 | 3.2593e-07 | 9.4187e-07 | 3.2922e-07 | 9.5138e-07
510 | feeder2_line121 | 2 | 99 | 0.74331 | 0.74331 | 0.75082 | 0.75082
510 | feeder2_line121 | 3 | 99 | 3.2536e-07 | 9.3827e-07 | 3.2865e-07 | 9.4775e-07
510 | feeder2_line122 | 1 | 354.6 | 2.067 | 2.0668 | 0.58291 | 0.58286
510 | feeder2_line122 | 2 | 354.6 | 1.1938 | 1.1937 | 0.33666 | 0.33664
510 | feeder2_line122 | 3 | 354.6 | 3.1347 | 3.1344 | 0.884 | 0.88393
510 | feeder2_line123 | 1 | 99 | 5.7708e-07 | 9.7598e-07 | 5.8291e-07 | 9.8584e-07
510 | feeder2_line123 | 2 | 99 | 5.7774e-07 | 9.7711e-07 | 5.8358e-07 | 9.8698e-07
510 | feeder2_line123 | 3 | 99 | 0.077025 | 0.077022 | 0.077803 | 0.0778
510 | feeder2_line124 | 1 | 354.6 | 2.067 | 2.0668 | 0.5829 | 0.58286
510 | feeder2_line124 | 2 | 354.6 | 1.1938 | 1.1937 | 0.33667 | 0.33664
510 | feeder2_line124 | 3 | 354.6 | 3.0726 | 3.0724 | 0.8665 | 0.86644
510 | feeder2_line125 | 1 | 99 | 5.7707e-07 | 9.0727e-07 | 5.829e-07 | 9.1643e-07
510 | feeder2_line125 | 2 | 99 | 5.7775e-07 | 9.0832e-07 | 5.8358e-07 | 9.175e-07
510 | feeder2_line125 | 3 | 99 | 0.10107 | 0.10102 | 0.10209 | 0.10204
510 | feeder2_line126 | 1 | 354.6 | 2.0671 | 2.0668 | 0.58294 | 0.58286
510 | feeder2_line126 | 2 | 354.6 | 1.194 | 1.1937 | 0.33671 | 0.33664
510 | feeder2_line126 | 3 | 354.6 | 2.9918 | 2.9914 | 0.8437 | 0.8436
510 | feeder2_line127 | 1 | 99 | 5.7707e-07 | 1.0861e-06 | 5.829e-07 | 1.0971e-06
510 | feeder2_line127 | 2 | 99 | 5.7774e-07 | 1.0874e-06 | 5.8358e-07 | 1.0984e-06
510 | feeder2_line127 | 3 | 99 | 0.96858 | 0.96857 | 0.97836 | 0.97836
510 | feeder2_line128 | 1 | 354.6 | 2.0671 | 2.0668 | 0.58293 | 0.58286
510 | feeder2_line128 | 2 | 354.6 | 1.1939 | 1.1937 | 0.3367 | 0.33664
510 | feeder2_line128 | 3 | 354.6 | 2.0855 | 2.0852 | 0.58811 | 0.58803
510 | feeder2_line129 | 1 | 99 | 5.5214e-07 | 8.8068e-07 | 5.5771e-07 | 8.8958e-07
510 | feeder2_line129 | 2 | 99 | 1.1937 | 1.1937 | 1.2057 | 1.2058
510 | feeder2_line129 | 3 | 99 | 5.4953e-07 | 8.7731e-07 | 5.5508e-07 | 8.8617e-07
510 | feeder2_line130 | 1 | 354.6 | 2.0671 | 2.0668 | 0.58293 | 0.58286
510 | feeder2_line130 | 2 | 354.6 | 0.00031063 | 4.6658e-06 | 8.76e-05 | 1.3158e-06
510 | feeder2_line130 | 3 | 354.6 | 2.0855 | 2.0852 | 0.58812 | 0.58803
510 | feeder2_line131 | 1 | 99 | 5.7705e-07 | 9.7609e-07 | 5.8288e-07 | 9.8595e-07
510 | feeder2_line131 | 2 | 99 | 5.7775e-07 | 9.7726e-07 | 5.8358e-07 | 9.8714e-07
510 | feeder2_line131 | 3 | 99 | 2.0198 | 2.0197 | 2.0402 | 2.0401
510 | feeder2_line132 | 1 | 354.6 | 2.0669 | 2.0668 | 0.58288 | 0.58286
510 | feeder2_line132 | 2 | 354.6 | 0.00012652 | 2.9334e-06 | 3.5681e-05 | 8.2725e-07
510 | feeder2_line132 | 3 | 354.6 | 0.077259 | 0.077184 | 0.021788 | 0.021766
510 | feeder2_line133 | 1 | 99 | 2.0668 | 2.0668 | 2.0877 | 2.0877
510 | feeder2_line133 | 2 | 99 | 3.0136e-07 | 9.8507e-07 | 3.0441e-07 | 9.9502e-07
510 | feeder2_line133 | 3 | 99 | 3.0005e-07 | 9.8011e-07 | 3.0308e-07 | 9.9001e-07
510 | feeder2_line134 | 1 | 354.6 | 2.3728e-12 | 1.7939e-06 | 6.6915e-13 | 5.0591e-07
510 | feeder2_line134 | 2 | 354.6 | 1.1354e-11 | 1.7962e-06 | 3.2019e-12 | 5.0654e-07
510 | feeder2_line134 | 3 | 354.6 | 0.07719 | 0.077184 | 0.021768 | 0.021766
510 | feeder2_line135 | 1 | 99 | 0.052427 | 0.052464 | 0.052957 | 0.052994
510 | feeder2_line135 | 2 | 99 | 5.0185e-08 | 5.9044e-07 | 5.0692e-08 | 5.9641e-07
510 | feeder2_line135 | 3 | 99 | 5.0732e-08 | 5.8781e-07 | 5.1244e-08 | 5.9375e-07
510 | feeder2_line136 | 1 | 354.6 | 97.6171 | 97.6245 | 27.5288 | 27.5309
510 | feeder2_line136 | 2 | 354.6 | 97.0619 | 97.0597 | 27.3722 | 27.3716
510 | feeder2_line136 | 3 | 354.6 | 98.1813 | 98.1758 | 27.6879 | 27.6863
510 | feeder2_line137 | 1 | 99 | 0.085084 | 0.085112 | 0.085943 | 0.085972
510 | feeder2_line137 | 2 | 99 | 8.5702e-07 | 1.5905e-06 | 8.6568e-07 | 1.6065e-06
510 | feeder2_line137 | 3 | 99 | 8.5298e-07 | 1.5834e-06 | 8.616e-07 | 1.5994e-06
510 | feeder2_line138 | 1 | 354.6 | 97.7021 | 97.7094 | 27.5528 | 27.5548
510 | feeder2_line138 | 2 | 354.6 | 97.0619 | 97.0597 | 27.3722 | 27.3716
510 | feeder2_line138 | 3 | 354.6 | 98.1813 | 98.1758 | 27.6879 | 27.6863
510 | feeder2_line139 | 1 | 99 | 5.0036e-08 | 4.9524e-07 | 5.0541e-08 | 5.0024e-07
510 | feeder2_line139 | 2 | 99 | 5.0207e-08 | 4.9563e-07 | 5.0714e-08 | 5.0064e-07
510 | feeder2_line139 | 3 | 99 | 0.70181 | 0.70142 | 0.7089 | 0.7085
510 | feeder2_line140 | 1 | 354.6 | 97.7022 | 97.7094 | 27.5528 | 27.5548
510 | feeder2_line140 | 2 | 354.6 | 97.062 | 97.0597 | 27.3723 | 27.3716
510 | feeder2_line140 | 3 | 354.6 | 98.8832 | 98.8771 | 27.8858 | 27.8841
510 | feeder2_line141 | 1 | 99 | 2.5471e-06 | 4.8995e-07 | 2.5728e-06 | 4.949e-07
510 | feeder2_line141 | 2 | 99 | 0.076365 | 0.076363 | 0.077137 | 0.077134
510 | feeder2_line141 | 3 | 99 | 2.5314e-06 | 4.8818e-07 | 2.557e-06 | 4.9311e-07
510 | feeder2_line142 | 1 | 354.6 | 97.702 | 97.7094 | 27.5527 | 27.5548
510 | feeder2_line142 | 2 | 354.6 | 97.1381 | 97.1359 | 27.3937 | 27.3931
510 | feeder2_line142 | 3 | 354.6 | 98.883 | 98.8771 | 27.8858 | 27.8841
510 | feeder2_line143 | 1 | 99 | 8.5679e-07 | 1.7411e-06 | 8.6544e-07 | 1.7587e-06
510 | feeder2_line143 | 2 | 99 | 1.0516 | 1.0516 | 1.0622 | 1.0622
510 | feeder2_line143 | 3 | 99 | 8.5342e-07 | 1.7348e-06 | 8.6204e-07 | 1.7523e-06
510 | feeder2_line144 | 1 | 354.6 | 97.7018 | 97.7094 | 27.5527 | 27.5548
510 | feeder2_line144 | 2 | 354.6 | 97.7778 | 97.7759 | 27.5741 | 27.5736
510 | feeder2_line144 | 3 | 354.6 | 98.8828 | 98.8771 | 27.8857 | 27.8841
510 | feeder2_line145 | 1 | 99 | 2.503e-08 | 4.8825e-07 | 2.5282e-08 | 4.9318e-07
510 | feeder2_line145 | 2 | 99 | 0.069078 | 0.069075 | 0.069775 | 0.069773
510 | feeder2_line145 | 3 | 99 | 2.5384e-08 | 4.8647e-07 | 2.5641e-08 | 4.9139e-07
510 | feeder2_line146 | 1 | 354.6 | 97.7017 | 97.7094 | 27.5527 | 27.5548
510 | feeder2_line146 | 2 | 354.6 | 97.8467 | 97.8448 | 27.5935 | 27.593
510 | feeder2_line146 | 3 | 354.6 | 98.8827 | 98.8771 | 27.8857 | 27.8841
510 | feeder2_line147 | 1 | 99 | 0.08027 | 0.080277 | 0.081081 | 0.081088
510 | feeder2_line147 | 2 | 99 | 1.1602e-06 | 2.2539e-06 | 1.1719e-06 | 2.2767e-06
510 | feeder2_line147 | 3 | 99 | 1.155e-06 | 2.244e-06 | 1.1667e-06 | 2.2667e-06
510 | feeder2_line148 | 1 | 99 | 0.084256 | 0.084267 | 0.085107 | 0.085118
510 | feeder2_line148 | 2 | 99 | 6.0522e-07 | 1.5103e-06 | 6.1134e-07 | 1.5256e-06
510 | feeder2_line148 | 3 | 99 | 6.0291e-07 | 1.5036e-06 | 6.09e-07 | 1.5188e-06
510 | feeder2_line149 | 1 | 354.6 | 97.8661 | 97.8737 | 27.599 | 27.6012
510 | feeder2_line149 | 2 | 354.6 | 97.8469 | 97.8448 | 27.5936 | 27.593
510 | feeder2_line149 | 3 | 354.6 | 98.8829 | 98.8771 | 27.8858 | 27.8841
510 | feeder2_line150 | 1 | 354.6 | 97.8662 | 97.8737 | 27.5991 | 27.6012
510 | feeder2_line150 | 2 | 354.6 | 98.3439 | 98.3418 | 27.7338 | 27.7332
510 | feeder2_line150 | 3 | 354.6 | 98.883 | 98.8771 | 27.8858 | 27.8841
510 | feeder2_line151 | 1 | 99 | 9.8512e-06 | 1.7929e-06 | 9.9507e-06 | 1.811e-06
510 | feeder2_line151 | 2 | 99 | 0.49957 | 0.49957 | 0.50461 | 0.50462
510 | feeder2_line151 | 3 | 99 | 9.7819e-06 | 1.7864e-06 | 9.8807e-06 | 1.8045e-06
510 | feeder2_line152 | 1 | 354.6 | 8.2456e-12 | 1.1949e-06 | 2.3253e-12 | 3.3698e-07
510 | feeder2_line152 | 2 | 354.6 | 1.3712e-11 | 1.1959e-06 | 3.8669e-12 | 3.3726e-07
510 | feeder2_line152 | 3 | 354.6 | 0.076683 | 0.076678 | 0.021625 | 0.021624
510 | feeder2_line153 | 1 | 99 | 0.74447 | 0.74446 | 0.75199 | 0.75198
510 | feeder2_line153 | 2 | 99 | 5.0283e-08 | 5.9842e-07 | 5.0791e-08 | 6.0447e-07
510 | feeder2_line153 | 3 | 99 | 5.0822e-08 | 5.958e-07 | 5.1336e-08 | 6.0182e-07
510 | feeder2_line154 | 1 | 99 | 5.8023e-07 | 8.8978e-07 | 5.8609e-07 | 8.9877e-07
510 | feeder2_line154 | 2 | 99 | 5.8069e-07 | 8.9048e-07 | 5.8655e-07 | 8.9948e-07
510 | feeder2_line154 | 3 | 99 | 0.040621 | 0.040566 | 0.041031 | 0.040976
510 | feeder2_line155 | 1 | 99 | 98.3075 | 98.315 | 99.3005 | 99.3081
510 | feeder2_line155 | 2 | 99 | 98.3438 | 98.3418 | 99.3372 | 99.3352
510 | feeder2_line155 | 3 | 99 | 99 | 98.9942 | 100 | 99.9941
510 | feeder2_line156 | 1 | 99 | 6.0501e-07 | 1.1708e-06 | 6.1112e-07 | 1.1826e-06
510 | feeder2_line156 | 2 | 99 | 0.41071 | 0.41071 | 0.41486 | 0.41486
510 | feeder2_line156 | 3 | 99 | 6.0324e-07 | 1.1665e-06 | 6.0933e-07 | 1.1783e-06
510 | feeder2_line157 | 1 | 99 | 2.5048e-08 | 2.5415e-07 | 2.5301e-08 | 2.5672e-07
510 | feeder2_line157 | 2 | 99 | 0.088941 | 0.08894 | 0.08984 | 0.089838
510 | feeder2_line157 | 3 | 99 | 2.54e-08 | 2.5325e-07 | 2.5656e-08 | 2.5581e-07
540 | feeder2_line1 | 1 | 354.6 | 51.4973 | 51.4997 | 14.5227 | 14.5233
540 | feeder2_line1 | 2 | 354.6 | 43.8378 | 43.843 | 12.3626 | 12.3641
540 | feeder2_line1 | 3 | 354.6 | 52.5819 | 52.5775 | 14.8285 | 14.8273
540 | feeder2_line2 | 1 | 354.6 | 52.0259 | 52.028 | 14.6717 | 14.6723
540 | feeder2_line2 | 2 | 354.6 | 43.8379 | 43.843 | 12.3626 | 12.3641
540 | feeder2_line2 | 3 | 354.6 | 52.5821 | 52.5775 | 14.8286 | 14.8273
540 | feeder2_line3 | 1 | 80.1 | 1.321 | 1.321 | 1.6492 | 1.6492
540 | feeder2_line3 | 2 | 80.1 | 5.7131e-07 | 1.0558e-06 | 7.1325e-07 | 1.3181e-06
540 | feeder2_line3 | 3 | 80.1 | 5.7157e-07 | 1.0562e-06 | 7.1357e-07 | 1.3187e-06
540 | feeder2_line4 | 1 | 354.6 | 52.026 | 52.028 | 14.6718 | 14.6723
540 | feeder2_line4 | 2 | 354.6 | 43.9246 | 43.9296 | 12.3871 | 12.3885
540 | feeder2_line4 | 3 | 354.6 | 52.5823 | 52.5775 | 14.8286 | 14.8273
540 | feeder2_line5 | 1 | 80.1 | 5.7177e-07 | 9.9768e-07 | 7.1381e-07 | 1.2455e-06
540 | feeder2_line5 | 2 | 80.1 | 0.090177 | 0.090179 | 0.11258 | 0.11258
540 | feeder2_line5 | 3 | 80.1 | 5.716e-07 | 9.9738e-07 | 7.136e-07 | 1.2452e-06
540 | feeder2_line6 | 1 | 80.1 | 5.7182e-07 | 1.1737e-06 | 7.1388e-07 | 1.4654e-06
540 | feeder2_line6 | 2 | 80.1 | 5.7135e-07 | 1.1728e-06 | 7.1329e-07 | 1.4642e-06
540 | feeder2_line6 | 3 | 80.1 | 1.2593 | 1.2594 | 1.5722 | 1.5722
540 | feeder2_line7 | 1 | 354.6 | 52.0261 | 52.028 | 14.6718 | 14.6723
540 | feeder2_line7 | 2 | 354.6 | 43.9247 | 43.9296 | 12.3871 | 12.3885
540 | feeder2_line7 | 3 | 354.6 | 53.0252 | 53.0202 | 14.9535 | 14.9521
540 | feeder2_line8 | 1 | 80.1 | 19.0478 | 19.0479 | 23.7801 | 23.7801
540 | feeder2_line8 | 2 | 80.1 | 5.7137e-07 | 1.1309e-06 | 7.1333e-07 | 1.4119e-06
540 | feeder2_line8 | 3 | 80.1 | 5.7172e-07 | 1.1316e-06 | 7.1375e-07 | 1.4127e-06
540 | feeder2_line9 | 1 | 354.6 | 70.6851 | 70.6869 | 19.9337 | 19.9343
540 | feeder2_line9 | 2 | 354.6 | 43.9248 | 43.9296 | 12.3871 | 12.3885
540 | feeder2_line9 | 3 | 354.6 | 53.0252 | 53.0202 | 14.9535 | 14.9521
540 | feeder2_line10 | 1 | 80.1 | 8.4548e-07 | 1.4947e-06 | 1.0555e-06 | 1.8661e-06
540 | feeder2_line10 | 2 | 80.1 | 19.017 | 19.017 | 23.7416 | 23.7416
540 | feeder2_line10 | 3 | 80.1 | 8.4515e-07 | 1.4941e-06 | 1.0551e-06 | 1.8654e-06
540 | feeder2_line11 | 1 | 354.6 | 70.685 | 70.6869 | 19.9337 | 19.9343
540 | feeder2_line11 | 2 | 354.6 | 62.0403 | 62.0449 | 17.4958 | 17.4972
540 | feeder2_line11 | 3 | 354.6 | 53.0252 | 53.0202 | 14.9535 | 14.9521
540 | feeder2_line12 | 1 | 80.1 | 5.4721e-07 | 9.9168e-07 | 6.8316e-07 | 1.2381e-06
540 | feeder2_line12 | 2 | 80.1 | 5.4661e-07 | 9.9069e-07 | 6.8241e-07 | 1.2368e-06
540 | feeder2_line12 | 3 | 80.1 | 0.70802 | 0.70802 | 0.88391 | 0.88391
540 | feeder2_line13 | 1 | 354.6 | 70.685 | 70.6869 | 19.9337 | 19.9343
540 | feeder2_line13 | 2 | 354.6 | 62.0403 | 62.0449 | 17.4958 | 17.4972
540 | feeder2_line13 | 3 | 354.6 | 53.7151 | 53.7102 | 15.1481 | 15.1467
540 | feeder2_line14 | 1 | 80.1 | 10.0922 | 10.0922 | 12.5995 | 12.5995
540 | feeder2_line14 | 2 | 80.1 | 2.9821e-07 | 6.4606e-07 | 3.7229e-07 | 8.0656e-07
540 | feeder2_line14 | 3 | 80.1 | 2.9833e-07 | 6.4637e-07 | 3.7245e-07 | 8.0696e-07
540 | feeder2_line15 | 1 | 354.6 | 80.6522 | 80.654 | 22.7445 | 22.7451
540 | feeder2_line15 | 2 | 354.6 | 62.0403 | 62.0449 | 17.4958 | 17.4972
540 | feeder2_line15 | 3 | 354.6 | 53.7151 | 53.7102 | 15.1481 | 15.1467
540 | feeder2_line16 | 1 | 80.1 | 5.723e-07 | 1.031e-06 | 7.1448e-07 | 1.2872e-06
540 | feeder2_line16 | 2 | 80.1 | 0.028905 | 0.028904 | 0.036086 | 0.036084
540 | feeder2_line16 | 3 | 80.1 | 5.7186e-07 | 1.0302e-06 | 7.1393e-07 | 1.2862e-06
540 | feeder2_line17 | 1 | 354.6 | 80.6522 | 80.654 | 22.7446 | 22.7451
540 | feeder2_line17 | 2 | 354.6 | 62.0688 | 62.0734 | 17.5039 | 17.5052
540 | feeder2_line17 | 3 | 354.6 | 53.7152 | 53.7102 | 15.1481 | 15.1467
540 | feeder2_line18 | 1 | 80.1 | 5.4813e-07 | 7.3888e-07 | 6.8431e-07 | 9.2245e-07
540 | feeder2_line18 | 2 | 80.1 | 5.4706e-07 | 7.3761e-07 | 6.8297e-07 | 9.2087e-07
540 | feeder2_line18 | 3 | 80.1 | 0.040247 | 0.040235 | 0.050245 | 0.050231
540 | feeder2_line19 | 1 | 354.6 | 80.6522 | 80.654 | 22.7446 | 22.7451
540 | feeder2_line19 | 2 | 354.6 | 62.0688 | 62.0734 | 17.5039 | 17.5052
540 | feeder2_line19 | 3 | 354.6 | 53.7541 | 53.7491 | 15.1591 | 15.1577
540 | feeder2_line20 | 1 | 99 | 5.4839e-07 | 8.8626e-07 | 5.5393e-07 | 8.9521e-07
540 | feeder2_line20 | 2 | 99 | 5.4718e-07 | 8.8455e-07 | 5.5271e-07 | 8.9349e-07
540 | feeder2_line20 | 3 | 99 | 1.4017 | 1.4017 | 1.4158 | 1.4159
540 | feeder2_line21 | 1 | 354.6 | 80.6523 | 80.654 | 22.7446 | 22.7451
540 | feeder2_line21 | 2 | 354.6 | 62.0689 | 62.0734 | 17.5039 | 17.5052
540 | feeder2_line21 | 3 | 354.6 | 54.2755 | 54.2703 | 15.3061 | 15.3047
540 | feeder2_line22 | 1 | 99 | 5.7337e-07 | 1.0163e-06 | 5.7916e-07 | 1.0265e-06
540 | feeder2_line22 | 2 | 99 | 2.2721 | 2.2721 | 2.2951 | 2.2951
540 | feeder2_line22 | 3 | 99 | 5.7211e-07 | 1.014e-06 | 5.7789e-07 | 1.0243e-06
540 | feeder2_line23 | 1 | 99 | 5.7336e-07 | 9.5129e-07 | 5.7915e-07 | 9.609e-07
540 | feeder2_line23 | 2 | 99 | 5.7217e-07 | 9.4934e-07 | 5.7795e-07 | 9.5893e-07
540 | feeder2_line23 | 3 | 99 | 10.258 | 10.2581 | 10.3616 | 10.3617
540 | feeder2_line24 | 1 | 354.6 | 80.6524 | 80.654 | 22.7446 | 22.7451
540 | feeder2_line24 | 2 | 354.6 | 64.193 | 64.1974 | 18.1029 | 18.1042
540 | feeder2_line24 | 3 | 354.6 | 64.2262 | 64.221 | 18.1123 | 18.1108
540 | feeder2_line25 | 1 | 99 | 2.269 | 2.269 | 2.2919 | 2.2919
540 | feeder2_line25 | 2 | 99 | 4.9886e-08 | 6.9036e-07 | 5.039e-08 | 6.9733e-07
540 | feeder2_line25 | 3 | 99 | 4.9859e-08 | 6.9026e-07 | 5.0363e-08 | 6.9723e-07
540 | feeder2_line26 | 1 | 99 | 0.085083 | 0.085085 | 0.085943 | 0.085944
540 | feeder2_line26 | 2 | 99 | 5.4738e-07 | 8.5531e-07 | 5.5291e-07 | 8.6395e-07
540 | feeder2_line26 | 3 | 99 | 5.4731e-07 | 8.5519e-07 | 5.5284e-07 | 8.6383e-07
540 | feeder2_line27 | 1 | 354.6 | 82.9295 | 82.9312 | 23.3868 | 23.3872
540 | feeder2_line27 | 2 | 354.6 | 64.193 | 64.1974 | 18.1029 | 18.1042
540 | feeder2_line27 | 3 | 354.6 | 64.2262 | 64.221 | 18.1123 | 18.1108
540 | feeder2_line28 | 1 | 99 | 2.5476e-06 | 7.1214e-07 | 2.5734e-06 | 7.1933e-07
540 | feeder2_line28 | 2 | 99 | 1.9727 | 1.9727 | 1.9926 | 1.9926
540 | feeder2_line28 | 3 | 99 | 2.5378e-06 | 7.1013e-07 | 2.5635e-06 | 7.1731e-07
540 | feeder2_line29 | 1 | 354.6 | 82.9295 | 82.9312 | 23.3868 | 23.3872
540 | feeder2_line29 | 2 | 354.6 | 64.9946 | 64.999 | 18.329 | 18.3302
540 | feeder2_line29 | 3 | 354.6 | 64.2262 | 64.221 | 18.1123 | 18.1108
540 | feeder2_line30 | 1 | 266.4 | 5.3098 | 5.3098 | 1.9932 | 1.9932
540 | feeder2_line30 | 2 | 266.4 | 4.7025 | 4.7026 | 1.7652 | 1.7653
540 | feeder2_line30 | 3 | 266.4 | 8.3808 | 8.3805 | 3.1459 | 3.1458
540 | feeder2_line31 | 1 | 354.6 | 87.6301 | 87.6315 | 24.7124 | 24.7128
540 | feeder2_line31 | 2 | 354.6 | 67.9442 | 67.9481 | 19.1608 | 19.1619
540 | feeder2_line31 | 3 | 354.6 | 71.8745 | 71.8688 | 20.2692 | 20.2676
540 | feeder2_line32 | 1 | 354.6 | 87.6301 | 87.6315 | 24.7124 | 24.7128
540 | feeder2_line32 | 2 | 354.6 | 68.0213 | 68.0252 | 19.1825 | 19.1836
540 | feeder2_line32 | 3 | 354.6 | 71.8745 | 71.8688 | 20.2692 | 20.2676
540 | feeder2_line33 | 1 | 99 | 4.9652e-08 | 6.8816e-07 | 5.0154e-08 | 6.9511e-07
540 | feeder2_line33 | 2 | 99 | 0.077274 | 0.077277 | 0.078054 | 0.078057
540 | feeder2_line33 | 3 | 99 | 4.9978e-08 | 6.8567e-07 | 5.0483e-08 | 6.926e-07
540 | feeder2_line34 | 1 | 354.6 | 87.6301 | 87.6315 | 24.7124 | 24.7128
540 | feeder2_line34 | 2 | 354.6 | 68.0213 | 68.0252 | 19.1825 | 19.1836
540 | feeder2_line34 | 3 | 354.6 | 72.6511 | 72.6454 | 20.4882 | 20.4866
540 | feeder2_line35 | 1 | 99 | 3e-07 | 7.6227e-07 | 3.0303e-07 | 7.6996e-07
540 | feeder2_line35 | 2 | 99 | 2.9908e-07 | 7.5961e-07 | 3.0211e-07 | 7.6728e-07
540 | feeder2_line35 | 3 | 99 | 0.7818 | 0.7818 | 0.7897 | 0.7897
540 | feeder2_line36 | 1 | 354.6 | 87.658 | 87.6594 | 24.7203 | 24.7207
540 | feeder2_line36 | 2 | 354.6 | 68.0213 | 68.0252 | 19.1825 | 19.1836
540 | feeder2_line36 | 3 | 354.6 | 72.6511 | 72.6454 | 20.4882 | 20.4866
540 | feeder2_line37 | 1 | 99 | 0.027995 | 0.028032 | 0.028278 | 0.028315
540 | feeder2_line37 | 2 | 99 | 2.9914e-07 | 8.4062e-07 | 3.0216e-07 | 8.4911e-07
540 | feeder2_line37 | 3 | 99 | 2.9906e-07 | 8.4042e-07 | 3.0208e-07 | 8.4891e-07
540 | feeder2_line38 | 1 | 99 | 3.2457e-07 | 7.7766e-07 | 3.2785e-07 | 7.8552e-07
540 | feeder2_line38 | 2 | 99 | 0.077336 | 0.077339 | 0.078117 | 0.07812
540 | feeder2_line38 | 3 | 99 | 3.2381e-07 | 7.75e-07 | 3.2708e-07 | 7.8283e-07
540 | feeder2_line39 | 1 | 266.4 | 5.3098 | 5.3098 | 1.9932 | 1.9932
540 | feeder2_line39 | 2 | 266.4 | 4.6492 | 4.6494 | 1.7452 | 1.7453
540 | feeder2_line39 | 3 | 266.4 | 8.3808 | 8.3805 | 3.1459 | 3.1458
540 | feeder2_line40 | 1 | 354.6 | 89.8677 | 89.8691 | 25.3434 | 25.3438
540 | feeder2_line40 | 2 | 354.6 | 68.0213 | 68.0252 | 19.1825 | 19.1836
540 | feeder2_line40 | 3 | 354.6 | 72.6511 | 72.6454 | 20.4882 | 20.4866
540 | feeder2_line41 | 1 | 99 | 2.2659 | 2.2659 | 2.2888 | 2.2888
540 | feeder2_line41 | 2 | 99 | 5.0065e-08 | 7.3461e-07 | 5.057e-08 | 7.4204e-07
540 | feeder2_line41 | 3 | 99 | 5.0007e-08 | 7.3445e-07 | 5.0512e-08 | 7.4186e-07
540 | feeder2_line42 | 1 | 99 | 2.9974e-07 | 7.5059e-07 | 3.0276e-07 | 7.5818e-07
540 | feeder2_line42 | 2 | 99 | 2.9892e-07 | 7.4827e-07 | 3.0194e-07 | 7.5583e-07
540 | feeder2_line42 | 3 | 99 | 0.75976 | 0.75976 | 0.76743 | 0.76743
540 | feeder2_line43 | 1 | 266.4 | 5.3098 | 5.3098 | 1.9932 | 1.9932
540 | feeder2_line43 | 2 | 266.4 | 4.6493 | 4.6494 | 1.7452 | 1.7453
540 | feeder2_line43 | 3 | 266.4 | 7.6552 | 7.655 | 2.8736 | 2.8735
540 | feeder2_line44 | 1 | 354.6 | 89.8677 | 89.8691 | 25.3434 | 25.3438
540 | feeder2_line44 | 2 | 354.6 | 68.0214 | 68.0252 | 19.1826 | 19.1836
540 | feeder2_line44 | 3 | 354.6 | 73.3182 | 73.3124 | 20.6763 | 20.6747
540 | feeder2_line45 | 1 | 99 | 4.9659e-08 | 5.816e-07 | 5.0161e-08 | 5.8747e-07
540 | feeder2_line45 | 2 | 99 | 5.0079e-08 | 5.7939e-07 | 5.0585e-08 | 5.8524e-07
540 | feeder2_line45 | 3 | 99 | 1.4025 | 1.4025 | 1.4166 | 1.4166
540 | feeder2_line46 | 1 | 99 | 5.7466e-07 | 1.3607e-06 | 5.8046e-07 | 1.3744e-06
540 | feeder2_line46 | 2 | 99 | 5.7285e-07 | 1.3565e-06 | 5.7864e-07 | 1.3702e-06
540 | feeder2_line46 | 3 | 99 | 0.89744 | 0.89745 | 0.90651 | 0.90651
540 | feeder2_line47 | 1 | 266.4 | 5.3099 | 5.3098 | 1.9932 | 1.9932
540 | feeder2_line47 | 2 | 266.4 | 4.6494 | 4.6494 | 1.7453 | 1.7453
540 | feeder2_line47 | 3 | 266.4 | 6.9587 | 6.9584 | 2.6121 | 2.612
540 | feeder2_line48 | 1 | 99 | 0.081588 | 0.081589 | 0.082412 | 0.082413
540 | feeder2_line48 | 2 | 99 | 4.998e-08 | 7.3034e-07 | 5.0485e-08 | 7.3772e-07
540 | feeder2_line48 | 3 | 99 | 4.9959e-08 | 7.3005e-07 | 5.0464e-08 | 7.3743e-07
540 | feeder2_line49 | 1 | 266.4 | 5.2359 | 5.2358 | 1.9654 | 1.9654
540 | feeder2_line49 | 2 | 266.4 | 4.6494 | 4.6494 | 1.7453 | 1.7453
540 | feeder2_line49 | 3 | 266.4 | 6.9587 | 6.9584 | 2.6121 | 2.612
540 | feeder2_line50 | 1 | 99 | 5.7463e-07 | 1.2383e-06 | 5.8044e-07 | 1.2508e-06
540 | feeder2_line50 | 2 | 99 | 1.2599 | 1.2599 | 1.2726 | 1.2727
540 | feeder2_line50 | 3 | 99 | 5.7261e-07 | 1.234e-06 | 5.784e-07 | 1.2464e-06
540 | feeder2_line51 | 1 | 99 | 0.044704 | 0.04474 | 0.045156 | 0.045192
540 | feeder2_line51 | 2 | 99 | 5.7284e-07 | 1.3401e-06 | 5.7863e-07 | 1.3537e-06
540 | feeder2_line51 | 3 | 99 | 5.7261e-07 | 1.3396e-06 | 5.7839e-07 | 1.3531e-06
540 | feeder2_line52 | 1 | 266.4 | 5.1946 | 5.1945 | 1.9499 | 1.9499
540 | feeder2_line52 | 2 | 266.4 | 3.4169 | 3.4169 | 1.2826 | 1.2826
540 | feeder2_line52 | 3 | 266.4 | 6.9586 | 6.9584 | 2.6121 | 2.612
540 | feeder2_line53 | 1 | 99 | 5.4982e-07 | 7.5574e-07 | 5.5537e-07 | 7.6338e-07
540 | feeder2_line53 | 2 | 99 | 3.4169 | 3.4169 | 3.4514 | 3.4514
540 | feeder2_line53 | 3 | 99 | 5.4763e-07 | 7.531e-07 | 5.5316e-07 | 7.6071e-07
540 | feeder2_line54 | 1 | 266.4 | 5.1945 | 5.1945 | 1.9499 | 1.9499
540 | feeder2_line54 | 2 | 266.4 | 8.5454e-05 | 4.622e-06 | 3.2077e-05 | 1.735e-06
540 | feeder2_line54 | 3 | 266.4 | 6.9584 | 6.9584 | 2.612 | 2.612
540 | feeder2_line55 | 1 | 99 | 1.1016 | 1.1016 | 1.1127 | 1.1127
540 | feeder2_line55 | 2 | 99 | 5.0129e-08 | 7.3024e-07 | 5.0636e-08 | 7.3762e-07
540 | feeder2_line55 | 3 | 99 | 5.0048e-08 | 7.3012e-07 | 5.0554e-08 | 7.375e-07
540 | feeder2_line56 | 1 | 354.6 | 90.4354 | 90.4367 | 25.5035 | 25.5039
540 | feeder2_line56 | 2 | 354.6 | 68.0214 | 68.0252 | 19.1826 | 19.1836
540 | feeder2_line56 | 3 | 354.6 | 73.3182 | 73.3124 | 20.6763 | 20.6747
540 | feeder2_line57 | 1 | 99 | 7.4449e-07 | 1.548e-06 | 7.5201e-07 | 1.5636e-06
540 | feeder2_line57 | 2 | 99 | 7.496e-07 | 1.5433e-06 | 7.5717e-07 | 1.5589e-06
540 | feeder2_line57 | 3 | 99 | 6.9585 | 6.9584 | 7.0288 | 7.0287
540 | feeder2_line58 | 1 | 266.4 | 5.1945 | 5.1945 | 1.9499 | 1.9499
540 | feeder2_line58 | 2 | 266.4 | 1.8935e-05 | 2.6835e-06 | 7.1078e-06 | 1.0073e-06
540 | feeder2_line58 | 3 | 266.4 | 1.8915e-05 | 2.6823e-06 | 7.1004e-06 | 1.0069e-06
540 | feeder2_line59 | 1 | 99 | 4.9629e-08 | 5.3809e-07 | 5.0131e-08 | 5.4352e-07
540 | feeder2_line59 | 2 | 99 | 4.9973e-08 | 5.3645e-07 | 5.0478e-08 | 5.4187e-07
540 | feeder2_line59 | 3 | 99 | 6.2731 | 6.273 | 6.3364 | 6.3363
540 | feeder2_line60 | 1 | 99 | 2.9972e-07 | 8.1322e-07 | 3.0274e-07 | 8.2143e-07
540 | feeder2_line60 | 2 | 99 | 2.9892e-07 | 8.1073e-07 | 3.0194e-07 | 8.1892e-07
540 | feeder2_line60 | 3 | 99 | 0.70819 | 0.7082 | 0.71535 | 0.71535
540 | feeder2_line61 | 1 | 266.4 | 0.08525 | 0.085421 | 0.032001 | 0.032065
540 | feeder2_line61 | 2 | 266.4 | 10.932 | 10.9321 | 4.1036 | 4.1036
540 | feeder2_line61 | 3 | 266.4 | 13.0327 | 13.033 | 4.8922 | 4.8923
540 | feeder2_line62 | 1 | 354.6 | 90.5206 | 90.5221 | 25.5275 | 25.528
540 | feeder2_line62 | 2 | 354.6 | 78.7582 | 78.7621 | 22.2104 | 22.2115
540 | feeder2_line62 | 3 | 354.6 | 86.075 | 86.0695 | 24.2738 | 24.2723
540 | feeder2_line63 | 1 | 99 | 0.4133 | 0.4133 | 0.41748 | 0.41748
540 | feeder2_line63 | 2 | 99 | 5.7285e-07 | 1.2189e-06 | 5.7863e-07 | 1.2312e-06
540 | feeder2_line63 | 3 | 99 | 5.726e-07 | 1.2184e-06 | 5.7838e-07 | 1.2307e-06
540 | feeder2_line64 | 1 | 99 | 4.8184 | 4.8184 | 4.8671 | 4.8671
540 | feeder2_line64 | 2 | 99 | 5.8054e-12 | 3.2108e-07 | 5.864e-12 | 3.2432e-07
540 | feeder2_line64 | 3 | 99 | 6.6251e-12 | 3.2095e-07 | 6.692e-12 | 3.2419e-07
540 | feeder2_line65 | 1 | 99 | 4.9681e-08 | 6.4486e-07 | 5.0183e-08 | 6.5138e-07
540 | feeder2_line65 | 2 | 99 | 0.089882 | 0.089887 | 0.09079 | 0.090795
540 | feeder2_line65 | 3 | 99 | 5.0101e-08 | 6.4182e-07 | 5.0607e-08 | 6.483e-07
540 | feeder2_line66 | 1 | 354.6 | 90.5205 | 90.5221 | 25.5275 | 25.528
540 | feeder2_line66 | 2 | 354.6 | 78.8479 | 78.8519 | 22.2357 | 22.2368
540 | feeder2_line66 | 3 | 354.6 | 86.075 | 86.0695 | 24.2738 | 24.2723
540 | feeder2_line67 | 1 | 99 | 2.4818e-08 | 3.6435e-07 | 2.5069e-08 | 3.6803e-07
540 | feeder2_line67 | 2 | 99 | 2.5093e-08 | 3.6268e-07 | 2.5346e-08 | 3.6634e-07
540 | feeder2_line67 | 3 | 99 | 2.27 | 2.27 | 2.2929 | 2.2929
540 | feeder2_line68 | 1 | 266.4 | 0.085289 | 0.085421 | 0.032015 | 0.032065
540 | feeder2_line68 | 2 | 266.4 | 10.9321 | 10.9321 | 4.1036 | 4.1036
540 | feeder2_line68 | 3 | 266.4 | 10.7665 | 10.7667 | 4.0415 | 4.0416
540 | feeder2_line69 | 1 | 99 | 0.10045 | 0.10044 | 0.10146 | 0.10145
540 | feeder2_line69 | 2 | 99 | 2.5443e-06 | 6.6643e-07 | 2.57e-06 | 6.7316e-07
540 | feeder2_line69 | 3 | 99 | 2.5451e-06 | 6.6643e-07 | 2.5708e-06 | 6.7316e-07
540 | feeder2_line70 | 1 | 354.6 | 90.6209 | 90.6225 | 25.5558 | 25.5563
540 | feeder2_line70 | 2 | 354.6 | 78.8479 | 78.8519 | 22.2357 | 22.2368
540 | feeder2_line70 | 3 | 354.6 | 86.0749 | 86.0695 | 24.2738 | 24.2723
540 | feeder2_line71 | 1 | 99 | 4.9697e-08 | 7.1974e-07 | 5.0199e-08 | 7.2701e-07
540 | feeder2_line71 | 2 | 99 | 1.2465 | 1.2465 | 1.2591 | 1.2591
540 | feeder2_line71 | 3 | 99 | 5.0121e-08 | 7.1629e-07 | 5.0627e-08 | 7.2353e-07
540 | feeder2_line72 | 1 | 354.6 | 90.621 | 90.6225 | 25.5558 | 25.5563
540 | feeder2_line72 | 2 | 354.6 | 79.4753 | 79.4792 | 22.4127 | 22.4138
540 | feeder2_line72 | 3 | 354.6 | 86.075 | 86.0695 | 24.2738 | 24.2723
540 | feeder2_line73 | 1 | 99 | 6.0128e-07 | 1.5426e-06 | 6.0735e-07 | 1.5582e-06
540 | feeder2_line73 | 2 | 99 | 0.077215 | 0.077219 | 0.077995 | 0.077999
540 | feeder2_line73 | 3 | 99 | 5.9868e-07 | 1.5351e-06 | 6.0472e-07 | 1.5506e-06
540 | feeder2_line74 | 1 | 99 | 4.9639e-08 | 4.6008e-07 | 5.014e-08 | 4.6473e-07
540 | feeder2_line74 | 2 | 99 | 10.7666 | 10.7665 | 10.8754 | 10.8753
540 | feeder2_line74 | 3 | 99 | 5.0072e-08 | 4.5785e-07 | 5.0578e-08 | 4.6247e-07
540 | feeder2_line75 | 1 | 266.4 | 0.085387 | 0.085421 | 0.032052 | 0.032065
540 | feeder2_line75 | 2 | 266.4 | 0.089851 | 0.089886 | 0.033728 | 0.033741
540 | feeder2_line75 | 3 | 266.4 | 10.7666 | 10.7667 | 4.0415 | 4.0416
540 | feeder2_line76 | 1 | 99 | 0.085419 | 0.085421 | 0.086282 | 0.086284
540 | feeder2_line76 | 2 | 99 | 8.4803e-07 | 1.5838e-06 | 8.566e-07 | 1.5998e-06
540 | feeder2_line76 | 3 | 99 | 8.4788e-07 | 1.5834e-06 | 8.5645e-07 | 1.5994e-06
540 | feeder2_line77 | 1 | 99 | 2.4814e-08 | 5.7817e-07 | 2.5065e-08 | 5.8401e-07
540 | feeder2_line77 | 2 | 99 | 2.5081e-08 | 5.7544e-07 | 2.5334e-08 | 5.8125e-07
540 | feeder2_line77 | 3 | 99 | 10.7666 | 10.7667 | 10.8754 | 10.8755
540 | feeder2_line78 | 1 | 266.4 | 3.2633e-12 | 9.5858e-07 | 1.225e-12 | 3.5983e-07
540 | feeder2_line78 | 2 | 266.4 | 0.089884 | 0.089886 | 0.03374 | 0.033741
540 | feeder2_line78 | 3 | 266.4 | 8.204e-12 | 9.543e-07 | 3.0796e-12 | 3.5822e-07
540 | feeder2_line79 | 1 | 354.6 | 1.208 | 1.2078 | 0.34067 | 0.3406
540 | feeder2_line79 | 2 | 354.6 | 16.0964 | 16.0959 | 4.5393 | 4.5392
540 | feeder2_line79 | 3 | 354.6 | 10.3163 | 10.3157 | 2.9093 | 2.9091
540 | feeder2_line80 | 1 | 354.6 | 91.5504 | 91.5515 | 25.8179 | 25.8182
540 | feeder2_line80 | 2 | 354.6 | 94.8878 | 94.891 | 26.7591 | 26.76
540 | feeder2_line80 | 3 | 354.6 | 94.6449 | 94.6388 | 26.6906 | 26.6889
540 | feeder2_line81 | 1 | 354.6 | 91.5504 | 91.5515 | 25.8179 | 25.8182
540 | feeder2_line81 | 2 | 354.6 | 94.8877 | 94.891 | 26.7591 | 26.76
540 | feeder2_line81 | 3 | 354.6 | 95.24 | 95.2339 | 26.8584 | 26.8567
540 | feeder2_line82 | 1 | 354.6 | 1.7509e-11 | 7.385e-07 | 4.9376e-12 | 2.0826e-07
540 | feeder2_line82 | 2 | 354.6 | 3.4873e-11 | 7.351e-07 | 9.8345e-12 | 2.073e-07
540 | feeder2_line82 | 3 | 354.6 | 1.0393 | 1.0393 | 0.2931 | 0.29309
540 | feeder2_line83 | 1 | 354.6 | 91.5506 | 91.5515 | 25.818 | 25.8182
540 | feeder2_line83 | 2 | 354.6 | 94.977 | 94.9801 | 26.7843 | 26.7851
540 | feeder2_line83 | 3 | 354.6 | 95.2402 | 95.2339 | 26.8585 | 26.8567
540 | feeder2_line84 | 1 | 354.6 | 2.7538e-11 | 1.3054e-06 | 7.7661e-12 | 3.6814e-07
540 | feeder2_line84 | 2 | 354.6 | 0.089138 | 0.089163 | 0.025138 | 0.025145
540 | feeder2_line84 | 3 | 354.6 | 2.055e-11 | 1.2996e-06 | 5.7954e-12 | 3.6649e-07
540 | feeder2_line85 | 1 | 99 | 0.076607 | 0.076609 | 0.077381 | 0.077382
540 | feeder2_line85 | 2 | 99 | 5.0309e-08 | 4.6377e-07 | 5.0817e-08 | 4.6846e-07
540 | feeder2_line85 | 3 | 99 | 5.0172e-08 | 4.6384e-07 | 5.0679e-08 | 4.6853e-07
540 | feeder2_line86 | 1 | 354.6 | 91.6273 | 91.6281 | 25.8396 | 25.8398
540 | feeder2_line86 | 2 | 354.6 | 94.9771 | 94.9801 | 26.7843 | 26.7851
540 | feeder2_line86 | 3 | 354.6 | 95.2403 | 95.2339 | 26.8585 | 26.8567
540 | feeder2_line87 | 1 | 354.6 | 91.6275 | 91.6281 | 25.8397 | 25.8398
540 | feeder2_line87 | 2 | 354.6 | 95.406 | 95.4089 | 26.9052 | 26.9061
540 | feeder2_line87 | 3 | 354.6 | 96.5519 | 96.5453 | 27.2284 | 27.2265
540 | feeder2_line88 | 1 | 354.6 | 0.00011567 | 3.3852e-06 | 3.2619e-05 | 9.5466e-07
540 | feeder2_line88 | 2 | 354.6 | 0.4289 | 0.42888 | 0.12095 | 0.12095
540 | feeder2_line88 | 3 | 354.6 | 2.3363 | 2.3362 | 0.65884 | 0.65883
540 | feeder2_line89 | 1 | 354.6 | 91.6252 | 91.6281 | 25.839 | 25.8398
540 | feeder2_line89 | 2 | 354.6 | 96.0284 | 96.0336 | 27.0808 | 27.0822
540 | feeder2_line89 | 3 | 354.6 | 96.5496 | 96.5453 | 27.2278 | 27.2265
540 | feeder2_line90 | 1 | 354.6 | 0.00073001 | 2.0428e-06 | 0.00020587 | 5.761e-07
540 | feeder2_line90 | 2 | 354.6 | 0.95375 | 0.95375 | 0.26896 | 0.26896
540 | feeder2_line90 | 3 | 354.6 | 0.00072511 | 2.0346e-06 | 0.00020449 | 5.7377e-07
540 | feeder2_line91 | 1 | 354.6 | 91.6251 | 91.6281 | 25.839 | 25.8398
540 | feeder2_line91 | 2 | 354.6 | 96.0283 | 96.0336 | 27.0807 | 27.0822
540 | feeder2_line91 | 3 | 354.6 | 97.2584 | 97.2542 | 27.4276 | 27.4264
540 | feeder2_line92 | 1 | 354.6 | 1.0963e-11 | 1.0308e-06 | 3.0915e-12 | 2.9069e-07
540 | feeder2_line92 | 2 | 354.6 | 1.5765e-11 | 1.0262e-06 | 4.4458e-12 | 2.8938e-07
540 | feeder2_line92 | 3 | 354.6 | 0.70945 | 0.70946 | 0.20007 | 0.20007
540 | feeder2_line93 | 1 | 99 | 2.4899e-08 | 3.4417e-07 | 2.515e-08 | 3.4764e-07
540 | feeder2_line93 | 2 | 99 | 0.089065 | 0.089091 | 0.089964 | 0.089991
540 | feeder2_line93 | 3 | 99 | 2.5103e-08 | 3.4254e-07 | 2.5356e-08 | 3.46e-07
540 | feeder2_line94 | 1 | 354.6 | 2.4897e-06 | 1.6752e-06 | 7.0212e-07 | 4.7241e-07
540 | feeder2_line94 | 2 | 354.6 | 0.9004 | 0.90042 | 0.25392 | 0.25392
540 | feeder2_line94 | 3 | 354.6 | 2.5103e-06 | 1.6679e-06 | 7.0791e-07 | 4.7035e-07
540 | feeder2_line95 | 1 | 99 | 3.5925e-06 | 2.6251e-06 | 3.6288e-06 | 2.6517e-06
540 | feeder2_line95 | 2 | 99 | 0.4288 | 0.42888 | 0.43313 | 0.43321
540 | feeder2_line95 | 3 | 99 | 3.5689e-06 | 2.6127e-06 | 3.6049e-06 | 2.639e-06
540 | feeder2_line96 | 1 | 354.6 | 0.00012188 | 6.255e-07 | 3.4371e-05 | 1.764e-07
540 | feeder2_line96 | 2 | 354.6 | 0.00012118 | 6.2284e-07 | 3.4175e-05 | 1.7565e-07
540 | feeder2_line96 | 3 | 354.6 | 2.3362 | 2.3362 | 0.65883 | 0.65883
540 | feeder2_line97 | 1 | 354.6 | 92.3765 | 92.3793 | 26.0509 | 26.0517
540 | feeder2_line97 | 2 | 354.6 | 96.0285 | 96.0336 | 27.0808 | 27.0822
540 | feeder2_line97 | 3 | 354.6 | 97.2586 | 97.2542 | 27.4277 | 27.4264
540 | feeder2_line98 | 1 | 354.6 | 1.3472 | 1.3464 | 0.37993 | 0.37971
540 | feeder2_line98 | 2 | 354.6 | 0.001697 | 6.2227e-07 | 0.00047858 | 1.7549e-07
540 | feeder2_line98 | 3 | 354.6 | 0.0017081 | 6.2215e-07 | 0.00048169 | 1.7545e-07
540 | feeder2_line99 | 1 | 99 | 2.4885e-08 | 4.4988e-07 | 2.5136e-08 | 4.5442e-07
540 | feeder2_line99 | 2 | 99 | 2.5167e-08 | 4.4765e-07 | 2.5421e-08 | 4.5217e-07
540 | feeder2_line99 | 3 | 99 | 2.3362 | 2.3362 | 2.3598 | 2.3598
540 | feeder2_line100 | 1 | 99 | 1.3464 | 1.3464 | 1.36 | 1.36
540 | feeder2_line100 | 2 | 99 | 2.5184e-08 | 6.1491e-07 | 2.5439e-08 | 6.2112e-07
540 | feeder2_line100 | 3 | 99 | 2.5107e-08 | 6.1506e-07 | 2.5361e-08 | 6.2127e-07
540 | feeder2_line101 | 1 | 354.6 | 0.90216 | 0.90203 | 0.25442 | 0.25438
540 | feeder2_line101 | 2 | 354.6 | 16.0964 | 16.0959 | 4.5393 | 4.5392
540 | feeder2_line101 | 3 | 354.6 | 10.3163 | 10.3157 | 2.9093 | 2.9091
540 | feeder2_line102 | 1 | 99 | 0.42253 | 0.42252 | 0.4268 | 0.42679
540 | feeder2_line102 | 2 | 99 | 2.3302e-06 | 8.785e-07 | 2.3537e-06 | 8.8737e-07
540 | feeder2_line102 | 3 | 99 | 2.3377e-06 | 8.7866e-07 | 2.3613e-06 | 8.8754e-07
540 | feeder2_line103 | 1 | 99 | 5.5265e-07 | 8.0834e-07 | 5.5823e-07 | 8.1651e-07
540 | feeder2_line103 | 2 | 99 | 0.3406 | 0.3406 | 0.34404 | 0.34404
540 | feeder2_line103 | 3 | 99 | 5.4945e-07 | 8.0421e-07 | 5.55e-07 | 8.1233e-07
540 | feeder2_line104 | 1 | 354.6 | 0.90216 | 0.90203 | 0.25442 | 0.25438
540 | feeder2_line104 | 2 | 354.6 | 15.7642 | 15.7638 | 4.4456 | 4.4455
540 | feeder2_line104 | 3 | 354.6 | 10.3162 | 10.3157 | 2.9093 | 2.9091
540 | feeder2_line105 | 1 | 99 | 2.5645e-06 | 7.4379e-07 | 2.5904e-06 | 7.5131e-07
540 | feeder2_line105 | 2 | 99 | 2.5449e-06 | 7.3979e-07 | 2.5706e-06 | 7.4726e-07
540 | feeder2_line105 | 3 | 99 | 0.040088 | 0.040062 | 0.040493 | 0.040467
540 | feeder2_line106 | 1 | 354.6 | 0.90214 | 0.90203 | 0.25441 | 0.25438
540 | feeder2_line106 | 2 | 354.6 | 15.7641 | 15.7638 | 4.4456 | 4.4455
540 | feeder2_line106 | 3 | 354.6 | 10.2817 | 10.2813 | 2.8995 | 2.8994
540 | feeder2_line107 | 1 | 99 | 3.2602e-07 | 9.0645e-07 | 3.2931e-07 | 9.1561e-07
540 | feeder2_line107 | 2 | 99 | 1.0481 | 1.0481 | 1.0587 | 1.0587
540 | feeder2_line107 | 3 | 99 | 3.2483e-07 | 9.0167e-07 | 3.2811e-07 | 9.1078e-07
540 | feeder2_line108 | 1 | 354.6 | 0.90215 | 0.90203 | 0.25441 | 0.25438
540 | feeder2_line108 | 2 | 354.6 | 14.9611 | 14.9607 | 4.2191 | 4.219
540 | feeder2_line108 | 3 | 354.6 | 10.2817 | 10.2813 | 2.8995 | 2.8994
540 | feeder2_line109 | 1 | 354.6 | 93.8538 | 93.8555 | 26.4675 | 26.468
540 | feeder2_line109 | 2 | 354.6 | 96.0297 | 96.0336 | 27.0811 | 27.0822
540 | feeder2_line109 | 3 | 354.6 | 97.2598 | 97.2542 | 27.428 | 27.4264
540 | feeder2_line110 | 1 | 99 | 1.8064 | 1.8058 | 1.8247 | 1.824
540 | feeder2_line110 | 2 | 99 | 0.00080471 | 9.0946e-07 | 0.00081284 | 9.1865e-07
540 | feeder2_line110 | 3 | 99 | 0.00080541 | 9.1047e-07 | 0.00081355 | 9.1967e-07
540 | feeder2_line111 | 1 | 99 | 2.4888e-08 | 3.8422e-07 | 2.5139e-08 | 3.881e-07
540 | feeder2_line111 | 2 | 99 | 0.045483 | 0.045509 | 0.045942 | 0.045969
540 | feeder2_line111 | 3 | 99 | 2.5093e-08 | 3.824e-07 | 2.5346e-08 | 3.8626e-07
540 | feeder2_line112 | 1 | 99 | 3.2629e-07 | 9.2332e-07 | 3.2959e-07 | 9.3264e-07
540 | feeder2_line112 | 2 | 99 | 0.38332 | 0.38338 | 0.3872 | 0.38726
540 | feeder2_line112 | 3 | 99 | 3.2522e-07 | 9.1892e-07 | 3.285e-07 | 9.282e-07
540 | feeder2_line113 | 1 | 99 | 1.5205 | 1.5205 | 1.5358 | 1.5359
540 | feeder2_line113 | 2 | 99 | 3.2566e-07 | 9.0695e-07 | 3.2895e-07 | 9.1611e-07
540 | feeder2_line113 | 3 | 99 | 3.2563e-07 | 9.0721e-07 | 3.2892e-07 | 9.1637e-07
540 | feeder2_line114 | 1 | 99 | 0.34139 | 0.34139 | 0.34484 | 0.34484
540 | feeder2_line114 | 2 | 99 | 2.5144e-08 | 4.3684e-07 | 2.5398e-08 | 4.4125e-07
540 | feeder2_line114 | 3 | 99 | 2.5072e-08 | 4.3692e-07 | 2.5326e-08 | 4.4134e-07
540 | feeder2_line115 | 1 | 99 | 2.4834e-08 | 5.6568e-07 | 2.5085e-08 | 5.714e-07
540 | feeder2_line115 | 2 | 99 | 10.9711 | 10.9709 | 11.0819 | 11.0818
540 | feeder2_line115 | 3 | 99 | 2.5064e-08 | 5.6263e-07 | 2.5317e-08 | 5.6831e-07
540 | feeder2_line116 | 1 | 354.6 | 0.90216 | 0.90203 | 0.25442 | 0.25438
540 | feeder2_line116 | 2 | 354.6 | 4.544 | 4.5438 | 1.2814 | 1.2814
540 | feeder2_line116 | 3 | 354.6 | 10.2817 | 10.2813 | 2.8995 | 2.8994
540 | feeder2_line117 | 1 | 99 | 4.9866e-08 | 6.4724e-07 | 5.037e-08 | 6.5378e-07
540 | feeder2_line117 | 2 | 99 | 0.89884 | 0.89887 | 0.90792 | 0.90795
540 | feeder2_line117 | 3 | 99 | 5.026e-08 | 6.4433e-07 | 5.0767e-08 | 6.5084e-07
540 | feeder2_line118 | 1 | 354.6 | 93.8539 | 93.8555 | 26.4675 | 26.468
540 | feeder2_line118 | 2 | 354.6 | 96.5613 | 96.5653 | 27.2311 | 27.2322
540 | feeder2_line118 | 3 | 354.6 | 97.2598 | 97.2542 | 27.428 | 27.4264
540 | feeder2_line119 | 1 | 99 | 2.4827e-08 | 6.0872e-07 | 2.5078e-08 | 6.1487e-07
540 | feeder2_line119 | 2 | 99 | 2.5141e-08 | 6.0522e-07 | 2.5395e-08 | 6.1134e-07
540 | feeder2_line119 | 3 | 99 | 7.1828 | 7.1827 | 7.2553 | 7.2552
540 | feeder2_line120 | 1 | 354.6 | 0.90216 | 0.90203 | 0.25442 | 0.25438
540 | feeder2_line120 | 2 | 354.6 | 4.544 | 4.5438 | 1.2814 | 1.2814
540 | feeder2_line120 | 3 | 354.6 | 3.4331 | 3.4329 | 0.96817 | 0.96811
540 | feeder2_line121 | 1 | 99 | 3.2602e-07 | 9.4262e-07 | 3.2931e-07 | 9.5215e-07
540 | feeder2_line121 | 2 | 99 | 2.4012 | 2.4011 | 2.4254 | 2.4254
540 | feeder2_line121 | 3 | 99 | 3.2476e-07 | 9.3735e-07 | 3.2804e-07 | 9.4682e-07
540 | feeder2_line122 | 1 | 354.6 | 0.90213 | 0.90203 | 0.25441 | 0.25438
540 | feeder2_line122 | 2 | 354.6 | 2.2041 | 2.2039 | 0.62158 | 0.62152
540 | feeder2_line122 | 3 | 354.6 | 3.4331 | 3.4329 | 0.96816 | 0.96811
540 | feeder2_line123 | 1 | 99 | 5.7756e-07 | 9.7679e-07 | 5.834e-07 | 9.8665e-07
540 | feeder2_line123 | 2 | 99 | 5.7418e-07 | 9.7112e-07 | 5.7998e-07 | 9.8093e-07
540 | feeder2_line123 | 3 | 99 | 1.9747 | 1.9747 | 1.9947 | 1.9946
540 | feeder2_line124 | 1 | 354.6 | 0.90218 | 0.90203 | 0.25442 | 0.25438
540 | feeder2_line124 | 2 | 354.6 | 2.2041 | 2.2039 | 0.62157 | 0.62152
540 | feeder2_line124 | 3 | 354.6 | 1.4675 | 1.4673 | 0.41384 | 0.41378
540 | feeder2_line125 | 1 | 99 | 5.7756e-07 | 9.0802e-07 | 5.834e-07 | 9.1719e-07
540 | feeder2_line125 | 2 | 99 | 5.7417e-07 | 9.0275e-07 | 5.7997e-07 | 9.1187e-07
540 | feeder2_line125 | 3 | 99 | 1.3428 | 1.3427 | 1.3563 | 1.3563
540 | feeder2_line126 | 1 | 354.6 | 0.90231 | 0.90204 | 0.25446 | 0.25438
540 | feeder2_line126 | 2 | 354.6 | 2.2042 | 2.2039 | 0.62161 | 0.62152
540 | feeder2_line126 | 3 | 354.6 | 0.20396 | 0.20364 | 0.057517 | 0.057427
540 | feeder2_line127 | 1 | 99 | 5.7756e-07 | 1.087e-06 | 5.834e-07 | 1.098e-06
540 | feeder2_line127 | 2 | 99 | 5.7417e-07 | 1.0807e-06 | 5.7997e-07 | 1.0916e-06
540 | feeder2_line127 | 3 | 99 | 0.07717 | 0.077164 | 0.07795 | 0.077944
540 | feeder2_line128 | 1 | 354.6 | 0.90229 | 0.90204 | 0.25445 | 0.25438
540 | feeder2_line128 | 2 | 354.6 | 2.2042 | 2.2039 | 0.6216 | 0.62152
540 | feeder2_line128 | 3 | 354.6 | 0.12673 | 0.1265 | 0.035738 | 0.035673
540 | feeder2_line129 | 1 | 99 | 5.5273e-07 | 8.8143e-07 | 5.5831e-07 | 8.9034e-07
540 | feeder2_line129 | 2 | 99 | 2.2039 | 2.2039 | 2.2262 | 2.2262
540 | feeder2_line129 | 3 | 99 | 5.4922e-07 | 8.7648e-07 | 5.5477e-07 | 8.8534e-07
540 | feeder2_line130 | 1 | 354.6 | 0.90233 | 0.90204 | 0.25446 | 0.25438
540 | feeder2_line130 | 2 | 354.6 | 0.00030893 | 4.6378e-06 | 8.712e-05 | 1.3079e-06
540 | feeder2_line130 | 3 | 354.6 | 0.12674 | 0.1265 | 0.035742 | 0.035673
540 | feeder2_line131 | 1 | 99 | 5.7756e-07 | 9.7693e-07 | 5.8339e-07 | 9.868e-07
540 | feeder2_line131 | 2 | 99 | 5.7416e-07 | 9.7124e-07 | 5.7996e-07 | 9.8105e-07
540 | feeder2_line131 | 3 | 99 | 0.049437 | 0.049433 | 0.049936 | 0.049932
540 | feeder2_line132 | 1 | 354.6 | 0.90216 | 0.90204 | 0.25442 | 0.25438
540 | feeder2_line132 | 2 | 354.6 | 0.00012557 | 2.9159e-06 | 3.541e-05 | 8.2232e-07
540 | feeder2_line132 | 3 | 354.6 | 0.077238 | 0.077164 | 0.021782 | 0.021761
540 | feeder2_line133 | 1 | 99 | 0.90203 | 0.90204 | 0.91114 | 0.91115
540 | feeder2_line133 | 2 | 99 | 2.9965e-07 | 9.7899e-07 | 3.0268e-07 | 9.8888e-07
540 | feeder2_line133 | 3 | 99 | 2.9968e-07 | 9.792e-07 | 3.0271e-07 | 9.8909e-07
540 | feeder2_line134 | 1 | 354.6 | 1.1393e-11 | 1.7953e-06 | 3.2128e-12 | 5.0628e-07
540 | feeder2_line134 | 2 | 354.6 | 9.6983e-12 | 1.7856e-06 | 2.735e-12 | 5.0356e-07
540 | feeder2_line134 | 3 | 354.6 | 0.077169 | 0.077164 | 0.021762 | 0.021761
540 | feeder2_line135 | 1 | 99 | 1.2516 | 1.2516 | 1.2643 | 1.2643
540 | feeder2_line135 | 2 | 99 | 5.0446e-08 | 5.8722e-07 | 5.0956e-08 | 5.9315e-07
540 | feeder2_line135 | 3 | 99 | 5.0286e-08 | 5.8743e-07 | 5.0794e-08 | 5.9336e-07
540 | feeder2_line136 | 1 | 354.6 | 94.5454 | 94.547 | 26.6625 | 26.663
540 | feeder2_line136 | 2 | 354.6 | 96.5613 | 96.5653 | 27.2311 | 27.2322
540 | feeder2_line136 | 3 | 354.6 | 97.2598 | 97.2542 | 27.428 | 27.4264
540 | feeder2_line137 | 1 | 99 | 1.6142 | 1.6142 | 1.6305 | 1.6305
540 | feeder2_line137 | 2 | 99 | 8.5217e-07 | 1.5818e-06 | 8.6078e-07 | 1.5977e-06
540 | feeder2_line137 | 3 | 99 | 8.5254e-07 | 1.5824e-06 | 8.6115e-07 | 1.5983e-06
540 | feeder2_line138 | 1 | 354.6 | 96.0584 | 96.06 | 27.0892 | 27.0897
540 | feeder2_line138 | 2 | 354.6 | 96.5614 | 96.5653 | 27.2311 | 27.2322
540 | feeder2_line138 | 3 | 354.6 | 97.2598 | 97.2542 | 27.428 | 27.4264
540 | feeder2_line139 | 1 | 99 | 4.9913e-08 | 4.953e-07 | 5.0417e-08 | 5.0031e-07
540 | feeder2_line139 | 2 | 99 | 5.0466e-08 | 4.9293e-07 | 5.0975e-08 | 4.9791e-07
540 | feeder2_line139 | 3 | 99 | 1.0549 | 1.0546 | 1.0656 | 1.0652
540 | feeder2_line140 | 1 | 354.6 | 96.0585 | 96.06 | 27.0893 | 27.0897
540 | feeder2_line140 | 2 | 354.6 | 96.5615 | 96.5653 | 27.2311 | 27.2322
540 | feeder2_line140 | 3 | 354.6 | 98.3144 | 98.3083 | 27.7254 | 27.7237
540 | feeder2_line141 | 1 | 99 | 2.5483e-06 | 4.9002e-07 | 2.574e-06 | 4.9497e-07
540 | feeder2_line141 | 2 | 99 | 0.76135 | 0.76135 | 0.76904 | 0.76904
540 | feeder2_line141 | 3 | 99 | 2.5327e-06 | 4.8786e-07 | 2.5583e-06 | 4.9278e-07
540 | feeder2_line142 | 1 | 354.6 | 96.0583 | 96.06 | 27.0892 | 27.0897
540 | feeder2_line142 | 2 | 354.6 | 97.3223 | 97.3263 | 27.4457 | 27.4468
540 | feeder2_line142 | 3 | 354.6 | 98.3143 | 98.3083 | 27.7254 | 27.7237
540 | feeder2_line143 | 1 | 99 | 8.5693e-07 | 1.7413e-06 | 8.6558e-07 | 1.7589e-06
540 | feeder2_line143 | 2 | 99 | 1.0494 | 1.0494 | 1.06 | 1.06
540 | feeder2_line143 | 3 | 99 | 8.5298e-07 | 1.7337e-06 | 8.616e-07 | 1.7512e-06
540 | feeder2_line144 | 1 | 354.6 | 96.0581 | 96.06 | 27.0892 | 27.0897
540 | feeder2_line144 | 2 | 354.6 | 97.9499 | 97.9541 | 27.6226 | 27.6238
540 | feeder2_line144 | 3 | 354.6 | 98.3141 | 98.3083 | 27.7253 | 27.7237
540 | feeder2_line145 | 1 | 99 | 2.4968e-08 | 4.883e-07 | 2.5221e-08 | 4.9323e-07
540 | feeder2_line145 | 2 | 99 | 1.0404 | 1.0404 | 1.0509 | 1.0509
540 | feeder2_line145 | 3 | 99 | 2.5161e-08 | 4.8615e-07 | 2.5416e-08 | 4.9106e-07
540 | feeder2_line146 | 1 | 354.6 | 96.058 | 96.06 | 27.0891 | 27.0897
540 | feeder2_line146 | 2 | 354.6 | 98.5694 | 98.5738 | 27.7974 | 27.7986
540 | feeder2_line146 | 3 | 354.6 | 98.314 | 98.3083 | 27.7253 | 27.7237
540 | feeder2_line147 | 1 | 99 | 0.38709 | 0.3871 | 0.391 | 0.39101
540 | feeder2_line147 | 2 | 99 | 1.1538e-06 | 2.2416e-06 | 1.1655e-06 | 2.2643e-06
540 | feeder2_line147 | 3 | 99 | 1.1543e-06 | 2.2425e-06 | 1.166e-06 | 2.2652e-06
540 | feeder2_line148 | 1 | 99 | 0.084221 | 0.084223 | 0.085071 | 0.085074
540 | feeder2_line148 | 2 | 99 | 6.0216e-07 | 1.502e-06 | 6.0824e-07 | 1.5172e-06
540 | feeder2_line148 | 3 | 99 | 6.0232e-07 | 1.5027e-06 | 6.084e-07 | 1.5178e-06
540 | feeder2_line149 | 1 | 354.6 | 96.5283 | 96.5301 | 27.2217 | 27.2223
540 | feeder2_line149 | 2 | 354.6 | 98.5696 | 98.5738 | 27.7974 | 27.7986
540 | feeder2_line149 | 3 | 354.6 | 98.3141 | 98.3083 | 27.7254 | 27.7237
540 | feeder2_line150 | 1 | 354.6 | 96.5284 | 96.5301 | 27.2218 | 27.2223
540 | feeder2_line150 | 2 | 354.6 | 99.0001 | 99.0041 | 27.9188 | 27.92
540 | feeder2_line150 | 3 | 354.6 | 98.3142 | 98.3083 | 27.7254 | 27.7237
540 | feeder2_line151 | 1 | 99 | 9.8531e-06 | 1.7931e-06 | 9.9527e-06 | 1.8112e-06
540 | feeder2_line151 | 2 | 99 | 0.43038 | 0.43039 | 0.43472 | 0.43474
540 | feeder2_line151 | 3 | 99 | 9.7922e-06 | 1.7853e-06 | 9.8911e-06 | 1.8033e-06
540 | feeder2_line152 | 1 | 354.6 | 7.5847e-12 | 1.1949e-06 | 2.1389e-12 | 3.3698e-07
540 | feeder2_line152 | 2 | 354.6 | 2.2401e-11 | 1.1898e-06 | 6.3172e-12 | 3.3552e-07
540 | feeder2_line152 | 3 | 354.6 | 0.076641 | 0.076637 | 0.021613 | 0.021612
540 | feeder2_line153 | 1 | 99 | 2.4102 | 2.4102 | 2.4346 | 2.4345
540 | feeder2_line153 | 2 | 99 | 5.0544e-08 | 5.9516e-07 | 5.1055e-08 | 6.0118e-07
540 | feeder2_line153 | 3 | 99 | 5.0372e-08 | 5.954e-07 | 5.0881e-08 | 6.0142e-07
540 | feeder2_line154 | 1 | 99 | 5.8027e-07 | 8.8983e-07 | 5.8613e-07 | 8.9882e-07
540 | feeder2_line154 | 2 | 99 | 5.7749e-07 | 8.8563e-07 | 5.8333e-07 | 8.9458e-07
540 | feeder2_line154 | 3 | 99 | 0.88411 | 0.88409 | 0.89304 | 0.89302
540 | feeder2_line155 | 1 | 99 | 98.2315 | 98.2333 | 99.2237 | 99.2256
540 | feeder2_line155 | 2 | 99 | 99 | 99.0041 | 100 | 100.0042
540 | feeder2_line155 | 3 | 99 | 98.9032 | 98.8973 | 99.9022 | 99.8963
540 | feeder2_line156 | 1 | 99 | 6.05e-07 | 1.1708e-06 | 6.1111e-07 | 1.1827e-06
540 | feeder2_line156 | 2 | 99 | 0.34109 | 0.34109 | 0.34454 | 0.34454
540 | feeder2_line156 | 3 | 99 | 6.0265e-07 | 1.1658e-06 | 6.0873e-07 | 1.1775e-06
540 | feeder2_line157 | 1 | 99 | 2.5e-08 | 2.542e-07 | 2.5253e-08 | 2.5677e-07
540 | feeder2_line157 | 2 | 99 | 0.089451 | 0.089455 | 0.090355 | 0.090358
540 | feeder2_line157 | 3 | 99 | 2.5176e-08 | 2.5308e-07 | 2.543e-08 | 2.5564e-07
570 | feeder2_line1 | 1 | 354.6 | 61.4636 | 61.4603 | 17.3332 | 17.3323
570 | feeder2_line1 | 2 | 354.6 | 53.921 | 53.9273 | 15.2061 | 15.2079
570 | feeder2_line1 | 3 | 354.6 | 44.2543 | 44.2535 | 12.4801 | 12.4798
570 | feeder2_line2 | 1 | 354.6 | 61.6217 | 61.6182 | 17.3778 | 17.3768
570 | feeder2_line2 | 2 | 354.6 | 53.9212 | 53.9273 | 15.2062 | 15.2079
570 | feeder2_line2 | 3 | 354.6 | 44.2545 | 44.2535 | 12.4801 | 12.4798
570 | feeder2_line3 | 1 | 80.1 | 1.3928 | 1.3929 | 1.7389 | 1.7389
570 | feeder2_line3 | 2 | 80.1 | 5.6999e-07 | 1.0533e-06 | 7.1159e-07 | 1.315e-06
570 | feeder2_line3 | 3 | 80.1 | 5.7029e-07 | 1.0539e-06 | 7.1197e-07 | 1.3157e-06
570 | feeder2_line4 | 1 | 354.6 | 61.6218 | 61.6182 | 17.3778 | 17.3768
570 | feeder2_line4 | 2 | 354.6 | 53.4472 | 53.4533 | 15.0725 | 15.0743
570 | feeder2_line4 | 3 | 354.6 | 44.2546 | 44.2535 | 12.4801 | 12.4798
570 | feeder2_line5 | 1 | 80.1 | 5.7161e-07 | 9.974e-07 | 7.1363e-07 | 1.2452e-06
570 | feeder2_line5 | 2 | 80.1 | 1.4025 | 1.4026 | 1.751 | 1.751
570 | feeder2_line5 | 3 | 80.1 | 5.7029e-07 | 9.9511e-07 | 7.1197e-07 | 1.2423e-06
570 | feeder2_line6 | 1 | 80.1 | 5.7168e-07 | 1.1735e-06 | 7.1371e-07 | 1.465e-06
570 | feeder2_line6 | 2 | 80.1 | 5.6996e-07 | 1.17e-06 | 7.1156e-07 | 1.4606e-06
570 | feeder2_line6 | 3 | 80.1 | 0.08563 | 0.085632 | 0.1069 | 0.10691
570 | feeder2_line7 | 1 | 354.6 | 61.6219 | 61.6182 | 17.3779 | 17.3768
570 | feeder2_line7 | 2 | 354.6 | 53.4472 | 53.4533 | 15.0725 | 15.0743
570 | feeder2_line7 | 3 | 354.6 | 44.3202 | 44.3191 | 12.4987 | 12.4983
570 | feeder2_line8 | 1 | 80.1 | 19.3773 | 19.3773 | 24.1914 | 24.1914
570 | feeder2_line8 | 2 | 80.1 | 5.6986e-07 | 1.128e-06 | 7.1144e-07 | 1.4082e-06
570 | feeder2_line8 | 3 | 80.1 | 5.7021e-07 | 1.1286e-06 | 7.1187e-07 | 1.409e-06
570 | feeder2_line9 | 1 | 354.6 | 78.945 | 78.9412 | 22.2631 | 22.262
570 | feeder2_line9 | 2 | 354.6 | 53.4472 | 53.4533 | 15.0725 | 15.0743
570 | feeder2_line9 | 3 | 354.6 | 44.3202 | 44.3191 | 12.4987 | 12.4983
570 | feeder2_line10 | 1 | 80.1 | 8.4544e-07 | 1.4945e-06 | 1.0555e-06 | 1.8658e-06
570 | feeder2_line10 | 2 | 80.1 | 19.2675 | 19.2673 | 24.0543 | 24.0541
570 | feeder2_line10 | 3 | 80.1 | 8.4285e-07 | 1.4902e-06 | 1.0522e-06 | 1.8604e-06
570 | feeder2_line11 | 1 | 354.6 | 78.945 | 78.9412 | 22.2631 | 22.262
570 | feeder2_line11 | 2 | 354.6 | 65.8374 | 65.8442 | 18.5667 | 18.5686
570 | feeder2_line11 | 3 | 354.6 | 44.3203 | 44.3191 | 12.4987 | 12.4983
570 | feeder2_line12 | 1 | 80.1 | 5.4732e-07 | 9.9153e-07 | 6.833e-07 | 1.2379e-06
570 | feeder2_line12 | 2 | 80.1 | 5.45e-07 | 9.8797e-07 | 6.804e-07 | 1.2334e-06
570 | feeder2_line12 | 3 | 80.1 | 10.1047 | 10.1048 | 12.6151 | 12.6152
570 | feeder2_line13 | 1 | 354.6 | 78.945 | 78.9412 | 22.2631 | 22.262
570 | feeder2_line13 | 2 | 354.6 | 65.8374 | 65.8442 | 18.5667 | 18.5686
570 | feeder2_line13 | 3 | 354.6 | 52.0154 | 52.014 | 14.6688 | 14.6683
570 | feeder2_line14 | 1 | 80.1 | 1.6277 | 1.6277 | 2.0321 | 2.0321
570 | feeder2_line14 | 2 | 80.1 | 2.9742e-07 | 6.4425e-07 | 3.7131e-07 | 8.0431e-07
570 | feeder2_line14 | 3 | 80.1 | 2.9753e-07 | 6.4455e-07 | 3.7145e-07 | 8.0469e-07
570 | feeder2_line15 | 1 | 354.6 | 80.372 | 80.3681 | 22.6655 | 22.6645
570 | feeder2_line15 | 2 | 354.6 | 65.8374 | 65.8442 | 18.5667 | 18.5686
570 | feeder2_line15 | 3 | 354.6 | 52.0155 | 52.014 | 14.6688 | 14.6683
570 | feeder2_line16 | 1 | 80.1 | 5.7223e-07 | 1.0309e-06 | 7.144e-07 | 1.287e-06
570 | feeder2_line16 | 2 | 80.1 | 0.87232 | 0.87233 | 1.089 | 1.089
570 | feeder2_line16 | 3 | 80.1 | 5.7019e-07 | 1.0272e-06 | 7.1185e-07 | 1.2825e-06
570 | feeder2_line17 | 1 | 354.6 | 80.372 | 80.3681 | 22.6655 | 22.6645
570 | feeder2_line17 | 2 | 354.6 | 65.7479 | 65.7547 | 18.5414 | 18.5433
570 | feeder2_line17 | 3 | 354.6 | 52.0155 | 52.014 | 14.6688 | 14.6683
570 | feeder2_line18 | 1 | 80.1 | 5.4826e-07 | 7.3872e-07 | 6.8447e-07 | 9.2225e-07
570 | feeder2_line18 | 2 | 80.1 | 5.4506e-07 | 7.3509e-07 | 6.8048e-07 | 9.1772e-07
570 | feeder2_line18 | 3 | 80.1 | 2.2087 | 2.2087 | 2.7574 | 2.7574
570 | feeder2_line19 | 1 | 354.6 | 80.372 | 80.3681 | 22.6655 | 22.6645
570 | feeder2_line19 | 2 | 354.6 | 65.7479 | 65.7547 | 18.5414 | 18.5433
570 | feeder2_line19 | 3 | 354.6 | 53.0625 | 53.0609 | 14.9641 | 14.9636
570 | feeder2_line20 | 1 | 99 | 5.4851e-07 | 8.8605e-07 | 5.5405e-07 | 8.95e-07
570 | feeder2_line20 | 2 | 99 | 5.4508e-07 | 8.8137e-07 | 5.5058e-07 | 8.9028e-07
570 | feeder2_line20 | 3 | 99 | 5.0723 | 5.0723 | 5.1235 | 5.1235
570 | feeder2_line21 | 1 | 354.6 | 80.3721 | 80.3681 | 22.6656 | 22.6645
570 | feeder2_line21 | 2 | 354.6 | 65.748 | 65.7547 | 18.5415 | 18.5433
570 | feeder2_line21 | 3 | 354.6 | 57.3416 | 57.3397 | 16.1708 | 16.1703
570 | feeder2_line22 | 1 | 99 | 5.7325e-07 | 1.016e-06 | 5.7904e-07 | 1.0263e-06
570 | feeder2_line22 | 2 | 99 | 1.5411 | 1.5411 | 1.5566 | 1.5566
570 | feeder2_line22 | 3 | 99 | 5.7013e-07 | 1.0105e-06 | 5.7589e-07 | 1.0208e-06
570 | feeder2_line23 | 1 | 99 | 5.7324e-07 | 9.5106e-07 | 5.7903e-07 | 9.6066e-07
570 | feeder2_line23 | 2 | 99 | 5.7004e-07 | 9.4582e-07 | 5.758e-07 | 9.5538e-07
570 | feeder2_line23 | 3 | 99 | 7.5094 | 7.5095 | 7.5853 | 7.5853
570 | feeder2_line24 | 1 | 354.6 | 80.3722 | 80.3681 | 22.6656 | 22.6645
570 | feeder2_line24 | 2 | 354.6 | 66.9169 | 66.9236 | 18.8711 | 18.873
570 | feeder2_line24 | 3 | 354.6 | 63.8388 | 63.8368 | 18.003 | 18.0025
570 | feeder2_line25 | 1 | 99 | 1.5333 | 1.5333 | 1.5488 | 1.5488
570 | feeder2_line25 | 2 | 99 | 4.9979e-08 | 6.8766e-07 | 5.0483e-08 | 6.9461e-07
570 | feeder2_line25 | 3 | 99 | 4.9893e-08 | 6.8779e-07 | 5.0397e-08 | 6.9474e-07
570 | feeder2_line26 | 1 | 99 | 0.084988 | 0.084986 | 0.085847 | 0.085845
570 | feeder2_line26 | 2 | 99 | 5.4508e-07 | 8.5197e-07 | 5.5059e-07 | 8.6058e-07
570 | feeder2_line26 | 3 | 99 | 5.4524e-07 | 8.5214e-07 | 5.5075e-07 | 8.6075e-07
570 | feeder2_line27 | 1 | 354.6 | 81.8819 | 81.8778 | 23.0913 | 23.0902
570 | feeder2_line27 | 2 | 354.6 | 66.9169 | 66.9236 | 18.8711 | 18.873
570 | feeder2_line27 | 3 | 354.6 | 63.8388 | 63.8368 | 18.0031 | 18.0025
570 | feeder2_line28 | 1 | 99 | 2.5502e-06 | 7.1189e-07 | 2.576e-06 | 7.1908e-07
570 | feeder2_line28 | 2 | 99 | 1.9691 | 1.9691 | 1.989 | 1.989
570 | feeder2_line28 | 3 | 99 | 2.5269e-06 | 7.0746e-07 | 2.5524e-06 | 7.1461e-07
570 | feeder2_line29 | 1 | 354.6 | 81.8819 | 81.8778 | 23.0913 | 23.0902
570 | feeder2_line29 | 2 | 354.6 | 66.8064 | 66.8132 | 18.8399 | 18.8419
570 | feeder2_line29 | 3 | 354.6 | 63.8388 | 63.8368 | 18.0031 | 18.0025
570 | feeder2_line30 | 1 | 266.4 | 3.2922 | 3.2918 | 1.2358 | 1.2357
570 | feeder2_line30 | 2 | 266.4 | 3.7737 | 3.7737 | 1.4165 | 1.4166
570 | feeder2_line30 | 3 | 266.4 | 11.8765 | 11.8763 | 4.4582 | 4.4581
570 | feeder2_line31 | 1 | 354.6 | 84.8814 | 84.8767 | 23.9372 | 23.9359
570 | feeder2_line31 | 2 | 354.6 | 68.0041 | 68.0105 | 19.1777 | 19.1795
570 | feeder2_line31 | 3 | 354.6 | 74.154 | 74.1513 | 20.912 | 20.9113
570 | feeder2_line32 | 1 | 354.6 | 84.8814 | 84.8767 | 23.9372 | 23.9359
570 | feeder2_line32 | 2 | 354.6 | 68.0706 | 68.077 | 19.1965 | 19.1983
570 | feeder2_line32 | 3 | 354.6 | 74.154 | 74.1513 | 20.912 | 20.9113
570 | feeder2_line33 | 1 | 99 | 4.9043e-08 | 6.8781e-07 | 4.9538e-08 | 6.9475e-07
570 | feeder2_line33 | 2 | 99 | 0.077702 | 0.077707 | 0.078486 | 0.078492
570 | feeder2_line33 | 3 | 99 | 4.9998e-08 | 6.8285e-07 | 5.0503e-08 | 6.8974e-07
570 | feeder2_line34 | 1 | 354.6 | 84.8814 | 84.8767 | 23.9372 | 23.9359
570 | feeder2_line34 | 2 | 354.6 | 68.0706 | 68.077 | 19.1965 | 19.1983
570 | feeder2_line34 | 3 | 354.6 | 74.7171 | 74.7144 | 21.0708 | 21.07
570 | feeder2_line35 | 1 | 99 | 2.997e-07 | 7.6184e-07 | 3.0272e-07 | 7.6953e-07
570 | feeder2_line35 | 2 | 99 | 2.9764e-07 | 7.5572e-07 | 3.0064e-07 | 7.6335e-07
570 | feeder2_line35 | 3 | 99 | 0.60718 | 0.60718 | 0.61332 | 0.61331
570 | feeder2_line36 | 1 | 354.6 | 84.9079 | 84.9032 | 23.9447 | 23.9434
570 | feeder2_line36 | 2 | 354.6 | 68.0706 | 68.077 | 19.1964 | 19.1983
570 | feeder2_line36 | 3 | 354.6 | 74.717 | 74.7144 | 21.0708 | 21.07
570 | feeder2_line37 | 1 | 99 | 0.02796 | 0.027861 | 0.028242 | 0.028142
570 | feeder2_line37 | 2 | 99 | 2.9765e-07 | 8.362e-07 | 3.0066e-07 | 8.4464e-07
570 | feeder2_line37 | 3 | 99 | 2.9785e-07 | 8.3688e-07 | 3.0086e-07 | 8.4533e-07
570 | feeder2_line38 | 1 | 99 | 3.2402e-07 | 7.7733e-07 | 3.2729e-07 | 7.8518e-07
570 | feeder2_line38 | 2 | 99 | 0.077743 | 0.077748 | 0.078529 | 0.078533
570 | feeder2_line38 | 3 | 99 | 3.2267e-07 | 7.7185e-07 | 3.2593e-07 | 7.7965e-07
570 | feeder2_line39 | 1 | 266.4 | 3.2922 | 3.2918 | 1.2358 | 1.2357
570 | feeder2_line39 | 2 | 266.4 | 3.7137 | 3.7137 | 1.394 | 1.394
570 | feeder2_line39 | 3 | 266.4 | 11.8765 | 11.8763 | 4.4582 | 4.4581
570 | feeder2_line40 | 1 | 354.6 | 86.348 | 86.3432 | 24.3508 | 24.3495
570 | feeder2_line40 | 2 | 354.6 | 68.0706 | 68.077 | 19.1965 | 19.1983
570 | feeder2_line40 | 3 | 354.6 | 74.7171 | 74.7144 | 21.0708 | 21.07
570 | feeder2_line41 | 1 | 99 | 1.5303 | 1.5303 | 1.5457 | 1.5457
570 | feeder2_line41 | 2 | 99 | 5.0189e-08 | 7.307e-07 | 5.0696e-08 | 7.3808e-07
570 | feeder2_line41 | 3 | 99 | 5.0019e-08 | 7.3133e-07 | 5.0524e-08 | 7.3872e-07
570 | feeder2_line42 | 1 | 99 | 2.9949e-07 | 7.503e-07 | 3.0251e-07 | 7.5788e-07
570 | feeder2_line42 | 2 | 99 | 2.9759e-07 | 7.4474e-07 | 3.006e-07 | 7.5226e-07
570 | feeder2_line42 | 3 | 99 | 1.8169 | 1.8169 | 1.8352 | 1.8352
570 | feeder2_line43 | 1 | 266.4 | 3.2921 | 3.2918 | 1.2358 | 1.2357
570 | feeder2_line43 | 2 | 266.4 | 3.7137 | 3.7137 | 1.394 | 1.394
570 | feeder2_line43 | 3 | 266.4 | 10.2524 | 10.2523 | 3.8485 | 3.8485
570 | feeder2_line44 | 1 | 354.6 | 86.3481 | 86.3432 | 24.3508 | 24.3495
570 | feeder2_line44 | 2 | 354.6 | 68.0707 | 68.077 | 19.1965 | 19.1983
570 | feeder2_line44 | 3 | 354.6 | 79.4347 | 79.432 | 22.4012 | 22.4004
570 | feeder2_line45 | 1 | 99 | 4.9013e-08 | 5.8121e-07 | 4.9508e-08 | 5.8708e-07
570 | feeder2_line45 | 2 | 99 | 5.0202e-08 | 5.7625e-07 | 5.0709e-08 | 5.8207e-07
570 | feeder2_line45 | 3 | 99 | 5.0765 | 5.0765 | 5.1278 | 5.1278
570 | feeder2_line46 | 1 | 99 | 5.7445e-07 | 1.3602e-06 | 5.8026e-07 | 1.3739e-06
570 | feeder2_line46 | 2 | 99 | 5.7015e-07 | 1.3501e-06 | 5.759e-07 | 1.3637e-06
570 | feeder2_line46 | 3 | 99 | 0.072822 | 0.072827 | 0.073558 | 0.073563
570 | feeder2_line47 | 1 | 266.4 | 3.2921 | 3.2918 | 1.2358 | 1.2357
570 | feeder2_line47 | 2 | 266.4 | 3.7138 | 3.7137 | 1.3941 | 1.394
570 | feeder2_line47 | 3 | 266.4 | 10.1797 | 10.1796 | 3.8212 | 3.8212
570 | feeder2_line48 | 1 | 99 | 0.35299 | 0.35299 | 0.35655 | 0.35655
570 | feeder2_line48 | 2 | 99 | 5.0089e-08 | 7.269e-07 | 5.0595e-08 | 7.3425e-07
570 | feeder2_line48 | 3 | 99 | 4.9996e-08 | 7.2704e-07 | 5.0501e-08 | 7.3439e-07
570 | feeder2_line49 | 1 | 266.4 | 2.9399 | 2.9396 | 1.1036 | 1.1035
570 | feeder2_line49 | 2 | 266.4 | 3.7138 | 3.7137 | 1.3941 | 1.394
570 | feeder2_line49 | 3 | 266.4 | 10.1797 | 10.1796 | 3.8212 | 3.8212
570 | feeder2_line50 | 1 | 99 | 5.7445e-07 | 1.2378e-06 | 5.8025e-07 | 1.2503e-06
570 | feeder2_line50 | 2 | 99 | 0.085747 | 0.08577 | 0.086613 | 0.086637
570 | feeder2_line50 | 3 | 99 | 5.7023e-07 | 1.2289e-06 | 5.7599e-07 | 1.2413e-06
570 | feeder2_line51 | 1 | 99 | 0.80779 | 0.80769 | 0.81595 | 0.81585
570 | feeder2_line51 | 2 | 99 | 5.7014e-07 | 1.3338e-06 | 5.7589e-07 | 1.3473e-06
570 | feeder2_line51 | 3 | 99 | 5.7023e-07 | 1.3341e-06 | 5.7599e-07 | 1.3475e-06
570 | feeder2_line52 | 1 | 266.4 | 2.1364 | 2.1364 | 0.80197 | 0.80194
570 | feeder2_line52 | 2 | 266.4 | 3.6475 | 3.6475 | 1.3692 | 1.3692
570 | feeder2_line52 | 3 | 266.4 | 10.1796 | 10.1796 | 3.8212 | 3.8212
570 | feeder2_line53 | 1 | 99 | 5.4993e-07 | 7.5547e-07 | 5.5548e-07 | 7.631e-07
570 | feeder2_line53 | 2 | 99 | 3.6476 | 3.6475 | 3.6844 | 3.6844
570 | feeder2_line53 | 3 | 99 | 5.4523e-07 | 7.4998e-07 | 5.5074e-07 | 7.5756e-07
570 | feeder2_line54 | 1 | 266.4 | 2.1363 | 2.1364 | 0.80191 | 0.80194
570 | feeder2_line54 | 2 | 266.4 | 8.5065e-05 | 4.6006e-06 | 3.1931e-05 | 1.727e-06
570 | feeder2_line54 | 3 | 266.4 | 10.1794 | 10.1796 | 3.8211 | 3.8212
570 | feeder2_line55 | 1 | 99 | 0.045331 | 0.045329 | 0.045789 | 0.045787
570 | feeder2_line55 | 2 | 99 | 5.0263e-08 | 7.2601e-07 | 5.0771e-08 | 7.3335e-07
570 | feeder2_line55 | 3 | 99 | 5.0042e-08 | 7.2696e-07 | 5.0548e-08 | 7.3431e-07
570 | feeder2_line56 | 1 | 354.6 | 86.3913 | 86.3864 | 24.363 | 24.3617
570 | feeder2_line56 | 2 | 354.6 | 68.0707 | 68.077 | 19.1965 | 19.1983
570 | feeder2_line56 | 3 | 354.6 | 79.4348 | 79.432 | 22.4012 | 22.4004
570 | feeder2_line57 | 1 | 99 | 7.3545e-07 | 1.5474e-06 | 7.4288e-07 | 1.5631e-06
570 | feeder2_line57 | 2 | 99 | 7.5121e-07 | 1.536e-06 | 7.5879e-07 | 1.5515e-06
570 | feeder2_line57 | 3 | 99 | 10.1795 | 10.1796 | 10.2823 | 10.2824
570 | feeder2_line58 | 1 | 266.4 | 2.1364 | 2.1364 | 0.80193 | 0.80194
570 | feeder2_line58 | 2 | 266.4 | 1.8848e-05 | 2.6711e-06 | 7.075e-06 | 1.0027e-06
570 | feeder2_line58 | 3 | 266.4 | 1.8819e-05 | 2.6713e-06 | 7.0644e-06 | 1.0027e-06
570 | feeder2_line59 | 1 | 99 | 4.9031e-08 | 5.379e-07 | 4.9526e-08 | 5.4333e-07
570 | feeder2_line59 | 2 | 99 | 5.0089e-08 | 5.3392e-07 | 5.0595e-08 | 5.3931e-07
570 | feeder2_line59 | 3 | 99 | 0.081679 | 0.081677 | 0.082504 | 0.082502
570 | feeder2_line60 | 1 | 99 | 2.9947e-07 | 8.1293e-07 | 3.025e-07 | 8.2114e-07
570 | feeder2_line60 | 2 | 99 | 2.9758e-07 | 8.0691e-07 | 3.0059e-07 | 8.1506e-07
570 | feeder2_line60 | 3 | 99 | 10.0981 | 10.0981 | 10.2001 | 10.2001
570 | feeder2_line61 | 1 | 266.4 | 0.49313 | 0.49331 | 0.18511 | 0.18518
570 | feeder2_line61 | 2 | 266.4 | 3.6415 | 3.6417 | 1.3669 | 1.367
570 | feeder2_line61 | 3 | 266.4 | 3.7038 | 3.704 | 1.3903 | 1.3904
570 | feeder2_line62 | 1 | 354.6 | 86.8554 | 86.8507 | 24.4939 | 24.4926
570 | feeder2_line62 | 2 | 354.6 | 69.4898 | 69.4964 | 19.5967 | 19.5985
570 | feeder2_line62 | 3 | 354.6 | 82.5411 | 82.5384 | 23.2772 | 23.2765
570 | feeder2_line63 | 1 | 99 | 0.41343 | 0.41342 | 0.4176 | 0.4176
570 | feeder2_line63 | 2 | 99 | 5.7014e-07 | 1.2132e-06 | 5.759e-07 | 1.2254e-06
570 | feeder2_line63 | 3 | 99 | 5.702e-07 | 1.2133e-06 | 5.7596e-07 | 1.2256e-06
570 | feeder2_line64 | 1 | 99 | 1.7274 | 1.7274 | 1.7449 | 1.7449
570 | feeder2_line64 | 2 | 99 | 5.0794e-12 | 3.1959e-07 | 5.1307e-12 | 3.2282e-07
570 | feeder2_line64 | 3 | 99 | 5.8546e-12 | 3.1961e-07 | 5.9138e-12 | 3.2284e-07
570 | feeder2_line65 | 1 | 99 | 4.8975e-08 | 6.4421e-07 | 4.9469e-08 | 6.5072e-07
570 | feeder2_line65 | 2 | 99 | 1.4021 | 1.4021 | 1.4163 | 1.4163
570 | feeder2_line65 | 3 | 99 | 5.0067e-08 | 6.3892e-07 | 5.0573e-08 | 6.4538e-07
570 | feeder2_line66 | 1 | 354.6 | 86.8554 | 86.8507 | 24.4939 | 24.4926
570 | feeder2_line66 | 2 | 354.6 | 69.6299 | 69.6367 | 19.6362 | 19.6381
570 | feeder2_line66 | 3 | 354.6 | 82.541 | 82.5384 | 23.2772 | 23.2765
570 | feeder2_line67 | 1 | 99 | 2.4491e-08 | 3.6401e-07 | 2.4738e-08 | 3.6768e-07
570 | feeder2_line67 | 2 | 99 | 2.515e-08 | 3.6048e-07 | 2.5404e-08 | 3.6413e-07
570 | feeder2_line67 | 3 | 99 | 1.5393 | 1.5393 | 1.5549 | 1.5549
570 | feeder2_line68 | 1 | 266.4 | 0.49318 | 0.49331 | 0.18513 | 0.18518
570 | feeder2_line68 | 2 | 266.4 | 3.6416 | 3.6417 | 1.3669 | 1.367
570 | feeder2_line68 | 3 | 266.4 | 2.2316 | 2.2317 | 0.83768 | 0.83772
570 | feeder2_line69 | 1 | 99 | 2.785 | 2.7849 | 2.8131 | 2.813
570 | feeder2_line69 | 2 | 99 | 2.5243e-06 | 6.6203e-07 | 2.5498e-06 | 6.6872e-07
570 | feeder2_line69 | 3 | 99 | 2.5323e-06 | 6.6338e-07 | 2.5579e-06 | 6.7008e-07
570 | feeder2_line70 | 1 | 354.6 | 87.661 | 87.6564 | 24.7211 | 24.7198
570 | feeder2_line70 | 2 | 354.6 | 69.6298 | 69.6367 | 19.6362 | 19.6381
570 | feeder2_line70 | 3 | 354.6 | 82.5409 | 82.5384 | 23.2772 | 23.2765
570 | feeder2_line71 | 1 | 99 | 4.8967e-08 | 7.1898e-07 | 4.9462e-08 | 7.2624e-07
570 | feeder2_line71 | 2 | 99 | 2.4586 | 2.4585 | 2.4834 | 2.4834
570 | feeder2_line71 | 3 | 99 | 5.0077e-08 | 7.1299e-07 | 5.0583e-08 | 7.2019e-07
570 | feeder2_line72 | 1 | 354.6 | 87.6611 | 87.6564 | 24.7211 | 24.7198
570 | feeder2_line72 | 2 | 354.6 | 69.8485 | 69.8554 | 19.6978 | 19.6998
570 | feeder2_line72 | 3 | 354.6 | 82.541 | 82.5384 | 23.2772 | 23.2765
570 | feeder2_line73 | 1 | 99 | 6.0042e-07 | 1.5411e-06 | 6.0648e-07 | 1.5567e-06
570 | feeder2_line73 | 2 | 99 | 0.077728 | 0.077735 | 0.078513 | 0.078521
570 | feeder2_line73 | 3 | 99 | 5.9621e-07 | 1.5286e-06 | 6.0223e-07 | 1.544e-06
570 | feeder2_line74 | 1 | 99 | 4.8974e-08 | 4.5964e-07 | 4.9468e-08 | 4.6428e-07
570 | feeder2_line74 | 2 | 99 | 2.2335 | 2.2335 | 2.2561 | 2.2561
570 | feeder2_line74 | 3 | 99 | 5.0057e-08 | 4.559e-07 | 5.0563e-08 | 4.6051e-07
570 | feeder2_line75 | 1 | 266.4 | 0.49328 | 0.49331 | 0.18516 | 0.18518
570 | feeder2_line75 | 2 | 266.4 | 1.4742 | 1.4742 | 0.55338 | 0.55339
570 | feeder2_line75 | 3 | 266.4 | 2.2317 | 2.2317 | 0.83772 | 0.83772
570 | feeder2_line76 | 1 | 99 | 0.49331 | 0.49331 | 0.49829 | 0.49829
570 | feeder2_line76 | 2 | 99 | 8.4281e-07 | 1.5743e-06 | 8.5132e-07 | 1.5902e-06
570 | feeder2_line76 | 3 | 99 | 8.4426e-07 | 1.5768e-06 | 8.5279e-07 | 1.5927e-06
570 | feeder2_line77 | 1 | 99 | 2.4492e-08 | 5.7762e-07 | 2.474e-08 | 5.8345e-07
570 | feeder2_line77 | 2 | 99 | 2.5151e-08 | 5.72e-07 | 2.5405e-08 | 5.7778e-07
570 | feeder2_line77 | 3 | 99 | 2.2317 | 2.2317 | 2.2543 | 2.2542
570 | feeder2_line78 | 1 | 266.4 | 1.0427e-11 | 9.5726e-07 | 3.914e-12 | 3.5933e-07
570 | feeder2_line78 | 2 | 266.4 | 1.4742 | 1.4742 | 0.5534 | 0.55339
570 | feeder2_line78 | 3 | 266.4 | 4.187e-12 | 9.504e-07 | 1.5717e-12 | 3.5676e-07
570 | feeder2_line79 | 1 | 354.6 | 4.5436 | 4.5433 | 1.2813 | 1.2812
570 | feeder2_line79 | 2 | 354.6 | 30.0673 | 30.0672 | 8.4792 | 8.4792
570 | feeder2_line79 | 3 | 354.6 | 5.369 | 5.3686 | 1.5141 | 1.514
570 | feeder2_line80 | 1 | 354.6 | 90.2828 | 90.2776 | 25.4605 | 25.459
570 | feeder2_line80 | 2 | 354.6 | 93.2132 | 93.2199 | 26.2869 | 26.2888
570 | feeder2_line80 | 3 | 354.6 | 86.1067 | 86.1035 | 24.2828 | 24.2819
570 | feeder2_line81 | 1 | 354.6 | 90.2828 | 90.2776 | 25.4605 | 25.459
570 | feeder2_line81 | 2 | 354.6 | 93.2131 | 93.2199 | 26.2868 | 26.2888
570 | feeder2_line81 | 3 | 354.6 | 86.1747 | 86.1715 | 24.3019 | 24.301
570 | feeder2_line82 | 1 | 354.6 | 2.4459e-11 | 7.3741e-07 | 6.8976e-12 | 2.0796e-07
570 | feeder2_line82 | 2 | 354.6 | 3.2451e-11 | 7.3003e-07 | 9.1514e-12 | 2.0587e-07
570 | feeder2_line82 | 3 | 354.6 | 0.069894 | 0.069891 | 0.019711 | 0.01971
570 | feeder2_line83 | 1 | 354.6 | 90.283 | 90.2776 | 25.4605 | 25.459
570 | feeder2_line83 | 2 | 354.6 | 93.3014 | 93.308 | 26.3117 | 26.3136
570 | feeder2_line83 | 3 | 354.6 | 86.1748 | 86.1715 | 24.302 | 24.301
570 | feeder2_line84 | 1 | 354.6 | 9.5898e-12 | 1.3034e-06 | 2.7044e-12 | 3.6758e-07
570 | feeder2_line84 | 2 | 354.6 | 0.089859 | 0.089884 | 0.025341 | 0.025348
570 | feeder2_line84 | 3 | 354.6 | 1.0869e-11 | 1.2932e-06 | 3.0652e-12 | 3.6471e-07
570 | feeder2_line85 | 1 | 99 | 0.076541 | 0.076537 | 0.077314 | 0.07731
570 | feeder2_line85 | 2 | 99 | 5.0468e-08 | 4.6044e-07 | 5.0978e-08 | 4.6509e-07
570 | feeder2_line85 | 3 | 99 | 5.0125e-08 | 4.6151e-07 | 5.0631e-08 | 4.6618e-07
570 | feeder2_line86 | 1 | 354.6 | 90.3582 | 90.3528 | 25.4817 | 25.4802
570 | feeder2_line86 | 2 | 354.6 | 93.3015 | 93.308 | 26.3118 | 26.3136
570 | feeder2_line86 | 3 | 354.6 | 86.1749 | 86.1715 | 24.302 | 24.301
570 | feeder2_line87 | 1 | 354.6 | 90.3584 | 90.3528 | 25.4818 | 25.4802
570 | feeder2_line87 | 2 | 354.6 | 94.4817 | 94.4882 | 26.6446 | 26.6464
570 | feeder2_line87 | 3 | 354.6 | 87.0678 | 87.0641 | 24.5538 | 24.5528
570 | feeder2_line88 | 1 | 354.6 | 0.00011689 | 3.3807e-06 | 3.2965e-05 | 9.5339e-07
570 | feeder2_line88 | 2 | 354.6 | 1.6801 | 1.6801 | 0.47379 | 0.47381
570 | feeder2_line88 | 3 | 354.6 | 2.6179 | 2.6178 | 0.73826 | 0.73824
570 | feeder2_line89 | 1 | 354.6 | 90.3561 | 90.3528 | 25.4811 | 25.4802
570 | feeder2_line89 | 2 | 354.6 | 94.9377 | 94.9465 | 26.7732 | 26.7757
570 | feeder2_line89 | 3 | 354.6 | 87.0655 | 87.0641 | 24.5532 | 24.5528
570 | feeder2_line90 | 1 | 354.6 | 0.00073104 | 2.04e-06 | 0.00020616 | 5.7531e-07
570 | feeder2_line90 | 2 | 354.6 | 0.95245 | 0.95248 | 0.2686 | 0.26861
570 | feeder2_line90 | 3 | 354.6 | 0.0007211 | 2.0229e-06 | 0.00020336 | 5.7048e-07
570 | feeder2_line91 | 1 | 354.6 | 90.3561 | 90.3528 | 25.4811 | 25.4802
570 | feeder2_line91 | 2 | 354.6 | 94.9377 | 94.9465 | 26.7732 | 26.7757
570 | feeder2_line91 | 3 | 354.6 | 96.8688 | 96.8675 | 27.3178 | 27.3174
570 | feeder2_line92 | 1 | 354.6 | 5.4861e-12 | 1.0291e-06 | 1.5471e-12 | 2.9021e-07
570 | feeder2_line92 | 2 | 354.6 | 4.2152e-12 | 1.019e-06 | 1.1887e-12 | 2.8735e-07
570 | feeder2_line92 | 3 | 354.6 | 10.1396 | 10.1397 | 2.8594 | 2.8595
570 | feeder2_line93 | 1 | 99 | 2.4503e-08 | 3.437e-07 | 2.4751e-08 | 3.4717e-07
570 | feeder2_line93 | 2 | 99 | 0.089794 | 0.08982 | 0.090701 | 0.090728
570 | feeder2_line93 | 3 | 99 | 2.5084e-08 | 3.4072e-07 | 2.5337e-08 | 3.4416e-07
570 | feeder2_line94 | 1 | 354.6 | 2.4503e-06 | 1.6723e-06 | 6.91e-07 | 4.7162e-07
570 | feeder2_line94 | 2 | 354.6 | 0.89831 | 0.89834 | 0.25333 | 0.25334
570 | feeder2_line94 | 3 | 354.6 | 2.5083e-06 | 1.6591e-06 | 7.0735e-07 | 4.6789e-07
570 | feeder2_line95 | 1 | 99 | 3.5932e-06 | 2.6218e-06 | 3.6295e-06 | 2.6483e-06
570 | feeder2_line95 | 2 | 99 | 1.68 | 1.6801 | 1.697 | 1.6971
570 | feeder2_line95 | 3 | 99 | 3.5458e-06 | 2.5992e-06 | 3.5816e-06 | 2.6255e-06
570 | feeder2_line96 | 1 | 354.6 | 0.0001218 | 6.2492e-07 | 3.4347e-05 | 1.7623e-07
570 | feeder2_line96 | 2 | 354.6 | 0.00012023 | 6.1854e-07 | 3.3906e-05 | 1.7443e-07
570 | feeder2_line96 | 3 | 354.6 | 2.6178 | 2.6178 | 0.73825 | 0.73824
570 | feeder2_line97 | 1 | 354.6 | 90.9211 | 90.9175 | 25.6405 | 25.6394
570 | feeder2_line97 | 2 | 354.6 | 94.9378 | 94.9465 | 26.7732 | 26.7757
570 | feeder2_line97 | 3 | 354.6 | 96.869 | 96.8675 | 27.3178 | 27.3174
570 | feeder2_line98 | 1 | 354.6 | 0.58784 | 0.58611 | 0.16578 | 0.16529
570 | feeder2_line98 | 2 | 354.6 | 0.0016732 | 6.1772e-07 | 0.00047186 | 1.742e-07
570 | feeder2_line98 | 3 | 354.6 | 0.0017042 | 6.2308e-07 | 0.00048058 | 1.7571e-07
570 | feeder2_line99 | 1 | 99 | 2.45e-08 | 4.4931e-07 | 2.4747e-08 | 4.5385e-07
570 | feeder2_line99 | 2 | 99 | 2.5233e-08 | 4.4441e-07 | 2.5488e-08 | 4.489e-07
570 | feeder2_line99 | 3 | 99 | 2.6178 | 2.6178 | 2.6443 | 2.6442
570 | feeder2_line100 | 1 | 99 | 0.58615 | 0.58611 | 0.59207 | 0.59203
570 | feeder2_line100 | 2 | 99 | 2.5256e-08 | 6.1038e-07 | 2.5512e-08 | 6.1655e-07
570 | feeder2_line100 | 3 | 99 | 2.5089e-08 | 6.1173e-07 | 2.5342e-08 | 6.1791e-07
570 | feeder2_line101 | 1 | 354.6 | 0.90265 | 0.90251 | 0.25456 | 0.25451
570 | feeder2_line101 | 2 | 354.6 | 30.0673 | 30.0672 | 8.4792 | 8.4792
570 | feeder2_line101 | 3 | 354.6 | 5.369 | 5.3686 | 1.5141 | 1.514
570 | feeder2_line102 | 1 | 99 | 3.6713 | 3.6713 | 3.7084 | 3.7084
570 | feeder2_line102 | 2 | 99 | 2.3042e-06 | 8.7207e-07 | 2.3275e-06 | 8.8088e-07
570 | feeder2_line102 | 3 | 99 | 2.3297e-06 | 8.7455e-07 | 2.3533e-06 | 8.8338e-07
570 | feeder2_line103 | 1 | 99 | 5.5243e-07 | 8.0747e-07 | 5.5801e-07 | 8.1562e-07
570 | feeder2_line103 | 2 | 99 | 2.3721 | 2.3721 | 2.3961 | 2.396
570 | feeder2_line103 | 3 | 99 | 5.4682e-07 | 8.0048e-07 | 5.5235e-07 | 8.0856e-07
570 | feeder2_line104 | 1 | 354.6 | 0.90266 | 0.90251 | 0.25456 | 0.25451
570 | feeder2_line104 | 2 | 354.6 | 27.7144 | 27.7143 | 7.8157 | 7.8157
570 | feeder2_line104 | 3 | 354.6 | 5.369 | 5.3686 | 1.5141 | 1.514
570 | feeder2_line105 | 1 | 99 | 2.5666e-06 | 7.4301e-07 | 2.5925e-06 | 7.5051e-07
570 | feeder2_line105 | 2 | 99 | 2.5221e-06 | 7.3425e-07 | 2.5475e-06 | 7.4167e-07
570 | feeder2_line105 | 3 | 99 | 2.2077 | 2.2077 | 2.23 | 2.23
570 | feeder2_line106 | 1 | 354.6 | 0.90264 | 0.90251 | 0.25455 | 0.25451
570 | feeder2_line106 | 2 | 354.6 | 27.7143 | 27.7143 | 7.8157 | 7.8157
570 | feeder2_line106 | 3 | 354.6 | 3.1681 | 3.1678 | 0.89343 | 0.89335
570 | feeder2_line107 | 1 | 99 | 3.2517e-07 | 9.0553e-07 | 3.2845e-07 | 9.1468e-07
570 | feeder2_line107 | 2 | 99 | 0.08572 | 0.08576 | 0.086586 | 0.086626
570 | feeder2_line107 | 3 | 99 | 3.2344e-07 | 8.9758e-07 | 3.2671e-07 | 9.0664e-07
570 | feeder2_line108 | 1 | 354.6 | 0.90264 | 0.90251 | 0.25455 | 0.25451
570 | feeder2_line108 | 2 | 354.6 | 27.6331 | 27.6331 | 7.7928 | 7.7928
570 | feeder2_line108 | 3 | 354.6 | 3.1681 | 3.1678 | 0.89343 | 0.89335
570 | feeder2_line109 | 1 | 354.6 | 92.8882 | 92.8835 | 26.1952 | 26.1939
570 | feeder2_line109 | 2 | 354.6 | 94.939 | 94.9465 | 26.7735 | 26.7757
570 | feeder2_line109 | 3 | 354.6 | 96.8702 | 96.8675 | 27.3182 | 27.3174
570 | feeder2_line110 | 1 | 99 | 2.0405 | 2.0397 | 2.0611 | 2.0603
570 | feeder2_line110 | 2 | 99 | 0.00079736 | 9.0473e-07 | 0.00080542 | 9.1387e-07
570 | feeder2_line110 | 3 | 99 | 0.0008004 | 9.054e-07 | 0.00080849 | 9.1455e-07
570 | feeder2_line111 | 1 | 99 | 2.4495e-08 | 3.8374e-07 | 2.4743e-08 | 3.8762e-07
570 | feeder2_line111 | 2 | 99 | 0.045727 | 0.045753 | 0.046189 | 0.046215
570 | feeder2_line111 | 3 | 99 | 2.507e-08 | 3.8043e-07 | 2.5323e-08 | 3.8427e-07
570 | feeder2_line112 | 1 | 99 | 3.2536e-07 | 9.2215e-07 | 3.2864e-07 | 9.3146e-07
570 | feeder2_line112 | 2 | 99 | 1.6417 | 1.6418 | 1.6583 | 1.6584
570 | feeder2_line112 | 3 | 99 | 3.2369e-07 | 9.1419e-07 | 3.2696e-07 | 9.2342e-07
570 | feeder2_line113 | 1 | 99 | 0.93381 | 0.9338 | 0.94324 | 0.94323
570 | feeder2_line113 | 2 | 99 | 3.236e-07 | 9.0021e-07 | 3.2687e-07 | 9.093e-07
570 | feeder2_line113 | 3 | 99 | 3.2401e-07 | 9.0223e-07 | 3.2728e-07 | 9.1135e-07
570 | feeder2_line114 | 1 | 99 | 2.3792 | 2.3791 | 2.4032 | 2.4032
570 | feeder2_line114 | 2 | 99 | 2.5238e-08 | 4.3364e-07 | 2.5493e-08 | 4.3802e-07
570 | feeder2_line114 | 3 | 99 | 2.5032e-08 | 4.3488e-07 | 2.5285e-08 | 4.3927e-07
570 | feeder2_line115 | 1 | 99 | 2.4446e-08 | 5.6515e-07 | 2.4693e-08 | 5.7085e-07
570 | feeder2_line115 | 2 | 99 | 0.76966 | 0.76967 | 0.77744 | 0.77745
570 | feeder2_line115 | 3 | 99 | 2.5016e-08 | 5.6013e-07 | 2.5269e-08 | 5.6579e-07
570 | feeder2_line116 | 1 | 354.6 | 0.90266 | 0.90251 | 0.25456 | 0.25451
570 | feeder2_line116 | 2 | 354.6 | 26.9329 | 26.9328 | 7.5953 | 7.5953
570 | feeder2_line116 | 3 | 354.6 | 3.1681 | 3.1678 | 0.89343 | 0.89335
570 | feeder2_line117 | 1 | 99 | 4.9065e-08 | 6.4622e-07 | 4.956e-08 | 6.5275e-07
570 | feeder2_line117 | 2 | 99 | 0.072735 | 0.072774 | 0.07347 | 0.073509
570 | feeder2_line117 | 3 | 99 | 5.021e-08 | 6.4073e-07 | 5.0717e-08 | 6.472e-07
570 | feeder2_line118 | 1 | 354.6 | 92.8882 | 92.8835 | 26.1952 | 26.1939
570 | feeder2_line118 | 2 | 354.6 | 95.0102 | 95.0177 | 26.7936 | 26.7957
570 | feeder2_line118 | 3 | 354.6 | 96.8702 | 96.8675 | 27.3182 | 27.3174
570 | feeder2_line119 | 1 | 99 | 2.4442e-08 | 6.0818e-07 | 2.4689e-08 | 6.1433e-07
570 | feeder2_line119 | 2 | 99 | 2.5282e-08 | 6.0031e-07 | 2.5537e-08 | 6.0637e-07
570 | feeder2_line119 | 3 | 99 | 0.72702 | 0.72701 | 0.73436 | 0.73435
570 | feeder2_line120 | 1 | 354.6 | 0.90265 | 0.90251 | 0.25456 | 0.25452
570 | feeder2_line120 | 2 | 354.6 | 26.9329 | 26.9328 | 7.5953 | 7.5953
570 | feeder2_line120 | 3 | 354.6 | 2.5125 | 2.5123 | 0.70854 | 0.70848
570 | feeder2_line121 | 1 | 99 | 3.252e-07 | 9.419e-07 | 3.2849e-07 | 9.5142e-07
570 | feeder2_line121 | 2 | 99 | 1.1341 | 1.1341 | 1.1455 | 1.1455
570 | feeder2_line121 | 3 | 99 | 3.2341e-07 | 9.3334e-07 | 3.2667e-07 | 9.4277e-07
570 | feeder2_line122 | 1 | 354.6 | 0.90262 | 0.90251 | 0.25455 | 0.25452
570 | feeder2_line122 | 2 | 354.6 | 25.9374 | 25.9374 | 7.3146 | 7.3146
570 | feeder2_line122 | 3 | 354.6 | 2.5125 | 2.5123 | 0.70854 | 0.70848
570 | feeder2_line123 | 1 | 99 | 5.7718e-07 | 9.7609e-07 | 5.8301e-07 | 9.8595e-07
570 | feeder2_line123 | 2 | 99 | 5.6917e-07 | 9.627e-07 | 5.7492e-07 | 9.7243e-07
570 | feeder2_line123 | 3 | 99 | 1.9717 | 1.9716 | 1.9916 | 1.9915
570 | feeder2_line124 | 1 | 354.6 | 0.90267 | 0.90251 | 0.25456 | 0.25452
570 | feeder2_line124 | 2 | 354.6 | 25.9374 | 25.9374 | 7.3145 | 7.3146
570 | feeder2_line124 | 3 | 354.6 | 0.78784 | 0.78768 | 0.22218 | 0.22213
570 | feeder2_line125 | 1 | 99 | 5.772e-07 | 9.0739e-07 | 5.8303e-07 | 9.1656e-07
570 | feeder2_line125 | 2 | 99 | 5.6912e-07 | 8.9484e-07 | 5.7486e-07 | 9.0388e-07
570 | feeder2_line125 | 3 | 99 | 0.58364 | 0.58364 | 0.58953 | 0.58954
570 | feeder2_line126 | 1 | 354.6 | 0.9028 | 0.90252 | 0.2546 | 0.25452
570 | feeder2_line126 | 2 | 354.6 | 25.9375 | 25.9374 | 7.3146 | 7.3146
570 | feeder2_line126 | 3 | 354.6 | 0.20469 | 0.20438 | 0.057723 | 0.057635
570 | feeder2_line127 | 1 | 99 | 5.7723e-07 | 1.0864e-06 | 5.8306e-07 | 1.0973e-06
570 | feeder2_line127 | 2 | 99 | 5.6901e-07 | 1.0711e-06 | 5.7475e-07 | 1.0819e-06
570 | feeder2_line127 | 3 | 99 | 0.077472 | 0.077469 | 0.078254 | 0.078251
570 | feeder2_line128 | 1 | 354.6 | 0.90278 | 0.90252 | 0.25459 | 0.25452
570 | feeder2_line128 | 2 | 354.6 | 25.9375 | 25.9374 | 7.3146 | 7.3146
570 | feeder2_line128 | 3 | 354.6 | 0.12716 | 0.12693 | 0.035859 | 0.035796
570 | feeder2_line129 | 1 | 99 | 5.5282e-07 | 8.8087e-07 | 5.584e-07 | 8.8977e-07
570 | feeder2_line129 | 2 | 99 | 25.9372 | 25.9374 | 26.1992 | 26.1994
570 | feeder2_line129 | 3 | 99 | 5.4688e-07 | 8.7277e-07 | 5.524e-07 | 8.8158e-07
570 | feeder2_line130 | 1 | 354.6 | 0.90283 | 0.90252 | 0.2546 | 0.25452
570 | feeder2_line130 | 2 | 354.6 | 0.00030693 | 4.5971e-06 | 8.6558e-05 | 1.2964e-06
570 | feeder2_line130 | 3 | 354.6 | 0.12717 | 0.12693 | 0.035863 | 0.035796
570 | feeder2_line131 | 1 | 99 | 5.7725e-07 | 9.7635e-07 | 5.8308e-07 | 9.8621e-07
570 | feeder2_line131 | 2 | 99 | 5.6895e-07 | 9.6248e-07 | 5.747e-07 | 9.722e-07
570 | feeder2_line131 | 3 | 99 | 0.049569 | 0.049567 | 0.05007 | 0.050068
570 | feeder2_line132 | 1 | 354.6 | 0.90265 | 0.90252 | 0.25456 | 0.25452
570 | feeder2_line132 | 2 | 354.6 | 0.00012422 | 2.8904e-06 | 3.5032e-05 | 8.1511e-07
570 | feeder2_line132 | 3 | 354.6 | 0.077538 | 0.077467 | 0.021866 | 0.021846
570 | feeder2_line133 | 1 | 99 | 0.90253 | 0.90252 | 0.91164 | 0.91164
570 | feeder2_line133 | 2 | 99 | 2.9713e-07 | 9.7016e-07 | 3.0013e-07 | 9.7996e-07
570 | feeder2_line133 | 3 | 99 | 2.9842e-07 | 9.7507e-07 | 3.0143e-07 | 9.8492e-07
570 | feeder2_line134 | 1 | 354.6 | 6.1131e-12 | 1.7935e-06 | 1.7239e-12 | 5.0577e-07
570 | feeder2_line134 | 2 | 354.6 | 5.9665e-12 | 1.7702e-06 | 1.6826e-12 | 4.9922e-07
570 | feeder2_line134 | 3 | 354.6 | 0.077469 | 0.077467 | 0.021847 | 0.021846
570 | feeder2_line135 | 1 | 99 | 2.478 | 2.478 | 2.5031 | 2.503
570 | feeder2_line135 | 2 | 99 | 5.0571e-08 | 5.8269e-07 | 5.1081e-08 | 5.8858e-07
570 | feeder2_line135 | 3 | 99 | 5.0229e-08 | 5.8407e-07 | 5.0737e-08 | 5.8997e-07
570 | feeder2_line136 | 1 | 354.6 | 93.7583 | 93.7536 | 26.4406 | 26.4393
570 | feeder2_line136 | 2 | 354.6 | 95.0102 | 95.0177 | 26.7936 | 26.7957
570 | feeder2_line136 | 3 | 354.6 | 96.8702 | 96.8675 | 27.3182 | 27.3174
570 | feeder2_line137 | 1 | 99 | 2.2631 | 2.2631 | 2.2859 | 2.2859
570 | feeder2_line137 | 2 | 99 | 8.4544e-07 | 1.5696e-06 | 8.5398e-07 | 1.5854e-06
570 | feeder2_line137 | 3 | 99 | 8.4757e-07 | 1.5733e-06 | 8.5613e-07 | 1.5892e-06
570 | feeder2_line138 | 1 | 354.6 | 94.9613 | 94.9566 | 26.7798 | 26.7785
570 | feeder2_line138 | 2 | 354.6 | 95.0102 | 95.0177 | 26.7936 | 26.7957
570 | feeder2_line138 | 3 | 354.6 | 96.8702 | 96.8675 | 27.3182 | 27.3174
570 | feeder2_line139 | 1 | 99 | 4.9101e-08 | 4.9442e-07 | 4.9597e-08 | 4.9942e-07
570 | feeder2_line139 | 2 | 99 | 5.0584e-08 | 4.8909e-07 | 5.1095e-08 | 4.9403e-07
570 | feeder2_line139 | 3 | 99 | 1.5825 | 1.5822 | 1.5985 | 1.5982
570 | feeder2_line140 | 1 | 354.6 | 94.9614 | 94.9566 | 26.7799 | 26.7785
570 | feeder2_line140 | 2 | 354.6 | 95.0103 | 95.0177 | 26.7937 | 26.7957
570 | feeder2_line140 | 3 | 354.6 | 98.0573 | 98.0544 | 27.6529 | 27.6521
570 | feeder2_line141 | 1 | 99 | 2.549e-06 | 4.8914e-07 | 2.5747e-06 | 4.9408e-07
570 | feeder2_line141 | 2 | 99 | 1.8174 | 1.8174 | 1.8358 | 1.8358
570 | feeder2_line141 | 3 | 99 | 2.5164e-06 | 4.8502e-07 | 2.5418e-06 | 4.8991e-07
570 | feeder2_line142 | 1 | 354.6 | 94.9612 | 94.9566 | 26.7798 | 26.7785
570 | feeder2_line142 | 2 | 354.6 | 96.3304 | 96.3379 | 27.1659 | 27.1681
570 | feeder2_line142 | 3 | 354.6 | 98.0572 | 98.0544 | 27.6529 | 27.6521
570 | feeder2_line143 | 1 | 99 | 8.5562e-07 | 1.7382e-06 | 8.6426e-07 | 1.7557e-06
570 | feeder2_line143 | 2 | 99 | 0.085371 | 0.085423 | 0.086234 | 0.086286
570 | feeder2_line143 | 3 | 99 | 8.4793e-07 | 1.7235e-06 | 8.5649e-07 | 1.7409e-06
570 | feeder2_line144 | 1 | 354.6 | 94.961 | 94.9566 | 26.7798 | 26.7785
570 | feeder2_line144 | 2 | 354.6 | 96.4139 | 96.4217 | 27.1895 | 27.1917
570 | feeder2_line144 | 3 | 354.6 | 98.057 | 98.0544 | 27.6528 | 27.6521
570 | feeder2_line145 | 1 | 99 | 2.4566e-08 | 4.8741e-07 | 2.4814e-08 | 4.9233e-07
570 | feeder2_line145 | 2 | 99 | 0.069934 | 0.069945 | 0.070641 | 0.070651
570 | feeder2_line145 | 3 | 99 | 2.5132e-08 | 4.8331e-07 | 2.5386e-08 | 4.8819e-07
570 | feeder2_line146 | 1 | 354.6 | 94.9609 | 94.9566 | 26.7797 | 26.7785
570 | feeder2_line146 | 2 | 354.6 | 96.4826 | 96.4905 | 27.2089 | 27.2111
570 | feeder2_line146 | 3 | 354.6 | 98.0569 | 98.0544 | 27.6528 | 27.6521
570 | feeder2_line147 | 1 | 99 | 1.1079 | 1.1079 | 1.1191 | 1.1191
570 | feeder2_line147 | 2 | 99 | 1.1447e-06 | 2.224e-06 | 1.1563e-06 | 2.2464e-06
570 | feeder2_line147 | 3 | 99 | 1.1475e-06 | 2.2293e-06 | 1.1591e-06 | 2.2518e-06
570 | feeder2_line148 | 1 | 99 | 0.08419 | 0.084185 | 0.08504 | 0.085035
570 | feeder2_line148 | 2 | 99 | 5.9765e-07 | 1.4902e-06 | 6.0369e-07 | 1.5053e-06
570 | feeder2_line148 | 3 | 99 | 5.9888e-07 | 1.4938e-06 | 6.0493e-07 | 1.5089e-06
570 | feeder2_line149 | 1 | 354.6 | 96.1334 | 96.1289 | 27.1104 | 27.1091
570 | feeder2_line149 | 2 | 354.6 | 96.4828 | 96.4905 | 27.2089 | 27.2111
570 | feeder2_line149 | 3 | 354.6 | 98.0571 | 98.0544 | 27.6529 | 27.6521
570 | feeder2_line150 | 1 | 354.6 | 96.1335 | 96.1289 | 27.1104 | 27.1091
570 | feeder2_line150 | 2 | 354.6 | 99.0001 | 99.0078 | 27.9188 | 27.921
570 | feeder2_line150 | 3 | 354.6 | 98.0572 | 98.0544 | 27.6529 | 27.6521
570 | feeder2_line151 | 1 | 99 | 9.86e-06 | 1.7897e-06 | 9.9596e-06 | 1.8077e-06
570 | feeder2_line151 | 2 | 99 | 3.7367 | 3.7366 | 3.7744 | 3.7744
570 | feeder2_line151 | 3 | 99 | 9.7294e-06 | 1.7746e-06 | 9.8277e-06 | 1.7925e-06
570 | feeder2_line152 | 1 | 354.6 | 3.3125e-12 | 1.1922e-06 | 9.3415e-13 | 3.362e-07
570 | feeder2_line152 | 2 | 354.6 | 4.9231e-12 | 1.1805e-06 | 1.3883e-12 | 3.3291e-07
570 | feeder2_line152 | 3 | 354.6 | 0.077108 | 0.077106 | 0.021745 | 0.021744
570 | feeder2_line153 | 1 | 99 | 1.1388 | 1.1388 | 1.1503 | 1.1503
570 | feeder2_line153 | 2 | 99 | 5.0645e-08 | 5.9037e-07 | 5.1156e-08 | 5.9634e-07
570 | feeder2_line153 | 3 | 99 | 5.0312e-08 | 5.9179e-07 | 5.082e-08 | 5.9777e-07
570 | feeder2_line154 | 1 | 99 | 5.7916e-07 | 8.8809e-07 | 5.8501e-07 | 8.9706e-07
570 | feeder2_line154 | 2 | 99 | 5.7282e-07 | 8.785e-07 | 5.7861e-07 | 8.8737e-07
570 | feeder2_line154 | 3 | 99 | 1.2406 | 1.2406 | 1.2532 | 1.2532
570 | feeder2_line155 | 1 | 99 | 97.272 | 97.2674 | 98.2545 | 98.2499
570 | feeder2_line155 | 2 | 99 | 99 | 99.0078 | 100 | 100.0079
570 | feeder2_line155 | 3 | 99 | 98.6266 | 98.6239 | 99.6228 | 99.6201
570 | feeder2_line156 | 1 | 99 | 6.035e-07 | 1.1686e-06 | 6.096e-07 | 1.1804e-06
570 | feeder2_line156 | 2 | 99 | 2.3738 | 2.3738 | 2.3978 | 2.3977
570 | feeder2_line156 | 3 | 99 | 5.9914e-07 | 1.1588e-06 | 6.052e-07 | 1.1705e-06
570 | feeder2_line157 | 1 | 99 | 2.4575e-08 | 2.537e-07 | 2.4823e-08 | 2.5627e-07
570 | feeder2_line157 | 2 | 99 | 1.4759 | 1.4759 | 1.4908 | 1.4908
570 | feeder2_line157 | 3 | 99 | 2.5146e-08 | 2.5156e-07 | 2.54e-08 | 2.5411e-07
600 | feeder2_line1 | 1 | 354.6 | 60.1319 | 60.1362 | 16.9577 | 16.9589
600 | feeder2_line1 | 2 | 354.6 | 62.6036 | 62.605 | 17.6547 | 17.6551
600 | feeder2_line1 | 3 | 354.6 | 39.9247 | 39.9233 | 11.2591 | 11.2587
600 | feeder2_line2 | 1 | 354.6 | 60.1926 | 60.1967 | 16.9748 | 16.976
600 | feeder2_line2 | 2 | 354.6 | 62.6038 | 62.605 | 17.6548 | 17.6551
600 | feeder2_line2 | 3 | 354.6 | 39.9249 | 39.9233 | 11.2591 | 11.2587
600 | feeder2_line3 | 1 | 80.1 | 0.069388 | 0.069392 | 0.086627 | 0.086631
600 | feeder2_line3 | 2 | 80.1 | 5.7113e-07 | 1.0554e-06 | 7.1303e-07 | 1.3177e-06
600 | feeder2_line3 | 3 | 80.1 | 5.6913e-07 | 1.0518e-06 | 7.1053e-07 | 1.3131e-06
600 | feeder2_line4 | 1 | 354.6 | 60.1927 | 60.1967 | 16.9748 | 16.976
600 | feeder2_line4 | 2 | 354.6 | 62.6762 | 62.6774 | 17.6752 | 17.6755
600 | feeder2_line4 | 3 | 354.6 | 39.9248 | 39.9233 | 11.2591 | 11.2587
600 | feeder2_line5 | 1 | 80.1 | 5.712e-07 | 9.9667e-07 | 7.1311e-07 | 1.2443e-06
600 | feeder2_line5 | 2 | 80.1 | 0.090172 | 0.090172 | 0.11257 | 0.11257
600 | feeder2_line5 | 3 | 80.1 | 5.691e-07 | 9.9305e-07 | 7.1048e-07 | 1.2398e-06
600 | feeder2_line6 | 1 | 80.1 | 5.7125e-07 | 1.1726e-06 | 7.1317e-07 | 1.4639e-06
600 | feeder2_line6 | 2 | 80.1 | 5.712e-07 | 1.1725e-06 | 7.1311e-07 | 1.4638e-06
600 | feeder2_line6 | 3 | 80.1 | 0.08588 | 0.085873 | 0.10722 | 0.10721
600 | feeder2_line7 | 1 | 354.6 | 60.1928 | 60.1967 | 16.9749 | 16.976
600 | feeder2_line7 | 2 | 354.6 | 62.6763 | 62.6774 | 17.6752 | 17.6755
600 | feeder2_line7 | 3 | 354.6 | 39.9435 | 39.9419 | 11.2644 | 11.2639
600 | feeder2_line8 | 1 | 80.1 | 19.1121 | 19.1121 | 23.8603 | 23.8603
600 | feeder2_line8 | 2 | 80.1 | 5.7126e-07 | 1.1307e-06 | 7.1318e-07 | 1.4116e-06
600 | feeder2_line8 | 3 | 80.1 | 5.688e-07 | 1.1259e-06 | 7.1011e-07 | 1.4056e-06
600 | feeder2_line9 | 1 | 354.6 | 76.6234 | 76.6273 | 21.6084 | 21.6095
600 | feeder2_line9 | 2 | 354.6 | 62.6763 | 62.6774 | 17.6752 | 17.6755
600 | feeder2_line9 | 3 | 354.6 | 39.9434 | 39.9419 | 11.2643 | 11.2639
600 | feeder2_line10 | 1 | 80.1 | 8.4472e-07 | 1.4932e-06 | 1.0546e-06 | 1.8642e-06
600 | feeder2_line10 | 2 | 80.1 | 19.0854 | 19.0855 | 23.8269 | 23.827
600 | feeder2_line10 | 3 | 80.1 | 8.4064e-07 | 1.4865e-06 | 1.0495e-06 | 1.8558e-06
600 | feeder2_line11 | 1 | 354.6 | 76.6234 | 76.6273 | 21.6084 | 21.6095
600 | feeder2_line11 | 2 | 354.6 | 78.0115 | 78.0122 | 21.9998 | 22.0001
600 | feeder2_line11 | 3 | 354.6 | 39.9435 | 39.9419 | 11.2644 | 11.2639
600 | feeder2_line12 | 1 | 80.1 | 5.4684e-07 | 9.9063e-07 | 6.827e-07 | 1.2367e-06
600 | feeder2_line12 | 2 | 80.1 | 5.4661e-07 | 9.9051e-07 | 6.824e-07 | 1.2366e-06
600 | feeder2_line12 | 3 | 80.1 | 12.0414 | 12.0414 | 15.033 | 15.033
600 | feeder2_line13 | 1 | 354.6 | 76.6234 | 76.6273 | 21.6084 | 21.6095
600 | feeder2_line13 | 2 | 354.6 | 78.0115 | 78.0122 | 21.9999 | 22.0001
600 | feeder2_line13 | 3 | 354.6 | 43.3047 | 43.3022 | 12.2123 | 12.2116
600 | feeder2_line14 | 1 | 80.1 | 5.8226 | 5.8229 | 7.2692 | 7.2695
600 | feeder2_line14 | 2 | 80.1 | 2.9813e-07 | 6.4597e-07 | 3.7219e-07 | 8.0646e-07
600 | feeder2_line14 | 3 | 80.1 | 2.9682e-07 | 6.4281e-07 | 3.7056e-07 | 8.0251e-07
600 | feeder2_line15 | 1 | 354.6 | 79.9131 | 79.9172 | 22.5361 | 22.5373
600 | feeder2_line15 | 2 | 354.6 | 78.0115 | 78.0122 | 21.9999 | 22.0001
600 | feeder2_line15 | 3 | 354.6 | 43.3047 | 43.3022 | 12.2123 | 12.2116
600 | feeder2_line16 | 1 | 80.1 | 5.7169e-07 | 1.0299e-06 | 7.1372e-07 | 1.2858e-06
600 | feeder2_line16 | 2 | 80.1 | 0.028894 | 0.028891 | 0.036073 | 0.036069
600 | feeder2_line16 | 3 | 80.1 | 5.6855e-07 | 1.0243e-06 | 7.098e-07 | 1.2788e-06
600 | feeder2_line17 | 1 | 354.6 | 79.9132 | 79.9172 | 22.5361 | 22.5373
600 | feeder2_line17 | 2 | 354.6 | 78.0372 | 78.0379 | 22.0071 | 22.0073
600 | feeder2_line17 | 3 | 354.6 | 43.3047 | 43.3022 | 12.2123 | 12.2116
600 | feeder2_line18 | 1 | 80.1 | 5.4769e-07 | 7.3795e-07 | 6.8376e-07 | 9.2129e-07
600 | feeder2_line18 | 2 | 80.1 | 5.4725e-07 | 7.3766e-07 | 6.8321e-07 | 9.2092e-07
600 | feeder2_line18 | 3 | 80.1 | 0.040618 | 0.040607 | 0.050709 | 0.050695
600 | feeder2_line19 | 1 | 354.6 | 79.9132 | 79.9172 | 22.5361 | 22.5373
600 | feeder2_line19 | 2 | 354.6 | 78.0372 | 78.0379 | 22.0071 | 22.0073
600 | feeder2_line19 | 3 | 354.6 | 43.3226 | 43.3201 | 12.2173 | 12.2166
600 | feeder2_line20 | 1 | 99 | 5.4792e-07 | 8.8509e-07 | 5.5345e-07 | 8.9403e-07
600 | feeder2_line20 | 2 | 99 | 5.4743e-07 | 8.8467e-07 | 5.5295e-07 | 8.936e-07
600 | feeder2_line20 | 3 | 99 | 1.3975 | 1.3976 | 1.4117 | 1.4117
600 | feeder2_line21 | 1 | 354.6 | 79.9133 | 79.9172 | 22.5362 | 22.5373
600 | feeder2_line21 | 2 | 354.6 | 78.0373 | 78.0379 | 22.0071 | 22.0073
600 | feeder2_line21 | 3 | 354.6 | 42.6959 | 42.6933 | 12.0406 | 12.0398
600 | feeder2_line22 | 1 | 99 | 5.7261e-07 | 1.0149e-06 | 5.784e-07 | 1.0251e-06
600 | feeder2_line22 | 2 | 99 | 1.807 | 1.807 | 1.8252 | 1.8252
600 | feeder2_line22 | 3 | 99 | 5.6781e-07 | 1.0065e-06 | 5.7354e-07 | 1.0166e-06
600 | feeder2_line23 | 1 | 99 | 5.7261e-07 | 9.5001e-07 | 5.7839e-07 | 9.596e-07
600 | feeder2_line23 | 2 | 99 | 5.7229e-07 | 9.4951e-07 | 5.7807e-07 | 9.591e-07
600 | feeder2_line23 | 3 | 99 | 4.4206 | 4.4206 | 4.4652 | 4.4653
600 | feeder2_line24 | 1 | 354.6 | 79.9133 | 79.9172 | 22.5362 | 22.5373
600 | feeder2_line24 | 2 | 354.6 | 79.594 | 79.5945 | 22.4461 | 22.4463
600 | feeder2_line24 | 3 | 354.6 | 44.7835 | 44.7806 | 12.6293 | 12.6285
600 | feeder2_line25 | 1 | 99 | 1.8053 | 1.8053 | 1.8235 | 1.8235
600 | feeder2_line25 | 2 | 99 | 4.9537e-08 | 6.9053e-07 | 5.0038e-08 | 6.9751e-07
600 | feeder2_line25 | 3 | 99 | 5.0346e-08 | 6.8477e-07 | 5.0855e-08 | 6.9169e-07
600 | feeder2_line26 | 1 | 99 | 0.08507 | 0.085072 | 0.085929 | 0.085931
600 | feeder2_line26 | 2 | 99 | 5.4771e-07 | 8.5553e-07 | 5.5325e-07 | 8.6417e-07
600 | feeder2_line26 | 3 | 99 | 5.4248e-07 | 8.4839e-07 | 5.4796e-07 | 8.5696e-07
600 | feeder2_line27 | 1 | 354.6 | 81.6669 | 81.6707 | 23.0307 | 23.0318
600 | feeder2_line27 | 2 | 354.6 | 79.5941 | 79.5945 | 22.4462 | 22.4463
600 | feeder2_line27 | 3 | 354.6 | 44.7835 | 44.7806 | 12.6293 | 12.6285
600 | feeder2_line28 | 1 | 99 | 2.5475e-06 | 7.1106e-07 | 2.5732e-06 | 7.1824e-07
600 | feeder2_line28 | 2 | 99 | 0.077089 | 0.077088 | 0.077868 | 0.077867
600 | feeder2_line28 | 3 | 99 | 2.5091e-06 | 7.0392e-07 | 2.5344e-06 | 7.1103e-07
600 | feeder2_line29 | 1 | 354.6 | 81.6669 | 81.6707 | 23.0307 | 23.0318
600 | feeder2_line29 | 2 | 354.6 | 79.6628 | 79.6633 | 22.4655 | 22.4657
600 | feeder2_line29 | 3 | 354.6 | 44.7835 | 44.7806 | 12.6293 | 12.6285
600 | feeder2_line30 | 1 | 266.4 | 3.1203 | 3.12 | 1.1713 | 1.1712
600 | feeder2_line30 | 2 | 266.4 | 2.0478 | 2.0478 | 0.76868 | 0.76868
600 | feeder2_line30 | 3 | 266.4 | 14.4836 | 14.4834 | 5.4368 | 5.4367
600 | feeder2_line31 | 1 | 354.6 | 84.583 | 84.5865 | 23.8531 | 23.8541
600 | feeder2_line31 | 2 | 354.6 | 80.7282 | 80.7281 | 22.766 | 22.766
600 | feeder2_line31 | 3 | 354.6 | 52.1256 | 52.1216 | 14.6998 | 14.6987
600 | feeder2_line32 | 1 | 354.6 | 84.583 | 84.5865 | 23.8531 | 23.8541
600 | feeder2_line32 | 2 | 354.6 | 80.7984 | 80.7983 | 22.7858 | 22.7858
600 | feeder2_line32 | 3 | 354.6 | 52.1257 | 52.1216 | 14.6998 | 14.6987
600 | feeder2_line33 | 1 | 99 | 4.892e-08 | 6.8697e-07 | 4.9414e-08 | 6.9391e-07
600 | feeder2_line33 | 2 | 99 | 0.077118 | 0.077117 | 0.077897 | 0.077896
600 | feeder2_line33 | 3 | 99 | 5.0647e-08 | 6.7856e-07 | 5.1159e-08 | 6.8541e-07
600 | feeder2_line34 | 1 | 354.6 | 84.583 | 84.5865 | 23.8531 | 23.8541
600 | feeder2_line34 | 2 | 354.6 | 80.7984 | 80.7983 | 22.7858 | 22.7858
600 | feeder2_line34 | 3 | 354.6 | 53.0938 | 53.0898 | 14.9729 | 14.9717
600 | feeder2_line35 | 1 | 99 | 2.9932e-07 | 7.6091e-07 | 3.0234e-07 | 7.686e-07
600 | feeder2_line35 | 2 | 99 | 2.9912e-07 | 7.6004e-07 | 3.0215e-07 | 7.6771e-07
600 | feeder2_line35 | 3 | 99 | 1.3305 | 1.3305 | 1.3439 | 1.3439
600 | feeder2_line36 | 1 | 354.6 | 84.8874 | 84.8911 | 23.9389 | 23.9399
600 | feeder2_line36 | 2 | 354.6 | 80.7984 | 80.7983 | 22.7858 | 22.7858
600 | feeder2_line36 | 3 | 354.6 | 53.0938 | 53.0898 | 14.9729 | 14.9717
600 | feeder2_line37 | 1 | 99 | 1.236 | 1.236 | 1.2485 | 1.2485
600 | feeder2_line37 | 2 | 99 | 2.9918e-07 | 8.411e-07 | 3.022e-07 | 8.496e-07
600 | feeder2_line37 | 3 | 99 | 2.9609e-07 | 8.3128e-07 | 2.9908e-07 | 8.3967e-07
600 | feeder2_line38 | 1 | 99 | 3.2358e-07 | 7.764e-07 | 3.2685e-07 | 7.8424e-07
600 | feeder2_line38 | 2 | 99 | 1.4519 | 1.4519 | 1.4666 | 1.4666
600 | feeder2_line38 | 3 | 99 | 3.2143e-07 | 7.673e-07 | 3.2467e-07 | 7.7505e-07
600 | feeder2_line39 | 1 | 266.4 | 3.1203 | 3.12 | 1.1713 | 1.1712
600 | feeder2_line39 | 2 | 266.4 | 0.74526 | 0.74492 | 0.27975 | 0.27962
600 | feeder2_line39 | 3 | 266.4 | 14.4836 | 14.4834 | 5.4368 | 5.4367
600 | feeder2_line40 | 1 | 354.6 | 86.5813 | 86.5849 | 24.4166 | 24.4176
600 | feeder2_line40 | 2 | 354.6 | 80.7984 | 80.7983 | 22.7858 | 22.7858
600 | feeder2_line40 | 3 | 354.6 | 53.0938 | 53.0898 | 14.9729 | 14.9717
600 | feeder2_line41 | 1 | 99 | 1.8027 | 1.8027 | 1.8209 | 1.8209
600 | feeder2_line41 | 2 | 99 | 4.9527e-08 | 7.3504e-07 | 5.0027e-08 | 7.4247e-07
600 | feeder2_line41 | 3 | 99 | 5.0723e-08 | 7.2635e-07 | 5.1235e-08 | 7.3369e-07
600 | feeder2_line42 | 1 | 99 | 2.9911e-07 | 7.4939e-07 | 3.0213e-07 | 7.5696e-07
600 | feeder2_line42 | 2 | 99 | 2.9898e-07 | 7.4872e-07 | 3.02e-07 | 7.5628e-07
600 | feeder2_line42 | 3 | 99 | 1.6545 | 1.6545 | 1.6712 | 1.6712
600 | feeder2_line43 | 1 | 266.4 | 3.1202 | 3.12 | 1.1712 | 1.1712
600 | feeder2_line43 | 2 | 266.4 | 0.74516 | 0.74492 | 0.27971 | 0.27962
600 | feeder2_line43 | 3 | 266.4 | 13.0121 | 13.0119 | 4.8844 | 4.8844
600 | feeder2_line44 | 1 | 354.6 | 86.5814 | 86.5849 | 24.4166 | 24.4176
600 | feeder2_line44 | 2 | 354.6 | 80.7984 | 80.7983 | 22.7858 | 22.7858
600 | feeder2_line44 | 3 | 354.6 | 53.0007 | 52.9965 | 14.9466 | 14.9454
600 | feeder2_line45 | 1 | 99 | 4.8873e-08 | 5.8051e-07 | 4.9366e-08 | 5.8637e-07
600 | feeder2_line45 | 2 | 99 | 4.9537e-08 | 5.7975e-07 | 5.0037e-08 | 5.856e-07
600 | feeder2_line45 | 3 | 99 | 1.396 | 1.396 | 1.4101 | 1.4101
600 | feeder2_line46 | 1 | 99 | 5.7377e-07 | 1.3585e-06 | 5.7956e-07 | 1.3723e-06
600 | feeder2_line46 | 2 | 99 | 5.7323e-07 | 1.3573e-06 | 5.7902e-07 | 1.371e-06
600 | feeder2_line46 | 3 | 99 | 1.4638 | 1.4638 | 1.4786 | 1.4786
600 | feeder2_line47 | 1 | 266.4 | 3.1202 | 3.12 | 1.1712 | 1.1712
600 | feeder2_line47 | 2 | 266.4 | 0.74516 | 0.74492 | 0.27972 | 0.27962
600 | feeder2_line47 | 3 | 266.4 | 12.0635 | 12.0633 | 4.5283 | 4.5283
600 | feeder2_line48 | 1 | 99 | 1.1029 | 1.1029 | 1.114 | 1.114
600 | feeder2_line48 | 2 | 99 | 4.9502e-08 | 7.3081e-07 | 5.0002e-08 | 7.3819e-07
600 | feeder2_line48 | 3 | 99 | 5.0608e-08 | 7.2272e-07 | 5.1119e-08 | 7.3002e-07
600 | feeder2_line49 | 1 | 266.4 | 2.0174 | 2.0173 | 0.75729 | 0.75724
600 | feeder2_line49 | 2 | 266.4 | 0.74514 | 0.74492 | 0.27971 | 0.27962
600 | feeder2_line49 | 3 | 266.4 | 12.0635 | 12.0633 | 4.5283 | 4.5283
600 | feeder2_line50 | 1 | 99 | 5.7376e-07 | 1.2363e-06 | 5.7955e-07 | 1.2488e-06
600 | feeder2_line50 | 2 | 99 | 0.085122 | 0.08513 | 0.085981 | 0.08599
600 | feeder2_line50 | 3 | 99 | 5.668e-07 | 1.2215e-06 | 5.7253e-07 | 1.2339e-06
600 | feeder2_line51 | 1 | 99 | 1.1605 | 1.1606 | 1.1722 | 1.1723
600 | feeder2_line51 | 2 | 99 | 5.7324e-07 | 1.341e-06 | 5.7903e-07 | 1.3546e-06
600 | feeder2_line51 | 3 | 99 | 5.668e-07 | 1.3261e-06 | 5.7253e-07 | 1.3395e-06
600 | feeder2_line52 | 1 | 266.4 | 0.8568 | 0.85671 | 0.32162 | 0.32159
600 | feeder2_line52 | 2 | 266.4 | 0.66002 | 0.65992 | 0.24775 | 0.24772
600 | feeder2_line52 | 3 | 266.4 | 12.0633 | 12.0633 | 4.5283 | 4.5283
600 | feeder2_line53 | 1 | 99 | 5.493e-07 | 7.5456e-07 | 5.5485e-07 | 7.6218e-07
600 | feeder2_line53 | 2 | 99 | 0.65992 | 0.65992 | 0.66659 | 0.66659
600 | feeder2_line53 | 3 | 99 | 5.4149e-07 | 7.4552e-07 | 5.4696e-07 | 7.5305e-07
600 | feeder2_line54 | 1 | 266.4 | 0.85662 | 0.85671 | 0.32155 | 0.32159
600 | feeder2_line54 | 2 | 266.4 | 8.5413e-05 | 4.6245e-06 | 3.2062e-05 | 1.7359e-06
600 | feeder2_line54 | 3 | 266.4 | 12.0632 | 12.0633 | 4.5282 | 4.5283
600 | feeder2_line55 | 1 | 99 | 0.045353 | 0.045356 | 0.045811 | 0.045814
600 | feeder2_line55 | 2 | 99 | 4.9545e-08 | 7.3071e-07 | 5.0046e-08 | 7.3809e-07
600 | feeder2_line55 | 3 | 99 | 5.0826e-08 | 7.2147e-07 | 5.134e-08 | 7.2876e-07
600 | feeder2_line56 | 1 | 354.6 | 86.6246 | 86.6281 | 24.4288 | 24.4298
600 | feeder2_line56 | 2 | 354.6 | 80.7985 | 80.7983 | 22.7858 | 22.7858
600 | feeder2_line56 | 3 | 354.6 | 53.0007 | 52.9965 | 14.9466 | 14.9454
600 | feeder2_line57 | 1 | 99 | 7.3385e-07 | 1.5456e-06 | 7.4127e-07 | 1.5612e-06
600 | feeder2_line57 | 2 | 99 | 7.4245e-07 | 1.5443e-06 | 7.4995e-07 | 1.5599e-06
600 | feeder2_line57 | 3 | 99 | 12.0632 | 12.0633 | 12.1851 | 12.1851
600 | feeder2_line58 | 1 | 266.4 | 0.85668 | 0.85671 | 0.32158 | 0.32159
600 | feeder2_line58 | 2 | 266.4 | 1.8982e-05 | 2.6849e-06 | 7.1253e-06 | 1.0078e-06
600 | feeder2_line58 | 3 | 266.4 | 1.8694e-05 | 2.656e-06 | 7.0173e-06 | 9.9701e-07
600 | feeder2_line59 | 1 | 99 | 4.8925e-08 | 5.3727e-07 | 4.9419e-08 | 5.427e-07
600 | feeder2_line59 | 2 | 99 | 4.9494e-08 | 5.368e-07 | 4.9994e-08 | 5.4222e-07
600 | feeder2_line59 | 3 | 99 | 0.082338 | 0.082337 | 0.08317 | 0.083169
600 | feeder2_line60 | 1 | 99 | 2.991e-07 | 8.1195e-07 | 3.0212e-07 | 8.2015e-07
600 | feeder2_line60 | 2 | 99 | 2.9898e-07 | 8.1125e-07 | 3.02e-07 | 8.1945e-07
600 | feeder2_line60 | 3 | 99 | 11.9812 | 11.9812 | 12.1022 | 12.1022
600 | feeder2_line61 | 1 | 266.4 | 1.7677 | 1.7679 | 0.66354 | 0.66361
600 | feeder2_line61 | 2 | 266.4 | 4.2912 | 4.2913 | 1.6108 | 1.6109
600 | feeder2_line61 | 3 | 266.4 | 5.1781 | 5.1782 | 1.9437 | 1.9438
600 | feeder2_line62 | 1 | 354.6 | 87.479 | 87.4827 | 24.6698 | 24.6708
600 | feeder2_line62 | 2 | 354.6 | 83.9691 | 83.969 | 23.6799 | 23.6799
600 | feeder2_line62 | 3 | 354.6 | 56.1759 | 56.1717 | 15.842 | 15.8409
600 | feeder2_line63 | 1 | 99 | 0.088796 | 0.088799 | 0.089693 | 0.089696
600 | feeder2_line63 | 2 | 99 | 5.7325e-07 | 1.2197e-06 | 5.7904e-07 | 1.2321e-06
600 | feeder2_line63 | 3 | 99 | 5.6676e-07 | 1.2061e-06 | 5.7248e-07 | 1.2182e-06
600 | feeder2_line64 | 1 | 99 | 0.76794 | 0.76795 | 0.7757 | 0.77571
600 | feeder2_line64 | 2 | 99 | 1.2204e-12 | 3.2129e-07 | 1.2327e-12 | 3.2454e-07
600 | feeder2_line64 | 3 | 99 | 1.154e-12 | 3.177e-07 | 1.1657e-12 | 3.2091e-07
600 | feeder2_line65 | 1 | 99 | 4.8768e-08 | 6.4348e-07 | 4.9261e-08 | 6.4998e-07
600 | feeder2_line65 | 2 | 99 | 0.089676 | 0.089675 | 0.090582 | 0.090581
600 | feeder2_line65 | 3 | 99 | 5.096e-08 | 6.3345e-07 | 5.1475e-08 | 6.3985e-07
600 | feeder2_line66 | 1 | 354.6 | 87.4789 | 87.4827 | 24.6698 | 24.6708
600 | feeder2_line66 | 2 | 354.6 | 84.052 | 84.0519 | 23.7033 | 23.7033
600 | feeder2_line66 | 3 | 354.6 | 56.1758 | 56.1717 | 15.842 | 15.8409
600 | feeder2_line67 | 1 | 99 | 2.4394e-08 | 3.6357e-07 | 2.4641e-08 | 3.6725e-07
600 | feeder2_line67 | 2 | 99 | 2.4776e-08 | 3.6294e-07 | 2.5026e-08 | 3.6661e-07
600 | feeder2_line67 | 3 | 99 | 1.8179 | 1.8179 | 1.8363 | 1.8363
600 | feeder2_line68 | 1 | 266.4 | 1.7677 | 1.7679 | 0.66356 | 0.66361
600 | feeder2_line68 | 2 | 266.4 | 4.2912 | 4.2913 | 1.6108 | 1.6109
600 | feeder2_line68 | 3 | 266.4 | 3.4365 | 3.4366 | 1.29 | 1.29
600 | feeder2_line69 | 1 | 99 | 0.10041 | 0.10043 | 0.10143 | 0.10144
600 | feeder2_line69 | 2 | 99 | 2.5508e-06 | 6.6684e-07 | 2.5765e-06 | 6.7358e-07
600 | feeder2_line69 | 3 | 99 | 2.501e-06 | 6.5757e-07 | 2.5262e-06 | 6.6421e-07
600 | feeder2_line70 | 1 | 354.6 | 87.5754 | 87.5792 | 24.6969 | 24.698
600 | feeder2_line70 | 2 | 354.6 | 84.0519 | 84.0519 | 23.7033 | 23.7033
600 | feeder2_line70 | 3 | 354.6 | 56.1758 | 56.1717 | 15.842 | 15.8409
600 | feeder2_line71 | 1 | 99 | 4.8752e-08 | 7.1818e-07 | 4.9245e-08 | 7.2543e-07
600 | feeder2_line71 | 2 | 99 | 0.052757 | 0.052767 | 0.05329 | 0.0533
600 | feeder2_line71 | 3 | 99 | 5.1011e-08 | 7.0661e-07 | 5.1526e-08 | 7.1375e-07
600 | feeder2_line72 | 1 | 354.6 | 87.5755 | 87.5792 | 24.697 | 24.698
600 | feeder2_line72 | 2 | 354.6 | 84.1003 | 84.1003 | 23.717 | 23.7169
600 | feeder2_line72 | 3 | 354.6 | 56.1759 | 56.1717 | 15.842 | 15.8409
600 | feeder2_line73 | 1 | 99 | 5.9963e-07 | 1.5393e-06 | 6.0569e-07 | 1.5548e-06
600 | feeder2_line73 | 2 | 99 | 0.077015 | 0.077014 | 0.077793 | 0.077792
600 | feeder2_line73 | 3 | 99 | 5.9198e-07 | 1.5162e-06 | 5.9796e-07 | 1.5316e-06
600 | feeder2_line74 | 1 | 99 | 4.8788e-08 | 4.5908e-07 | 4.9281e-08 | 4.6372e-07
600 | feeder2_line74 | 2 | 99 | 3.4095 | 3.4095 | 3.444 | 3.444
600 | feeder2_line74 | 3 | 99 | 5.089e-08 | 4.5223e-07 | 5.1404e-08 | 4.5679e-07
600 | feeder2_line75 | 1 | 266.4 | 1.7678 | 1.7679 | 0.6636 | 0.66361
600 | feeder2_line75 | 2 | 266.4 | 0.88981 | 0.88984 | 0.33401 | 0.33403
600 | feeder2_line75 | 3 | 266.4 | 3.4366 | 3.4366 | 1.29 | 1.29
600 | feeder2_line76 | 1 | 99 | 1.7679 | 1.7679 | 1.7857 | 1.7857
600 | feeder2_line76 | 2 | 99 | 8.4888e-07 | 1.5849e-06 | 8.5745e-07 | 1.601e-06
600 | feeder2_line76 | 3 | 99 | 8.3705e-07 | 1.564e-06 | 8.4551e-07 | 1.5798e-06
600 | feeder2_line77 | 1 | 99 | 2.4394e-08 | 5.7693e-07 | 2.464e-08 | 5.8275e-07
600 | feeder2_line77 | 2 | 99 | 2.478e-08 | 5.7588e-07 | 2.5031e-08 | 5.817e-07
600 | feeder2_line77 | 3 | 99 | 3.4367 | 3.4366 | 3.4714 | 3.4713
600 | feeder2_line78 | 1 | 266.4 | 1.2327e-11 | 9.5604e-07 | 4.6274e-12 | 3.5887e-07
600 | feeder2_line78 | 2 | 266.4 | 0.88984 | 0.88984 | 0.33403 | 0.33403
600 | feeder2_line78 | 3 | 266.4 | 9.078e-12 | 9.4352e-07 | 3.4077e-12 | 3.5417e-07
600 | feeder2_line79 | 1 | 354.6 | 3.0646 | 3.0642 | 0.86424 | 0.86413
600 | feeder2_line79 | 2 | 354.6 | 5.5004 | 5.5 | 1.5512 | 1.551
600 | feeder2_line79 | 3 | 354.6 | 17.3518 | 17.3514 | 4.8933 | 4.8932
600 | feeder2_line80 | 1 | 354.6 | 90.4988 | 90.5021 | 25.5214 | 25.5223
600 | feeder2_line80 | 2 | 354.6 | 89.0905 | 89.0899 | 25.1242 | 25.1241
600 | feeder2_line80 | 3 | 354.6 | 69.016 | 69.0113 | 19.4631 | 19.4617
600 | feeder2_line81 | 1 | 354.6 | 90.4987 | 90.5021 | 25.5214 | 25.5223
600 | feeder2_line81 | 2 | 354.6 | 89.0904 | 89.0899 | 25.1242 | 25.1241
600 | feeder2_line81 | 3 | 354.6 | 69.0812 | 69.0766 | 19.4815 | 19.4802
600 | feeder2_line82 | 1 | 354.6 | 3.8031e-11 | 7.3652e-07 | 1.0725e-11 | 2.077e-07
600 | feeder2_line82 | 2 | 354.6 | 1.0741e-11 | 7.3518e-07 | 3.029e-12 | 2.0733e-07
600 | feeder2_line82 | 3 | 354.6 | 0.070651 | 0.070647 | 0.019924 | 0.019923
600 | feeder2_line83 | 1 | 354.6 | 90.4989 | 90.5021 | 25.5214 | 25.5223
600 | feeder2_line83 | 2 | 354.6 | 89.7526 | 89.7518 | 25.3109 | 25.3107
600 | feeder2_line83 | 3 | 354.6 | 69.0814 | 69.0766 | 19.4815 | 19.4802
600 | feeder2_line84 | 1 | 354.6 | 2.1873e-11 | 1.3019e-06 | 6.1684e-12 | 3.6715e-07
600 | feeder2_line84 | 2 | 354.6 | 3.2748 | 3.2749 | 0.92353 | 0.92355
600 | feeder2_line84 | 3 | 354.6 | 1.6883e-11 | 1.2817e-06 | 4.761e-12 | 3.6144e-07
600 | feeder2_line85 | 1 | 99 | 1.4518 | 1.4518 | 1.4665 | 1.4665
600 | feeder2_line85 | 2 | 99 | 4.9593e-08 | 4.6394e-07 | 5.0094e-08 | 4.6862e-07
600 | feeder2_line85 | 3 | 99 | 5.1137e-08 | 4.5701e-07 | 5.1653e-08 | 4.6162e-07
600 | feeder2_line86 | 1 | 354.6 | 91.1726 | 91.1756 | 25.7114 | 25.7123
600 | feeder2_line86 | 2 | 354.6 | 89.7527 | 89.7518 | 25.311 | 25.3107
600 | feeder2_line86 | 3 | 354.6 | 69.0815 | 69.0766 | 19.4815 | 19.4802
600 | feeder2_line87 | 1 | 354.6 | 91.1728 | 91.1756 | 25.7114 | 25.7123
600 | feeder2_line87 | 2 | 354.6 | 90.4119 | 90.4108 | 25.4969 | 25.4966
600 | feeder2_line87 | 3 | 354.6 | 69.1587 | 69.1537 | 19.5033 | 19.5019
600 | feeder2_line88 | 1 | 354.6 | 0.00011964 | 3.3776e-06 | 3.374e-05 | 9.525e-07
600 | feeder2_line88 | 2 | 354.6 | 2.774 | 2.774 | 0.78228 | 0.78228
600 | feeder2_line88 | 3 | 354.6 | 0.083109 | 0.082976 | 0.023437 | 0.0234
600 | feeder2_line89 | 1 | 354.6 | 91.1705 | 91.1757 | 25.7108 | 25.7123
600 | feeder2_line89 | 2 | 354.6 | 92.6074 | 92.6084 | 26.116 | 26.1163
600 | feeder2_line89 | 3 | 354.6 | 69.1566 | 69.1537 | 19.5027 | 19.5019
600 | feeder2_line90 | 1 | 354.6 | 0.0007323 | 2.0375e-06 | 0.00020651 | 5.7458e-07
600 | feeder2_line90 | 2 | 354.6 | 4.2186 | 4.2187 | 1.1897 | 1.1897
600 | feeder2_line90 | 3 | 354.6 | 0.00070886 | 2.0052e-06 | 0.0001999 | 5.6549e-07
600 | feeder2_line91 | 1 | 354.6 | 91.1704 | 91.1757 | 25.7108 | 25.7123
600 | feeder2_line91 | 2 | 354.6 | 92.6074 | 92.6084 | 26.116 | 26.1163
600 | feeder2_line91 | 3 | 354.6 | 80.0491 | 80.0463 | 22.5745 | 22.5737
600 | feeder2_line92 | 1 | 354.6 | 1.0351e-11 | 1.028e-06 | 2.919e-12 | 2.899e-07
600 | feeder2_line92 | 2 | 354.6 | 1.2375e-11 | 1.026e-06 | 3.4899e-12 | 2.8933e-07
600 | feeder2_line92 | 3 | 354.6 | 11.9611 | 11.9612 | 3.3731 | 3.3731
600 | feeder2_line93 | 1 | 99 | 2.4337e-08 | 3.4338e-07 | 2.4583e-08 | 3.4685e-07
600 | feeder2_line93 | 2 | 99 | 3.2758 | 3.2759 | 3.3089 | 3.3089
600 | feeder2_line93 | 3 | 99 | 2.5604e-08 | 3.3726e-07 | 2.5863e-08 | 3.4066e-07
600 | feeder2_line94 | 1 | 354.6 | 2.4346e-06 | 1.6706e-06 | 6.8658e-07 | 4.7111e-07
600 | feeder2_line94 | 2 | 354.6 | 1.391 | 1.391 | 0.39227 | 0.39227
600 | feeder2_line94 | 3 | 354.6 | 2.5603e-06 | 1.6436e-06 | 7.2203e-07 | 4.635e-07
600 | feeder2_line95 | 1 | 99 | 3.5835e-06 | 2.6193e-06 | 3.6197e-06 | 2.6457e-06
600 | feeder2_line95 | 2 | 99 | 2.7739 | 2.774 | 2.802 | 2.802
600 | feeder2_line95 | 3 | 99 | 3.5041e-06 | 2.5734e-06 | 3.5395e-06 | 2.5994e-06
600 | feeder2_line96 | 1 | 354.6 | 0.00012177 | 6.2422e-07 | 3.4339e-05 | 1.7604e-07
600 | feeder2_line96 | 2 | 354.6 | 0.00012124 | 6.2305e-07 | 3.4191e-05 | 1.757e-07
600 | feeder2_line96 | 3 | 354.6 | 0.083095 | 0.082976 | 0.023434 | 0.0234
600 | feeder2_line97 | 1 | 354.6 | 91.9585 | 91.9634 | 25.933 | 25.9344
600 | feeder2_line97 | 2 | 354.6 | 92.6076 | 92.6084 | 26.1161 | 26.1163
600 | feeder2_line97 | 3 | 354.6 | 80.0492 | 80.0463 | 22.5745 | 22.5737
600 | feeder2_line98 | 1 | 354.6 | 0.82867 | 0.82697 | 0.23369 | 0.23321
600 | feeder2_line98 | 2 | 354.6 | 0.0016887 | 6.2142e-07 | 0.00047622 | 1.7524e-07
600 | feeder2_line98 | 3 | 354.6 | 0.0016637 | 6.1374e-07 | 0.00046918 | 1.7308e-07
600 | feeder2_line99 | 1 | 99 | 2.4347e-08 | 4.4886e-07 | 2.4592e-08 | 4.534e-07
600 | feeder2_line99 | 2 | 99 | 2.4799e-08 | 4.4779e-07 | 2.5049e-08 | 4.5231e-07
600 | feeder2_line99 | 3 | 99 | 0.083005 | 0.082976 | 0.083844 | 0.083814
600 | feeder2_line100 | 1 | 99 | 0.82696 | 0.82697 | 0.83531 | 0.83532
600 | feeder2_line100 | 2 | 99 | 2.4804e-08 | 6.1499e-07 | 2.5054e-08 | 6.212e-07
600 | feeder2_line100 | 3 | 99 | 2.5615e-08 | 6.0542e-07 | 2.5874e-08 | 6.1154e-07
600 | feeder2_line101 | 1 | 354.6 | 1.3941 | 1.3937 | 0.39314 | 0.39303
600 | feeder2_line101 | 2 | 354.6 | 5.5004 | 5.5 | 1.5512 | 1.551
600 | feeder2_line101 | 3 | 354.6 | 17.3518 | 17.3514 | 4.8933 | 4.8932
600 | feeder2_line102 | 1 | 99 | 1.6705 | 1.6705 | 1.6874 | 1.6874
600 | feeder2_line102 | 2 | 99 | 2.3313e-06 | 8.7917e-07 | 2.3549e-06 | 8.8805e-07
600 | feeder2_line102 | 3 | 99 | 2.287e-06 | 8.6607e-07 | 2.3101e-06 | 8.7482e-07
600 | feeder2_line103 | 1 | 99 | 5.5187e-07 | 8.065e-07 | 5.5745e-07 | 8.1465e-07
600 | feeder2_line103 | 2 | 99 | 1.5876 | 1.5876 | 1.6036 | 1.6036
600 | feeder2_line103 | 3 | 99 | 5.4064e-07 | 7.9265e-07 | 5.4611e-07 | 8.0066e-07
600 | feeder2_line104 | 1 | 354.6 | 1.394 | 1.3937 | 0.39312 | 0.39303
600 | feeder2_line104 | 2 | 354.6 | 3.9128 | 3.9125 | 1.1034 | 1.1034
600 | feeder2_line104 | 3 | 354.6 | 17.3517 | 17.3514 | 4.8933 | 4.8932
600 | feeder2_line105 | 1 | 99 | 2.5647e-06 | 7.4209e-07 | 2.5906e-06 | 7.4959e-07
600 | feeder2_line105 | 2 | 99 | 2.5527e-06 | 7.4045e-07 | 2.5784e-06 | 7.4793e-07
600 | feeder2_line105 | 3 | 99 | 0.040893 | 0.040866 | 0.041306 | 0.041279
600 | feeder2_line106 | 1 | 354.6 | 1.3939 | 1.3937 | 0.3931 | 0.39303
600 | feeder2_line106 | 2 | 354.6 | 3.9127 | 3.9125 | 1.1034 | 1.1034
600 | feeder2_line106 | 3 | 354.6 | 17.3117 | 17.3116 | 4.882 | 4.882
600 | feeder2_line107 | 1 | 99 | 3.2461e-07 | 9.0436e-07 | 3.2789e-07 | 9.1349e-07
600 | feeder2_line107 | 2 | 99 | 0.084719 | 0.084727 | 0.085575 | 0.085583
600 | feeder2_line107 | 3 | 99 | 3.2137e-07 | 8.886e-07 | 3.2462e-07 | 8.9758e-07
600 | feeder2_line108 | 1 | 354.6 | 1.3939 | 1.3937 | 0.3931 | 0.39303
600 | feeder2_line108 | 2 | 354.6 | 3.828 | 3.8278 | 1.0795 | 1.0795
600 | feeder2_line108 | 3 | 354.6 | 17.3117 | 17.3116 | 4.882 | 4.882
600 | feeder2_line109 | 1 | 354.6 | 93.4623 | 93.466 | 26.3571 | 26.3582
600 | feeder2_line109 | 2 | 354.6 | 92.6087 | 92.6084 | 26.1164 | 26.1163
600 | feeder2_line109 | 3 | 354.6 | 80.0503 | 80.0463 | 22.5748 | 22.5737
600 | feeder2_line110 | 1 | 99 | 1.5693 | 1.5685 | 1.5851 | 1.5843
600 | feeder2_line110 | 2 | 99 | 0.00080696 | 9.1122e-07 | 0.00081511 | 9.2043e-07
600 | feeder2_line110 | 3 | 99 | 0.00078761 | 8.9616e-07 | 0.00079557 | 9.0521e-07
600 | feeder2_line111 | 1 | 99 | 2.4341e-08 | 3.8335e-07 | 2.4587e-08 | 3.8723e-07
600 | feeder2_line111 | 2 | 99 | 1.4603 | 1.4603 | 1.475 | 1.475
600 | feeder2_line111 | 3 | 99 | 2.5585e-08 | 3.7666e-07 | 2.5844e-08 | 3.8046e-07
600 | feeder2_line112 | 1 | 99 | 3.2484e-07 | 9.2124e-07 | 3.2812e-07 | 9.3054e-07
600 | feeder2_line112 | 2 | 99 | 1.3137 | 1.3137 | 1.3269 | 1.327
600 | feeder2_line112 | 3 | 99 | 3.2161e-07 | 9.0513e-07 | 3.2486e-07 | 9.1427e-07
600 | feeder2_line113 | 1 | 99 | 0.096775 | 0.096778 | 0.097753 | 0.097756
600 | feeder2_line113 | 2 | 99 | 3.2509e-07 | 9.07e-07 | 3.2838e-07 | 9.1616e-07
600 | feeder2_line113 | 3 | 99 | 3.2178e-07 | 8.9276e-07 | 3.2503e-07 | 9.0178e-07
600 | feeder2_line114 | 1 | 99 | 1.5893 | 1.5893 | 1.6054 | 1.6054
600 | feeder2_line114 | 2 | 99 | 2.4786e-08 | 4.3717e-07 | 2.5036e-08 | 4.4159e-07
600 | feeder2_line114 | 3 | 99 | 2.5548e-08 | 4.3066e-07 | 2.5806e-08 | 4.3501e-07
600 | feeder2_line115 | 1 | 99 | 2.4338e-08 | 5.6438e-07 | 2.4584e-08 | 5.7008e-07
600 | feeder2_line115 | 2 | 99 | 1.0914 | 1.0914 | 1.1025 | 1.1025
600 | feeder2_line115 | 3 | 99 | 2.5566e-08 | 5.5443e-07 | 2.5824e-08 | 5.6003e-07
600 | feeder2_line116 | 1 | 354.6 | 1.3939 | 1.3937 | 0.3931 | 0.39303
600 | feeder2_line116 | 2 | 354.6 | 2.7777 | 2.7775 | 0.78334 | 0.78327
600 | feeder2_line116 | 3 | 354.6 | 17.3117 | 17.3116 | 4.882 | 4.882
600 | feeder2_line117 | 1 | 99 | 4.8701e-08 | 6.4569e-07 | 4.9193e-08 | 6.5222e-07
600 | feeder2_line117 | 2 | 99 | 1.4743 | 1.4743 | 1.4892 | 1.4892
600 | feeder2_line117 | 3 | 99 | 5.1298e-08 | 6.3383e-07 | 5.1816e-08 | 6.4023e-07
600 | feeder2_line118 | 1 | 354.6 | 93.4623 | 93.466 | 26.3571 | 26.3582
600 | feeder2_line118 | 2 | 354.6 | 93.0704 | 93.0701 | 26.2466 | 26.2465
600 | feeder2_line118 | 3 | 354.6 | 80.0503 | 80.0463 | 22.5748 | 22.5737
600 | feeder2_line119 | 1 | 99 | 2.4329e-08 | 6.0731e-07 | 2.4574e-08 | 6.1344e-07
600 | feeder2_line119 | 2 | 99 | 2.4765e-08 | 6.0597e-07 | 2.5015e-08 | 6.1209e-07
600 | feeder2_line119 | 3 | 99 | 1.9241 | 1.924 | 1.9435 | 1.9435
600 | feeder2_line120 | 1 | 354.6 | 1.3939 | 1.3937 | 0.3931 | 0.39303
600 | feeder2_line120 | 2 | 354.6 | 2.7777 | 2.7775 | 0.78334 | 0.78327
600 | feeder2_line120 | 3 | 354.6 | 15.4116 | 15.4114 | 4.3462 | 4.3461
600 | feeder2_line121 | 1 | 99 | 3.2461e-07 | 9.4046e-07 | 3.2789e-07 | 9.4996e-07
600 | feeder2_line121 | 2 | 99 | 0.043951 | 0.043951 | 0.044395 | 0.044395
600 | feeder2_line121 | 3 | 99 | 3.2122e-07 | 9.2343e-07 | 3.2447e-07 | 9.3276e-07
600 | feeder2_line122 | 1 | 354.6 | 1.3939 | 1.3937 | 0.3931 | 0.39303
600 | feeder2_line122 | 2 | 354.6 | 2.734 | 2.7337 | 0.771 | 0.77094
600 | feeder2_line122 | 3 | 354.6 | 15.4115 | 15.4114 | 4.3462 | 4.3461
600 | feeder2_line123 | 1 | 99 | 5.7627e-07 | 9.7454e-07 | 5.8209e-07 | 9.8438e-07
600 | feeder2_line123 | 2 | 99 | 5.7498e-07 | 9.7241e-07 | 5.8078e-07 | 9.8224e-07
600 | feeder2_line123 | 3 | 99 | 0.078442 | 0.07844 | 0.079234 | 0.079232
600 | feeder2_line124 | 1 | 354.6 | 1.3938 | 1.3937 | 0.39307 | 0.39303
600 | feeder2_line124 | 2 | 354.6 | 2.7339 | 2.7338 | 0.77098 | 0.77094
600 | feeder2_line124 | 3 | 354.6 | 15.336 | 15.3359 | 4.3249 | 4.3249
600 | feeder2_line125 | 1 | 99 | 5.7627e-07 | 9.0594e-07 | 5.8209e-07 | 9.1509e-07
600 | feeder2_line125 | 2 | 99 | 5.7499e-07 | 9.0397e-07 | 5.8079e-07 | 9.131e-07
600 | feeder2_line125 | 3 | 99 | 0.8176 | 0.81757 | 0.82586 | 0.82583
600 | feeder2_line126 | 1 | 354.6 | 1.394 | 1.3937 | 0.39312 | 0.39303
600 | feeder2_line126 | 2 | 354.6 | 2.7341 | 2.7338 | 0.77103 | 0.77094
600 | feeder2_line126 | 3 | 354.6 | 14.5374 | 14.5372 | 4.0997 | 4.0996
600 | feeder2_line127 | 1 | 99 | 5.7628e-07 | 1.0846e-06 | 5.821e-07 | 1.0955e-06
600 | feeder2_line127 | 2 | 99 | 5.7499e-07 | 1.0822e-06 | 5.808e-07 | 1.0931e-06
600 | feeder2_line127 | 3 | 99 | 1.4608 | 1.4608 | 1.4755 | 1.4756
600 | feeder2_line128 | 1 | 354.6 | 1.3939 | 1.3937 | 0.39309 | 0.39303
600 | feeder2_line128 | 2 | 354.6 | 2.734 | 2.7338 | 0.77101 | 0.77094
600 | feeder2_line128 | 3 | 354.6 | 13.4372 | 13.4371 | 3.7894 | 3.7894
600 | feeder2_line129 | 1 | 99 | 5.5198e-07 | 8.7942e-07 | 5.5755e-07 | 8.8831e-07
600 | feeder2_line129 | 2 | 99 | 2.7338 | 2.7338 | 2.7614 | 2.7614
600 | feeder2_line129 | 3 | 99 | 5.3993e-07 | 8.6321e-07 | 5.4538e-07 | 8.7193e-07
600 | feeder2_line130 | 1 | 354.6 | 1.3939 | 1.3937 | 0.3931 | 0.39303
600 | feeder2_line130 | 2 | 354.6 | 0.00031034 | 4.6432e-06 | 8.7518e-05 | 1.3094e-06
600 | feeder2_line130 | 3 | 354.6 | 13.4372 | 13.4371 | 3.7894 | 3.7894
600 | feeder2_line131 | 1 | 99 | 5.7626e-07 | 9.747e-07 | 5.8208e-07 | 9.8455e-07
600 | feeder2_line131 | 2 | 99 | 5.7499e-07 | 9.7261e-07 | 5.808e-07 | 9.8243e-07
600 | feeder2_line131 | 3 | 99 | 12.261 | 12.2611 | 12.3848 | 12.385
600 | feeder2_line132 | 1 | 354.6 | 1.3938 | 1.3937 | 0.39305 | 0.39303
600 | feeder2_line132 | 2 | 354.6 | 0.00012603 | 2.9191e-06 | 3.5541e-05 | 8.2322e-07
600 | feeder2_line132 | 3 | 354.6 | 1.4532 | 1.4531 | 0.40982 | 0.40978
600 | feeder2_line133 | 1 | 99 | 1.3937 | 1.3937 | 1.4078 | 1.4078
600 | feeder2_line133 | 2 | 99 | 2.9987e-07 | 9.8039e-07 | 3.029e-07 | 9.9029e-07
600 | feeder2_line133 | 3 | 99 | 2.9553e-07 | 9.6428e-07 | 2.9852e-07 | 9.7402e-07
600 | feeder2_line134 | 1 | 354.6 | 1.4052e-11 | 1.7904e-06 | 3.9628e-12 | 5.049e-07
600 | feeder2_line134 | 2 | 354.6 | 7.7977e-12 | 1.7874e-06 | 2.199e-12 | 5.0406e-07
600 | feeder2_line134 | 3 | 354.6 | 1.4531 | 1.4531 | 0.40978 | 0.40978
600 | feeder2_line135 | 1 | 99 | 0.052368 | 0.052387 | 0.052897 | 0.052916
600 | feeder2_line135 | 2 | 99 | 4.9654e-08 | 5.8711e-07 | 5.0155e-08 | 5.9304e-07
600 | feeder2_line135 | 3 | 99 | 5.134e-08 | 5.7762e-07 | 5.1859e-08 | 5.8346e-07
600 | feeder2_line136 | 1 | 354.6 | 93.513 | 93.5168 | 26.3714 | 26.3725
600 | feeder2_line136 | 2 | 354.6 | 93.0704 | 93.0701 | 26.2466 | 26.2465
600 | feeder2_line136 | 3 | 354.6 | 80.0503 | 80.0463 | 22.5748 | 22.5737
600 | feeder2_line137 | 1 | 99 | 1.0202 | 1.0203 | 1.0306 | 1.0306
600 | feeder2_line137 | 2 | 99 | 8.5224e-07 | 1.5814e-06 | 8.6085e-07 | 1.5974e-06
600 | feeder2_line137 | 3 | 99 | 8.3764e-07 | 1.5558e-06 | 8.461e-07 | 1.5715e-06
600 | feeder2_line138 | 1 | 354.6 | 94.4909 | 94.4946 | 26.6472 | 26.6482
600 | feeder2_line138 | 2 | 354.6 | 93.0704 | 93.0701 | 26.2466 | 26.2465
600 | feeder2_line138 | 3 | 354.6 | 80.0503 | 80.0463 | 22.5748 | 22.5737
600 | feeder2_line139 | 1 | 99 | 4.8706e-08 | 4.9403e-07 | 4.9198e-08 | 4.9902e-07
600 | feeder2_line139 | 2 | 99 | 4.9651e-08 | 4.928e-07 | 5.0153e-08 | 4.9778e-07
600 | feeder2_line139 | 3 | 99 | 19.9648 | 19.9647 | 20.1665 | 20.1664
600 | feeder2_line140 | 1 | 354.6 | 94.491 | 94.4946 | 26.6472 | 26.6482
600 | feeder2_line140 | 2 | 354.6 | 93.0705 | 93.0701 | 26.2466 | 26.2465
600 | feeder2_line140 | 3 | 354.6 | 98.5267 | 98.5226 | 27.7853 | 27.7841
600 | feeder2_line141 | 1 | 99 | 2.5496e-06 | 4.8875e-07 | 2.5753e-06 | 4.9368e-07
600 | feeder2_line141 | 2 | 99 | 1.6624 | 1.6624 | 1.6792 | 1.6792
600 | feeder2_line141 | 3 | 99 | 2.476e-06 | 4.7958e-07 | 2.5011e-06 | 4.8442e-07
600 | feeder2_line142 | 1 | 354.6 | 94.4908 | 94.4946 | 26.6472 | 26.6482
600 | feeder2_line142 | 2 | 354.6 | 94.0893 | 94.089 | 26.5339 | 26.5338
600 | feeder2_line142 | 3 | 354.6 | 98.5266 | 98.5226 | 27.7853 | 27.7841
600 | feeder2_line143 | 1 | 99 | 8.5503e-07 | 1.7368e-06 | 8.6366e-07 | 1.7543e-06
600 | feeder2_line143 | 2 | 99 | 0.084484 | 0.084495 | 0.085338 | 0.085348
600 | feeder2_line143 | 3 | 99 | 8.379e-07 | 1.7042e-06 | 8.4637e-07 | 1.7214e-06
600 | feeder2_line144 | 1 | 354.6 | 94.4906 | 94.4946 | 26.6471 | 26.6482
600 | feeder2_line144 | 2 | 354.6 | 94.1709 | 94.1708 | 26.5569 | 26.5569
600 | feeder2_line144 | 3 | 354.6 | 98.5264 | 98.5226 | 27.7852 | 27.7841
600 | feeder2_line145 | 1 | 99 | 2.4368e-08 | 4.8701e-07 | 2.4614e-08 | 4.9193e-07
600 | feeder2_line145 | 2 | 99 | 0.069329 | 0.069329 | 0.07003 | 0.070029
600 | feeder2_line145 | 3 | 99 | 2.5689e-08 | 4.7789e-07 | 2.5949e-08 | 4.8271e-07
600 | feeder2_line146 | 1 | 354.6 | 94.4905 | 94.4946 | 26.6471 | 26.6482
600 | feeder2_line146 | 2 | 354.6 | 94.2382 | 94.2382 | 26.5759 | 26.5759
600 | feeder2_line146 | 3 | 354.6 | 98.5263 | 98.5226 | 27.7852 | 27.7841
600 | feeder2_line147 | 1 | 99 | 1.4731 | 1.4731 | 1.488 | 1.488
600 | feeder2_line147 | 2 | 99 | 1.1534e-06 | 2.2407e-06 | 1.1651e-06 | 2.2633e-06
600 | feeder2_line147 | 3 | 99 | 1.1345e-06 | 2.2043e-06 | 1.146e-06 | 2.2266e-06
600 | feeder2_line148 | 1 | 99 | 0.084169 | 0.084174 | 0.085019 | 0.085024
600 | feeder2_line148 | 2 | 99 | 6.0154e-07 | 1.5015e-06 | 6.0761e-07 | 1.5166e-06
600 | feeder2_line148 | 3 | 99 | 5.9294e-07 | 1.4771e-06 | 5.9893e-07 | 1.492e-06
600 | feeder2_line149 | 1 | 354.6 | 95.9876 | 95.9915 | 27.0692 | 27.0704
600 | feeder2_line149 | 2 | 354.6 | 94.2384 | 94.2382 | 26.576 | 26.5759
600 | feeder2_line149 | 3 | 354.6 | 98.5264 | 98.5226 | 27.7852 | 27.7841
600 | feeder2_line150 | 1 | 354.6 | 95.9876 | 95.9915 | 27.0693 | 27.0704
600 | feeder2_line150 | 2 | 354.6 | 96.6474 | 96.6471 | 27.2553 | 27.2553
600 | feeder2_line150 | 3 | 354.6 | 98.5265 | 98.5226 | 27.7853 | 27.7841
600 | feeder2_line151 | 1 | 99 | 9.8735e-06 | 1.7881e-06 | 9.9732e-06 | 1.8062e-06
600 | feeder2_line151 | 2 | 99 | 2.4769 | 2.4769 | 2.5019 | 2.5019
600 | feeder2_line151 | 3 | 99 | 9.5571e-06 | 1.7546e-06 | 9.6536e-06 | 1.7723e-06
600 | feeder2_line152 | 1 | 354.6 | 1.0972e-11 | 1.1909e-06 | 3.0943e-12 | 3.3584e-07
600 | feeder2_line152 | 2 | 354.6 | 7.5419e-12 | 1.1884e-06 | 2.1269e-12 | 3.3515e-07
600 | feeder2_line152 | 3 | 354.6 | 1.1791 | 1.1791 | 0.33251 | 0.3325
600 | feeder2_line153 | 1 | 99 | 0.043536 | 0.043538 | 0.043976 | 0.043977
600 | feeder2_line153 | 2 | 99 | 4.9719e-08 | 5.9476e-07 | 5.0221e-08 | 6.0077e-07
600 | feeder2_line153 | 3 | 99 | 5.1418e-08 | 5.8512e-07 | 5.1937e-08 | 5.9103e-07
600 | feeder2_line154 | 1 | 99 | 5.7865e-07 | 8.8728e-07 | 5.8449e-07 | 8.9625e-07
600 | feeder2_line154 | 2 | 99 | 5.7714e-07 | 8.8503e-07 | 5.8297e-07 | 8.9397e-07
600 | feeder2_line154 | 3 | 99 | 0.041348 | 0.041316 | 0.041765 | 0.041733
600 | feeder2_line155 | 1 | 99 | 96.0295 | 96.0334 | 96.9995 | 97.0034
600 | feeder2_line155 | 2 | 99 | 96.6473 | 96.6471 | 97.6236 | 97.6234
600 | feeder2_line155 | 3 | 99 | 99 | 98.9961 | 100 | 99.9961
600 | feeder2_line156 | 1 | 99 | 6.0282e-07 | 1.1676e-06 | 6.0891e-07 | 1.1794e-06
600 | feeder2_line156 | 2 | 99 | 1.5888 | 1.5888 | 1.6049 | 1.6049
600 | feeder2_line156 | 3 | 99 | 5.9318e-07 | 1.1457e-06 | 5.9917e-07 | 1.1573e-06
600 | feeder2_line157 | 1 | 99 | 2.438e-08 | 2.5349e-07 | 2.4626e-08 | 2.5605e-07
600 | feeder2_line157 | 2 | 99 | 0.89088 | 0.89088 | 0.89988 | 0.89988
600 | feeder2_line157 | 3 | 99 | 2.5699e-08 | 2.4874e-07 | 2.5959e-08 | 2.5125e-07
630 | feeder2_line1 | 1 | 354.6 | 28.5243 | 28.5192 | 8.0441 | 8.0426
630 | feeder2_line1 | 2 | 354.6 | 34.7344 | 34.74 | 9.7954 | 9.797
630 | feeder2_line1 | 3 | 354.6 | 40.6981 | 40.6996 | 11.4772 | 11.4776
630 | feeder2_line2 | 1 | 354.6 | 29.1027 | 29.0974 | 8.2072 | 8.2057
630 | feeder2_line2 | 2 | 354.6 | 34.7346 | 34.74 | 9.7954 | 9.797
630 | feeder2_line2 | 3 | 354.6 | 40.6983 | 40.6996 | 11.4772 | 11.4776
630 | feeder2_line3 | 1 | 80.1 | 1.249 | 1.2491 | 1.5593 | 1.5594
630 | feeder2_line3 | 2 | 80.1 | 5.715e-07 | 1.0561e-06 | 7.1348e-07 | 1.3185e-06
630 | feeder2_line3 | 3 | 80.1 | 5.7187e-07 | 1.0568e-06 | 7.1394e-07 | 1.3193e-06
630 | feeder2_line4 | 1 | 354.6 | 29.1029 | 29.0974 | 8.2072 | 8.2057
630 | feeder2_line4 | 2 | 354.6 | 34.8243 | 34.8296 | 9.8207 | 9.8222
630 | feeder2_line4 | 3 | 354.6 | 40.6984 | 40.6996 | 11.4773 | 11.4776
630 | feeder2_line5 | 1 | 80.1 | 5.7136e-07 | 9.9698e-07 | 7.1331e-07 | 1.2447e-06
630 | feeder2_line5 | 2 | 80.1 | 0.090138 | 0.090139 | 0.11253 | 0.11253
630 | feeder2_line5 | 3 | 80.1 | 5.719e-07 | 9.9791e-07 | 7.1398e-07 | 1.2458e-06
630 | feeder2_line6 | 1 | 80.1 | 5.7138e-07 | 1.1729e-06 | 7.1334e-07 | 1.4642e-06
630 | feeder2_line6 | 2 | 80.1 | 5.7154e-07 | 1.1732e-06 | 7.1354e-07 | 1.4647e-06
630 | feeder2_line6 | 3 | 80.1 | 0.085368 | 0.085374 | 0.10658 | 0.10658
630 | feeder2_line7 | 1 | 354.6 | 29.103 | 29.0974 | 8.2073 | 8.2057
630 | feeder2_line7 | 2 | 354.6 | 34.8244 | 34.8296 | 9.8208 | 9.8222
630 | feeder2_line7 | 3 | 354.6 | 40.7839 | 40.7849 | 11.5014 | 11.5017
630 | feeder2_line8 | 1 | 80.1 | 19.0869 | 19.0871 | 23.8288 | 23.829
630 | feeder2_line8 | 2 | 80.1 | 5.7158e-07 | 1.1313e-06 | 7.1358e-07 | 1.4124e-06
630 | feeder2_line8 | 3 | 80.1 | 5.7203e-07 | 1.1322e-06 | 7.1415e-07 | 1.4135e-06
630 | feeder2_line9 | 1 | 354.6 | 48.0371 | 48.0316 | 13.5469 | 13.5453
630 | feeder2_line9 | 2 | 354.6 | 34.8245 | 34.8296 | 9.8208 | 9.8222
630 | feeder2_line9 | 3 | 354.6 | 40.7839 | 40.7849 | 11.5014 | 11.5017
630 | feeder2_line10 | 1 | 80.1 | 8.4468e-07 | 1.4934e-06 | 1.0545e-06 | 1.8644e-06
630 | feeder2_line10 | 2 | 80.1 | 19.0911 | 19.0911 | 23.8341 | 23.8341
630 | feeder2_line10 | 3 | 80.1 | 8.4562e-07 | 1.495e-06 | 1.0557e-06 | 1.8664e-06
630 | feeder2_line11 | 1 | 354.6 | 48.0371 | 48.0316 | 13.5468 | 13.5453
630 | feeder2_line11 | 2 | 354.6 | 53.6753 | 53.6804 | 15.1369 | 15.1383
630 | feeder2_line11 | 3 | 354.6 | 40.7839 | 40.7849 | 11.5014 | 11.5017
630 | feeder2_line12 | 1 | 80.1 | 5.4661e-07 | 9.9071e-07 | 6.8241e-07 | 1.2368e-06
630 | feeder2_line12 | 2 | 80.1 | 5.4685e-07 | 9.9103e-07 | 6.8271e-07 | 1.2372e-06
630 | feeder2_line12 | 3 | 80.1 | 9.2287 | 9.2287 | 11.5215 | 11.5215
630 | feeder2_line13 | 1 | 354.6 | 48.0371 | 48.0316 | 13.5468 | 13.5453
630 | feeder2_line13 | 2 | 354.6 | 53.6753 | 53.6804 | 15.1369 | 15.1383
630 | feeder2_line13 | 3 | 354.6 | 49.8821 | 49.8831 | 14.0671 | 14.0674
630 | feeder2_line14 | 1 | 80.1 | 1.8509 | 1.8509 | 2.3107 | 2.3107
630 | feeder2_line14 | 2 | 80.1 | 2.983e-07 | 6.4631e-07 | 3.7241e-07 | 8.0687e-07
630 | feeder2_line14 | 3 | 80.1 | 2.985e-07 | 6.4676e-07 | 3.7266e-07 | 8.0744e-07
630 | feeder2_line15 | 1 | 354.6 | 49.5209 | 49.5154 | 13.9653 | 13.9637
630 | feeder2_line15 | 2 | 354.6 | 53.6753 | 53.6804 | 15.1369 | 15.1383
630 | feeder2_line15 | 3 | 354.6 | 49.8821 | 49.8831 | 14.0672 | 14.0674
630 | feeder2_line16 | 1 | 80.1 | 5.7164e-07 | 1.0298e-06 | 7.1366e-07 | 1.2857e-06
630 | feeder2_line16 | 2 | 80.1 | 0.028891 | 0.02889 | 0.036069 | 0.036067
630 | feeder2_line16 | 3 | 80.1 | 5.7224e-07 | 1.0309e-06 | 7.144e-07 | 1.287e-06
630 | feeder2_line17 | 1 | 354.6 | 49.5209 | 49.5154 | 13.9653 | 13.9637
630 | feeder2_line17 | 2 | 354.6 | 53.7042 | 53.7093 | 15.145 | 15.1464
630 | feeder2_line17 | 3 | 354.6 | 49.8821 | 49.8831 | 14.0672 | 14.0674
630 | feeder2_line18 | 1 | 80.1 | 5.4708e-07 | 7.3762e-07 | 6.8299e-07 | 9.2087e-07
630 | feeder2_line18 | 2 | 80.1 | 5.4737e-07 | 7.3793e-07 | 6.8336e-07 | 9.2126e-07
630 | feeder2_line18 | 3 | 80.1 | 0.26582 | 0.26583 | 0.33187 | 0.33188
630 | feeder2_line19 | 1 | 354.6 | 49.5209 | 49.5154 | 13.9653 | 13.9637
630 | feeder2_line19 | 2 | 354.6 | 53.7042 | 53.7093 | 15.145 | 15.1464
630 | feeder2_line19 | 3 | 354.6 | 50.1472 | 50.1481 | 14.1419 | 14.1422
630 | feeder2_line20 | 1 | 99 | 5.472e-07 | 8.8456e-07 | 5.5272e-07 | 8.935e-07
630 | feeder2_line20 | 2 | 99 | 5.4751e-07 | 8.8496e-07 | 5.5304e-07 | 8.9389e-07
630 | feeder2_line20 | 3 | 99 | 0.086006 | 0.086019 | 0.086875 | 0.086888
630 | feeder2_line21 | 1 | 354.6 | 49.5211 | 49.5154 | 13.9653 | 13.9637
630 | feeder2_line21 | 2 | 354.6 | 53.7043 | 53.7093 | 15.145 | 15.1464
630 | feeder2_line21 | 3 | 354.6 | 50.2333 | 50.2341 | 14.1662 | 14.1664
630 | feeder2_line22 | 1 | 99 | 5.7219e-07 | 1.0142e-06 | 5.7797e-07 | 1.0244e-06
630 | feeder2_line22 | 2 | 99 | 1.3266 | 1.3266 | 1.34 | 1.34
630 | feeder2_line22 | 3 | 99 | 5.7275e-07 | 1.0152e-06 | 5.7853e-07 | 1.0254e-06
630 | feeder2_line23 | 1 | 99 | 5.7219e-07 | 9.4936e-07 | 5.7797e-07 | 9.5895e-07
630 | feeder2_line23 | 2 | 99 | 5.7246e-07 | 9.4979e-07 | 5.7824e-07 | 9.5939e-07
630 | feeder2_line23 | 3 | 99 | 0.82885 | 0.82884 | 0.83722 | 0.83721
630 | feeder2_line24 | 1 | 354.6 | 49.5211 | 49.5154 | 13.9653 | 13.9637
630 | feeder2_line24 | 2 | 354.6 | 55.0227 | 55.0276 | 15.5168 | 15.5182
630 | feeder2_line24 | 3 | 354.6 | 50.7174 | 50.7181 | 14.3027 | 14.3029
630 | feeder2_line25 | 1 | 99 | 1.3268 | 1.3268 | 1.3402 | 1.3402
630 | feeder2_line25 | 2 | 99 | 4.9738e-08 | 6.9071e-07 | 5.0241e-08 | 6.9769e-07
630 | feeder2_line25 | 3 | 99 | 4.9787e-08 | 6.9103e-07 | 5.029e-08 | 6.9801e-07
630 | feeder2_line26 | 1 | 99 | 0.085329 | 0.085326 | 0.086191 | 0.086188
630 | feeder2_line26 | 2 | 99 | 5.4775e-07 | 8.5575e-07 | 5.5328e-07 | 8.644e-07
630 | feeder2_line26 | 3 | 99 | 5.4799e-07 | 8.5614e-07 | 5.5352e-07 | 8.6479e-07
630 | feeder2_line27 | 1 | 354.6 | 50.9308 | 50.9251 | 14.3629 | 14.3613
630 | feeder2_line27 | 2 | 354.6 | 55.0227 | 55.0276 | 15.5168 | 15.5182
630 | feeder2_line27 | 3 | 354.6 | 50.7174 | 50.7181 | 14.3027 | 14.3029
630 | feeder2_line28 | 1 | 99 | 2.5387e-06 | 7.1029e-07 | 2.5643e-06 | 7.1746e-07
630 | feeder2_line28 | 2 | 99 | 0.077125 | 0.077126 | 0.077904 | 0.077905
630 | feeder2_line28 | 3 | 99 | 2.5417e-06 | 7.1094e-07 | 2.5673e-06 | 7.1812e-07
630 | feeder2_line29 | 1 | 354.6 | 50.9308 | 50.9251 | 14.3629 | 14.3613
630 | feeder2_line29 | 2 | 354.6 | 55.0997 | 55.1046 | 15.5386 | 15.5399
630 | feeder2_line29 | 3 | 354.6 | 50.7174 | 50.7181 | 14.3027 | 14.3029
630 | feeder2_line30 | 1 | 266.4 | 5.2509 | 5.2506 | 1.971 | 1.971
630 | feeder2_line30 | 2 | 266.4 | 10.3511 | 10.3506 | 3.8855 | 3.8854
630 | feeder2_line30 | 3 | 266.4 | 10.8429 | 10.8427 | 4.0702 | 4.0701
630 | feeder2_line31 | 1 | 354.6 | 55.8106 | 55.8044 | 15.739 | 15.7373
630 | feeder2_line31 | 2 | 354.6 | 65.3913 | 65.3958 | 18.4409 | 18.4421
630 | feeder2_line31 | 3 | 354.6 | 61.3504 | 61.3508 | 17.3013 | 17.3014
630 | feeder2_line32 | 1 | 354.6 | 55.8106 | 55.8044 | 15.739 | 15.7373
630 | feeder2_line32 | 2 | 354.6 | 65.6033 | 65.6077 | 18.5006 | 18.5019
630 | feeder2_line32 | 3 | 354.6 | 61.3505 | 61.3508 | 17.3013 | 17.3014
630 | feeder2_line33 | 1 | 99 | 4.9908e-08 | 6.8587e-07 | 5.0412e-08 | 6.928e-07
630 | feeder2_line33 | 2 | 99 | 0.21249 | 0.21249 | 0.21463 | 0.21464
630 | feeder2_line33 | 3 | 99 | 4.9883e-08 | 6.8648e-07 | 5.0386e-08 | 6.9342e-07
630 | feeder2_line34 | 1 | 354.6 | 55.8106 | 55.8044 | 15.739 | 15.7373
630 | feeder2_line34 | 2 | 354.6 | 65.6033 | 65.6077 | 18.5006 | 18.5019
630 | feeder2_line34 | 3 | 354.6 | 62.2299 | 62.2302 | 17.5493 | 17.5494
630 | feeder2_line35 | 1 | 99 | 2.9906e-07 | 7.5962e-07 | 3.0208e-07 | 7.673e-07
630 | feeder2_line35 | 2 | 99 | 2.9924e-07 | 7.6017e-07 | 3.0226e-07 | 7.6784e-07
630 | feeder2_line35 | 3 | 99 | 0.87951 | 0.87951 | 0.88839 | 0.88839
630 | feeder2_line36 | 1 | 354.6 | 55.8387 | 55.8324 | 15.7469 | 15.7452
630 | feeder2_line36 | 2 | 354.6 | 65.6032 | 65.6077 | 18.5006 | 18.5019
630 | feeder2_line36 | 3 | 354.6 | 62.2298 | 62.2302 | 17.5493 | 17.5494
630 | feeder2_line37 | 1 | 99 | 0.028136 | 0.027998 | 0.02842 | 0.02828
630 | feeder2_line37 | 2 | 99 | 2.993e-07 | 8.4128e-07 | 3.0233e-07 | 8.4978e-07
630 | feeder2_line37 | 3 | 99 | 2.9938e-07 | 8.4143e-07 | 3.024e-07 | 8.4993e-07
630 | feeder2_line38 | 1 | 99 | 3.2386e-07 | 7.7526e-07 | 3.2713e-07 | 7.8309e-07
630 | feeder2_line38 | 2 | 99 | 0.31955 | 0.31956 | 0.32278 | 0.32278
630 | feeder2_line38 | 3 | 99 | 3.2408e-07 | 7.759e-07 | 3.2735e-07 | 7.8374e-07
630 | feeder2_line39 | 1 | 266.4 | 5.2509 | 5.2506 | 1.971 | 1.971
630 | feeder2_line39 | 2 | 266.4 | 10.0334 | 10.0329 | 3.7663 | 3.7661
630 | feeder2_line39 | 3 | 266.4 | 10.8429 | 10.8427 | 4.0702 | 4.0701
630 | feeder2_line40 | 1 | 354.6 | 57.1645 | 57.1582 | 16.1208 | 16.1191
630 | feeder2_line40 | 2 | 354.6 | 65.6033 | 65.6077 | 18.5006 | 18.5019
630 | feeder2_line40 | 3 | 354.6 | 62.2299 | 62.2302 | 17.5493 | 17.5494
630 | feeder2_line41 | 1 | 99 | 1.3261 | 1.3261 | 1.3395 | 1.3395
630 | feeder2_line41 | 2 | 99 | 4.9802e-08 | 7.3521e-07 | 5.0305e-08 | 7.4264e-07
630 | feeder2_line41 | 3 | 99 | 4.9913e-08 | 7.3533e-07 | 5.0418e-08 | 7.4276e-07
630 | feeder2_line42 | 1 | 99 | 2.9891e-07 | 7.4829e-07 | 3.0193e-07 | 7.5585e-07
630 | feeder2_line42 | 2 | 99 | 2.9903e-07 | 7.4866e-07 | 3.0205e-07 | 7.5622e-07
630 | feeder2_line42 | 3 | 99 | 0.65046 | 0.65046 | 0.65703 | 0.65703
630 | feeder2_line43 | 1 | 266.4 | 5.2508 | 5.2506 | 1.971 | 1.971
630 | feeder2_line43 | 2 | 266.4 | 10.0333 | 10.0329 | 3.7662 | 3.7661
630 | feeder2_line43 | 3 | 266.4 | 10.2011 | 10.201 | 3.8293 | 3.8292
630 | feeder2_line44 | 1 | 354.6 | 57.1646 | 57.1582 | 16.1209 | 16.1191
630 | feeder2_line44 | 2 | 354.6 | 65.6033 | 65.6077 | 18.5007 | 18.5019
630 | feeder2_line44 | 3 | 354.6 | 62.3157 | 62.3159 | 17.5735 | 17.5736
630 | feeder2_line45 | 1 | 99 | 4.9938e-08 | 5.794e-07 | 5.0443e-08 | 5.8526e-07
630 | feeder2_line45 | 2 | 99 | 4.9803e-08 | 5.7987e-07 | 5.0306e-08 | 5.8573e-07
630 | feeder2_line45 | 3 | 99 | 0.085865 | 0.085885 | 0.086732 | 0.086753
630 | feeder2_line46 | 1 | 99 | 5.7288e-07 | 1.3565e-06 | 5.7866e-07 | 1.3702e-06
630 | feeder2_line46 | 2 | 99 | 5.7316e-07 | 1.3572e-06 | 5.7895e-07 | 1.3709e-06
630 | feeder2_line46 | 3 | 99 | 1.256 | 1.256 | 1.2687 | 1.2687
630 | feeder2_line47 | 1 | 266.4 | 5.2509 | 5.2506 | 1.9711 | 1.971
630 | feeder2_line47 | 2 | 266.4 | 10.0333 | 10.0329 | 3.7662 | 3.7661
630 | feeder2_line47 | 3 | 266.4 | 9.323 | 9.3228 | 3.4996 | 3.4995
630 | feeder2_line48 | 1 | 99 | 2.6454 | 2.6454 | 2.6721 | 2.6721
630 | feeder2_line48 | 2 | 99 | 4.9776e-08 | 7.307e-07 | 5.0279e-08 | 7.3808e-07
630 | feeder2_line48 | 3 | 99 | 4.985e-08 | 7.309e-07 | 5.0353e-08 | 7.3828e-07
630 | feeder2_line49 | 1 | 266.4 | 2.6078 | 2.6075 | 0.97889 | 0.97878
630 | feeder2_line49 | 2 | 266.4 | 10.0332 | 10.0329 | 3.7662 | 3.7661
630 | feeder2_line49 | 3 | 266.4 | 9.323 | 9.3228 | 3.4996 | 3.4995
630 | feeder2_line50 | 1 | 99 | 5.7287e-07 | 1.2345e-06 | 5.7866e-07 | 1.247e-06
630 | feeder2_line50 | 2 | 99 | 0.085209 | 0.085214 | 0.086069 | 0.086075
630 | feeder2_line50 | 3 | 99 | 5.7328e-07 | 1.2354e-06 | 5.7907e-07 | 1.2479e-06
630 | feeder2_line51 | 1 | 99 | 1.5283 | 1.5281 | 1.5437 | 1.5436
630 | feeder2_line51 | 2 | 99 | 5.7312e-07 | 1.3408e-06 | 5.7891e-07 | 1.3543e-06
630 | feeder2_line51 | 3 | 99 | 5.7327e-07 | 1.3411e-06 | 5.7906e-07 | 1.3547e-06
630 | feeder2_line52 | 1 | 266.4 | 1.2467 | 1.2467 | 0.46797 | 0.46798
630 | feeder2_line52 | 2 | 266.4 | 9.9482 | 9.948 | 3.7343 | 3.7342
630 | feeder2_line52 | 3 | 266.4 | 9.3228 | 9.3228 | 3.4996 | 3.4995
630 | feeder2_line53 | 1 | 99 | 5.4793e-07 | 7.5344e-07 | 5.5346e-07 | 7.6105e-07
630 | feeder2_line53 | 2 | 99 | 9.9481 | 9.948 | 10.0486 | 10.0485
630 | feeder2_line53 | 3 | 99 | 5.4834e-07 | 7.5396e-07 | 5.5387e-07 | 7.6158e-07
630 | feeder2_line54 | 1 | 266.4 | 1.2466 | 1.2467 | 0.46795 | 0.46798
630 | feeder2_line54 | 2 | 266.4 | 8.5485e-05 | 4.6239e-06 | 3.2089e-05 | 1.7357e-06
630 | feeder2_line54 | 3 | 266.4 | 9.3227 | 9.3228 | 3.4995 | 3.4995
630 | feeder2_line55 | 1 | 99 | 0.045515 | 0.045512 | 0.045975 | 0.045972
630 | feeder2_line55 | 2 | 99 | 4.9815e-08 | 7.3094e-07 | 5.0318e-08 | 7.3833e-07
630 | feeder2_line55 | 3 | 99 | 4.9955e-08 | 7.3102e-07 | 5.0459e-08 | 7.384e-07
630 | feeder2_line56 | 1 | 354.6 | 57.2101 | 57.2037 | 16.1337 | 16.1319
630 | feeder2_line56 | 2 | 354.6 | 65.6034 | 65.6077 | 18.5007 | 18.5019
630 | feeder2_line56 | 3 | 354.6 | 62.3157 | 62.3159 | 17.5735 | 17.5736
630 | feeder2_line57 | 1 | 99 | 7.4799e-07 | 1.5433e-06 | 7.5555e-07 | 1.5589e-06
630 | feeder2_line57 | 2 | 99 | 7.4658e-07 | 1.544e-06 | 7.5413e-07 | 1.5596e-06
630 | feeder2_line57 | 3 | 99 | 9.3228 | 9.3228 | 9.4169 | 9.4169
630 | feeder2_line58 | 1 | 266.4 | 1.2467 | 1.2467 | 0.46797 | 0.46798
630 | feeder2_line58 | 2 | 266.4 | 1.8943e-05 | 2.6845e-06 | 7.1107e-06 | 1.0077e-06
630 | feeder2_line58 | 3 | 266.4 | 1.8947e-05 | 2.6852e-06 | 7.1124e-06 | 1.008e-06
630 | feeder2_line59 | 1 | 99 | 4.9863e-08 | 5.3646e-07 | 5.0366e-08 | 5.4187e-07
630 | feeder2_line59 | 2 | 99 | 4.9777e-08 | 5.3668e-07 | 5.0279e-08 | 5.421e-07
630 | feeder2_line59 | 3 | 99 | 0.081196 | 0.081196 | 0.082016 | 0.082016
630 | feeder2_line60 | 1 | 99 | 2.9889e-07 | 8.1075e-07 | 3.0191e-07 | 8.1893e-07
630 | feeder2_line60 | 2 | 99 | 2.99e-07 | 8.111e-07 | 3.0202e-07 | 8.1929e-07
630 | feeder2_line60 | 3 | 99 | 9.2425 | 9.2425 | 9.3358 | 9.3358
630 | feeder2_line61 | 1 | 266.4 | 0.46024 | 0.46041 | 0.17276 | 0.17283
630 | feeder2_line61 | 2 | 266.4 | 2.8276 | 2.8278 | 1.0614 | 1.0615
630 | feeder2_line61 | 3 | 266.4 | 3.5696 | 3.5698 | 1.3399 | 1.34
630 | feeder2_line62 | 1 | 354.6 | 57.6702 | 57.664 | 16.2634 | 16.2617
630 | feeder2_line62 | 2 | 354.6 | 68.3219 | 68.3266 | 19.2673 | 19.2686
630 | feeder2_line62 | 3 | 354.6 | 65.8354 | 65.8359 | 18.5661 | 18.5662
630 | feeder2_line63 | 1 | 99 | 0.089171 | 0.089164 | 0.090071 | 0.090065
630 | feeder2_line63 | 2 | 99 | 5.7312e-07 | 1.2195e-06 | 5.7891e-07 | 1.2318e-06
630 | feeder2_line63 | 3 | 99 | 5.7325e-07 | 1.2198e-06 | 5.7904e-07 | 1.2321e-06
630 | feeder2_line64 | 1 | 99 | 1.1827 | 1.1827 | 1.1947 | 1.1947
630 | feeder2_line64 | 2 | 99 | 5.4475e-12 | 3.2124e-07 | 5.5025e-12 | 3.2449e-07
630 | feeder2_line64 | 3 | 99 | 7.0931e-12 | 3.2131e-07 | 7.1647e-12 | 3.2455e-07
630 | feeder2_line65 | 1 | 99 | 5.0014e-08 | 6.4182e-07 | 5.0519e-08 | 6.483e-07
630 | feeder2_line65 | 2 | 99 | 0.08971 | 0.089715 | 0.090616 | 0.090621
630 | feeder2_line65 | 3 | 99 | 5.0007e-08 | 6.4255e-07 | 5.0512e-08 | 6.4904e-07
630 | feeder2_line66 | 1 | 354.6 | 57.6701 | 57.664 | 16.2634 | 16.2617
630 | feeder2_line66 | 2 | 354.6 | 68.4116 | 68.4163 | 19.2926 | 19.2939
630 | feeder2_line66 | 3 | 354.6 | 65.8354 | 65.8359 | 18.5661 | 18.5662
630 | feeder2_line67 | 1 | 99 | 2.4994e-08 | 3.6273e-07 | 2.5246e-08 | 3.6639e-07
630 | feeder2_line67 | 2 | 99 | 2.4916e-08 | 3.6308e-07 | 2.5167e-08 | 3.6674e-07
630 | feeder2_line67 | 3 | 99 | 1.3252 | 1.3252 | 1.3386 | 1.3386
630 | feeder2_line68 | 1 | 266.4 | 0.46028 | 0.46041 | 0.17278 | 0.17283
630 | feeder2_line68 | 2 | 266.4 | 2.8276 | 2.8278 | 1.0614 | 1.0615
630 | feeder2_line68 | 3 | 266.4 | 2.2701 | 2.2702 | 0.85213 | 0.85218
630 | feeder2_line69 | 1 | 99 | 0.10106 | 0.10102 | 0.10208 | 0.10204
630 | feeder2_line69 | 2 | 99 | 2.55e-06 | 6.6715e-07 | 2.5757e-06 | 6.7389e-07
630 | feeder2_line69 | 3 | 99 | 2.5489e-06 | 6.6717e-07 | 2.5747e-06 | 6.739e-07
630 | feeder2_line70 | 1 | 354.6 | 57.7711 | 57.765 | 16.2919 | 16.2902
630 | feeder2_line70 | 2 | 354.6 | 68.4115 | 68.4163 | 19.2926 | 19.2939
630 | feeder2_line70 | 3 | 354.6 | 65.8353 | 65.8359 | 18.5661 | 18.5662
630 | feeder2_line71 | 1 | 99 | 5.0034e-08 | 7.162e-07 | 5.0539e-08 | 7.2344e-07
630 | feeder2_line71 | 2 | 99 | 0.052776 | 0.052786 | 0.053309 | 0.053319
630 | feeder2_line71 | 3 | 99 | 5.0026e-08 | 7.1706e-07 | 5.0531e-08 | 7.2431e-07
630 | feeder2_line72 | 1 | 354.6 | 57.7712 | 57.765 | 16.2919 | 16.2902
630 | feeder2_line72 | 2 | 354.6 | 68.4644 | 68.469 | 19.3075 | 19.3088
630 | feeder2_line72 | 3 | 354.6 | 65.8354 | 65.8359 | 18.5661 | 18.5662
630 | feeder2_line73 | 1 | 99 | 5.9884e-07 | 1.5357e-06 | 6.0489e-07 | 1.5512e-06
630 | feeder2_line73 | 2 | 99 | 0.2125 | 0.2125 | 0.21464 | 0.21465
630 | feeder2_line73 | 3 | 99 | 5.9941e-07 | 1.5372e-06 | 6.0547e-07 | 1.5527e-06
630 | feeder2_line74 | 1 | 99 | 4.9983e-08 | 4.5802e-07 | 5.0488e-08 | 4.6265e-07
630 | feeder2_line74 | 2 | 99 | 2.2698 | 2.2698 | 2.2927 | 2.2927
630 | feeder2_line74 | 3 | 99 | 4.998e-08 | 4.5847e-07 | 5.0485e-08 | 4.631e-07
630 | feeder2_line75 | 1 | 266.4 | 0.46037 | 0.46041 | 0.17281 | 0.17283
630 | feeder2_line75 | 2 | 266.4 | 0.36076 | 0.3608 | 0.13542 | 0.13543
630 | feeder2_line75 | 3 | 266.4 | 2.2702 | 2.2702 | 0.85216 | 0.85218
630 | feeder2_line76 | 1 | 99 | 0.46041 | 0.46041 | 0.46506 | 0.46506
630 | feeder2_line76 | 2 | 99 | 8.4914e-07 | 1.5856e-06 | 8.5771e-07 | 1.6016e-06
630 | feeder2_line76 | 3 | 99 | 8.4912e-07 | 1.5857e-06 | 8.577e-07 | 1.6017e-06
630 | feeder2_line77 | 1 | 99 | 2.4992e-08 | 5.7558e-07 | 2.5244e-08 | 5.8139e-07
630 | feeder2_line77 | 2 | 99 | 2.4915e-08 | 5.7612e-07 | 2.5167e-08 | 5.8194e-07
630 | feeder2_line77 | 3 | 99 | 2.2702 | 2.2702 | 2.2931 | 2.2931
630 | feeder2_line78 | 1 | 266.4 | 9.8173e-12 | 9.5463e-07 | 3.6852e-12 | 3.5835e-07
630 | feeder2_line78 | 2 | 266.4 | 0.36079 | 0.3608 | 0.13543 | 0.13543
630 | feeder2_line78 | 3 | 266.4 | 7.9798e-12 | 9.5554e-07 | 2.9954e-12 | 3.5869e-07
630 | feeder2_line79 | 1 | 354.6 | 11.5144 | 11.514 | 3.2471 | 3.2471
630 | feeder2_line79 | 2 | 354.6 | 15.5589 | 15.5584 | 4.3877 | 4.3876
630 | feeder2_line79 | 3 | 354.6 | 6.0211 | 6.0208 | 1.698 | 1.6979
630 | feeder2_line80 | 1 | 354.6 | 69.258 | 69.2514 | 19.5313 | 19.5294
630 | feeder2_line80 | 2 | 354.6 | 83.4063 | 83.4104 | 23.5212 | 23.5224
630 | feeder2_line80 | 3 | 354.6 | 71.4836 | 71.4836 | 20.1589 | 20.1589
630 | feeder2_line81 | 1 | 354.6 | 69.258 | 69.2514 | 19.5313 | 19.5294
630 | feeder2_line81 | 2 | 354.6 | 83.4063 | 83.4104 | 23.5212 | 23.5224
630 | feeder2_line81 | 3 | 354.6 | 71.5529 | 71.5529 | 20.1785 | 20.1785
630 | feeder2_line82 | 1 | 354.6 | 2.6797e-11 | 7.3486e-07 | 7.5569e-12 | 2.0724e-07
630 | feeder2_line82 | 2 | 354.6 | 2.4978e-11 | 7.3575e-07 | 7.0441e-12 | 2.0749e-07
630 | feeder2_line82 | 3 | 354.6 | 0.069543 | 0.069545 | 0.019612 | 0.019612
630 | feeder2_line83 | 1 | 354.6 | 69.2582 | 69.2514 | 19.5314 | 19.5294
630 | feeder2_line83 | 2 | 354.6 | 84.0073 | 84.0113 | 23.6907 | 23.6918
630 | feeder2_line83 | 3 | 354.6 | 71.5531 | 71.5529 | 20.1785 | 20.1785
630 | feeder2_line84 | 1 | 354.6 | 1.2538e-11 | 1.2989e-06 | 3.5359e-12 | 3.663e-07
630 | feeder2_line84 | 2 | 354.6 | 0.97643 | 0.97645 | 0.27536 | 0.27537
630 | feeder2_line84 | 3 | 354.6 | 9.9095e-12 | 1.3006e-06 | 2.7946e-12 | 3.6678e-07
630 | feeder2_line85 | 1 | 99 | 0.31891 | 0.3189 | 0.32213 | 0.32212
630 | feeder2_line85 | 2 | 99 | 4.9882e-08 | 4.6429e-07 | 5.0386e-08 | 4.6898e-07
630 | feeder2_line85 | 3 | 99 | 5.009e-08 | 4.6421e-07 | 5.0596e-08 | 4.689e-07
630 | feeder2_line86 | 1 | 354.6 | 69.5759 | 69.569 | 19.621 | 19.619
630 | feeder2_line86 | 2 | 354.6 | 84.0074 | 84.0113 | 23.6908 | 23.6918
630 | feeder2_line86 | 3 | 354.6 | 71.5532 | 71.5529 | 20.1786 | 20.1785
630 | feeder2_line87 | 1 | 354.6 | 69.5761 | 69.569 | 19.621 | 19.619
630 | feeder2_line87 | 2 | 354.6 | 84.653 | 84.6567 | 23.8728 | 23.8739
630 | feeder2_line87 | 3 | 354.6 | 71.6346 | 71.6342 | 20.2015 | 20.2014
630 | feeder2_line88 | 1 | 354.6 | 0.00011401 | 3.3671e-06 | 3.2151e-05 | 9.4956e-07
630 | feeder2_line88 | 2 | 354.6 | 1.0519 | 1.0519 | 0.29664 | 0.29665
630 | feeder2_line88 | 3 | 354.6 | 0.081703 | 0.081623 | 0.023041 | 0.023018
630 | feeder2_line89 | 1 | 354.6 | 69.5738 | 69.569 | 19.6204 | 19.619
630 | feeder2_line89 | 2 | 354.6 | 86.3331 | 86.3391 | 24.3466 | 24.3483
630 | feeder2_line89 | 3 | 354.6 | 71.6323 | 71.6342 | 20.2009 | 20.2014
630 | feeder2_line90 | 1 | 354.6 | 0.00072441 | 2.0316e-06 | 0.00020429 | 5.7292e-07
630 | feeder2_line90 | 2 | 354.6 | 1.8088 | 1.8091 | 0.51009 | 0.51017
630 | feeder2_line90 | 3 | 354.6 | 0.00072534 | 2.0355e-06 | 0.00020455 | 5.7402e-07
630 | feeder2_line91 | 1 | 354.6 | 69.5737 | 69.569 | 19.6203 | 19.619
630 | feeder2_line91 | 2 | 354.6 | 86.333 | 86.3391 | 24.3466 | 24.3483
630 | feeder2_line91 | 3 | 354.6 | 80.8954 | 80.8973 | 22.8131 | 22.8137
630 | feeder2_line92 | 1 | 354.6 | 7.7314e-12 | 1.0255e-06 | 2.1803e-12 | 2.8919e-07
630 | feeder2_line92 | 2 | 354.6 | 1.3154e-11 | 1.0271e-06 | 3.7094e-12 | 2.8966e-07
630 | feeder2_line92 | 3 | 354.6 | 9.2755 | 9.2754 | 2.6158 | 2.6157
630 | feeder2_line93 | 1 | 99 | 2.5058e-08 | 3.4226e-07 | 2.5311e-08 | 3.4572e-07
630 | feeder2_line93 | 2 | 99 | 0.97671 | 0.97672 | 0.98657 | 0.98659
630 | feeder2_line93 | 3 | 99 | 2.5066e-08 | 3.4273e-07 | 2.532e-08 | 3.4619e-07
630 | feeder2_line94 | 1 | 354.6 | 2.5062e-06 | 1.6665e-06 | 7.0678e-07 | 4.6995e-07
630 | feeder2_line94 | 2 | 354.6 | 1.0716 | 1.0716 | 0.30219 | 0.30219
630 | feeder2_line94 | 3 | 354.6 | 2.5067e-06 | 1.6687e-06 | 7.069e-07 | 4.7058e-07
630 | feeder2_line95 | 1 | 99 | 3.5685e-06 | 2.611e-06 | 3.6045e-06 | 2.6374e-06
630 | feeder2_line95 | 2 | 99 | 1.0518 | 1.0519 | 1.0625 | 1.0625
630 | feeder2_line95 | 3 | 99 | 3.5751e-06 | 2.6145e-06 | 3.6112e-06 | 2.6409e-06
630 | feeder2_line96 | 1 | 354.6 | 0.00012117 | 6.2232e-07 | 3.417e-05 | 1.755e-07
630 | feeder2_line96 | 2 | 354.6 | 0.00012139 | 6.2352e-07 | 3.4232e-05 | 1.7584e-07
630 | feeder2_line96 | 3 | 354.6 | 0.081688 | 0.081623 | 0.023037 | 0.023018
630 | feeder2_line97 | 1 | 354.6 | 70.8842 | 70.8793 | 19.9899 | 19.9885
630 | feeder2_line97 | 2 | 354.6 | 86.3331 | 86.3391 | 24.3466 | 24.3483
630 | feeder2_line97 | 3 | 354.6 | 80.8956 | 80.8973 | 22.8132 | 22.8137
630 | feeder2_line98 | 1 | 354.6 | 1.312 | 1.3103 | 0.37001 | 0.36952
630 | feeder2_line98 | 2 | 354.6 | 0.001709 | 6.2123e-07 | 0.00048195 | 1.7519e-07
630 | feeder2_line98 | 3 | 354.6 | 0.0017028 | 6.2771e-07 | 0.00048021 | 1.7702e-07
630 | feeder2_line99 | 1 | 99 | 2.5049e-08 | 4.4744e-07 | 2.5302e-08 | 4.5196e-07
630 | feeder2_line99 | 2 | 99 | 2.494e-08 | 4.4816e-07 | 2.5192e-08 | 4.5269e-07
630 | feeder2_line99 | 3 | 99 | 0.081596 | 0.081623 | 0.08242 | 0.082447
630 | feeder2_line100 | 1 | 99 | 1.3104 | 1.3103 | 1.3236 | 1.3235
630 | feeder2_line100 | 2 | 99 | 2.495e-08 | 6.1562e-07 | 2.5202e-08 | 6.2184e-07
630 | feeder2_line100 | 3 | 99 | 2.5074e-08 | 6.1536e-07 | 2.5328e-08 | 6.2157e-07
630 | feeder2_line101 | 1 | 354.6 | 1.0708 | 1.0703 | 0.30196 | 0.30184
630 | feeder2_line101 | 2 | 354.6 | 15.5589 | 15.5584 | 4.3877 | 4.3876
630 | feeder2_line101 | 3 | 354.6 | 6.0211 | 6.0208 | 1.698 | 1.6979
630 | feeder2_line102 | 1 | 99 | 10.4548 | 10.4549 | 10.5604 | 10.5605
630 | feeder2_line102 | 2 | 99 | 2.3406e-06 | 8.7948e-07 | 2.3643e-06 | 8.8836e-07
630 | feeder2_line102 | 3 | 99 | 2.3379e-06 | 8.7959e-07 | 2.3615e-06 | 8.8848e-07
630 | feeder2_line103 | 1 | 99 | 5.4936e-07 | 8.0403e-07 | 5.5491e-07 | 8.1215e-07
630 | feeder2_line103 | 2 | 99 | 9.9231 | 9.923 | 10.0234 | 10.0232
630 | feeder2_line103 | 3 | 99 | 5.5012e-07 | 8.0508e-07 | 5.5568e-07 | 8.1321e-07
630 | feeder2_line104 | 1 | 354.6 | 1.0706 | 1.0703 | 0.30193 | 0.30184
630 | feeder2_line104 | 2 | 354.6 | 6.3077 | 6.3075 | 1.7788 | 1.7788
630 | feeder2_line104 | 3 | 354.6 | 6.021 | 6.0208 | 1.698 | 1.6979
630 | feeder2_line105 | 1 | 99 | 2.5467e-06 | 7.3982e-07 | 2.5724e-06 | 7.473e-07
630 | feeder2_line105 | 2 | 99 | 2.551e-06 | 7.4064e-07 | 2.5768e-06 | 7.4812e-07
630 | feeder2_line105 | 3 | 99 | 0.26619 | 0.26621 | 0.26887 | 0.2689
630 | feeder2_line106 | 1 | 354.6 | 1.0706 | 1.0703 | 0.30192 | 0.30184
630 | feeder2_line106 | 2 | 354.6 | 6.3076 | 6.3075 | 1.7788 | 1.7788
630 | feeder2_line106 | 3 | 354.6 | 5.7723 | 5.7721 | 1.6278 | 1.6278
630 | feeder2_line107 | 1 | 99 | 3.2473e-07 | 9.016e-07 | 3.2801e-07 | 9.107e-07
630 | feeder2_line107 | 2 | 99 | 1.1923 | 1.1923 | 1.2043 | 1.2043
630 | feeder2_line107 | 3 | 99 | 3.2509e-07 | 9.0268e-07 | 3.2837e-07 | 9.118e-07
630 | feeder2_line108 | 1 | 354.6 | 1.0706 | 1.0703 | 0.30191 | 0.30184
630 | feeder2_line108 | 2 | 354.6 | 5.1861 | 5.186 | 1.4625 | 1.4625
630 | feeder2_line108 | 3 | 354.6 | 5.7723 | 5.7721 | 1.6278 | 1.6278
630 | feeder2_line109 | 1 | 354.6 | 83.5897 | 83.5838 | 23.5729 | 23.5713
630 | feeder2_line109 | 2 | 354.6 | 86.3344 | 86.3391 | 24.347 | 24.3483
630 | feeder2_line109 | 3 | 354.6 | 80.8968 | 80.8973 | 22.8135 | 22.8137
630 | feeder2_line110 | 1 | 99 | 12.7066 | 12.7061 | 12.835 | 12.8344
630 | feeder2_line110 | 2 | 99 | 0.00080711 | 9.1161e-07 | 0.00081527 | 9.2082e-07
630 | feeder2_line110 | 3 | 99 | 0.00080598 | 9.1087e-07 | 0.00081412 | 9.2007e-07
630 | feeder2_line111 | 1 | 99 | 2.5046e-08 | 3.8215e-07 | 2.5299e-08 | 3.8601e-07
630 | feeder2_line111 | 2 | 99 | 1.029 | 1.0291 | 1.0394 | 1.0395
630 | feeder2_line111 | 3 | 99 | 2.5055e-08 | 3.8267e-07 | 2.5308e-08 | 3.8653e-07
630 | feeder2_line112 | 1 | 99 | 3.2497e-07 | 9.1834e-07 | 3.2825e-07 | 9.2762e-07
630 | feeder2_line112 | 2 | 99 | 0.040725 | 0.040736 | 0.041137 | 0.041147
630 | feeder2_line112 | 3 | 99 | 3.2537e-07 | 9.1957e-07 | 3.2865e-07 | 9.2886e-07
630 | feeder2_line113 | 1 | 99 | 0.097439 | 0.097434 | 0.098423 | 0.098418
630 | feeder2_line113 | 2 | 99 | 3.2566e-07 | 9.0803e-07 | 3.2895e-07 | 9.172e-07
630 | feeder2_line113 | 3 | 99 | 3.2571e-07 | 9.0759e-07 | 3.29e-07 | 9.1676e-07
630 | feeder2_line114 | 1 | 99 | 9.9055 | 9.9056 | 10.0056 | 10.0057
630 | feeder2_line114 | 2 | 99 | 2.4924e-08 | 4.3732e-07 | 2.5176e-08 | 4.4174e-07
630 | feeder2_line114 | 3 | 99 | 2.5016e-08 | 4.3738e-07 | 2.5269e-08 | 4.418e-07
630 | feeder2_line115 | 1 | 99 | 2.5013e-08 | 5.6265e-07 | 2.5265e-08 | 5.6833e-07
630 | feeder2_line115 | 2 | 99 | 1.686 | 1.6861 | 1.7031 | 1.7031
630 | feeder2_line115 | 3 | 99 | 2.5024e-08 | 5.6328e-07 | 2.5276e-08 | 5.6897e-07
630 | feeder2_line116 | 1 | 354.6 | 1.0706 | 1.0703 | 0.30191 | 0.30184
630 | feeder2_line116 | 2 | 354.6 | 3.5021 | 3.5019 | 0.98763 | 0.98757
630 | feeder2_line116 | 3 | 354.6 | 5.7723 | 5.7721 | 1.6278 | 1.6278
630 | feeder2_line117 | 1 | 99 | 5.019e-08 | 6.4354e-07 | 5.0697e-08 | 6.5004e-07
630 | feeder2_line117 | 2 | 99 | 1.2588 | 1.2588 | 1.2715 | 1.2715
630 | feeder2_line117 | 3 | 99 | 5.0196e-08 | 6.4453e-07 | 5.0703e-08 | 6.5104e-07
630 | feeder2_line118 | 1 | 354.6 | 83.5897 | 83.5838 | 23.573 | 23.5713
630 | feeder2_line118 | 2 | 354.6 | 87.1042 | 87.1089 | 24.5641 | 24.5654
630 | feeder2_line118 | 3 | 354.6 | 80.8968 | 80.8973 | 22.8135 | 22.8137
630 | feeder2_line119 | 1 | 99 | 2.5014e-08 | 6.0543e-07 | 2.5267e-08 | 6.1155e-07
630 | feeder2_line119 | 2 | 99 | 2.4932e-08 | 6.0603e-07 | 2.5184e-08 | 6.1215e-07
630 | feeder2_line119 | 3 | 99 | 2.6 | 2.6001 | 2.6263 | 2.6264
630 | feeder2_line120 | 1 | 354.6 | 1.0706 | 1.0703 | 0.30191 | 0.30184
630 | feeder2_line120 | 2 | 354.6 | 3.5021 | 3.5019 | 0.98763 | 0.98757
630 | feeder2_line120 | 3 | 354.6 | 3.1925 | 3.1923 | 0.9003 | 0.90024
630 | feeder2_line121 | 1 | 99 | 3.2473e-07 | 9.3755e-07 | 3.2801e-07 | 9.4702e-07
630 | feeder2_line121 | 2 | 99 | 1.3165 | 1.3165 | 1.3298 | 1.3298
630 | feeder2_line121 | 3 | 99 | 3.2504e-07 | 9.3848e-07 | 3.2832e-07 | 9.4796e-07
630 | feeder2_line122 | 1 | 354.6 | 1.0706 | 1.0703 | 0.30191 | 0.30184
630 | feeder2_line122 | 2 | 354.6 | 2.3754 | 2.3752 | 0.66987 | 0.66982
630 | feeder2_line122 | 3 | 354.6 | 3.1924 | 3.1923 | 0.90029 | 0.90024
630 | feeder2_line123 | 1 | 99 | 5.7443e-07 | 9.7152e-07 | 5.8023e-07 | 9.8134e-07
630 | feeder2_line123 | 2 | 99 | 5.7497e-07 | 9.7243e-07 | 5.8078e-07 | 9.8225e-07
630 | feeder2_line123 | 3 | 99 | 0.076897 | 0.076897 | 0.077674 | 0.077674
630 | feeder2_line124 | 1 | 354.6 | 1.0705 | 1.0703 | 0.30188 | 0.30184
630 | feeder2_line124 | 2 | 354.6 | 2.3753 | 2.3752 | 0.66986 | 0.66982
630 | feeder2_line124 | 3 | 354.6 | 3.1206 | 3.1205 | 0.88004 | 0.88
630 | feeder2_line125 | 1 | 99 | 5.7443e-07 | 9.0313e-07 | 5.8023e-07 | 9.1225e-07
630 | feeder2_line125 | 2 | 99 | 5.7497e-07 | 9.0397e-07 | 5.8077e-07 | 9.131e-07
630 | feeder2_line125 | 3 | 99 | 1.3104 | 1.3104 | 1.3236 | 1.3236
630 | feeder2_line126 | 1 | 354.6 | 1.0706 | 1.0703 | 0.30193 | 0.30184
630 | feeder2_line126 | 2 | 354.6 | 2.3755 | 2.3752 | 0.66991 | 0.66982
630 | feeder2_line126 | 3 | 354.6 | 1.918 | 1.9177 | 0.54089 | 0.5408
630 | feeder2_line127 | 1 | 99 | 5.7443e-07 | 1.0812e-06 | 5.8023e-07 | 1.0921e-06
630 | feeder2_line127 | 2 | 99 | 5.7496e-07 | 1.0822e-06 | 5.8077e-07 | 1.0931e-06
630 | feeder2_line127 | 3 | 99 | 0.077057 | 0.077058 | 0.077836 | 0.077837
630 | feeder2_line128 | 1 | 354.6 | 1.0705 | 1.0703 | 0.3019 | 0.30184
630 | feeder2_line128 | 2 | 354.6 | 2.3754 | 2.3752 | 0.66989 | 0.66982
630 | feeder2_line128 | 3 | 354.6 | 1.8553 | 1.855 | 0.5232 | 0.52312
630 | feeder2_line129 | 1 | 99 | 5.4942e-07 | 8.7669e-07 | 5.5497e-07 | 8.8554e-07
630 | feeder2_line129 | 2 | 99 | 2.3752 | 2.3752 | 2.3992 | 2.3992
630 | feeder2_line129 | 3 | 99 | 5.4994e-07 | 8.7751e-07 | 5.5549e-07 | 8.8637e-07
630 | feeder2_line130 | 1 | 354.6 | 1.0706 | 1.0703 | 0.30191 | 0.30184
630 | feeder2_line130 | 2 | 354.6 | 0.00030873 | 4.6435e-06 | 8.7064e-05 | 1.3095e-06
630 | feeder2_line130 | 3 | 354.6 | 1.8553 | 1.855 | 0.52321 | 0.52312
630 | feeder2_line131 | 1 | 99 | 5.7442e-07 | 9.7167e-07 | 5.8023e-07 | 9.8149e-07
630 | feeder2_line131 | 2 | 99 | 5.7496e-07 | 9.7256e-07 | 5.8077e-07 | 9.8239e-07
630 | feeder2_line131 | 3 | 99 | 1.6122 | 1.6122 | 1.6285 | 1.6285
630 | feeder2_line132 | 1 | 354.6 | 1.0704 | 1.0703 | 0.30186 | 0.30184
630 | feeder2_line132 | 2 | 354.6 | 0.00012586 | 2.9193e-06 | 3.5495e-05 | 8.2327e-07
630 | feeder2_line132 | 3 | 354.6 | 0.31877 | 0.3187 | 0.089895 | 0.089877
630 | feeder2_line133 | 1 | 99 | 1.0703 | 1.0703 | 1.0811 | 1.0811
630 | feeder2_line133 | 2 | 99 | 2.9995e-07 | 9.8033e-07 | 3.0297e-07 | 9.9023e-07
630 | feeder2_line133 | 3 | 99 | 2.9999e-07 | 9.8034e-07 | 3.0302e-07 | 9.9024e-07
630 | feeder2_line134 | 1 | 354.6 | 1.2918e-11 | 1.7862e-06 | 3.6429e-12 | 5.0372e-07
630 | feeder2_line134 | 2 | 354.6 | 8.537e-12 | 1.7877e-06 | 2.4075e-12 | 5.0413e-07
630 | feeder2_line134 | 3 | 354.6 | 0.3187 | 0.3187 | 0.089876 | 0.089877
630 | feeder2_line135 | 1 | 99 | 0.052738 | 0.052695 | 0.05327 | 0.053227
630 | feeder2_line135 | 2 | 99 | 4.9964e-08 | 5.8789e-07 | 5.0469e-08 | 5.9383e-07
630 | feeder2_line135 | 3 | 99 | 5.0228e-08 | 5.8754e-07 | 5.0736e-08 | 5.9348e-07
630 | feeder2_line136 | 1 | 354.6 | 83.6423 | 83.6364 | 23.5878 | 23.5861
630 | feeder2_line136 | 2 | 354.6 | 87.1042 | 87.1089 | 24.5641 | 24.5654
630 | feeder2_line136 | 3 | 354.6 | 80.8968 | 80.8973 | 22.8135 | 22.8137
630 | feeder2_line137 | 1 | 99 | 0.5904 | 0.59037 | 0.59636 | 0.59634
630 | feeder2_line137 | 2 | 99 | 8.533e-07 | 1.5836e-06 | 8.6192e-07 | 1.5996e-06
630 | feeder2_line137 | 3 | 99 | 8.527e-07 | 1.5826e-06 | 8.6131e-07 | 1.5986e-06
630 | feeder2_line138 | 1 | 354.6 | 84.2325 | 84.2265 | 23.7542 | 23.7525
630 | feeder2_line138 | 2 | 354.6 | 87.1042 | 87.1089 | 24.5641 | 24.5654
630 | feeder2_line138 | 3 | 354.6 | 80.8968 | 80.8973 | 22.8135 | 22.8137
630 | feeder2_line139 | 1 | 99 | 5.0226e-08 | 4.9244e-07 | 5.0733e-08 | 4.9741e-07
630 | feeder2_line139 | 2 | 99 | 4.997e-08 | 4.9347e-07 | 5.0475e-08 | 4.9845e-07
630 | feeder2_line139 | 3 | 99 | 17.9907 | 17.9908 | 18.1724 | 18.1725
630 | feeder2_line140 | 1 | 354.6 | 84.2326 | 84.2265 | 23.7543 | 23.7525
630 | feeder2_line140 | 2 | 354.6 | 87.1043 | 87.1089 | 24.5641 | 24.5654
630 | feeder2_line140 | 3 | 354.6 | 98.8836 | 98.884 | 27.886 | 27.8861
630 | feeder2_line141 | 1 | 99 | 2.5291e-06 | 4.8716e-07 | 2.5546e-06 | 4.9208e-07
630 | feeder2_line141 | 2 | 99 | 0.6524 | 0.6524 | 0.65899 | 0.65899
630 | feeder2_line141 | 3 | 99 | 2.5336e-06 | 4.8793e-07 | 2.5592e-06 | 4.9286e-07
630 | feeder2_line142 | 1 | 354.6 | 84.2324 | 84.2265 | 23.7542 | 23.7525
630 | feeder2_line142 | 2 | 354.6 | 87.7564 | 87.7612 | 24.748 | 24.7493
630 | feeder2_line142 | 3 | 354.6 | 98.8834 | 98.884 | 27.8859 | 27.8861
630 | feeder2_line143 | 1 | 99 | 8.5174e-07 | 1.7312e-06 | 8.6034e-07 | 1.7486e-06
630 | feeder2_line143 | 2 | 99 | 1.1939 | 1.1939 | 1.206 | 1.206
630 | feeder2_line143 | 3 | 99 | 8.5315e-07 | 1.734e-06 | 8.6177e-07 | 1.7515e-06
630 | feeder2_line144 | 1 | 354.6 | 84.2322 | 84.2265 | 23.7541 | 23.7525
630 | feeder2_line144 | 2 | 354.6 | 88.508 | 88.5129 | 24.9599 | 24.9613
630 | feeder2_line144 | 3 | 354.6 | 98.8832 | 98.884 | 27.8858 | 27.8861
630 | feeder2_line145 | 1 | 99 | 2.5129e-08 | 4.8545e-07 | 2.5383e-08 | 4.9035e-07
630 | feeder2_line145 | 2 | 99 | 0.069303 | 0.069309 | 0.070003 | 0.070009
630 | feeder2_line145 | 3 | 99 | 2.5127e-08 | 4.8624e-07 | 2.5381e-08 | 4.9115e-07
630 | feeder2_line146 | 1 | 354.6 | 84.2321 | 84.2265 | 23.7541 | 23.7525
630 | feeder2_line146 | 2 | 354.6 | 88.5769 | 88.582 | 24.9794 | 24.9808
630 | feeder2_line146 | 3 | 354.6 | 98.8831 | 98.884 | 27.8858 | 27.8861
630 | feeder2_line147 | 1 | 99 | 12.6139 | 12.6142 | 12.7414 | 12.7416
630 | feeder2_line147 | 2 | 99 | 1.155e-06 | 2.2439e-06 | 1.1667e-06 | 2.2666e-06
630 | feeder2_line147 | 3 | 99 | 1.1545e-06 | 2.2429e-06 | 1.1661e-06 | 2.2655e-06
630 | feeder2_line148 | 1 | 99 | 0.084814 | 0.084807 | 0.085671 | 0.085663
630 | feeder2_line148 | 2 | 99 | 6.0256e-07 | 1.5037e-06 | 6.0864e-07 | 1.5188e-06
630 | feeder2_line148 | 3 | 99 | 6.024e-07 | 1.503e-06 | 6.0848e-07 | 1.5181e-06
630 | feeder2_line149 | 1 | 354.6 | 96.9298 | 96.9243 | 27.335 | 27.3334
630 | feeder2_line149 | 2 | 354.6 | 88.577 | 88.582 | 24.9794 | 24.9808
630 | feeder2_line149 | 3 | 354.6 | 98.8833 | 98.884 | 27.8859 | 27.8861
630 | feeder2_line150 | 1 | 354.6 | 96.9299 | 96.9243 | 27.335 | 27.3334
630 | feeder2_line150 | 2 | 354.6 | 98.9008 | 98.9055 | 27.8908 | 27.8921
630 | feeder2_line150 | 3 | 354.6 | 98.8834 | 98.884 | 27.8859 | 27.8861
630 | feeder2_line151 | 1 | 99 | 9.7753e-06 | 1.7826e-06 | 9.874e-06 | 1.8006e-06
630 | feeder2_line151 | 2 | 99 | 10.3266 | 10.3265 | 10.4309 | 10.4308
630 | feeder2_line151 | 3 | 99 | 9.7945e-06 | 1.7857e-06 | 9.8934e-06 | 1.8037e-06
630 | feeder2_line152 | 1 | 354.6 | 7.9128e-12 | 1.1883e-06 | 2.2315e-12 | 3.3512e-07
630 | feeder2_line152 | 2 | 354.6 | 2.3482e-11 | 1.1906e-06 | 6.6221e-12 | 3.3576e-07
630 | feeder2_line152 | 3 | 354.6 | 0.076602 | 0.076603 | 0.021602 | 0.021603
630 | feeder2_line153 | 1 | 99 | 1.3177 | 1.3177 | 1.331 | 1.3311
630 | feeder2_line153 | 2 | 99 | 5.0068e-08 | 5.9575e-07 | 5.0574e-08 | 6.0177e-07
630 | feeder2_line153 | 3 | 99 | 5.029e-08 | 5.9557e-07 | 5.0798e-08 | 6.0158e-07
630 | feeder2_line154 | 1 | 99 | 5.7688e-07 | 8.8467e-07 | 5.827e-07 | 8.936e-07
630 | feeder2_line154 | 2 | 99 | 5.7808e-07 | 8.865e-07 | 5.8392e-07 | 8.9545e-07
630 | feeder2_line154 | 3 | 99 | 0.040584 | 0.040614 | 0.040994 | 0.041024
630 | feeder2_line155 | 1 | 99 | 97.7009 | 97.6954 | 98.6878 | 98.6822
630 | feeder2_line155 | 2 | 99 | 98.9007 | 98.9055 | 99.8997 | 99.9045
630 | feeder2_line155 | 3 | 99 | 99 | 99.0008 | 100 | 100.0008
630 | feeder2_line156 | 1 | 99 | 6.0174e-07 | 1.164e-06 | 6.0781e-07 | 1.1758e-06
630 | feeder2_line156 | 2 | 99 | 9.9654 | 9.9652 | 10.0661 | 10.0659
630 | feeder2_line156 | 3 | 99 | 6.0271e-07 | 1.166e-06 | 6.088e-07 | 1.1778e-06
630 | feeder2_line157 | 1 | 99 | 2.5147e-08 | 2.5271e-07 | 2.5401e-08 | 2.5526e-07
630 | feeder2_line157 | 2 | 99 | 0.36127 | 0.36127 | 0.36492 | 0.36492
630 | feeder2_line157 | 3 | 99 | 2.5132e-08 | 2.5314e-07 | 2.5386e-08 | 2.557e-07
660 | feeder2_line1 | 1 | 354.6 | 11.6137 | 11.6158 | 3.2752 | 3.2757
660 | feeder2_line1 | 2 | 354.6 | 25.924 | 25.9256 | 7.3108 | 7.3112
660 | feeder2_line1 | 3 | 354.6 | 44.6537 | 44.6409 | 12.5927 | 12.5891
660 | feeder2_line2 | 1 | 354.6 | 11.6261 | 11.6282 | 3.2787 | 3.2792
660 | feeder2_line2 | 2 | 354.6 | 25.9241 | 25.9256 | 7.3108 | 7.3112
660 | feeder2_line2 | 3 | 354.6 | 44.6539 | 44.6409 | 12.5928 | 12.5891
660 | feeder2_line3 | 1 | 80.1 | 0.069615 | 0.069626 | 0.08691 | 0.086924
660 | feeder2_line3 | 2 | 80.1 | 5.7119e-07 | 1.0555e-06 | 7.1309e-07 | 1.3178e-06
660 | feeder2_line3 | 3 | 80.1 | 5.7225e-07 | 1.0575e-06 | 7.1442e-07 | 1.3202e-06
660 | feeder2_line4 | 1 | 354.6 | 11.6261 | 11.6282 | 3.2787 | 3.2792
660 | feeder2_line4 | 2 | 354.6 | 26.3987 | 26.4 | 7.4446 | 7.445
660 | feeder2_line4 | 3 | 354.6 | 44.6541 | 44.6409 | 12.5928 | 12.5891
660 | feeder2_line5 | 1 | 80.1 | 5.702e-07 | 9.9497e-07 | 7.1186e-07 | 1.2422e-06
660 | feeder2_line5 | 2 | 80.1 | 0.50176 | 0.50175 | 0.62642 | 0.62641
660 | feeder2_line5 | 3 | 80.1 | 5.7229e-07 | 9.9858e-07 | 7.1447e-07 | 1.2467e-06
660 | feeder2_line6 | 1 | 80.1 | 5.7016e-07 | 1.1704e-06 | 7.1181e-07 | 1.4612e-06
660 | feeder2_line6 | 2 | 80.1 | 5.7121e-07 | 1.1725e-06 | 7.1312e-07 | 1.4638e-06
660 | feeder2_line6 | 3 | 80.1 | 1.2656 | 1.2656 | 1.5801 | 1.5801
660 | feeder2_line7 | 1 | 354.6 | 11.6261 | 11.6282 | 3.2787 | 3.2792
660 | feeder2_line7 | 2 | 354.6 | 26.3988 | 26.4 | 7.4447 | 7.445
660 | feeder2_line7 | 3 | 354.6 | 45.2813 | 45.268 | 12.7697 | 12.7659
660 | feeder2_line8 | 1 | 80.1 | 0.072999 | 0.073001 | 0.091135 | 0.091138
660 | feeder2_line8 | 2 | 80.1 | 5.7127e-07 | 1.1307e-06 | 7.132e-07 | 1.4116e-06
660 | feeder2_line8 | 3 | 80.1 | 5.7256e-07 | 1.1332e-06 | 7.1481e-07 | 1.4148e-06
660 | feeder2_line9 | 1 | 354.6 | 11.6384 | 11.6406 | 3.2821 | 3.2828
660 | feeder2_line9 | 2 | 354.6 | 26.3989 | 26.4 | 7.4447 | 7.445
660 | feeder2_line9 | 3 | 354.6 | 45.2814 | 45.268 | 12.7697 | 12.7659
660 | feeder2_line10 | 1 | 80.1 | 8.4257e-07 | 1.4898e-06 | 1.0519e-06 | 1.8599e-06
660 | feeder2_line10 | 2 | 80.1 | 0.072719 | 0.072719 | 0.090786 | 0.090786
660 | feeder2_line10 | 3 | 80.1 | 8.4651e-07 | 1.4964e-06 | 1.0568e-06 | 1.8681e-06
660 | feeder2_line11 | 1 | 354.6 | 11.6385 | 11.6406 | 3.2821 | 3.2828
660 | feeder2_line11 | 2 | 354.6 | 26.4702 | 26.4713 | 7.4648 | 7.4651
660 | feeder2_line11 | 3 | 354.6 | 45.2814 | 45.268 | 12.7697 | 12.7659
660 | feeder2_line12 | 1 | 80.1 | 5.45e-07 | 9.8813e-07 | 6.804e-07 | 1.2336e-06
660 | feeder2_line12 | 2 | 80.1 | 5.4652e-07 | 9.9034e-07 | 6.823e-07 | 1.2364e-06
660 | feeder2_line12 | 3 | 80.1 | 1.4594 | 1.4594 | 1.8219 | 1.822
660 | feeder2_line13 | 1 | 354.6 | 11.6385 | 11.6406 | 3.2822 | 3.2828
660 | feeder2_line13 | 2 | 354.6 | 26.4702 | 26.4713 | 7.4648 | 7.4651
660 | feeder2_line13 | 3 | 354.6 | 46.4806 | 46.4673 | 13.1079 | 13.1041
660 | feeder2_line14 | 1 | 80.1 | 6.7733 | 6.7732 | 8.456 | 8.456
660 | feeder2_line14 | 2 | 80.1 | 2.9804e-07 | 6.458e-07 | 3.7209e-07 | 8.0624e-07
660 | feeder2_line14 | 3 | 80.1 | 2.9874e-07 | 6.4741e-07 | 3.7296e-07 | 8.0825e-07
660 | feeder2_line15 | 1 | 354.6 | 11.1582 | 11.1686 | 3.1467 | 3.1496
660 | feeder2_line15 | 2 | 354.6 | 26.4702 | 26.4713 | 7.4648 | 7.4651
660 | feeder2_line15 | 3 | 354.6 | 46.4806 | 46.4673 | 13.1079 | 13.1041
660 | feeder2_line16 | 1 | 80.1 | 5.6992e-07 | 1.0268e-06 | 7.1152e-07 | 1.2819e-06
660 | feeder2_line16 | 2 | 80.1 | 0.028902 | 0.028899 | 0.036082 | 0.036079
660 | feeder2_line16 | 3 | 80.1 | 5.7286e-07 | 1.032e-06 | 7.1519e-07 | 1.2884e-06
660 | feeder2_line17 | 1 | 354.6 | 11.1582 | 11.1686 | 3.1467 | 3.1496
660 | feeder2_line17 | 2 | 354.6 | 26.4986 | 26.4997 | 7.4728 | 7.4731
660 | feeder2_line17 | 3 | 354.6 | 46.4806 | 46.4673 | 13.1079 | 13.1041
660 | feeder2_line18 | 1 | 80.1 | 5.447e-07 | 7.3478e-07 | 6.8002e-07 | 9.1732e-07
660 | feeder2_line18 | 2 | 80.1 | 5.467e-07 | 7.3695e-07 | 6.8252e-07 | 9.2003e-07
660 | feeder2_line18 | 3 | 80.1 | 1.2643 | 1.2642 | 1.5784 | 1.5783
660 | feeder2_line19 | 1 | 354.6 | 11.1582 | 11.1686 | 3.1467 | 3.1496
660 | feeder2_line19 | 2 | 354.6 | 26.4986 | 26.4997 | 7.4728 | 7.4731
660 | feeder2_line19 | 3 | 354.6 | 47.2924 | 47.2791 | 13.3368 | 13.3331
660 | feeder2_line20 | 1 | 99 | 5.4462e-07 | 8.8086e-07 | 5.5012e-07 | 8.8975e-07
660 | feeder2_line20 | 2 | 99 | 5.4675e-07 | 8.8363e-07 | 5.5227e-07 | 8.9255e-07
660 | feeder2_line20 | 3 | 99 | 0.31158 | 0.31153 | 0.31473 | 0.31468
660 | feeder2_line21 | 1 | 354.6 | 11.1583 | 11.1686 | 3.1467 | 3.1496
660 | feeder2_line21 | 2 | 354.6 | 26.4987 | 26.4997 | 7.4728 | 7.4731
660 | feeder2_line21 | 3 | 354.6 | 47.6027 | 47.5891 | 13.4243 | 13.4205
660 | feeder2_line22 | 1 | 99 | 5.6966e-07 | 1.0097e-06 | 5.7541e-07 | 1.0199e-06
660 | feeder2_line22 | 2 | 99 | 1.7078 | 1.7077 | 1.725 | 1.725
660 | feeder2_line22 | 3 | 99 | 5.7368e-07 | 1.0168e-06 | 5.7947e-07 | 1.027e-06
660 | feeder2_line23 | 1 | 99 | 5.6966e-07 | 9.452e-07 | 5.7541e-07 | 9.5475e-07
660 | feeder2_line23 | 2 | 99 | 5.7154e-07 | 9.4827e-07 | 5.7731e-07 | 9.5784e-07
660 | feeder2_line23 | 3 | 99 | 2.1921 | 2.1921 | 2.2143 | 2.2143
660 | feeder2_line24 | 1 | 354.6 | 11.1584 | 11.1686 | 3.1468 | 3.1496
660 | feeder2_line24 | 2 | 354.6 | 28.1691 | 28.17 | 7.9439 | 7.9442
660 | feeder2_line24 | 3 | 354.6 | 48.7289 | 48.7154 | 13.7419 | 13.7381
660 | feeder2_line25 | 1 | 99 | 1.7129 | 1.713 | 1.7303 | 1.7303
660 | feeder2_line25 | 2 | 99 | 4.9551e-08 | 6.8947e-07 | 5.0052e-08 | 6.9643e-07
660 | feeder2_line25 | 3 | 99 | 4.9375e-08 | 6.9223e-07 | 4.9874e-08 | 6.9922e-07
660 | feeder2_line26 | 1 | 99 | 0.085843 | 0.085851 | 0.08671 | 0.086718
660 | feeder2_line26 | 2 | 99 | 5.4682e-07 | 8.5421e-07 | 5.5235e-07 | 8.6284e-07
660 | feeder2_line26 | 3 | 99 | 5.4921e-07 | 8.5763e-07 | 5.5476e-07 | 8.6629e-07
660 | feeder2_line27 | 1 | 354.6 | 12.4589 | 12.4703 | 3.5135 | 3.5167
660 | feeder2_line27 | 2 | 354.6 | 28.1692 | 28.17 | 7.9439 | 7.9442
660 | feeder2_line27 | 3 | 354.6 | 48.7289 | 48.7154 | 13.7419 | 13.7381
660 | feeder2_line28 | 1 | 99 | 2.5207e-06 | 7.0651e-07 | 2.5462e-06 | 7.1365e-07
660 | feeder2_line28 | 2 | 99 | 1.2561 | 1.2561 | 1.2688 | 1.2688
660 | feeder2_line28 | 3 | 99 | 2.5505e-06 | 7.1235e-07 | 2.5763e-06 | 7.1954e-07
660 | feeder2_line29 | 1 | 354.6 | 12.4589 | 12.4703 | 3.5135 | 3.5167
660 | feeder2_line29 | 2 | 354.6 | 28.6801 | 28.6806 | 8.088 | 8.0882
660 | feeder2_line29 | 3 | 354.6 | 48.7289 | 48.7154 | 13.7419 | 13.7381
660 | feeder2_line30 | 1 | 266.4 | 46.9107 | 46.9093 | 17.6091 | 17.6086
660 | feeder2_line30 | 2 | 266.4 | 2.1068 | 2.1069 | 0.79085 | 0.79087
660 | feeder2_line30 | 3 | 266.4 | 2.1169 | 2.1167 | 0.79464 | 0.79456
660 | feeder2_line31 | 1 | 354.6 | 56.4795 | 56.4933 | 15.9277 | 15.9316
660 | feeder2_line31 | 2 | 354.6 | 30.1868 | 30.1867 | 8.5129 | 8.5129
660 | feeder2_line31 | 3 | 354.6 | 50.7171 | 50.7033 | 14.3026 | 14.2987
660 | feeder2_line32 | 1 | 354.6 | 56.4795 | 56.4933 | 15.9277 | 15.9316
660 | feeder2_line32 | 2 | 354.6 | 31.5978 | 31.5974 | 8.9108 | 8.9107
660 | feeder2_line32 | 3 | 354.6 | 50.7171 | 50.7033 | 14.3026 | 14.2987
660 | feeder2_line33 | 1 | 99 | 5.0352e-08 | 6.8171e-07 | 5.086e-08 | 6.886e-07
660 | feeder2_line33 | 2 | 99 | 1.8193 | 1.8193 | 1.8377 | 1.8376
660 | feeder2_line33 | 3 | 99 | 4.929e-08 | 6.8807e-07 | 4.9787e-08 | 6.9502e-07
660 | feeder2_line34 | 1 | 354.6 | 56.4795 | 56.4933 | 15.9277 | 15.9316
660 | feeder2_line34 | 2 | 354.6 | 31.5978 | 31.5974 | 8.9108 | 8.9107
660 | feeder2_line34 | 3 | 354.6 | 51.4577 | 51.4438 | 14.5115 | 14.5076
660 | feeder2_line35 | 1 | 99 | 2.9743e-07 | 7.5506e-07 | 3.0044e-07 | 7.6268e-07
660 | feeder2_line35 | 2 | 99 | 2.9832e-07 | 7.5783e-07 | 3.0133e-07 | 7.6548e-07
660 | feeder2_line35 | 3 | 99 | 0.74194 | 0.74194 | 0.74943 | 0.74943
660 | feeder2_line36 | 1 | 354.6 | 57.0602 | 57.0744 | 16.0914 | 16.0954
660 | feeder2_line36 | 2 | 354.6 | 31.5977 | 31.5974 | 8.9108 | 8.9107
660 | feeder2_line36 | 3 | 354.6 | 51.4576 | 51.4438 | 14.5115 | 14.5076
660 | feeder2_line37 | 1 | 99 | 1.2296 | 1.2298 | 1.242 | 1.2423
660 | feeder2_line37 | 2 | 99 | 2.9833e-07 | 8.3853e-07 | 3.0134e-07 | 8.47e-07
660 | feeder2_line37 | 3 | 99 | 2.999e-07 | 8.4337e-07 | 3.0293e-07 | 8.5189e-07
660 | feeder2_line38 | 1 | 99 | 3.2237e-07 | 7.7028e-07 | 3.2562e-07 | 7.7806e-07
660 | feeder2_line38 | 2 | 99 | 0.49994 | 0.49994 | 0.50499 | 0.50499
660 | feeder2_line38 | 3 | 99 | 3.2435e-07 | 7.7778e-07 | 3.2763e-07 | 7.8564e-07
660 | feeder2_line39 | 1 | 266.4 | 46.9107 | 46.9093 | 17.6091 | 17.6086
660 | feeder2_line39 | 2 | 266.4 | 1.7326 | 1.7328 | 0.65037 | 0.65043
660 | feeder2_line39 | 3 | 266.4 | 2.1169 | 2.1167 | 0.79464 | 0.79456
660 | feeder2_line40 | 1 | 354.6 | 58.769 | 58.7832 | 16.5733 | 16.5773
660 | feeder2_line40 | 2 | 354.6 | 31.5978 | 31.5974 | 8.9108 | 8.9107
660 | feeder2_line40 | 3 | 354.6 | 51.4577 | 51.4438 | 14.5115 | 14.5076
660 | feeder2_line41 | 1 | 99 | 1.7128 | 1.7128 | 1.7301 | 1.7301
660 | feeder2_line41 | 2 | 99 | 4.9665e-08 | 7.3273e-07 | 5.0167e-08 | 7.4013e-07
660 | feeder2_line41 | 3 | 99 | 4.9279e-08 | 7.3702e-07 | 4.9777e-08 | 7.4447e-07
660 | feeder2_line42 | 1 | 99 | 2.9704e-07 | 7.4311e-07 | 3.0004e-07 | 7.5062e-07
660 | feeder2_line42 | 2 | 99 | 2.9831e-07 | 7.4695e-07 | 3.0132e-07 | 7.5449e-07
660 | feeder2_line42 | 3 | 99 | 0.45865 | 0.45863 | 0.46328 | 0.46326
660 | feeder2_line43 | 1 | 266.4 | 46.9106 | 46.9093 | 17.6091 | 17.6086
660 | feeder2_line43 | 2 | 266.4 | 1.7326 | 1.7328 | 0.65039 | 0.65043
660 | feeder2_line43 | 3 | 266.4 | 1.701 | 1.7008 | 0.6385 | 0.63846
660 | feeder2_line44 | 1 | 354.6 | 58.7691 | 58.7832 | 16.5733 | 16.5773
660 | feeder2_line44 | 2 | 354.6 | 31.5978 | 31.5974 | 8.9108 | 8.9107
660 | feeder2_line44 | 3 | 354.6 | 51.7693 | 51.7553 | 14.5993 | 14.5954
660 | feeder2_line45 | 1 | 99 | 5.0355e-08 | 5.7598e-07 | 5.0864e-08 | 5.818e-07
660 | feeder2_line45 | 2 | 99 | 4.9686e-08 | 5.7785e-07 | 5.0188e-08 | 5.8368e-07
660 | feeder2_line45 | 3 | 99 | 0.3118 | 0.31173 | 0.31495 | 0.31487
660 | feeder2_line46 | 1 | 99 | 5.6886e-07 | 1.3471e-06 | 5.7461e-07 | 1.3607e-06
660 | feeder2_line46 | 2 | 99 | 5.7187e-07 | 1.3541e-06 | 5.7764e-07 | 1.3678e-06
660 | feeder2_line46 | 3 | 99 | 0.071998 | 0.071942 | 0.072726 | 0.072669
660 | feeder2_line47 | 1 | 266.4 | 46.9106 | 46.9093 | 17.6091 | 17.6086
660 | feeder2_line47 | 2 | 266.4 | 1.7328 | 1.7328 | 0.65045 | 0.65043
660 | feeder2_line47 | 3 | 266.4 | 1.6362 | 1.636 | 0.61418 | 0.61412
660 | feeder2_line48 | 1 | 99 | 44.9797 | 44.9783 | 45.434 | 45.4326
660 | feeder2_line48 | 2 | 99 | 4.9444e-08 | 7.2905e-07 | 4.9944e-08 | 7.3641e-07
660 | feeder2_line48 | 3 | 99 | 4.923e-08 | 7.328e-07 | 4.9728e-08 | 7.4021e-07
660 | feeder2_line49 | 1 | 266.4 | 1.931 | 1.9311 | 0.72486 | 0.72491
660 | feeder2_line49 | 2 | 266.4 | 1.7328 | 1.7328 | 0.65045 | 0.65043
660 | feeder2_line49 | 3 | 266.4 | 1.6361 | 1.636 | 0.61417 | 0.61412
660 | feeder2_line50 | 1 | 99 | 5.6871e-07 | 1.2256e-06 | 5.7446e-07 | 1.238e-06
660 | feeder2_line50 | 2 | 99 | 1.2654 | 1.2654 | 1.2781 | 1.2782
660 | feeder2_line50 | 3 | 99 | 5.7484e-07 | 1.2387e-06 | 5.8065e-07 | 1.2512e-06
660 | feeder2_line51 | 1 | 99 | 1.5916 | 1.5919 | 1.6077 | 1.608
660 | feeder2_line51 | 2 | 99 | 5.7188e-07 | 1.3379e-06 | 5.7766e-07 | 1.3514e-06
660 | feeder2_line51 | 3 | 99 | 5.7483e-07 | 1.3447e-06 | 5.8064e-07 | 1.3583e-06
660 | feeder2_line52 | 1 | 266.4 | 0.33932 | 0.33924 | 0.12737 | 0.12734
660 | feeder2_line52 | 2 | 266.4 | 0.50607 | 0.50604 | 0.18996 | 0.18995
660 | feeder2_line52 | 3 | 266.4 | 1.636 | 1.636 | 0.61413 | 0.61412
660 | feeder2_line53 | 1 | 99 | 5.4351e-07 | 7.4803e-07 | 5.49e-07 | 7.5559e-07
660 | feeder2_line53 | 2 | 99 | 0.50604 | 0.50604 | 0.51115 | 0.51115
660 | feeder2_line53 | 3 | 99 | 5.5021e-07 | 7.5599e-07 | 5.5576e-07 | 7.6363e-07
660 | feeder2_line54 | 1 | 266.4 | 0.33914 | 0.33924 | 0.12731 | 0.12734
660 | feeder2_line54 | 2 | 266.4 | 8.5321e-05 | 4.6137e-06 | 3.2028e-05 | 1.7319e-06
660 | feeder2_line54 | 3 | 266.4 | 1.6359 | 1.636 | 0.61409 | 0.61413
660 | feeder2_line55 | 1 | 99 | 0.045732 | 0.045741 | 0.046194 | 0.046203
660 | feeder2_line55 | 2 | 99 | 4.9748e-08 | 7.2802e-07 | 5.0251e-08 | 7.3538e-07
660 | feeder2_line55 | 3 | 99 | 4.9272e-08 | 7.3268e-07 | 4.9769e-08 | 7.4008e-07
660 | feeder2_line56 | 1 | 354.6 | 58.8147 | 58.8288 | 16.5862 | 16.5902
660 | feeder2_line56 | 2 | 354.6 | 31.5978 | 31.5974 | 8.9108 | 8.9107
660 | feeder2_line56 | 3 | 354.6 | 51.7693 | 51.7553 | 14.5994 | 14.5954
660 | feeder2_line57 | 1 | 99 | 7.5634e-07 | 1.5322e-06 | 7.6398e-07 | 1.5477e-06
660 | feeder2_line57 | 2 | 99 | 7.4234e-07 | 1.5406e-06 | 7.4984e-07 | 1.5562e-06
660 | feeder2_line57 | 3 | 99 | 1.636 | 1.636 | 1.6525 | 1.6526
660 | feeder2_line58 | 1 | 266.4 | 0.3392 | 0.33924 | 0.12733 | 0.12734
660 | feeder2_line58 | 2 | 266.4 | 1.8887e-05 | 2.6786e-06 | 7.0898e-06 | 1.0055e-06
660 | feeder2_line58 | 3 | 266.4 | 1.9029e-05 | 2.6919e-06 | 7.1432e-06 | 1.0105e-06
660 | feeder2_line59 | 1 | 99 | 5.042e-08 | 5.3261e-07 | 5.0929e-08 | 5.3799e-07
660 | feeder2_line59 | 2 | 99 | 4.9485e-08 | 5.3553e-07 | 4.9985e-08 | 5.4094e-07
660 | feeder2_line59 | 3 | 99 | 0.19387 | 0.19387 | 0.19583 | 0.19582
660 | feeder2_line60 | 1 | 99 | 2.9696e-07 | 8.0494e-07 | 2.9996e-07 | 8.1307e-07
660 | feeder2_line60 | 2 | 99 | 2.9831e-07 | 8.0935e-07 | 3.0133e-07 | 8.1752e-07
660 | feeder2_line60 | 3 | 99 | 1.4622 | 1.4622 | 1.477 | 1.477
660 | feeder2_line61 | 1 | 266.4 | 9.7178 | 9.7177 | 3.6478 | 3.6478
660 | feeder2_line61 | 2 | 266.4 | 3.4744 | 3.4746 | 1.3042 | 1.3043
660 | feeder2_line61 | 3 | 266.4 | 3.3973 | 3.3974 | 1.2753 | 1.2753
660 | feeder2_line62 | 1 | 354.6 | 67.3304 | 67.3445 | 18.9877 | 18.9917
660 | feeder2_line62 | 2 | 354.6 | 34.8347 | 34.8343 | 9.8237 | 9.8235
660 | feeder2_line62 | 3 | 354.6 | 55.1658 | 55.1518 | 15.5572 | 15.5533
660 | feeder2_line63 | 1 | 99 | 0.089985 | 0.089999 | 0.090894 | 0.090908
660 | feeder2_line63 | 2 | 99 | 5.7188e-07 | 1.2168e-06 | 5.7766e-07 | 1.2291e-06
660 | feeder2_line63 | 3 | 99 | 5.7483e-07 | 1.2231e-06 | 5.8064e-07 | 1.2354e-06
660 | feeder2_line64 | 1 | 99 | 0.24935 | 0.24935 | 0.25187 | 0.25187
660 | feeder2_line64 | 2 | 99 | 7.6528e-12 | 3.2056e-07 | 7.7301e-12 | 3.2379e-07
660 | feeder2_line64 | 3 | 99 | 1.0903e-11 | 3.2218e-07 | 1.1013e-11 | 3.2543e-07
660 | feeder2_line65 | 1 | 99 | 5.0356e-08 | 6.3831e-07 | 5.0864e-08 | 6.4476e-07
660 | feeder2_line65 | 2 | 99 | 0.50172 | 0.50171 | 0.50679 | 0.50678
660 | feeder2_line65 | 3 | 99 | 4.9267e-08 | 6.4396e-07 | 4.9764e-08 | 6.5047e-07
660 | feeder2_line66 | 1 | 354.6 | 67.3303 | 67.3445 | 18.9877 | 18.9917
660 | feeder2_line66 | 2 | 354.6 | 35.3308 | 35.3304 | 9.9636 | 9.9635
660 | feeder2_line66 | 3 | 354.6 | 55.1657 | 55.1518 | 15.5572 | 15.5533
660 | feeder2_line67 | 1 | 99 | 2.518e-08 | 3.6064e-07 | 2.5434e-08 | 3.6428e-07
660 | feeder2_line67 | 2 | 99 | 2.4891e-08 | 3.6148e-07 | 2.5142e-08 | 3.6513e-07
660 | feeder2_line67 | 3 | 99 | 1.6996 | 1.6996 | 1.7168 | 1.7167
660 | feeder2_line68 | 1 | 266.4 | 9.7178 | 9.7177 | 3.6478 | 3.6478
660 | feeder2_line68 | 2 | 266.4 | 3.4744 | 3.4746 | 1.3042 | 1.3043
660 | feeder2_line68 | 3 | 266.4 | 1.6985 | 1.6985 | 0.63757 | 0.63759
660 | feeder2_line69 | 1 | 99 | 1.4827 | 1.4828 | 1.4977 | 1.4978
660 | feeder2_line69 | 2 | 99 | 2.5356e-06 | 6.6385e-07 | 2.5612e-06 | 6.7055e-07
660 | feeder2_line69 | 3 | 99 | 2.5602e-06 | 6.6861e-07 | 2.5861e-06 | 6.7537e-07
660 | feeder2_line70 | 1 | 354.6 | 68.2012 | 68.2156 | 19.2333 | 19.2373
660 | feeder2_line70 | 2 | 354.6 | 35.3308 | 35.3304 | 9.9636 | 9.9635
660 | feeder2_line70 | 3 | 354.6 | 55.1656 | 55.1518 | 15.5571 | 15.5533
660 | feeder2_line71 | 1 | 99 | 5.035e-08 | 7.1241e-07 | 5.0858e-08 | 7.1961e-07
660 | feeder2_line71 | 2 | 99 | 0.053039 | 0.05309 | 0.053575 | 0.053627
660 | feeder2_line71 | 3 | 99 | 4.927e-08 | 7.186e-07 | 4.9768e-08 | 7.2586e-07
660 | feeder2_line72 | 1 | 354.6 | 68.2013 | 68.2156 | 19.2333 | 19.2373
660 | feeder2_line72 | 2 | 354.6 | 35.3839 | 35.3835 | 9.9785 | 9.9784
660 | feeder2_line72 | 3 | 354.6 | 55.1657 | 55.1518 | 15.5572 | 15.5533
660 | feeder2_line73 | 1 | 99 | 5.9563e-07 | 1.5267e-06 | 6.0165e-07 | 1.5421e-06
660 | feeder2_line73 | 2 | 99 | 1.819 | 1.819 | 1.8373 | 1.8373
660 | feeder2_line73 | 3 | 99 | 6.0041e-07 | 1.5407e-06 | 6.0647e-07 | 1.5563e-06
660 | feeder2_line74 | 1 | 99 | 5.036e-08 | 4.5534e-07 | 5.0869e-08 | 4.5994e-07
660 | feeder2_line74 | 2 | 99 | 1.7011 | 1.7011 | 1.7183 | 1.7183
660 | feeder2_line74 | 3 | 99 | 4.9254e-08 | 4.5953e-07 | 4.9751e-08 | 4.6417e-07
660 | feeder2_line75 | 1 | 266.4 | 9.7179 | 9.7177 | 3.6479 | 3.6478
660 | feeder2_line75 | 2 | 266.4 | 0.090037 | 0.09007 | 0.033798 | 0.03381
660 | feeder2_line75 | 3 | 266.4 | 1.6986 | 1.6985 | 0.6376 | 0.63759
660 | feeder2_line76 | 1 | 99 | 9.718 | 9.7177 | 9.8161 | 9.8158
660 | feeder2_line76 | 2 | 99 | 8.4533e-07 | 1.5786e-06 | 8.5387e-07 | 1.5946e-06
660 | feeder2_line76 | 3 | 99 | 8.5132e-07 | 1.5893e-06 | 8.5992e-07 | 1.6054e-06
660 | feeder2_line77 | 1 | 99 | 2.5186e-08 | 5.7218e-07 | 2.5441e-08 | 5.7796e-07
660 | feeder2_line77 | 2 | 99 | 2.4894e-08 | 5.7359e-07 | 2.5146e-08 | 5.7938e-07
660 | feeder2_line77 | 3 | 99 | 1.6986 | 1.6985 | 1.7158 | 1.7157
660 | feeder2_line78 | 1 | 266.4 | 1.5299e-11 | 9.4943e-07 | 5.7429e-12 | 3.5639e-07
660 | feeder2_line78 | 2 | 266.4 | 0.09007 | 0.09007 | 0.03381 | 0.03381
660 | feeder2_line78 | 3 | 266.4 | 1.7399e-11 | 9.5721e-07 | 6.5312e-12 | 3.5931e-07
660 | feeder2_line79 | 1 | 354.6 | 24.2703 | 24.2691 | 6.8444 | 6.8441
660 | feeder2_line79 | 2 | 354.6 | 26.9266 | 26.9261 | 7.5935 | 7.5934
660 | feeder2_line79 | 3 | 354.6 | 16.0569 | 16.0565 | 4.5282 | 4.5281
660 | feeder2_line80 | 1 | 354.6 | 92.4193 | 92.4322 | 26.063 | 26.0666
660 | feeder2_line80 | 2 | 354.6 | 62.0276 | 62.0261 | 17.4923 | 17.4919
660 | feeder2_line80 | 3 | 354.6 | 70.6746 | 70.6605 | 19.9308 | 19.9268
660 | feeder2_line81 | 1 | 354.6 | 92.4193 | 92.4322 | 26.063 | 26.0666
660 | feeder2_line81 | 2 | 354.6 | 62.0276 | 62.0261 | 17.4923 | 17.4919
660 | feeder2_line81 | 3 | 354.6 | 81.6626 | 81.649 | 23.0295 | 23.0257
660 | feeder2_line82 | 1 | 354.6 | 3.3195e-11 | 7.3142e-07 | 9.3612e-12 | 2.0627e-07
660 | feeder2_line82 | 2 | 354.6 | 3.3194e-11 | 7.3174e-07 | 9.3609e-12 | 2.0636e-07
660 | feeder2_line82 | 3 | 354.6 | 11.013 | 11.0134 | 3.1057 | 3.1059
660 | feeder2_line83 | 1 | 354.6 | 92.4195 | 92.4322 | 26.063 | 26.0666
660 | feeder2_line83 | 2 | 354.6 | 62.117 | 62.1154 | 17.5175 | 17.517
660 | feeder2_line83 | 3 | 354.6 | 81.6628 | 81.649 | 23.0295 | 23.0257
660 | feeder2_line84 | 1 | 354.6 | 1.4964e-11 | 1.293e-06 | 4.22e-12 | 3.6464e-07
660 | feeder2_line84 | 2 | 354.6 | 0.0895 | 0.089542 | 0.02524 | 0.025252
660 | feeder2_line84 | 3 | 354.6 | 1.1497e-11 | 1.3027e-06 | 3.2423e-12 | 3.6738e-07
660 | feeder2_line85 | 1 | 99 | 0.50042 | 0.50044 | 0.50548 | 0.5055
660 | feeder2_line85 | 2 | 99 | 5.0006e-08 | 4.6158e-07 | 5.0511e-08 | 4.6624e-07
660 | feeder2_line85 | 3 | 99 | 4.9289e-08 | 4.652e-07 | 4.9787e-08 | 4.699e-07
660 | feeder2_line86 | 1 | 354.6 | 92.9193 | 92.9319 | 26.204 | 26.2075
660 | feeder2_line86 | 2 | 354.6 | 62.1172 | 62.1154 | 17.5175 | 17.517
660 | feeder2_line86 | 3 | 354.6 | 81.6629 | 81.649 | 23.0296 | 23.0257
660 | feeder2_line87 | 1 | 354.6 | 92.9194 | 92.9319 | 26.204 | 26.2075
660 | feeder2_line87 | 2 | 354.6 | 62.5194 | 62.5176 | 17.631 | 17.6305
660 | feeder2_line87 | 3 | 354.6 | 81.744 | 81.7298 | 23.0525 | 23.0484
660 | feeder2_line88 | 1 | 354.6 | 0.0001113 | 3.352e-06 | 3.1387e-05 | 9.4529e-07
660 | feeder2_line88 | 2 | 354.6 | 0.40219 | 0.40223 | 0.11342 | 0.11343
660 | feeder2_line88 | 3 | 354.6 | 0.081383 | 0.081174 | 0.022951 | 0.022892
660 | feeder2_line89 | 1 | 354.6 | 92.9172 | 92.9319 | 26.2034 | 26.2075
660 | feeder2_line89 | 2 | 354.6 | 72.3657 | 72.3663 | 20.4077 | 20.4079
660 | feeder2_line89 | 3 | 354.6 | 81.7417 | 81.7298 | 23.0518 | 23.0484
660 | feeder2_line90 | 1 | 354.6 | 0.00071943 | 2.0258e-06 | 0.00020289 | 5.7131e-07
660 | feeder2_line90 | 2 | 354.6 | 9.8485 | 9.8491 | 2.7773 | 2.7775
660 | feeder2_line90 | 3 | 354.6 | 0.00072978 | 2.0397e-06 | 0.0002058 | 5.752e-07
660 | feeder2_line91 | 1 | 354.6 | 92.9171 | 92.9319 | 26.2034 | 26.2075
660 | feeder2_line91 | 2 | 354.6 | 72.3656 | 72.3663 | 20.4077 | 20.4079
660 | feeder2_line91 | 3 | 354.6 | 83.0676 | 83.0559 | 23.4257 | 23.4224
660 | feeder2_line92 | 1 | 354.6 | 8.6495e-12 | 1.0213e-06 | 2.4392e-12 | 2.88e-07
660 | feeder2_line92 | 2 | 354.6 | 1.4263e-11 | 1.0209e-06 | 4.0223e-12 | 2.8789e-07
660 | feeder2_line92 | 3 | 354.6 | 1.4648 | 1.4649 | 0.41309 | 0.4131
660 | feeder2_line93 | 1 | 99 | 2.5175e-08 | 3.4078e-07 | 2.5429e-08 | 3.4423e-07
660 | feeder2_line93 | 2 | 99 | 0.089487 | 0.089531 | 0.090391 | 0.090436
660 | feeder2_line93 | 3 | 99 | 2.4652e-08 | 3.4352e-07 | 2.4901e-08 | 3.4699e-07
660 | feeder2_line94 | 1 | 354.6 | 2.5174e-06 | 1.6597e-06 | 7.0994e-07 | 4.6805e-07
660 | feeder2_line94 | 2 | 354.6 | 9.7598 | 9.7599 | 2.7523 | 2.7524
660 | feeder2_line94 | 3 | 354.6 | 2.4646e-06 | 1.6717e-06 | 6.9504e-07 | 4.7144e-07
660 | feeder2_line95 | 1 | 99 | 3.5532e-06 | 2.5991e-06 | 3.5891e-06 | 2.6253e-06
660 | feeder2_line95 | 2 | 99 | 0.40209 | 0.40223 | 0.40615 | 0.4063
660 | feeder2_line95 | 3 | 99 | 3.5886e-06 | 2.6203e-06 | 3.6249e-06 | 2.6467e-06
660 | feeder2_line96 | 1 | 354.6 | 0.00012053 | 6.1942e-07 | 3.3991e-05 | 1.7468e-07
660 | feeder2_line96 | 2 | 354.6 | 0.00012064 | 6.1992e-07 | 3.4021e-05 | 1.7482e-07
660 | feeder2_line96 | 3 | 354.6 | 0.081365 | 0.081174 | 0.022946 | 0.022892
660 | feeder2_line97 | 1 | 354.6 | 94.6903 | 94.7052 | 26.7034 | 26.7076
660 | feeder2_line97 | 2 | 354.6 | 72.3658 | 72.3663 | 20.4077 | 20.4079
660 | feeder2_line97 | 3 | 354.6 | 83.0678 | 83.0559 | 23.4258 | 23.4224
660 | feeder2_line98 | 1 | 354.6 | 2.0569 | 2.0557 | 0.58007 | 0.57974
660 | feeder2_line98 | 2 | 354.6 | 0.0017008 | 6.199e-07 | 0.00047965 | 1.7482e-07
660 | feeder2_line98 | 3 | 354.6 | 0.0017178 | 6.2586e-07 | 0.00048443 | 1.765e-07
660 | feeder2_line99 | 1 | 99 | 2.5177e-08 | 4.454e-07 | 2.5431e-08 | 4.499e-07
660 | feeder2_line99 | 2 | 99 | 2.5025e-08 | 4.4546e-07 | 2.5277e-08 | 4.4996e-07
660 | feeder2_line99 | 3 | 99 | 0.081274 | 0.081174 | 0.082095 | 0.081994
660 | feeder2_line100 | 1 | 99 | 2.0556 | 2.0557 | 2.0764 | 2.0765
660 | feeder2_line100 | 2 | 99 | 2.506e-08 | 6.1166e-07 | 2.5314e-08 | 6.1784e-07
660 | feeder2_line100 | 3 | 99 | 2.4656e-08 | 6.1677e-07 | 2.4905e-08 | 6.23e-07
660 | feeder2_line101 | 1 | 354.6 | 9.7257 | 9.725 | 2.7427 | 2.7425
660 | feeder2_line101 | 2 | 354.6 | 26.9266 | 26.9261 | 7.5935 | 7.5934
660 | feeder2_line101 | 3 | 354.6 | 16.0568 | 16.0565 | 4.5282 | 4.5281
660 | feeder2_line102 | 1 | 99 | 14.5594 | 14.5589 | 14.7065 | 14.7059
660 | feeder2_line102 | 2 | 99 | 2.3291e-06 | 8.7455e-07 | 2.3526e-06 | 8.8338e-07
660 | feeder2_line102 | 3 | 99 | 2.3513e-06 | 8.8135e-07 | 2.375e-06 | 8.9025e-07
660 | feeder2_line103 | 1 | 99 | 5.4621e-07 | 7.9984e-07 | 5.5172e-07 | 8.0791e-07
660 | feeder2_line103 | 2 | 99 | 14.5062 | 14.5061 | 14.6527 | 14.6526
660 | feeder2_line103 | 3 | 99 | 5.5168e-07 | 8.0666e-07 | 5.5726e-07 | 8.1481e-07
660 | feeder2_line104 | 1 | 354.6 | 9.7256 | 9.725 | 2.7427 | 2.7425
660 | feeder2_line104 | 2 | 354.6 | 12.4302 | 12.4299 | 3.5054 | 3.5053
660 | feeder2_line104 | 3 | 354.6 | 16.0568 | 16.0565 | 4.5281 | 4.5281
660 | feeder2_line105 | 1 | 99 | 2.5297e-06 | 7.3596e-07 | 2.5553e-06 | 7.4339e-07
660 | feeder2_line105 | 2 | 99 | 2.5344e-06 | 7.3646e-07 | 2.56e-06 | 7.439e-07
660 | feeder2_line105 | 3 | 99 | 1.2661 | 1.2661 | 1.2789 | 1.2788
660 | feeder2_line106 | 1 | 354.6 | 9.7256 | 9.725 | 2.7427 | 2.7425
660 | feeder2_line106 | 2 | 354.6 | 12.4301 | 12.4299 | 3.5054 | 3.5053
660 | feeder2_line106 | 3 | 354.6 | 14.9652 | 14.9651 | 4.2203 | 4.2203
660 | feeder2_line107 | 1 | 99 | 3.2342e-07 | 8.9683e-07 | 3.2668e-07 | 9.0589e-07
660 | feeder2_line107 | 2 | 99 | 0.97549 | 0.97546 | 0.98534 | 0.98531
660 | feeder2_line107 | 3 | 99 | 3.2505e-07 | 9.0439e-07 | 3.2834e-07 | 9.1353e-07
660 | feeder2_line108 | 1 | 354.6 | 9.7256 | 9.725 | 2.7427 | 2.7425
660 | feeder2_line108 | 2 | 354.6 | 11.7413 | 11.7411 | 3.3112 | 3.3111
660 | feeder2_line108 | 3 | 354.6 | 14.9652 | 14.9651 | 4.2203 | 4.2203
660 | feeder2_line109 | 1 | 354.6 | 96.3965 | 96.4102 | 27.1846 | 27.1884
660 | feeder2_line109 | 2 | 354.6 | 72.367 | 72.3663 | 20.4081 | 20.4079
660 | feeder2_line109 | 3 | 354.6 | 83.0691 | 83.0559 | 23.4261 | 23.4224
660 | feeder2_line110 | 1 | 99 | 2.0158 | 2.0152 | 2.0362 | 2.0355
660 | feeder2_line110 | 2 | 99 | 0.00080027 | 9.0516e-07 | 0.00080835 | 9.143e-07
660 | feeder2_line110 | 3 | 99 | 0.00081042 | 9.1319e-07 | 0.00081861 | 9.2241e-07
660 | feeder2_line111 | 1 | 99 | 2.5169e-08 | 3.8042e-07 | 2.5423e-08 | 3.8426e-07
660 | feeder2_line111 | 2 | 99 | 0.045614 | 0.04566 | 0.046074 | 0.046121
660 | feeder2_line111 | 3 | 99 | 2.4647e-08 | 3.8351e-07 | 2.4896e-08 | 3.8739e-07
660 | feeder2_line112 | 1 | 99 | 3.2384e-07 | 9.1415e-07 | 3.2711e-07 | 9.2339e-07
660 | feeder2_line112 | 2 | 99 | 0.35653 | 0.35663 | 0.36013 | 0.36024
660 | feeder2_line112 | 3 | 99 | 3.2541e-07 | 9.2159e-07 | 3.287e-07 | 9.309e-07
660 | feeder2_line113 | 1 | 99 | 1.4138 | 1.4138 | 1.4281 | 1.4281
660 | feeder2_line113 | 2 | 99 | 3.2392e-07 | 9.0203e-07 | 3.2719e-07 | 9.1114e-07
660 | feeder2_line113 | 3 | 99 | 3.2575e-07 | 9.0967e-07 | 3.2904e-07 | 9.1886e-07
660 | feeder2_line114 | 1 | 99 | 14.4782 | 14.4776 | 14.6245 | 14.6239
660 | feeder2_line114 | 2 | 99 | 2.4962e-08 | 4.3488e-07 | 2.5214e-08 | 4.3927e-07
660 | feeder2_line114 | 3 | 99 | 2.4619e-08 | 4.3825e-07 | 2.4868e-08 | 4.4268e-07
660 | feeder2_line115 | 1 | 99 | 2.5158e-08 | 5.5964e-07 | 2.5412e-08 | 5.6529e-07
660 | feeder2_line115 | 2 | 99 | 9.8463 | 9.8463 | 9.9458 | 9.9457
660 | feeder2_line115 | 3 | 99 | 2.4623e-08 | 5.6431e-07 | 2.4872e-08 | 5.7001e-07
660 | feeder2_line116 | 1 | 354.6 | 9.7256 | 9.725 | 2.7427 | 2.7425
660 | feeder2_line116 | 2 | 354.6 | 2.0868 | 2.0866 | 0.5885 | 0.58844
660 | feeder2_line116 | 3 | 354.6 | 14.9652 | 14.9651 | 4.2203 | 4.2203
660 | feeder2_line117 | 1 | 99 | 5.0372e-08 | 6.4114e-07 | 5.088e-08 | 6.4762e-07
660 | feeder2_line117 | 2 | 99 | 0.072494 | 0.072558 | 0.073226 | 0.07329
660 | feeder2_line117 | 3 | 99 | 4.9351e-08 | 6.4601e-07 | 4.985e-08 | 6.5254e-07
660 | feeder2_line118 | 1 | 354.6 | 96.3965 | 96.4102 | 27.1846 | 27.1884
660 | feeder2_line118 | 2 | 354.6 | 72.4395 | 72.4388 | 20.4285 | 20.4283
660 | feeder2_line118 | 3 | 354.6 | 83.0691 | 83.0559 | 23.4261 | 23.4224
660 | feeder2_line119 | 1 | 99 | 2.5161e-08 | 6.0214e-07 | 2.5415e-08 | 6.0822e-07
660 | feeder2_line119 | 2 | 99 | 2.4952e-08 | 6.0263e-07 | 2.5204e-08 | 6.0872e-07
660 | feeder2_line119 | 3 | 99 | 10.4659 | 10.4662 | 10.5716 | 10.5719
660 | feeder2_line120 | 1 | 354.6 | 9.7256 | 9.725 | 2.7427 | 2.7425
660 | feeder2_line120 | 2 | 354.6 | 2.0868 | 2.0866 | 0.5885 | 0.58844
660 | feeder2_line120 | 3 | 354.6 | 5.0333 | 5.033 | 1.4194 | 1.4193
660 | feeder2_line121 | 1 | 99 | 3.2334e-07 | 9.3232e-07 | 3.2661e-07 | 9.4174e-07
660 | feeder2_line121 | 2 | 99 | 0.044288 | 0.044288 | 0.044736 | 0.044736
660 | feeder2_line121 | 3 | 99 | 3.2497e-07 | 9.4012e-07 | 3.2825e-07 | 9.4962e-07
660 | feeder2_line122 | 1 | 354.6 | 9.7255 | 9.725 | 2.7427 | 2.7425
660 | feeder2_line122 | 2 | 354.6 | 2.0478 | 2.0476 | 0.57748 | 0.57743
660 | feeder2_line122 | 3 | 354.6 | 5.0333 | 5.033 | 1.4194 | 1.4193
660 | feeder2_line123 | 1 | 99 | 5.7116e-07 | 9.6604e-07 | 5.7693e-07 | 9.758e-07
660 | feeder2_line123 | 2 | 99 | 5.7178e-07 | 9.6705e-07 | 5.7755e-07 | 9.7681e-07
660 | feeder2_line123 | 3 | 99 | 1.2599 | 1.2599 | 1.2726 | 1.2727
660 | feeder2_line124 | 1 | 354.6 | 9.7255 | 9.725 | 2.7427 | 2.7425
660 | feeder2_line124 | 2 | 354.6 | 2.0477 | 2.0476 | 0.57748 | 0.57743
660 | feeder2_line124 | 3 | 354.6 | 3.8669 | 3.8666 | 1.0905 | 1.0904
660 | feeder2_line125 | 1 | 99 | 5.7114e-07 | 8.9801e-07 | 5.7691e-07 | 9.0708e-07
660 | feeder2_line125 | 2 | 99 | 5.7178e-07 | 8.9897e-07 | 5.7755e-07 | 9.0805e-07
660 | feeder2_line125 | 3 | 99 | 2.0496 | 2.0495 | 2.0703 | 2.0702
660 | feeder2_line126 | 1 | 354.6 | 9.7256 | 9.725 | 2.7427 | 2.7425
660 | feeder2_line126 | 2 | 354.6 | 2.0479 | 2.0476 | 0.57752 | 0.57743
660 | feeder2_line126 | 3 | 354.6 | 1.8255 | 1.8251 | 0.5148 | 0.51469
660 | feeder2_line127 | 1 | 99 | 5.7111e-07 | 1.075e-06 | 5.7688e-07 | 1.0859e-06
660 | feeder2_line127 | 2 | 99 | 5.7178e-07 | 1.0762e-06 | 5.7756e-07 | 1.0871e-06
660 | feeder2_line127 | 3 | 99 | 0.97035 | 0.97035 | 0.98015 | 0.98015
660 | feeder2_line128 | 1 | 354.6 | 9.7255 | 9.725 | 2.7427 | 2.7425
660 | feeder2_line128 | 2 | 354.6 | 2.0478 | 2.0476 | 0.57751 | 0.57744
660 | feeder2_line128 | 3 | 354.6 | 1.0753 | 1.075 | 0.30325 | 0.30317
660 | feeder2_line129 | 1 | 99 | 5.4592e-07 | 8.7163e-07 | 5.5144e-07 | 8.8043e-07
660 | feeder2_line129 | 2 | 99 | 2.0476 | 2.0476 | 2.0683 | 2.0683
660 | feeder2_line129 | 3 | 99 | 5.514e-07 | 8.7907e-07 | 5.5697e-07 | 8.8795e-07
660 | feeder2_line130 | 1 | 354.6 | 9.7256 | 9.725 | 2.7427 | 2.7425
660 | feeder2_line130 | 2 | 354.6 | 0.0003064 | 4.6183e-06 | 8.6408e-05 | 1.3024e-06
660 | feeder2_line130 | 3 | 354.6 | 1.0753 | 1.075 | 0.30325 | 0.30317
660 | feeder2_line131 | 1 | 99 | 5.7105e-07 | 9.66e-07 | 5.7682e-07 | 9.7576e-07
660 | feeder2_line131 | 2 | 99 | 5.718e-07 | 9.6722e-07 | 5.7757e-07 | 9.7699e-07
660 | feeder2_line131 | 3 | 99 | 0.57744 | 0.57741 | 0.58327 | 0.58324
660 | feeder2_line132 | 1 | 354.6 | 9.7254 | 9.725 | 2.7426 | 2.7425
660 | feeder2_line132 | 2 | 354.6 | 0.00012508 | 2.9038e-06 | 3.5273e-05 | 8.189e-07
660 | feeder2_line132 | 3 | 354.6 | 0.49801 | 0.49791 | 0.14044 | 0.14042
660 | feeder2_line133 | 1 | 99 | 9.7253 | 9.725 | 9.8235 | 9.8232
660 | feeder2_line133 | 2 | 99 | 2.9835e-07 | 9.7493e-07 | 3.0137e-07 | 9.8478e-07
660 | feeder2_line133 | 3 | 99 | 3.0032e-07 | 9.821e-07 | 3.0336e-07 | 9.9202e-07
660 | feeder2_line134 | 1 | 354.6 | 4.913e-12 | 1.7763e-06 | 1.3855e-12 | 5.0092e-07
660 | feeder2_line134 | 2 | 354.6 | 4.9131e-12 | 1.7781e-06 | 1.3855e-12 | 5.0144e-07
660 | feeder2_line134 | 3 | 354.6 | 0.49793 | 0.49791 | 0.14042 | 0.14042
660 | feeder2_line135 | 1 | 99 | 0.052937 | 0.052987 | 0.053472 | 0.053522
660 | feeder2_line135 | 2 | 99 | 5.026e-08 | 5.8377e-07 | 5.0767e-08 | 5.8966e-07
660 | feeder2_line135 | 3 | 99 | 4.9376e-08 | 5.889e-07 | 4.9875e-08 | 5.9485e-07
660 | feeder2_line136 | 1 | 354.6 | 96.4493 | 96.4631 | 27.1995 | 27.2033
660 | feeder2_line136 | 2 | 354.6 | 72.4394 | 72.4388 | 20.4285 | 20.4283
660 | feeder2_line136 | 3 | 354.6 | 83.069 | 83.0559 | 23.4261 | 23.4224
660 | feeder2_line137 | 1 | 99 | 1.5479 | 1.548 | 1.5636 | 1.5636
660 | feeder2_line137 | 2 | 99 | 8.4708e-07 | 1.5724e-06 | 8.5564e-07 | 1.5883e-06
660 | feeder2_line137 | 3 | 99 | 8.5497e-07 | 1.5863e-06 | 8.6361e-07 | 1.6023e-06
660 | feeder2_line138 | 1 | 354.6 | 97.7504 | 97.7641 | 27.5664 | 27.5703
660 | feeder2_line138 | 2 | 354.6 | 72.4395 | 72.4388 | 20.4285 | 20.4283
660 | feeder2_line138 | 3 | 354.6 | 83.0691 | 83.0559 | 23.4261 | 23.4224
660 | feeder2_line139 | 1 | 99 | 5.0366e-08 | 4.9075e-07 | 5.0874e-08 | 4.9571e-07
660 | feeder2_line139 | 2 | 99 | 5.0275e-08 | 4.8996e-07 | 5.0782e-08 | 4.949e-07
660 | feeder2_line139 | 3 | 99 | 14.498 | 14.4978 | 14.6445 | 14.6443
660 | feeder2_line140 | 1 | 354.6 | 97.7505 | 97.7641 | 27.5664 | 27.5703
660 | feeder2_line140 | 2 | 354.6 | 72.4396 | 72.4388 | 20.4285 | 20.4283
660 | feeder2_line140 | 3 | 354.6 | 97.5638 | 97.5502 | 27.5138 | 27.5099
660 | feeder2_line141 | 1 | 99 | 2.5185e-06 | 4.8554e-07 | 2.544e-06 | 4.9045e-07
660 | feeder2_line141 | 2 | 99 | 0.46157 | 0.46158 | 0.46624 | 0.46624
660 | feeder2_line141 | 3 | 99 | 2.5465e-06 | 4.8906e-07 | 2.5722e-06 | 4.94e-07
660 | feeder2_line142 | 1 | 354.6 | 97.7503 | 97.7641 | 27.5664 | 27.5703
660 | feeder2_line142 | 2 | 354.6 | 72.8987 | 72.8981 | 20.558 | 20.5578
660 | feeder2_line142 | 3 | 354.6 | 97.5636 | 97.5502 | 27.5137 | 27.5099
660 | feeder2_line143 | 1 | 99 | 8.4885e-07 | 1.7255e-06 | 8.5743e-07 | 1.7429e-06
660 | feeder2_line143 | 2 | 99 | 0.97596 | 0.97592 | 0.98582 | 0.98578
660 | feeder2_line143 | 3 | 99 | 8.5542e-07 | 1.738e-06 | 8.6406e-07 | 1.7555e-06
660 | feeder2_line144 | 1 | 354.6 | 97.7501 | 97.7641 | 27.5663 | 27.5703
660 | feeder2_line144 | 2 | 354.6 | 73.5129 | 73.5124 | 20.7312 | 20.7311
660 | feeder2_line144 | 3 | 354.6 | 97.5634 | 97.5502 | 27.5137 | 27.5099
660 | feeder2_line145 | 1 | 99 | 2.5195e-08 | 4.8387e-07 | 2.5449e-08 | 4.8876e-07
660 | feeder2_line145 | 2 | 99 | 10.9182 | 10.9182 | 11.0285 | 11.0285
660 | feeder2_line145 | 3 | 99 | 2.4695e-08 | 4.8735e-07 | 2.4945e-08 | 4.9228e-07
660 | feeder2_line146 | 1 | 354.6 | 97.75 | 97.7641 | 27.5663 | 27.5703
660 | feeder2_line146 | 2 | 354.6 | 84.4031 | 84.4027 | 23.8023 | 23.8022
660 | feeder2_line146 | 3 | 354.6 | 97.5633 | 97.5502 | 27.5136 | 27.5099
660 | feeder2_line147 | 1 | 99 | 0.82492 | 0.82493 | 0.83326 | 0.83326
660 | feeder2_line147 | 2 | 99 | 1.1467e-06 | 2.2277e-06 | 1.1582e-06 | 2.2502e-06
660 | feeder2_line147 | 3 | 99 | 1.1573e-06 | 2.2481e-06 | 1.169e-06 | 2.2708e-06
660 | feeder2_line148 | 1 | 99 | 0.085129 | 0.085148 | 0.085989 | 0.086008
660 | feeder2_line148 | 2 | 99 | 5.985e-07 | 1.4927e-06 | 6.0454e-07 | 1.5078e-06
660 | feeder2_line148 | 3 | 99 | 6.0333e-07 | 1.5064e-06 | 6.0943e-07 | 1.5216e-06
660 | feeder2_line149 | 1 | 354.6 | 98.6586 | 98.6726 | 27.8225 | 27.8265
660 | feeder2_line149 | 2 | 354.6 | 84.4033 | 84.4027 | 23.8024 | 23.8022
660 | feeder2_line149 | 3 | 354.6 | 97.5635 | 97.5502 | 27.5137 | 27.5099
660 | feeder2_line150 | 1 | 354.6 | 98.6587 | 98.6726 | 27.8225 | 27.8265
660 | feeder2_line150 | 2 | 354.6 | 99.0001 | 98.9992 | 27.9188 | 27.9186
660 | feeder2_line150 | 3 | 354.6 | 97.5636 | 97.5502 | 27.5137 | 27.5099
660 | feeder2_line151 | 1 | 99 | 9.7293e-06 | 1.7769e-06 | 9.8276e-06 | 1.7949e-06
660 | feeder2_line151 | 2 | 99 | 14.6184 | 14.6183 | 14.7661 | 14.766
660 | feeder2_line151 | 3 | 99 | 9.8526e-06 | 1.7897e-06 | 9.9521e-06 | 1.8078e-06
660 | feeder2_line152 | 1 | 354.6 | 1.6417e-11 | 1.1848e-06 | 4.6297e-12 | 3.3412e-07
660 | feeder2_line152 | 2 | 354.6 | 9.9483e-12 | 1.1824e-06 | 2.8055e-12 | 3.3344e-07
660 | feeder2_line152 | 3 | 354.6 | 0.076249 | 0.076239 | 0.021503 | 0.0215
660 | feeder2_line153 | 1 | 99 | 0.04407 | 0.044076 | 0.044515 | 0.044521
660 | feeder2_line153 | 2 | 99 | 5.0397e-08 | 5.9141e-07 | 5.0906e-08 | 5.9738e-07
660 | feeder2_line153 | 3 | 99 | 4.9441e-08 | 5.969e-07 | 4.9941e-08 | 6.0293e-07
660 | feeder2_line154 | 1 | 99 | 5.7505e-07 | 8.8189e-07 | 5.8086e-07 | 8.908e-07
660 | feeder2_line154 | 2 | 99 | 5.7385e-07 | 8.8004e-07 | 5.7965e-07 | 8.8893e-07
660 | feeder2_line154 | 3 | 99 | 0.040422 | 0.040317 | 0.04083 | 0.040725
660 | feeder2_line155 | 1 | 99 | 98.7027 | 98.7166 | 99.6996 | 99.7138
660 | feeder2_line155 | 2 | 99 | 99 | 98.9992 | 100 | 99.9992
660 | feeder2_line155 | 3 | 99 | 97.6797 | 97.6664 | 98.6664 | 98.6529
660 | feeder2_line156 | 1 | 99 | 5.9993e-07 | 1.1603e-06 | 6.0599e-07 | 1.172e-06
660 | feeder2_line156 | 2 | 99 | 14.5294 | 14.5293 | 14.6762 | 14.6761
660 | feeder2_line156 | 3 | 99 | 6.0363e-07 | 1.1686e-06 | 6.0972e-07 | 1.1804e-06
660 | feeder2_line157 | 1 | 99 | 2.5191e-08 | 2.5191e-07 | 2.5446e-08 | 2.5446e-07
660 | feeder2_line157 | 2 | 99 | 0.089966 | 0.089966 | 0.090875 | 0.090875
660 | feeder2_line157 | 3 | 99 | 2.4704e-08 | 2.5371e-07 | 2.4953e-08 | 2.5628e-07
690 | feeder2_line1 | 1 | 354.6 | 49.2803 | 49.2722 | 13.8974 | 13.8951
690 | feeder2_line1 | 2 | 354.6 | 47.1233 | 47.1308 | 13.2891 | 13.2912
690 | feeder2_line1 | 3 | 354.6 | 60.6936 | 60.6963 | 17.1161 | 17.1168
690 | feeder2_line2 | 1 | 354.6 | 50.0162 | 50.0079 | 14.105 | 14.1026
690 | feeder2_line2 | 2 | 354.6 | 47.1235 | 47.1308 | 13.2892 | 13.2912
690 | feeder2_line2 | 3 | 354.6 | 60.6937 | 60.6963 | 17.1161 | 17.1168
690 | feeder2_line3 | 1 | 80.1 | 1.3927 | 1.3927 | 1.7387 | 1.7387
690 | feeder2_line3 | 2 | 80.1 | 5.7148e-07 | 1.0561e-06 | 7.1346e-07 | 1.3185e-06
690 | feeder2_line3 | 3 | 80.1 | 5.7207e-07 | 1.0572e-06 | 7.142e-07 | 1.3198e-06
690 | feeder2_line4 | 1 | 354.6 | 50.0163 | 50.0079 | 14.105 | 14.1026
690 | feeder2_line4 | 2 | 354.6 | 48.0516 | 48.0588 | 13.5509 | 13.553
690 | feeder2_line4 | 3 | 354.6 | 60.6939 | 60.6963 | 17.1162 | 17.1168
690 | feeder2_line5 | 1 | 80.1 | 5.7194e-07 | 9.98e-07 | 7.1404e-07 | 1.2459e-06
690 | feeder2_line5 | 2 | 80.1 | 1.7129 | 1.7129 | 2.1384 | 2.1385
690 | feeder2_line5 | 3 | 80.1 | 5.7211e-07 | 9.9828e-07 | 7.1425e-07 | 1.2463e-06
690 | feeder2_line6 | 1 | 80.1 | 5.72e-07 | 1.1741e-06 | 7.141e-07 | 1.4658e-06
690 | feeder2_line6 | 2 | 80.1 | 5.7153e-07 | 1.1732e-06 | 7.1352e-07 | 1.4646e-06
690 | feeder2_line6 | 3 | 80.1 | 1.9673 | 1.9674 | 2.4561 | 2.4561
690 | feeder2_line7 | 1 | 354.6 | 50.0165 | 50.0079 | 14.105 | 14.1026
690 | feeder2_line7 | 2 | 354.6 | 48.0517 | 48.0588 | 13.551 | 13.553
690 | feeder2_line7 | 3 | 354.6 | 62.1025 | 62.1047 | 17.5134 | 17.514
690 | feeder2_line8 | 1 | 80.1 | 0.072644 | 0.072643 | 0.090691 | 0.09069
690 | feeder2_line8 | 2 | 80.1 | 5.7163e-07 | 1.1314e-06 | 7.1365e-07 | 1.4125e-06
690 | feeder2_line8 | 3 | 80.1 | 5.7235e-07 | 1.1328e-06 | 7.1454e-07 | 1.4142e-06
690 | feeder2_line9 | 1 | 354.6 | 50.0892 | 50.0806 | 14.1255 | 14.1231
690 | feeder2_line9 | 2 | 354.6 | 48.0518 | 48.0588 | 13.551 | 13.553
690 | feeder2_line9 | 3 | 354.6 | 62.1025 | 62.1047 | 17.5134 | 17.514
690 | feeder2_line10 | 1 | 80.1 | 8.4578e-07 | 1.4952e-06 | 1.0559e-06 | 1.8667e-06
690 | feeder2_line10 | 2 | 80.1 | 0.07271 | 0.072711 | 0.090774 | 0.090775
690 | feeder2_line10 | 3 | 80.1 | 8.4613e-07 | 1.4958e-06 | 1.0563e-06 | 1.8674e-06
690 | feeder2_line11 | 1 | 354.6 | 50.0891 | 50.0806 | 14.1255 | 14.1231
690 | feeder2_line11 | 2 | 354.6 | 48.1234 | 48.1305 | 13.5712 | 13.5732
690 | feeder2_line11 | 3 | 354.6 | 62.1025 | 62.1047 | 17.5134 | 17.514
690 | feeder2_line12 | 1 | 80.1 | 5.4731e-07 | 9.9192e-07 | 6.8329e-07 | 1.2384e-06
690 | feeder2_line12 | 2 | 80.1 | 5.4681e-07 | 9.9102e-07 | 6.8266e-07 | 1.2372e-06
690 | feeder2_line12 | 3 | 80.1 | 0.98042 | 0.98042 | 1.224 | 1.224
690 | feeder2_line13 | 1 | 354.6 | 50.0891 | 50.0806 | 14.1255 | 14.1231
690 | feeder2_line13 | 2 | 354.6 | 48.1234 | 48.1305 | 13.5712 | 13.5732
690 | feeder2_line13 | 3 | 354.6 | 63.0735 | 63.0757 | 17.7872 | 17.7878
690 | feeder2_line14 | 1 | 80.1 | 0.95608 | 0.95608 | 1.1936 | 1.1936
690 | feeder2_line14 | 2 | 80.1 | 2.983e-07 | 6.4626e-07 | 3.7241e-07 | 8.0682e-07
690 | feeder2_line14 | 3 | 80.1 | 2.9868e-07 | 6.4715e-07 | 3.7289e-07 | 8.0793e-07
690 | feeder2_line15 | 1 | 354.6 | 51.0415 | 51.033 | 14.3941 | 14.3917
690 | feeder2_line15 | 2 | 354.6 | 48.1234 | 48.1305 | 13.5712 | 13.5732
690 | feeder2_line15 | 3 | 354.6 | 63.0735 | 63.0757 | 17.7872 | 17.7878
690 | feeder2_line16 | 1 | 80.1 | 5.7233e-07 | 1.0311e-06 | 7.1452e-07 | 1.2873e-06
690 | feeder2_line16 | 2 | 80.1 | 0.60203 | 0.60203 | 0.7516 | 0.75159
690 | feeder2_line16 | 3 | 80.1 | 5.7261e-07 | 1.0316e-06 | 7.1487e-07 | 1.2879e-06
690 | feeder2_line17 | 1 | 354.6 | 51.0415 | 51.033 | 14.3941 | 14.3917
690 | feeder2_line17 | 2 | 354.6 | 48.7062 | 48.7132 | 13.7355 | 13.7375
690 | feeder2_line17 | 3 | 354.6 | 63.0735 | 63.0757 | 17.7872 | 17.7878
690 | feeder2_line18 | 1 | 80.1 | 5.4776e-07 | 7.3851e-07 | 6.8384e-07 | 9.2199e-07
690 | feeder2_line18 | 2 | 80.1 | 5.4712e-07 | 7.3766e-07 | 6.8305e-07 | 9.2093e-07
690 | feeder2_line18 | 3 | 80.1 | 0.67575 | 0.67576 | 0.84363 | 0.84365
690 | feeder2_line19 | 1 | 354.6 | 51.0415 | 51.033 | 14.3941 | 14.3917
690 | feeder2_line19 | 2 | 354.6 | 48.7062 | 48.7132 | 13.7355 | 13.7375
690 | feeder2_line19 | 3 | 354.6 | 63.7483 | 63.7505 | 17.9775 | 17.9781
690 | feeder2_line20 | 1 | 99 | 5.4788e-07 | 8.8563e-07 | 5.5341e-07 | 8.9458e-07
690 | feeder2_line20 | 2 | 99 | 5.472e-07 | 8.8456e-07 | 5.5273e-07 | 8.935e-07
690 | feeder2_line20 | 3 | 99 | 1.4028 | 1.4029 | 1.417 | 1.417
690 | feeder2_line21 | 1 | 354.6 | 51.0417 | 51.033 | 14.3942 | 14.3917
690 | feeder2_line21 | 2 | 354.6 | 48.7064 | 48.7132 | 13.7356 | 13.7375
690 | feeder2_line21 | 3 | 354.6 | 64.4625 | 64.4645 | 18.1789 | 18.1795
690 | feeder2_line22 | 1 | 99 | 5.7288e-07 | 1.0154e-06 | 5.7866e-07 | 1.0257e-06
690 | feeder2_line22 | 2 | 99 | 5.3455 | 5.3455 | 5.3994 | 5.3995
690 | feeder2_line22 | 3 | 99 | 5.7335e-07 | 1.0162e-06 | 5.7914e-07 | 1.0265e-06
690 | feeder2_line23 | 1 | 99 | 5.7289e-07 | 9.5052e-07 | 5.7868e-07 | 9.6012e-07
690 | feeder2_line23 | 2 | 99 | 5.7216e-07 | 9.4932e-07 | 5.7794e-07 | 9.5891e-07
690 | feeder2_line23 | 3 | 99 | 2.1908 | 2.1907 | 2.2129 | 2.2129
690 | feeder2_line24 | 1 | 354.6 | 51.0417 | 51.033 | 14.3942 | 14.3917
690 | feeder2_line24 | 2 | 354.6 | 53.2058 | 53.2128 | 15.0045 | 15.0064
690 | feeder2_line24 | 3 | 354.6 | 65.581 | 65.5829 | 18.4944 | 18.4949
690 | feeder2_line25 | 1 | 99 | 5.3425 | 5.3424 | 5.3964 | 5.3964
690 | feeder2_line25 | 2 | 99 | 4.9843e-08 | 6.9032e-07 | 5.0347e-08 | 6.9729e-07
690 | feeder2_line25 | 3 | 99 | 4.9737e-08 | 6.9183e-07 | 5.0239e-08 | 6.9882e-07
690 | feeder2_line26 | 1 | 99 | 0.27288 | 0.27288 | 0.27564 | 0.27564
690 | feeder2_line26 | 2 | 99 | 5.4737e-07 | 8.5526e-07 | 5.529e-07 | 8.639e-07
690 | feeder2_line26 | 3 | 99 | 5.4868e-07 | 8.5714e-07 | 5.5422e-07 | 8.658e-07
690 | feeder2_line27 | 1 | 354.6 | 56.2145 | 56.2057 | 15.8529 | 15.8504
690 | feeder2_line27 | 2 | 354.6 | 53.2059 | 53.2128 | 15.0045 | 15.0064
690 | feeder2_line27 | 3 | 354.6 | 65.581 | 65.5829 | 18.4944 | 18.4949
690 | feeder2_line28 | 1 | 99 | 2.5421e-06 | 7.1119e-07 | 2.5678e-06 | 7.1837e-07
690 | feeder2_line28 | 2 | 99 | 0.75562 | 0.75564 | 0.76325 | 0.76327
690 | feeder2_line28 | 3 | 99 | 2.5459e-06 | 7.1189e-07 | 2.5716e-06 | 7.1908e-07
690 | feeder2_line29 | 1 | 354.6 | 56.2145 | 56.2057 | 15.8529 | 15.8504
690 | feeder2_line29 | 2 | 354.6 | 53.5756 | 53.5826 | 15.1087 | 15.1107
690 | feeder2_line29 | 3 | 354.6 | 65.581 | 65.5829 | 18.4944 | 18.4949
690 | feeder2_line30 | 1 | 266.4 | 22.1813 | 22.1811 | 8.3263 | 8.3262
690 | feeder2_line30 | 2 | 266.4 | 4.9371 | 4.9372 | 1.8533 | 1.8533
690 | feeder2_line30 | 3 | 266.4 | 7.9929 | 7.9927 | 3.0003 | 3.0003
690 | feeder2_line31 | 1 | 354.6 | 78.3814 | 78.3725 | 22.1042 | 22.1017
690 | feeder2_line31 | 2 | 354.6 | 57.0619 | 57.0686 | 16.0919 | 16.0938
690 | feeder2_line31 | 3 | 354.6 | 73.3803 | 73.3819 | 20.6938 | 20.6943
690 | feeder2_line32 | 1 | 354.6 | 78.3815 | 78.3725 | 22.1042 | 22.1017
690 | feeder2_line32 | 2 | 354.6 | 57.9366 | 57.9433 | 16.3386 | 16.3405
690 | feeder2_line32 | 3 | 354.6 | 73.3803 | 73.3819 | 20.6938 | 20.6943
690 | feeder2_line33 | 1 | 99 | 4.9947e-08 | 6.8694e-07 | 5.0451e-08 | 6.9388e-07
690 | feeder2_line33 | 2 | 99 | 0.88026 | 0.88026 | 0.88915 | 0.88915
690 | feeder2_line33 | 3 | 99 | 4.9796e-08 | 6.8762e-07 | 5.0299e-08 | 6.9457e-07
690 | feeder2_line34 | 1 | 354.6 | 78.3814 | 78.3725 | 22.1042 | 22.1017
690 | feeder2_line34 | 2 | 354.6 | 57.9366 | 57.9433 | 16.3386 | 16.3405
690 | feeder2_line34 | 3 | 354.6 | 73.4658 | 73.4673 | 20.7179 | 20.7184
690 | feeder2_line35 | 1 | 99 | 2.9955e-07 | 7.609e-07 | 3.0258e-07 | 7.6858e-07
690 | feeder2_line35 | 2 | 99 | 2.9897e-07 | 7.5936e-07 | 3.0199e-07 | 7.6703e-07
690 | feeder2_line35 | 3 | 99 | 0.085461 | 0.085463 | 0.086324 | 0.086326
690 | feeder2_line36 | 1 | 354.6 | 78.4095 | 78.4003 | 22.1121 | 22.1095
690 | feeder2_line36 | 2 | 354.6 | 57.9365 | 57.9433 | 16.3386 | 16.3405
690 | feeder2_line36 | 3 | 354.6 | 73.4657 | 73.4673 | 20.7179 | 20.7184
690 | feeder2_line37 | 1 | 99 | 0.028079 | 0.027855 | 0.028363 | 0.028136
690 | feeder2_line37 | 2 | 99 | 2.9902e-07 | 8.4031e-07 | 3.0204e-07 | 8.488e-07
690 | feeder2_line37 | 3 | 99 | 2.9986e-07 | 8.4289e-07 | 3.0289e-07 | 8.5141e-07
690 | feeder2_line38 | 1 | 99 | 3.2425e-07 | 7.762e-07 | 3.2753e-07 | 7.8404e-07
690 | feeder2_line38 | 2 | 99 | 0.2576 | 0.2576 | 0.2602 | 0.2602
690 | feeder2_line38 | 3 | 99 | 3.2448e-07 | 7.7715e-07 | 3.2776e-07 | 7.85e-07
690 | feeder2_line39 | 1 | 266.4 | 22.1813 | 22.1811 | 8.3263 | 8.3262
690 | feeder2_line39 | 2 | 266.4 | 4.7367 | 4.7368 | 1.778 | 1.7781
690 | feeder2_line39 | 3 | 266.4 | 7.9929 | 7.9927 | 3.0003 | 3.0003
690 | feeder2_line40 | 1 | 354.6 | 83.3952 | 83.386 | 23.5181 | 23.5155
690 | feeder2_line40 | 2 | 354.6 | 57.9366 | 57.9433 | 16.3386 | 16.3405
690 | feeder2_line40 | 3 | 354.6 | 73.4658 | 73.4673 | 20.7179 | 20.7184
690 | feeder2_line41 | 1 | 99 | 5.3379 | 5.3379 | 5.3918 | 5.3918
690 | feeder2_line41 | 2 | 99 | 4.9999e-08 | 7.3433e-07 | 5.0504e-08 | 7.4174e-07
690 | feeder2_line41 | 3 | 99 | 4.9809e-08 | 7.3662e-07 | 5.0312e-08 | 7.4406e-07
690 | feeder2_line42 | 1 | 99 | 2.9921e-07 | 7.4905e-07 | 3.0223e-07 | 7.5661e-07
690 | feeder2_line42 | 2 | 99 | 2.9885e-07 | 7.4815e-07 | 3.0187e-07 | 7.5571e-07
690 | feeder2_line42 | 3 | 99 | 5.7907 | 5.7908 | 5.8492 | 5.8492
690 | feeder2_line43 | 1 | 266.4 | 22.1812 | 22.1811 | 8.3263 | 8.3262
690 | feeder2_line43 | 2 | 266.4 | 4.7367 | 4.7368 | 1.7781 | 1.7781
690 | feeder2_line43 | 3 | 266.4 | 2.4282 | 2.4282 | 0.91148 | 0.91148
690 | feeder2_line44 | 1 | 354.6 | 83.3952 | 83.386 | 23.5181 | 23.5155
690 | feeder2_line44 | 2 | 354.6 | 57.9366 | 57.9433 | 16.3386 | 16.3405
690 | feeder2_line44 | 3 | 354.6 | 74.2643 | 74.2657 | 20.9431 | 20.9435
690 | feeder2_line45 | 1 | 99 | 4.9956e-08 | 5.8054e-07 | 5.0461e-08 | 5.864e-07
690 | feeder2_line45 | 2 | 99 | 5.0014e-08 | 5.7915e-07 | 5.052e-08 | 5.85e-07
690 | feeder2_line45 | 3 | 99 | 1.4043 | 1.4043 | 1.4185 | 1.4185
690 | feeder2_line46 | 1 | 99 | 5.7346e-07 | 1.3579e-06 | 5.7925e-07 | 1.3716e-06
690 | feeder2_line46 | 2 | 99 | 5.7277e-07 | 1.3563e-06 | 5.7855e-07 | 1.37e-06
690 | feeder2_line46 | 3 | 99 | 1.4722 | 1.4721 | 1.487 | 1.487
690 | feeder2_line47 | 1 | 266.4 | 22.1812 | 22.1811 | 8.3263 | 8.3262
690 | feeder2_line47 | 2 | 266.4 | 4.7369 | 4.7368 | 1.7781 | 1.7781
690 | feeder2_line47 | 3 | 266.4 | 1.2292 | 1.229 | 0.46141 | 0.46132
690 | feeder2_line48 | 1 | 99 | 10.5531 | 10.5533 | 10.6597 | 10.6598
690 | feeder2_line48 | 2 | 99 | 4.9863e-08 | 7.3023e-07 | 5.0366e-08 | 7.376e-07
690 | feeder2_line48 | 3 | 99 | 4.9767e-08 | 7.3213e-07 | 5.027e-08 | 7.3953e-07
690 | feeder2_line49 | 1 | 266.4 | 11.6281 | 11.6279 | 4.3649 | 4.3648
690 | feeder2_line49 | 2 | 266.4 | 4.7369 | 4.7368 | 1.7781 | 1.7781
690 | feeder2_line49 | 3 | 266.4 | 1.2292 | 1.229 | 0.46141 | 0.46132
690 | feeder2_line50 | 1 | 99 | 5.7336e-07 | 1.2356e-06 | 5.7916e-07 | 1.2481e-06
690 | feeder2_line50 | 2 | 99 | 1.9669 | 1.967 | 1.9868 | 1.9869
690 | feeder2_line50 | 3 | 99 | 5.7428e-07 | 1.2375e-06 | 5.8008e-07 | 1.25e-06
690 | feeder2_line51 | 1 | 99 | 11.3679 | 11.3679 | 11.4827 | 11.4827
690 | feeder2_line51 | 2 | 99 | 5.7274e-07 | 1.3399e-06 | 5.7852e-07 | 1.3535e-06
690 | feeder2_line51 | 3 | 99 | 5.7426e-07 | 1.3434e-06 | 5.8006e-07 | 1.357e-06
690 | feeder2_line52 | 1 | 266.4 | 0.26203 | 0.2619 | 0.09836 | 0.098311
690 | feeder2_line52 | 2 | 266.4 | 2.7741 | 2.7741 | 1.0413 | 1.0413
690 | feeder2_line52 | 3 | 266.4 | 1.2291 | 1.229 | 0.46136 | 0.46132
690 | feeder2_line53 | 1 | 99 | 5.4839e-07 | 7.541e-07 | 5.5393e-07 | 7.6172e-07
690 | feeder2_line53 | 2 | 99 | 2.7742 | 2.7741 | 2.8022 | 2.8022
690 | feeder2_line53 | 3 | 99 | 5.4939e-07 | 7.5528e-07 | 5.5494e-07 | 7.6291e-07
690 | feeder2_line54 | 1 | 266.4 | 0.26184 | 0.2619 | 0.098289 | 0.098311
690 | feeder2_line54 | 2 | 266.4 | 8.545e-05 | 4.6212e-06 | 3.2076e-05 | 1.7347e-06
690 | feeder2_line54 | 3 | 266.4 | 1.2289 | 1.229 | 0.46129 | 0.46132
690 | feeder2_line55 | 1 | 99 | 0.045441 | 0.045436 | 0.0459 | 0.045895
690 | feeder2_line55 | 2 | 99 | 5.0074e-08 | 7.2986e-07 | 5.058e-08 | 7.3723e-07
690 | feeder2_line55 | 3 | 99 | 4.9845e-08 | 7.3238e-07 | 5.0348e-08 | 7.3978e-07
690 | feeder2_line56 | 1 | 354.6 | 83.4407 | 83.4314 | 23.5309 | 23.5283
690 | feeder2_line56 | 2 | 354.6 | 57.9367 | 57.9433 | 16.3386 | 16.3405
690 | feeder2_line56 | 3 | 354.6 | 74.2643 | 74.2657 | 20.9431 | 20.9435
690 | feeder2_line57 | 1 | 99 | 7.4931e-07 | 1.5446e-06 | 7.5688e-07 | 1.5603e-06
690 | feeder2_line57 | 2 | 99 | 7.4804e-07 | 1.543e-06 | 7.556e-07 | 1.5586e-06
690 | feeder2_line57 | 3 | 99 | 1.229 | 1.229 | 1.2414 | 1.2414
690 | feeder2_line58 | 1 | 266.4 | 0.2619 | 0.2619 | 0.098311 | 0.098311
690 | feeder2_line58 | 2 | 266.4 | 1.8926e-05 | 2.683e-06 | 7.1043e-06 | 1.0071e-06
690 | feeder2_line58 | 3 | 266.4 | 1.8984e-05 | 2.6898e-06 | 7.1262e-06 | 1.0097e-06
690 | feeder2_line59 | 1 | 99 | 4.9956e-08 | 5.3693e-07 | 5.0461e-08 | 5.4235e-07
690 | feeder2_line59 | 2 | 99 | 4.9865e-08 | 5.3637e-07 | 5.0369e-08 | 5.4178e-07
690 | feeder2_line59 | 3 | 99 | 0.24719 | 0.24719 | 0.24969 | 0.24969
690 | feeder2_line60 | 1 | 99 | 2.9918e-07 | 8.1147e-07 | 3.022e-07 | 8.1967e-07
690 | feeder2_line60 | 2 | 99 | 2.9885e-07 | 8.1061e-07 | 3.0187e-07 | 8.188e-07
690 | feeder2_line60 | 3 | 99 | 0.98221 | 0.98221 | 0.99214 | 0.99213
690 | feeder2_line61 | 1 | 266.4 | 1.227 | 1.2272 | 0.46059 | 0.46066
690 | feeder2_line61 | 2 | 266.4 | 3.226 | 3.2262 | 1.2109 | 1.211
690 | feeder2_line61 | 3 | 266.4 | 6.4922 | 6.4924 | 2.437 | 2.4371
690 | feeder2_line62 | 1 | 354.6 | 84.6675 | 84.6585 | 23.8769 | 23.8744
690 | feeder2_line62 | 2 | 354.6 | 60.8142 | 60.8212 | 17.1501 | 17.1521
690 | feeder2_line62 | 3 | 354.6 | 80.4296 | 80.4312 | 22.6818 | 22.6822
690 | feeder2_line63 | 1 | 99 | 0.089109 | 0.089099 | 0.090009 | 0.089999
690 | feeder2_line63 | 2 | 99 | 5.7276e-07 | 1.2187e-06 | 5.7855e-07 | 1.231e-06
690 | feeder2_line63 | 3 | 99 | 5.7427e-07 | 1.2219e-06 | 5.8007e-07 | 1.2343e-06
690 | feeder2_line64 | 1 | 99 | 0.17307 | 0.17306 | 0.17481 | 0.1748
690 | feeder2_line64 | 2 | 99 | 9.5031e-12 | 3.2104e-07 | 9.5991e-12 | 3.2428e-07
690 | feeder2_line64 | 3 | 99 | 1.7442e-11 | 3.2188e-07 | 1.7618e-11 | 3.2513e-07
690 | feeder2_line65 | 1 | 99 | 4.9966e-08 | 6.4374e-07 | 5.0471e-08 | 6.5024e-07
690 | feeder2_line65 | 2 | 99 | 1.7135 | 1.7135 | 1.7308 | 1.7308
690 | feeder2_line65 | 3 | 99 | 4.9881e-08 | 6.4387e-07 | 5.0384e-08 | 6.5038e-07
690 | feeder2_line66 | 1 | 354.6 | 84.6675 | 84.6585 | 23.8769 | 23.8744
690 | feeder2_line66 | 2 | 354.6 | 61.9978 | 62.0048 | 17.4839 | 17.4859
690 | feeder2_line66 | 3 | 354.6 | 80.4296 | 80.4312 | 22.6818 | 22.6822
690 | feeder2_line67 | 1 | 99 | 2.4977e-08 | 3.637e-07 | 2.523e-08 | 3.6737e-07
690 | feeder2_line67 | 2 | 99 | 2.5054e-08 | 3.6248e-07 | 2.5307e-08 | 3.6614e-07
690 | feeder2_line67 | 3 | 99 | 5.3331 | 5.3332 | 5.387 | 5.387
690 | feeder2_line68 | 1 | 266.4 | 1.2271 | 1.2272 | 0.46061 | 0.46066
690 | feeder2_line68 | 2 | 266.4 | 3.226 | 3.2262 | 1.211 | 1.211
690 | feeder2_line68 | 3 | 266.4 | 1.2209 | 1.2211 | 0.45829 | 0.45835
690 | feeder2_line69 | 1 | 99 | 0.10071 | 0.10066 | 0.10173 | 0.10167
690 | feeder2_line69 | 2 | 99 | 2.5421e-06 | 6.6586e-07 | 2.5678e-06 | 6.7258e-07
690 | feeder2_line69 | 3 | 99 | 2.5559e-06 | 6.6857e-07 | 2.5817e-06 | 6.7532e-07
690 | feeder2_line70 | 1 | 354.6 | 84.7679 | 84.759 | 23.9052 | 23.9027
690 | feeder2_line70 | 2 | 354.6 | 61.9977 | 62.0048 | 17.4838 | 17.4859
690 | feeder2_line70 | 3 | 354.6 | 80.4295 | 80.4312 | 22.6817 | 22.6822
690 | feeder2_line71 | 1 | 99 | 4.9978e-08 | 7.1853e-07 | 5.0483e-08 | 7.2578e-07
690 | feeder2_line71 | 2 | 99 | 0.052927 | 0.052939 | 0.053461 | 0.053473
690 | feeder2_line71 | 3 | 99 | 4.9892e-08 | 7.186e-07 | 5.0396e-08 | 7.2586e-07
690 | feeder2_line72 | 1 | 354.6 | 84.768 | 84.759 | 23.9053 | 23.9027
690 | feeder2_line72 | 2 | 354.6 | 62.0507 | 62.0578 | 17.4988 | 17.5008
690 | feeder2_line72 | 3 | 354.6 | 80.4296 | 80.4312 | 22.6818 | 22.6822
690 | feeder2_line73 | 1 | 99 | 6.0035e-07 | 1.5397e-06 | 6.0642e-07 | 1.5553e-06
690 | feeder2_line73 | 2 | 99 | 0.88048 | 0.88048 | 0.88938 | 0.88938
690 | feeder2_line73 | 3 | 99 | 6.0047e-07 | 1.5401e-06 | 6.0653e-07 | 1.5557e-06
690 | feeder2_line74 | 1 | 99 | 4.9957e-08 | 4.5923e-07 | 5.0461e-08 | 4.6387e-07
690 | feeder2_line74 | 2 | 99 | 1.223 | 1.223 | 1.2354 | 1.2354
690 | feeder2_line74 | 3 | 99 | 4.9867e-08 | 4.5936e-07 | 5.037e-08 | 4.64e-07
690 | feeder2_line75 | 1 | 266.4 | 1.2272 | 1.2272 | 0.46064 | 0.46066
690 | feeder2_line75 | 2 | 266.4 | 1.4774 | 1.4774 | 0.55458 | 0.55458
690 | feeder2_line75 | 3 | 266.4 | 1.221 | 1.2211 | 0.45833 | 0.45835
690 | feeder2_line76 | 1 | 99 | 1.2272 | 1.2272 | 1.2396 | 1.2396
690 | feeder2_line76 | 2 | 99 | 8.476e-07 | 1.5829e-06 | 8.5616e-07 | 1.5989e-06
690 | feeder2_line76 | 3 | 99 | 8.5083e-07 | 1.5887e-06 | 8.5943e-07 | 1.6048e-06
690 | feeder2_line77 | 1 | 99 | 2.4983e-08 | 5.771e-07 | 2.5236e-08 | 5.8293e-07
690 | feeder2_line77 | 2 | 99 | 2.5059e-08 | 5.7516e-07 | 2.5312e-08 | 5.8097e-07
690 | feeder2_line77 | 3 | 99 | 1.221 | 1.2211 | 1.2334 | 1.2334
690 | feeder2_line78 | 1 | 266.4 | 4.859e-12 | 9.5707e-07 | 1.8239e-12 | 3.5926e-07
690 | feeder2_line78 | 2 | 266.4 | 1.4774 | 1.4774 | 0.55459 | 0.55458
690 | feeder2_line78 | 3 | 266.4 | 9.8001e-12 | 9.5724e-07 | 3.6787e-12 | 3.5933e-07
690 | feeder2_line79 | 1 | 354.6 | 8.8245 | 8.8242 | 2.4886 | 2.4885
690 | feeder2_line79 | 2 | 354.6 | 18.6554 | 18.6547 | 5.261 | 5.2608
690 | feeder2_line79 | 3 | 354.6 | 5.6116 | 5.6113 | 1.5825 | 1.5824
690 | feeder2_line80 | 1 | 354.6 | 93.501 | 93.4915 | 26.368 | 26.3654
690 | feeder2_line80 | 2 | 354.6 | 80.505 | 80.5113 | 22.703 | 22.7048
690 | feeder2_line80 | 3 | 354.6 | 85.3726 | 85.3737 | 24.0757 | 24.0761
690 | feeder2_line81 | 1 | 354.6 | 93.501 | 93.4915 | 26.368 | 26.3654
690 | feeder2_line81 | 2 | 354.6 | 80.505 | 80.5113 | 22.703 | 22.7048
690 | feeder2_line81 | 3 | 354.6 | 86.4868 | 86.488 | 24.39 | 24.3903
690 | feeder2_line82 | 1 | 354.6 | 2.2484e-11 | 7.3746e-07 | 6.3407e-12 | 2.0797e-07
690 | feeder2_line82 | 2 | 354.6 | 2.479e-11 | 7.3425e-07 | 6.991e-12 | 2.0706e-07
690 | feeder2_line82 | 3 | 354.6 | 1.1144 | 1.1144 | 0.31426 | 0.31426
690 | feeder2_line83 | 1 | 354.6 | 93.5012 | 93.4915 | 26.3681 | 26.3654
690 | feeder2_line83 | 2 | 354.6 | 80.5942 | 80.6004 | 22.7282 | 22.7299
690 | feeder2_line83 | 3 | 354.6 | 86.487 | 86.488 | 24.39 | 24.3903
690 | feeder2_line84 | 1 | 354.6 | 7.6779e-12 | 1.3037e-06 | 2.1652e-12 | 3.6765e-07
690 | feeder2_line84 | 2 | 354.6 | 0.089251 | 0.089257 | 0.025169 | 0.025171
690 | feeder2_line84 | 3 | 354.6 | 6.3639e-12 | 1.3035e-06 | 1.7947e-12 | 3.6759e-07
690 | feeder2_line85 | 1 | 99 | 0.25785 | 0.25784 | 0.26046 | 0.26045
690 | feeder2_line85 | 2 | 99 | 5.0313e-08 | 4.6322e-07 | 5.0822e-08 | 4.679e-07
690 | feeder2_line85 | 3 | 99 | 4.9939e-08 | 4.6531e-07 | 5.0444e-08 | 4.7001e-07
690 | feeder2_line86 | 1 | 354.6 | 93.759 | 93.7492 | 26.4408 | 26.438
690 | feeder2_line86 | 2 | 354.6 | 80.5944 | 80.6004 | 22.7282 | 22.7299
690 | feeder2_line86 | 3 | 354.6 | 86.4871 | 86.488 | 24.39 | 24.3903
690 | feeder2_line87 | 1 | 354.6 | 93.7591 | 93.7492 | 26.4408 | 26.438
690 | feeder2_line87 | 2 | 354.6 | 81.6982 | 81.7041 | 23.0395 | 23.0412
690 | feeder2_line87 | 3 | 354.6 | 87.1521 | 87.1528 | 24.5776 | 24.5778
690 | feeder2_line88 | 1 | 354.6 | 0.00011443 | 3.3805e-06 | 3.2271e-05 | 9.5334e-07
690 | feeder2_line88 | 2 | 354.6 | 1.3918 | 1.3918 | 0.3925 | 0.3925
690 | feeder2_line88 | 3 | 354.6 | 1.0459 | 1.0458 | 0.29494 | 0.29492
690 | feeder2_line89 | 1 | 354.6 | 93.7569 | 93.7492 | 26.4402 | 26.438
690 | feeder2_line89 | 2 | 354.6 | 83.1541 | 83.1623 | 23.4501 | 23.4524
690 | feeder2_line89 | 3 | 354.6 | 87.1498 | 87.1528 | 24.5769 | 24.5778
690 | feeder2_line90 | 1 | 354.6 | 0.00072804 | 2.0408e-06 | 0.00020531 | 5.7551e-07
690 | feeder2_line90 | 2 | 354.6 | 1.4721 | 1.4726 | 0.41515 | 0.41528
690 | feeder2_line90 | 3 | 354.6 | 0.00072835 | 2.0411e-06 | 0.0002054 | 5.756e-07
690 | feeder2_line91 | 1 | 354.6 | 93.7568 | 93.7492 | 26.4401 | 26.438
690 | feeder2_line91 | 2 | 354.6 | 83.154 | 83.1623 | 23.4501 | 23.4524
690 | feeder2_line91 | 3 | 354.6 | 88.1345 | 88.1375 | 24.8546 | 24.8555
690 | feeder2_line92 | 1 | 354.6 | 2.0693e-12 | 1.0296e-06 | 5.8357e-13 | 2.9036e-07
690 | feeder2_line92 | 2 | 354.6 | 1.8305e-11 | 1.0248e-06 | 5.1622e-12 | 2.8901e-07
690 | feeder2_line92 | 3 | 354.6 | 0.98502 | 0.98502 | 0.27778 | 0.27778
690 | feeder2_line93 | 1 | 99 | 2.501e-08 | 3.4371e-07 | 2.5262e-08 | 3.4718e-07
690 | feeder2_line93 | 2 | 99 | 0.089198 | 0.089205 | 0.090099 | 0.090106
690 | feeder2_line93 | 3 | 99 | 2.4989e-08 | 3.436e-07 | 2.5241e-08 | 3.4707e-07
690 | feeder2_line94 | 1 | 354.6 | 2.501e-06 | 1.6733e-06 | 7.0531e-07 | 4.7187e-07
690 | feeder2_line94 | 2 | 354.6 | 1.3854 | 1.3854 | 0.39069 | 0.39069
690 | feeder2_line94 | 3 | 354.6 | 2.4989e-06 | 1.6727e-06 | 7.047e-07 | 4.717e-07
690 | feeder2_line95 | 1 | 99 | 3.5869e-06 | 2.6214e-06 | 3.6231e-06 | 2.6479e-06
690 | feeder2_line95 | 2 | 99 | 1.3917 | 1.3918 | 1.4058 | 1.4059
690 | feeder2_line95 | 3 | 99 | 3.583e-06 | 2.6208e-06 | 3.6192e-06 | 2.6473e-06
690 | feeder2_line96 | 1 | 354.6 | 0.00012167 | 6.2485e-07 | 3.431e-05 | 1.7621e-07
690 | feeder2_line96 | 2 | 354.6 | 0.00012104 | 6.2217e-07 | 3.4133e-05 | 1.7546e-07
690 | feeder2_line96 | 3 | 354.6 | 1.0458 | 1.0458 | 0.29493 | 0.29493
690 | feeder2_line97 | 1 | 354.6 | 94.7916 | 94.7838 | 26.732 | 26.7298
690 | feeder2_line97 | 2 | 354.6 | 83.1542 | 83.1623 | 23.4501 | 23.4524
690 | feeder2_line97 | 3 | 354.6 | 88.1346 | 88.1375 | 24.8547 | 24.8555
690 | feeder2_line98 | 1 | 354.6 | 1.0367 | 1.035 | 0.29237 | 0.29187
690 | feeder2_line98 | 2 | 354.6 | 0.0016976 | 6.2011e-07 | 0.00047874 | 1.7488e-07
690 | feeder2_line98 | 3 | 354.6 | 0.0017161 | 6.2682e-07 | 0.00048395 | 1.7677e-07
690 | feeder2_line99 | 1 | 99 | 2.5008e-08 | 4.4923e-07 | 2.5261e-08 | 4.5377e-07
690 | feeder2_line99 | 2 | 99 | 2.5165e-08 | 4.4708e-07 | 2.5419e-08 | 4.516e-07
690 | feeder2_line99 | 3 | 99 | 1.0458 | 1.0458 | 1.0564 | 1.0564
690 | feeder2_line100 | 1 | 99 | 1.0351 | 1.035 | 1.0455 | 1.0454
690 | feeder2_line100 | 2 | 99 | 2.5195e-08 | 6.1404e-07 | 2.5449e-08 | 6.2024e-07
690 | feeder2_line100 | 3 | 99 | 2.4997e-08 | 6.1692e-07 | 2.525e-08 | 6.2315e-07
690 | feeder2_line101 | 1 | 354.6 | 1.3864 | 1.386 | 0.39097 | 0.39085
690 | feeder2_line101 | 2 | 354.6 | 18.6554 | 18.6547 | 5.261 | 5.2608
690 | feeder2_line101 | 3 | 354.6 | 5.6115 | 5.6113 | 1.5825 | 1.5824
690 | feeder2_line102 | 1 | 99 | 7.4383 | 7.4384 | 7.5134 | 7.5135
690 | feeder2_line102 | 2 | 99 | 2.3299e-06 | 8.7751e-07 | 2.3534e-06 | 8.8637e-07
690 | feeder2_line102 | 3 | 99 | 2.3488e-06 | 8.8161e-07 | 2.3725e-06 | 8.9052e-07
690 | feeder2_line103 | 1 | 99 | 5.5149e-07 | 8.0693e-07 | 5.5706e-07 | 8.1508e-07
690 | feeder2_line103 | 2 | 99 | 6.4572 | 6.4571 | 6.5225 | 6.5223
690 | feeder2_line103 | 3 | 99 | 5.5154e-07 | 8.0694e-07 | 5.5711e-07 | 8.1509e-07
690 | feeder2_line104 | 1 | 354.6 | 1.3863 | 1.386 | 0.39095 | 0.39085
690 | feeder2_line104 | 2 | 354.6 | 12.2435 | 12.243 | 3.4528 | 3.4526
690 | feeder2_line104 | 3 | 354.6 | 5.6115 | 5.6113 | 1.5825 | 1.5824
690 | feeder2_line105 | 1 | 99 | 2.5576e-06 | 7.4249e-07 | 2.5834e-06 | 7.4999e-07
690 | feeder2_line105 | 2 | 99 | 2.5417e-06 | 7.3895e-07 | 2.5674e-06 | 7.4641e-07
690 | feeder2_line105 | 3 | 99 | 0.67271 | 0.67275 | 0.6795 | 0.67954
690 | feeder2_line106 | 1 | 354.6 | 1.3862 | 1.386 | 0.39093 | 0.39085
690 | feeder2_line106 | 2 | 354.6 | 12.2434 | 12.243 | 3.4527 | 3.4526
690 | feeder2_line106 | 3 | 354.6 | 5.0591 | 5.0589 | 1.4267 | 1.4267
690 | feeder2_line107 | 1 | 99 | 3.2572e-07 | 9.0485e-07 | 3.2901e-07 | 9.1399e-07
690 | feeder2_line107 | 2 | 99 | 1.0477 | 1.0477 | 1.0583 | 1.0583
690 | feeder2_line107 | 3 | 99 | 3.2564e-07 | 9.048e-07 | 3.2893e-07 | 9.1394e-07
690 | feeder2_line108 | 1 | 354.6 | 1.3862 | 1.386 | 0.39093 | 0.39085
690 | feeder2_line108 | 2 | 354.6 | 11.4934 | 11.493 | 3.2412 | 3.2411
690 | feeder2_line108 | 3 | 354.6 | 5.0591 | 5.0589 | 1.4267 | 1.4267
690 | feeder2_line109 | 1 | 354.6 | 95.9266 | 95.9175 | 27.0521 | 27.0495
690 | feeder2_line109 | 2 | 354.6 | 83.1554 | 83.1623 | 23.4505 | 23.4524
690 | feeder2_line109 | 3 | 354.6 | 88.1359 | 88.1375 | 24.855 | 24.8555
690 | feeder2_line110 | 1 | 99 | 1.1356 | 1.1348 | 1.1471 | 1.1462
690 | feeder2_line110 | 2 | 99 | 0.00080323 | 9.0936e-07 | 0.00081134 | 9.1854e-07
690 | feeder2_line110 | 3 | 99 | 0.00080879 | 9.1321e-07 | 0.00081696 | 9.2243e-07
690 | feeder2_line111 | 1 | 99 | 2.5002e-08 | 3.8369e-07 | 2.5254e-08 | 3.8756e-07
690 | feeder2_line111 | 2 | 99 | 0.045525 | 0.045531 | 0.045985 | 0.045991
690 | feeder2_line111 | 3 | 99 | 2.4978e-08 | 3.836e-07 | 2.523e-08 | 3.8747e-07
690 | feeder2_line112 | 1 | 99 | 3.2606e-07 | 9.2201e-07 | 3.2935e-07 | 9.3132e-07
690 | feeder2_line112 | 2 | 99 | 1.3569 | 1.357 | 1.3706 | 1.3707
690 | feeder2_line112 | 3 | 99 | 3.2596e-07 | 9.218e-07 | 3.2925e-07 | 9.3111e-07
690 | feeder2_line113 | 1 | 99 | 0.096992 | 0.096984 | 0.097972 | 0.097964
690 | feeder2_line113 | 2 | 99 | 3.2526e-07 | 9.0561e-07 | 3.2854e-07 | 9.1476e-07
690 | feeder2_line113 | 3 | 99 | 3.2633e-07 | 9.099e-07 | 3.2962e-07 | 9.1909e-07
690 | feeder2_line114 | 1 | 99 | 6.4965 | 6.4967 | 6.5622 | 6.5623
690 | feeder2_line114 | 2 | 99 | 2.5132e-08 | 4.3635e-07 | 2.5386e-08 | 4.4075e-07
690 | feeder2_line114 | 3 | 99 | 2.4941e-08 | 4.3839e-07 | 2.5193e-08 | 4.4282e-07
690 | feeder2_line115 | 1 | 99 | 2.4981e-08 | 5.6468e-07 | 2.5233e-08 | 5.7038e-07
690 | feeder2_line115 | 2 | 99 | 9.5029 | 9.5026 | 9.5988 | 9.5986
690 | feeder2_line115 | 3 | 99 | 2.4933e-08 | 5.6461e-07 | 2.5185e-08 | 5.7032e-07
690 | feeder2_line116 | 1 | 354.6 | 1.3862 | 1.386 | 0.39093 | 0.39085
690 | feeder2_line116 | 2 | 354.6 | 2.2623 | 2.2621 | 0.63798 | 0.63792
690 | feeder2_line116 | 3 | 354.6 | 5.0591 | 5.0589 | 1.4267 | 1.4267
690 | feeder2_line117 | 1 | 99 | 5.0054e-08 | 6.4658e-07 | 5.056e-08 | 6.5311e-07
690 | feeder2_line117 | 2 | 99 | 1.472 | 1.472 | 1.4869 | 1.4869
690 | feeder2_line117 | 3 | 99 | 5.0045e-08 | 6.4619e-07 | 5.0551e-08 | 6.5272e-07
690 | feeder2_line118 | 1 | 354.6 | 95.9266 | 95.9175 | 27.0521 | 27.0495
690 | feeder2_line118 | 2 | 354.6 | 84.0353 | 84.0422 | 23.6986 | 23.7006
690 | feeder2_line118 | 3 | 354.6 | 88.1359 | 88.1375 | 24.855 | 24.8555
690 | feeder2_line119 | 1 | 99 | 2.4985e-08 | 6.0761e-07 | 2.5237e-08 | 6.1375e-07
690 | feeder2_line119 | 2 | 99 | 2.5149e-08 | 6.0458e-07 | 2.5403e-08 | 6.1068e-07
690 | feeder2_line119 | 3 | 99 | 0.54379 | 0.54379 | 0.54928 | 0.54928
690 | feeder2_line120 | 1 | 354.6 | 1.3862 | 1.386 | 0.39093 | 0.39085
690 | feeder2_line120 | 2 | 354.6 | 2.2623 | 2.2621 | 0.63798 | 0.63792
690 | feeder2_line120 | 3 | 354.6 | 4.5256 | 4.5255 | 1.2763 | 1.2762
690 | feeder2_line121 | 1 | 99 | 3.2572e-07 | 9.4091e-07 | 3.2901e-07 | 9.5041e-07
690 | feeder2_line121 | 2 | 99 | 0.04418 | 0.044182 | 0.044626 | 0.044628
690 | feeder2_line121 | 3 | 99 | 3.256e-07 | 9.4071e-07 | 3.2888e-07 | 9.5021e-07
690 | feeder2_line122 | 1 | 354.6 | 1.3862 | 1.386 | 0.39093 | 0.39085
690 | feeder2_line122 | 2 | 354.6 | 2.2249 | 2.2247 | 0.62744 | 0.62739
690 | feeder2_line122 | 3 | 354.6 | 4.5256 | 4.5255 | 1.2763 | 1.2762
690 | feeder2_line123 | 1 | 99 | 5.7649e-07 | 9.75e-07 | 5.8231e-07 | 9.8485e-07
690 | feeder2_line123 | 2 | 99 | 5.7358e-07 | 9.7012e-07 | 5.7938e-07 | 9.7992e-07
690 | feeder2_line123 | 3 | 99 | 0.75702 | 0.75704 | 0.76467 | 0.76469
690 | feeder2_line124 | 1 | 354.6 | 1.3862 | 1.386 | 0.39091 | 0.39085
690 | feeder2_line124 | 2 | 354.6 | 2.2249 | 2.2247 | 0.62744 | 0.62739
690 | feeder2_line124 | 3 | 354.6 | 3.8074 | 3.8073 | 1.0737 | 1.0737
690 | feeder2_line125 | 1 | 99 | 5.7649e-07 | 9.0635e-07 | 5.8231e-07 | 9.1551e-07
690 | feeder2_line125 | 2 | 99 | 5.7359e-07 | 9.0183e-07 | 5.7938e-07 | 9.1094e-07
690 | feeder2_line125 | 3 | 99 | 1.0366 | 1.0367 | 1.0471 | 1.0472
690 | feeder2_line126 | 1 | 354.6 | 1.3863 | 1.386 | 0.39095 | 0.39085
690 | feeder2_line126 | 2 | 354.6 | 2.2251 | 2.2247 | 0.62748 | 0.62739
690 | feeder2_line126 | 3 | 354.6 | 2.9667 | 2.9664 | 0.83664 | 0.83655
690 | feeder2_line127 | 1 | 99 | 5.7649e-07 | 1.0851e-06 | 5.8232e-07 | 1.096e-06
690 | feeder2_line127 | 2 | 99 | 5.7357e-07 | 1.0796e-06 | 5.7937e-07 | 1.0905e-06
690 | feeder2_line127 | 3 | 99 | 2.4074 | 2.4073 | 2.4317 | 2.4317
690 | feeder2_line128 | 1 | 354.6 | 1.3863 | 1.386 | 0.39093 | 0.39085
690 | feeder2_line128 | 2 | 354.6 | 2.225 | 2.2247 | 0.62747 | 0.62739
690 | feeder2_line128 | 3 | 354.6 | 0.83616 | 0.83594 | 0.2358 | 0.23574
690 | feeder2_line129 | 1 | 99 | 5.5151e-07 | 8.7981e-07 | 5.5708e-07 | 8.887e-07
690 | feeder2_line129 | 2 | 99 | 2.2247 | 2.2247 | 2.2472 | 2.2472
690 | feeder2_line129 | 3 | 99 | 5.5139e-07 | 8.7958e-07 | 5.5696e-07 | 8.8847e-07
690 | feeder2_line130 | 1 | 354.6 | 1.3863 | 1.386 | 0.39094 | 0.39085
690 | feeder2_line130 | 2 | 354.6 | 0.00030821 | 4.6332e-06 | 8.6919e-05 | 1.3066e-06
690 | feeder2_line130 | 3 | 354.6 | 0.83618 | 0.83594 | 0.23581 | 0.23574
690 | feeder2_line131 | 1 | 99 | 5.7648e-07 | 9.7513e-07 | 5.823e-07 | 9.8498e-07
690 | feeder2_line131 | 2 | 99 | 5.7358e-07 | 9.7026e-07 | 5.7937e-07 | 9.8006e-07
690 | feeder2_line131 | 3 | 99 | 0.57811 | 0.57812 | 0.58395 | 0.58396
690 | feeder2_line132 | 1 | 354.6 | 1.3861 | 1.386 | 0.39089 | 0.39085
690 | feeder2_line132 | 2 | 354.6 | 0.00012542 | 2.913e-06 | 3.5369e-05 | 8.2148e-07
690 | feeder2_line132 | 3 | 354.6 | 0.2579 | 0.25783 | 0.07273 | 0.072709
690 | feeder2_line133 | 1 | 99 | 1.386 | 1.386 | 1.4 | 1.4
690 | feeder2_line133 | 2 | 99 | 2.9936e-07 | 9.7801e-07 | 3.0238e-07 | 9.8789e-07
690 | feeder2_line133 | 3 | 99 | 3.0064e-07 | 9.8266e-07 | 3.0367e-07 | 9.9259e-07
690 | feeder2_line134 | 1 | 354.6 | 6.2706e-12 | 1.7923e-06 | 1.7684e-12 | 5.0544e-07
690 | feeder2_line134 | 2 | 354.6 | 1.2691e-11 | 1.7839e-06 | 3.5791e-12 | 5.0307e-07
690 | feeder2_line134 | 3 | 354.6 | 0.25783 | 0.25783 | 0.072709 | 0.072709
690 | feeder2_line135 | 1 | 99 | 0.052472 | 0.052405 | 0.053002 | 0.052935
690 | feeder2_line135 | 2 | 99 | 5.0504e-08 | 5.8623e-07 | 5.1014e-08 | 5.9215e-07
690 | feeder2_line135 | 3 | 99 | 5.0075e-08 | 5.8908e-07 | 5.0581e-08 | 5.9503e-07
690 | feeder2_line136 | 1 | 354.6 | 95.9789 | 95.9698 | 27.0668 | 27.0642
690 | feeder2_line136 | 2 | 354.6 | 84.0352 | 84.0422 | 23.6986 | 23.7006
690 | feeder2_line136 | 3 | 354.6 | 88.1358 | 88.1375 | 24.855 | 24.8555
690 | feeder2_line137 | 1 | 99 | 0.97313 | 0.97306 | 0.98296 | 0.98289
690 | feeder2_line137 | 2 | 99 | 8.5066e-07 | 1.5791e-06 | 8.5926e-07 | 1.595e-06
690 | feeder2_line137 | 3 | 99 | 8.5503e-07 | 1.5868e-06 | 8.6367e-07 | 1.6028e-06
690 | feeder2_line138 | 1 | 354.6 | 96.7691 | 96.7599 | 27.2897 | 27.2871
690 | feeder2_line138 | 2 | 354.6 | 84.0353 | 84.0422 | 23.6986 | 23.7006
690 | feeder2_line138 | 3 | 354.6 | 88.1359 | 88.1375 | 24.855 | 24.8555
690 | feeder2_line139 | 1 | 99 | 5.0073e-08 | 4.9488e-07 | 5.0579e-08 | 4.9988e-07
690 | feeder2_line139 | 2 | 99 | 5.0522e-08 | 4.9206e-07 | 5.1032e-08 | 4.9703e-07
690 | feeder2_line139 | 3 | 99 | 10.0398 | 10.0398 | 10.1412 | 10.1413
690 | feeder2_line140 | 1 | 354.6 | 96.7692 | 96.7599 | 27.2897 | 27.2871
690 | feeder2_line140 | 2 | 354.6 | 84.0354 | 84.0422 | 23.6986 | 23.7006
690 | feeder2_line140 | 3 | 354.6 | 98.1731 | 98.1747 | 27.6856 | 27.6861
690 | feeder2_line141 | 1 | 99 | 2.5448e-06 | 4.8961e-07 | 2.5705e-06 | 4.9456e-07
690 | feeder2_line141 | 2 | 99 | 5.7869 | 5.787 | 5.8453 | 5.8455
690 | feeder2_line141 | 3 | 99 | 2.5423e-06 | 4.8921e-07 | 2.568e-06 | 4.9415e-07
690 | feeder2_line142 | 1 | 354.6 | 96.7691 | 96.7599 | 27.2896 | 27.2871
690 | feeder2_line142 | 2 | 354.6 | 89.822 | 89.8292 | 25.3305 | 25.3325
690 | feeder2_line142 | 3 | 354.6 | 98.1729 | 98.1747 | 27.6855 | 27.6861
690 | feeder2_line143 | 1 | 99 | 8.5618e-07 | 1.7399e-06 | 8.6483e-07 | 1.7575e-06
690 | feeder2_line143 | 2 | 99 | 1.0487 | 1.0488 | 1.0593 | 1.0593
690 | feeder2_line143 | 3 | 99 | 8.5547e-07 | 1.7385e-06 | 8.6411e-07 | 1.7561e-06
690 | feeder2_line144 | 1 | 354.6 | 96.7689 | 96.7599 | 27.2896 | 27.2871
690 | feeder2_line144 | 2 | 354.6 | 90.4817 | 90.489 | 25.5165 | 25.5186
690 | feeder2_line144 | 3 | 354.6 | 98.1728 | 98.1747 | 27.6855 | 27.6861
690 | feeder2_line145 | 1 | 99 | 2.5043e-08 | 4.8791e-07 | 2.5296e-08 | 4.9284e-07
690 | feeder2_line145 | 2 | 99 | 1.116 | 1.116 | 1.1273 | 1.1273
690 | feeder2_line145 | 3 | 99 | 2.5053e-08 | 4.8751e-07 | 2.5306e-08 | 4.9243e-07
690 | feeder2_line146 | 1 | 354.6 | 96.7688 | 96.7599 | 27.2896 | 27.2871
690 | feeder2_line146 | 2 | 354.6 | 91.5975 | 91.605 | 25.8312 | 25.8333
690 | feeder2_line146 | 3 | 354.6 | 98.1726 | 98.1747 | 27.6855 | 27.6861
690 | feeder2_line147 | 1 | 99 | 1.0365 | 1.0365 | 1.047 | 1.0469
690 | feeder2_line147 | 2 | 99 | 1.1517e-06 | 2.2375e-06 | 1.1633e-06 | 2.2601e-06
690 | feeder2_line147 | 3 | 99 | 1.1576e-06 | 2.2488e-06 | 1.1692e-06 | 2.2715e-06
690 | feeder2_line148 | 1 | 99 | 0.27225 | 0.27224 | 0.275 | 0.27499
690 | feeder2_line148 | 2 | 99 | 6.0114e-07 | 1.4993e-06 | 6.0721e-07 | 1.5145e-06
690 | feeder2_line148 | 3 | 99 | 6.0383e-07 | 1.5069e-06 | 6.0993e-07 | 1.5221e-06
690 | feeder2_line149 | 1 | 354.6 | 98.0759 | 98.0669 | 27.6582 | 27.6556
690 | feeder2_line149 | 2 | 354.6 | 91.5977 | 91.605 | 25.8313 | 25.8333
690 | feeder2_line149 | 3 | 354.6 | 98.1728 | 98.1747 | 27.6855 | 27.6861
690 | feeder2_line150 | 1 | 354.6 | 98.076 | 98.0669 | 27.6582 | 27.6556
690 | feeder2_line150 | 2 | 354.6 | 99.0001 | 99.0072 | 27.9188 | 27.9208
690 | feeder2_line150 | 3 | 354.6 | 98.1729 | 98.1747 | 27.6855 | 27.6861
690 | feeder2_line151 | 1 | 99 | 9.8378e-06 | 1.7917e-06 | 9.9372e-06 | 1.8098e-06
690 | feeder2_line151 | 2 | 99 | 7.4802 | 7.4801 | 7.5558 | 7.5556
690 | feeder2_line151 | 3 | 99 | 9.8325e-06 | 1.7903e-06 | 9.9318e-06 | 1.8083e-06
690 | feeder2_line152 | 1 | 354.6 | 1.3966e-11 | 1.1942e-06 | 3.9386e-12 | 3.3679e-07
690 | feeder2_line152 | 2 | 354.6 | 3.0838e-11 | 1.1876e-06 | 8.6964e-12 | 3.3492e-07
690 | feeder2_line152 | 3 | 354.6 | 0.076374 | 0.076376 | 0.021538 | 0.021539
690 | feeder2_line153 | 1 | 99 | 0.043612 | 0.043608 | 0.044052 | 0.044048
690 | feeder2_line153 | 2 | 99 | 5.0614e-08 | 5.9406e-07 | 5.1125e-08 | 6.0006e-07
690 | feeder2_line153 | 3 | 99 | 5.016e-08 | 5.9708e-07 | 5.0666e-08 | 6.0311e-07
690 | feeder2_line154 | 1 | 99 | 5.7986e-07 | 8.8922e-07 | 5.8572e-07 | 8.982e-07
690 | feeder2_line154 | 2 | 99 | 5.7641e-07 | 8.8398e-07 | 5.8224e-07 | 8.9291e-07
690 | feeder2_line154 | 3 | 99 | 0.040479 | 0.04053 | 0.040888 | 0.040939
690 | feeder2_line155 | 1 | 99 | 98.1195 | 98.1105 | 99.1106 | 99.1015
690 | feeder2_line155 | 2 | 99 | 99 | 99.0072 | 100 | 100.0073
690 | feeder2_line155 | 3 | 99 | 98.2892 | 98.2912 | 99.282 | 99.284
690 | feeder2_line156 | 1 | 99 | 6.0464e-07 | 1.17e-06 | 6.1074e-07 | 1.1818e-06
690 | feeder2_line156 | 2 | 99 | 6.4798 | 6.4796 | 6.5453 | 6.5451
690 | feeder2_line156 | 3 | 99 | 6.0415e-07 | 1.169e-06 | 6.1025e-07 | 1.1808e-06
690 | feeder2_line157 | 1 | 99 | 2.5064e-08 | 2.5402e-07 | 2.5317e-08 | 2.5659e-07
690 | feeder2_line157 | 2 | 99 | 1.4793 | 1.4793 | 1.4942 | 1.4942
690 | feeder2_line157 | 3 | 99 | 2.5066e-08 | 2.5379e-07 | 2.532e-08 | 2.5635e-07
720 | feeder2_line1 | 1 | 354.6 | 61.4361 | 61.435 | 17.3255 | 17.3251
720 | feeder2_line1 | 2 | 354.6 | 64.0375 | 64.0357 | 18.0591 | 18.0586
720 | feeder2_line1 | 3 | 354.6 | 70.7726 | 70.7776 | 19.9584 | 19.9598
720 | feeder2_line2 | 1 | 354.6 | 61.5055 | 61.5042 | 17.345 | 17.3447
720 | feeder2_line2 | 2 | 354.6 | 64.0377 | 64.0357 | 18.0591 | 18.0586
720 | feeder2_line2 | 3 | 354.6 | 70.7727 | 70.7776 | 19.9585 | 19.9598
720 | feeder2_line3 | 1 | 80.1 | 0.069365 | 0.069365 | 0.086598 | 0.086598
720 | feeder2_line3 | 2 | 80.1 | 5.7196e-07 | 1.057e-06 | 7.1406e-07 | 1.3196e-06
720 | feeder2_line3 | 3 | 80.1 | 5.7241e-07 | 1.0578e-06 | 7.1462e-07 | 1.3206e-06
720 | feeder2_line4 | 1 | 354.6 | 61.5057 | 61.5042 | 17.3451 | 17.3447
720 | feeder2_line4 | 2 | 354.6 | 64.527 | 64.5248 | 18.1971 | 18.1965
720 | feeder2_line4 | 3 | 354.6 | 70.7729 | 70.7776 | 19.9585 | 19.9598
720 | feeder2_line5 | 1 | 80.1 | 5.7204e-07 | 9.9817e-07 | 7.1416e-07 | 1.2462e-06
720 | feeder2_line5 | 2 | 80.1 | 0.5017 | 0.50169 | 0.62634 | 0.62633
720 | feeder2_line5 | 3 | 80.1 | 5.7245e-07 | 9.9887e-07 | 7.1467e-07 | 1.247e-06
720 | feeder2_line6 | 1 | 80.1 | 5.7209e-07 | 1.1743e-06 | 7.1423e-07 | 1.4661e-06
720 | feeder2_line6 | 2 | 80.1 | 5.7204e-07 | 1.1742e-06 | 7.1416e-07 | 1.4659e-06
720 | feeder2_line6 | 3 | 80.1 | 1.6663 | 1.6663 | 2.0803 | 2.0803
720 | feeder2_line7 | 1 | 354.6 | 61.5058 | 61.5042 | 17.3451 | 17.3447
720 | feeder2_line7 | 2 | 354.6 | 64.5271 | 64.5248 | 18.1971 | 18.1965
720 | feeder2_line7 | 3 | 354.6 | 72.2127 | 72.2174 | 20.3646 | 20.3659
720 | feeder2_line8 | 1 | 80.1 | 9.3945 | 9.3945 | 11.7284 | 11.7285
720 | feeder2_line8 | 2 | 80.1 | 5.7217e-07 | 1.1325e-06 | 7.1433e-07 | 1.4138e-06
720 | feeder2_line8 | 3 | 80.1 | 5.7272e-07 | 1.1336e-06 | 7.1501e-07 | 1.4152e-06
720 | feeder2_line9 | 1 | 354.6 | 70.7991 | 70.7975 | 19.9659 | 19.9654
720 | feeder2_line9 | 2 | 354.6 | 64.5271 | 64.5248 | 18.1972 | 18.1965
720 | feeder2_line9 | 3 | 354.6 | 72.2128 | 72.2174 | 20.3646 | 20.3659
720 | feeder2_line10 | 1 | 80.1 | 8.4592e-07 | 1.4955e-06 | 1.0561e-06 | 1.8671e-06
720 | feeder2_line10 | 2 | 80.1 | 9.3928 | 9.3928 | 11.7263 | 11.7263
720 | feeder2_line10 | 3 | 80.1 | 8.4668e-07 | 1.4968e-06 | 1.057e-06 | 1.8687e-06
720 | feeder2_line11 | 1 | 354.6 | 70.7991 | 70.7975 | 19.9659 | 19.9654
720 | feeder2_line11 | 2 | 354.6 | 73.7956 | 73.7932 | 20.8109 | 20.8103
720 | feeder2_line11 | 3 | 354.6 | 72.2128 | 72.2174 | 20.3646 | 20.3659
720 | feeder2_line12 | 1 | 80.1 | 5.4744e-07 | 9.9218e-07 | 6.8344e-07 | 1.2387e-06
720 | feeder2_line12 | 2 | 80.1 | 5.474e-07 | 9.9208e-07 | 6.834e-07 | 1.2385e-06
720 | feeder2_line12 | 3 | 80.1 | 0.91401 | 0.91401 | 1.1411 | 1.1411
720 | feeder2_line13 | 1 | 354.6 | 70.7991 | 70.7975 | 19.9659 | 19.9654
720 | feeder2_line13 | 2 | 354.6 | 73.7955 | 73.7932 | 20.8109 | 20.8103
720 | feeder2_line13 | 3 | 354.6 | 73.126 | 73.1306 | 20.6221 | 20.6234
720 | feeder2_line14 | 1 | 80.1 | 9.4135 | 9.4135 | 11.7521 | 11.7521
720 | feeder2_line14 | 2 | 80.1 | 2.9862e-07 | 6.4698e-07 | 3.7281e-07 | 8.0772e-07
720 | feeder2_line14 | 3 | 80.1 | 2.9889e-07 | 6.4761e-07 | 3.7314e-07 | 8.085e-07
720 | feeder2_line15 | 1 | 354.6 | 80.1352 | 80.1336 | 22.5988 | 22.5983
720 | feeder2_line15 | 2 | 354.6 | 73.7955 | 73.7932 | 20.8109 | 20.8103
720 | feeder2_line15 | 3 | 354.6 | 73.126 | 73.1306 | 20.6221 | 20.6234
720 | feeder2_line16 | 1 | 80.1 | 5.7255e-07 | 1.0315e-06 | 7.148e-07 | 1.2878e-06
720 | feeder2_line16 | 2 | 80.1 | 0.71552 | 0.71552 | 0.89329 | 0.89329
720 | feeder2_line16 | 3 | 80.1 | 5.7302e-07 | 1.0323e-06 | 7.1538e-07 | 1.2888e-06
720 | feeder2_line17 | 1 | 354.6 | 80.1352 | 80.1336 | 22.5988 | 22.5983
720 | feeder2_line17 | 2 | 354.6 | 74.5032 | 74.5009 | 21.0105 | 21.0098
720 | feeder2_line17 | 3 | 354.6 | 73.126 | 73.1306 | 20.6221 | 20.6234
720 | feeder2_line18 | 1 | 80.1 | 5.4823e-07 | 7.3912e-07 | 6.8443e-07 | 9.2275e-07
720 | feeder2_line18 | 2 | 80.1 | 5.4799e-07 | 7.3883e-07 | 6.8413e-07 | 9.2238e-07
720 | feeder2_line18 | 3 | 80.1 | 0.8309 | 0.83091 | 1.0373 | 1.0373
720 | feeder2_line19 | 1 | 354.6 | 80.1353 | 80.1336 | 22.5988 | 22.5983
720 | feeder2_line19 | 2 | 354.6 | 74.5033 | 74.5009 | 21.0105 | 21.0098
720 | feeder2_line19 | 3 | 354.6 | 73.9566 | 73.9612 | 20.8564 | 20.8576
720 | feeder2_line20 | 1 | 99 | 5.4844e-07 | 8.865e-07 | 5.5398e-07 | 8.9546e-07
720 | feeder2_line20 | 2 | 99 | 5.4815e-07 | 8.8608e-07 | 5.5369e-07 | 8.9503e-07
720 | feeder2_line20 | 3 | 99 | 0.085882 | 0.085893 | 0.08675 | 0.086761
720 | feeder2_line21 | 1 | 354.6 | 80.1354 | 80.1336 | 22.5988 | 22.5983
720 | feeder2_line21 | 2 | 354.6 | 74.5034 | 74.5009 | 21.0105 | 21.0098
720 | feeder2_line21 | 3 | 354.6 | 74.0427 | 74.0471 | 20.8806 | 20.8819
720 | feeder2_line22 | 1 | 99 | 5.7351e-07 | 1.0165e-06 | 5.793e-07 | 1.0268e-06
720 | feeder2_line22 | 2 | 99 | 0.54483 | 0.54484 | 0.55034 | 0.55034
720 | feeder2_line22 | 3 | 99 | 5.7378e-07 | 1.017e-06 | 5.7957e-07 | 1.0273e-06
720 | feeder2_line23 | 1 | 99 | 5.7351e-07 | 9.5154e-07 | 5.793e-07 | 9.6115e-07
720 | feeder2_line23 | 2 | 99 | 5.732e-07 | 9.5103e-07 | 5.7899e-07 | 9.6063e-07
720 | feeder2_line23 | 3 | 99 | 0.081776 | 0.081777 | 0.082602 | 0.082603
720 | feeder2_line24 | 1 | 354.6 | 80.1354 | 80.1336 | 22.5988 | 22.5983
720 | feeder2_line24 | 2 | 354.6 | 74.9773 | 74.9748 | 21.1442 | 21.1435
720 | feeder2_line24 | 3 | 354.6 | 74.1244 | 74.1289 | 20.9037 | 20.9049
720 | feeder2_line25 | 1 | 99 | 0.54456 | 0.54457 | 0.55006 | 0.55007
720 | feeder2_line25 | 2 | 99 | 4.993e-08 | 6.9164e-07 | 5.0434e-08 | 6.9863e-07
720 | feeder2_line25 | 3 | 99 | 4.9858e-08 | 6.9234e-07 | 5.0362e-08 | 6.9933e-07
720 | feeder2_line26 | 1 | 99 | 0.085115 | 0.085114 | 0.085975 | 0.085974
720 | feeder2_line26 | 2 | 99 | 5.4842e-07 | 8.5689e-07 | 5.5396e-07 | 8.6555e-07
720 | feeder2_line26 | 3 | 99 | 5.4904e-07 | 8.5777e-07 | 5.5459e-07 | 8.6643e-07
720 | feeder2_line27 | 1 | 354.6 | 80.7018 | 80.7 | 22.7586 | 22.758
720 | feeder2_line27 | 2 | 354.6 | 74.9773 | 74.9748 | 21.1442 | 21.1435
720 | feeder2_line27 | 3 | 354.6 | 74.1245 | 74.1289 | 20.9037 | 20.9049
720 | feeder2_line28 | 1 | 99 | 2.5464e-06 | 7.1224e-07 | 2.5722e-06 | 7.1944e-07
720 | feeder2_line28 | 2 | 99 | 0.756 | 0.75602 | 0.76363 | 0.76366
720 | feeder2_line28 | 3 | 99 | 2.5471e-06 | 7.1242e-07 | 2.5728e-06 | 7.1961e-07
720 | feeder2_line29 | 1 | 354.6 | 80.7018 | 80.7 | 22.7586 | 22.758
720 | feeder2_line29 | 2 | 354.6 | 75.3794 | 75.3769 | 21.2576 | 21.2569
720 | feeder2_line29 | 3 | 354.6 | 74.1245 | 74.1289 | 20.9037 | 20.9049
720 | feeder2_line30 | 1 | 266.4 | 4.2535 | 4.2533 | 1.5967 | 1.5966
720 | feeder2_line30 | 2 | 266.4 | 3.0806 | 3.0806 | 1.1564 | 1.1564
720 | feeder2_line30 | 3 | 266.4 | 4.3635 | 4.3636 | 1.638 | 1.638
720 | feeder2_line31 | 1 | 354.6 | 84.3804 | 84.3782 | 23.796 | 23.7953
720 | feeder2_line31 | 2 | 354.6 | 77.6033 | 77.6005 | 21.8848 | 21.8839
720 | feeder2_line31 | 3 | 354.6 | 77.7648 | 77.7689 | 21.9303 | 21.9314
720 | feeder2_line32 | 1 | 354.6 | 84.3805 | 84.3782 | 23.796 | 23.7953
720 | feeder2_line32 | 2 | 354.6 | 78.9357 | 78.9328 | 22.2605 | 22.2597
720 | feeder2_line32 | 3 | 354.6 | 77.7648 | 77.7689 | 21.9303 | 21.9314
720 | feeder2_line33 | 1 | 99 | 4.9922e-08 | 6.8817e-07 | 5.0426e-08 | 6.9512e-07
720 | feeder2_line33 | 2 | 99 | 1.3372 | 1.3372 | 1.3507 | 1.3507
720 | feeder2_line33 | 3 | 99 | 4.9965e-08 | 6.8813e-07 | 5.0469e-08 | 6.9508e-07
720 | feeder2_line34 | 1 | 354.6 | 84.3805 | 84.3782 | 23.796 | 23.7953
720 | feeder2_line34 | 2 | 354.6 | 78.9357 | 78.9328 | 22.2605 | 22.2597
720 | feeder2_line34 | 3 | 354.6 | 77.8502 | 77.8543 | 21.9544 | 21.9555
720 | feeder2_line35 | 1 | 99 | 3.0005e-07 | 7.6224e-07 | 3.0309e-07 | 7.6994e-07
720 | feeder2_line35 | 2 | 99 | 2.9975e-07 | 7.6136e-07 | 3.0278e-07 | 7.6905e-07
720 | feeder2_line35 | 3 | 99 | 0.085441 | 0.085445 | 0.086304 | 0.086308
720 | feeder2_line36 | 1 | 354.6 | 84.4084 | 84.4062 | 23.8038 | 23.8032
720 | feeder2_line36 | 2 | 354.6 | 78.9356 | 78.9328 | 22.2605 | 22.2597
720 | feeder2_line36 | 3 | 354.6 | 77.8502 | 77.8543 | 21.9544 | 21.9555
720 | feeder2_line37 | 1 | 99 | 0.028021 | 0.027978 | 0.028304 | 0.028261
720 | feeder2_line37 | 2 | 99 | 2.9983e-07 | 8.4261e-07 | 3.0286e-07 | 8.5112e-07
720 | feeder2_line37 | 3 | 99 | 3.0011e-07 | 8.4351e-07 | 3.0314e-07 | 8.5203e-07
720 | feeder2_line38 | 1 | 99 | 3.2478e-07 | 7.7768e-07 | 3.2806e-07 | 7.8554e-07
720 | feeder2_line38 | 2 | 99 | 0.077168 | 0.077166 | 0.077947 | 0.077945
720 | feeder2_line38 | 3 | 99 | 3.2482e-07 | 7.7773e-07 | 3.281e-07 | 7.8559e-07
720 | feeder2_line39 | 1 | 266.4 | 4.2535 | 4.2533 | 1.5967 | 1.5966
720 | feeder2_line39 | 2 | 266.4 | 3.024 | 3.0241 | 1.1351 | 1.1352
720 | feeder2_line39 | 3 | 266.4 | 4.3636 | 4.3636 | 1.638 | 1.638
720 | feeder2_line40 | 1 | 354.6 | 84.8966 | 84.8943 | 23.9415 | 23.9409
720 | feeder2_line40 | 2 | 354.6 | 78.9357 | 78.9328 | 22.2605 | 22.2597
720 | feeder2_line40 | 3 | 354.6 | 77.8503 | 77.8543 | 21.9544 | 21.9555
720 | feeder2_line41 | 1 | 99 | 0.54386 | 0.54387 | 0.54936 | 0.54936
720 | feeder2_line41 | 2 | 99 | 5.0092e-08 | 7.3638e-07 | 5.0598e-08 | 7.4381e-07
720 | feeder2_line41 | 3 | 99 | 5.0001e-08 | 7.3716e-07 | 5.0506e-08 | 7.4461e-07
720 | feeder2_line42 | 1 | 99 | 2.9981e-07 | 7.5062e-07 | 3.0284e-07 | 7.582e-07
720 | feeder2_line42 | 2 | 99 | 2.9956e-07 | 7.499e-07 | 3.0258e-07 | 7.5748e-07
720 | feeder2_line42 | 3 | 99 | 1.4904 | 1.4904 | 1.5055 | 1.5055
720 | feeder2_line43 | 1 | 266.4 | 4.2535 | 4.2533 | 1.5967 | 1.5966
720 | feeder2_line43 | 2 | 266.4 | 3.0241 | 3.0241 | 1.1352 | 1.1352
720 | feeder2_line43 | 3 | 266.4 | 2.8913 | 2.8913 | 1.0853 | 1.0853
720 | feeder2_line44 | 1 | 354.6 | 84.8967 | 84.8943 | 23.9415 | 23.9409
720 | feeder2_line44 | 2 | 354.6 | 78.9357 | 78.9328 | 22.2605 | 22.2597
720 | feeder2_line44 | 3 | 354.6 | 77.9359 | 77.94 | 21.9786 | 21.9797
720 | feeder2_line45 | 1 | 99 | 4.9943e-08 | 5.8154e-07 | 5.0448e-08 | 5.8742e-07
720 | feeder2_line45 | 2 | 99 | 5.0105e-08 | 5.808e-07 | 5.0611e-08 | 5.8667e-07
720 | feeder2_line45 | 3 | 99 | 0.085683 | 0.085701 | 0.086549 | 0.086567
720 | feeder2_line46 | 1 | 99 | 5.7467e-07 | 1.3607e-06 | 5.8047e-07 | 1.3745e-06
720 | feeder2_line46 | 2 | 99 | 5.7411e-07 | 1.3594e-06 | 5.7991e-07 | 1.3732e-06
720 | feeder2_line46 | 3 | 99 | 0.89849 | 0.89852 | 0.90757 | 0.9076
720 | feeder2_line47 | 1 | 266.4 | 4.2536 | 4.2533 | 1.5967 | 1.5966
720 | feeder2_line47 | 2 | 266.4 | 3.0242 | 3.0241 | 1.1352 | 1.1352
720 | feeder2_line47 | 3 | 266.4 | 2.1204 | 2.1201 | 0.79593 | 0.79585
720 | feeder2_line48 | 1 | 99 | 2.0262 | 2.0262 | 2.0467 | 2.0467
720 | feeder2_line48 | 2 | 99 | 5.0015e-08 | 7.3194e-07 | 5.0521e-08 | 7.3933e-07
720 | feeder2_line48 | 3 | 99 | 4.9937e-08 | 7.3268e-07 | 5.0442e-08 | 7.4008e-07
720 | feeder2_line49 | 1 | 266.4 | 2.249 | 2.2487 | 0.8442 | 0.84411
720 | feeder2_line49 | 2 | 266.4 | 3.0242 | 3.0241 | 1.1352 | 1.1352
720 | feeder2_line49 | 3 | 266.4 | 2.1203 | 2.1201 | 0.79592 | 0.79585
720 | feeder2_line50 | 1 | 99 | 5.7465e-07 | 1.2383e-06 | 5.8045e-07 | 1.2508e-06
720 | feeder2_line50 | 2 | 99 | 1.6648 | 1.6648 | 1.6816 | 1.6816
720 | feeder2_line50 | 3 | 99 | 5.7469e-07 | 1.2384e-06 | 5.8049e-07 | 1.2509e-06
720 | feeder2_line51 | 1 | 99 | 0.96781 | 0.96776 | 0.97758 | 0.97753
720 | feeder2_line51 | 2 | 99 | 5.741e-07 | 1.3431e-06 | 5.799e-07 | 1.3567e-06
720 | feeder2_line51 | 3 | 99 | 5.7469e-07 | 1.3444e-06 | 5.8049e-07 | 1.358e-06
720 | feeder2_line52 | 1 | 266.4 | 1.3913 | 1.3913 | 0.52225 | 0.52225
720 | feeder2_line52 | 2 | 266.4 | 1.4595 | 1.4595 | 0.54786 | 0.54787
720 | feeder2_line52 | 3 | 266.4 | 2.1202 | 2.1202 | 0.79588 | 0.79585
720 | feeder2_line53 | 1 | 99 | 5.497e-07 | 7.5578e-07 | 5.5525e-07 | 7.6342e-07
720 | feeder2_line53 | 2 | 99 | 1.4596 | 1.4595 | 1.4743 | 1.4743
720 | feeder2_line53 | 3 | 99 | 5.4972e-07 | 7.5583e-07 | 5.5527e-07 | 7.6347e-07
720 | feeder2_line54 | 1 | 266.4 | 1.3912 | 1.3913 | 0.52222 | 0.52225
720 | feeder2_line54 | 2 | 266.4 | 8.5646e-05 | 4.632e-06 | 3.2149e-05 | 1.7387e-06
720 | feeder2_line54 | 3 | 266.4 | 2.1201 | 2.1202 | 0.79583 | 0.79585
720 | feeder2_line55 | 1 | 99 | 1.1011 | 1.1011 | 1.1122 | 1.1122
720 | feeder2_line55 | 2 | 99 | 5.0145e-08 | 7.3213e-07 | 5.0651e-08 | 7.3953e-07
720 | feeder2_line55 | 3 | 99 | 5.0044e-08 | 7.3292e-07 | 5.0549e-08 | 7.4032e-07
720 | feeder2_line56 | 1 | 354.6 | 85.4851 | 85.4827 | 24.1075 | 24.1068
720 | feeder2_line56 | 2 | 354.6 | 78.9358 | 78.9328 | 22.2605 | 22.2597
720 | feeder2_line56 | 3 | 354.6 | 77.936 | 77.94 | 21.9786 | 21.9797
720 | feeder2_line57 | 1 | 99 | 7.4859e-07 | 1.5481e-06 | 7.5615e-07 | 1.5637e-06
720 | feeder2_line57 | 2 | 99 | 7.5022e-07 | 1.5466e-06 | 7.578e-07 | 1.5623e-06
720 | feeder2_line57 | 3 | 99 | 2.1202 | 2.1202 | 2.1416 | 2.1416
720 | feeder2_line58 | 1 | 266.4 | 1.3913 | 1.3913 | 0.52225 | 0.52225
720 | feeder2_line58 | 2 | 266.4 | 1.8973e-05 | 2.6893e-06 | 7.1219e-06 | 1.0095e-06
720 | feeder2_line58 | 3 | 266.4 | 1.8993e-05 | 2.6919e-06 | 7.1294e-06 | 1.0105e-06
720 | feeder2_line59 | 1 | 99 | 4.9901e-08 | 5.3812e-07 | 5.0405e-08 | 5.4356e-07
720 | feeder2_line59 | 2 | 99 | 5.0017e-08 | 5.3762e-07 | 5.0523e-08 | 5.4305e-07
720 | feeder2_line59 | 3 | 99 | 1.2792 | 1.2792 | 1.2921 | 1.2921
720 | feeder2_line60 | 1 | 99 | 2.998e-07 | 8.1327e-07 | 3.0283e-07 | 8.2149e-07
720 | feeder2_line60 | 2 | 99 | 2.9955e-07 | 8.1251e-07 | 3.0258e-07 | 8.2071e-07
720 | feeder2_line60 | 3 | 99 | 0.91527 | 0.91527 | 0.92452 | 0.92451
720 | feeder2_line61 | 1 | 266.4 | 2.2339 | 2.2341 | 0.83855 | 0.83862
720 | feeder2_line61 | 2 | 266.4 | 2.5129 | 2.513 | 0.94327 | 0.94333
720 | feeder2_line61 | 3 | 266.4 | 1.6028 | 1.603 | 0.60165 | 0.60173
720 | feeder2_line62 | 1 | 354.6 | 87.3085 | 87.3063 | 24.6217 | 24.6211
720 | feeder2_line62 | 2 | 354.6 | 81.4395 | 81.4368 | 22.9666 | 22.9658
720 | feeder2_line62 | 3 | 354.6 | 79.513 | 79.5173 | 22.4233 | 22.4245
720 | feeder2_line63 | 1 | 99 | 0.088893 | 0.088891 | 0.089791 | 0.089789
720 | feeder2_line63 | 2 | 99 | 5.7411e-07 | 1.2216e-06 | 5.799e-07 | 1.2339e-06
720 | feeder2_line63 | 3 | 99 | 5.7469e-07 | 1.2228e-06 | 5.8049e-07 | 1.2352e-06
720 | feeder2_line64 | 1 | 99 | 1.3213 | 1.3213 | 1.3347 | 1.3347
720 | feeder2_line64 | 2 | 99 | 4.3297e-12 | 3.2178e-07 | 4.3735e-12 | 3.2503e-07
720 | feeder2_line64 | 3 | 99 | 1.2771e-11 | 3.2211e-07 | 1.29e-11 | 3.2537e-07
720 | feeder2_line65 | 1 | 99 | 4.9982e-08 | 6.4471e-07 | 5.0487e-08 | 6.5122e-07
720 | feeder2_line65 | 2 | 99 | 0.50131 | 0.50131 | 0.50638 | 0.50637
720 | feeder2_line65 | 3 | 99 | 5.0111e-08 | 6.443e-07 | 5.0617e-08 | 6.508e-07
720 | feeder2_line66 | 1 | 354.6 | 87.3084 | 87.3063 | 24.6217 | 24.6211
720 | feeder2_line66 | 2 | 354.6 | 81.9354 | 81.9326 | 23.1064 | 23.1056
720 | feeder2_line66 | 3 | 354.6 | 79.513 | 79.5173 | 22.4233 | 22.4245
720 | feeder2_line67 | 1 | 99 | 2.4987e-08 | 3.6424e-07 | 2.524e-08 | 3.6792e-07
720 | feeder2_line67 | 2 | 99 | 2.5089e-08 | 3.6368e-07 | 2.5342e-08 | 3.6735e-07
720 | feeder2_line67 | 3 | 99 | 0.54369 | 0.5437 | 0.54919 | 0.54919
720 | feeder2_line68 | 1 | 266.4 | 2.234 | 2.2341 | 0.83857 | 0.83862
720 | feeder2_line68 | 2 | 266.4 | 2.5129 | 2.513 | 0.94329 | 0.94333
720 | feeder2_line68 | 3 | 266.4 | 1.085 | 1.0851 | 0.40727 | 0.40732
720 | feeder2_line69 | 1 | 99 | 2.9588 | 2.9588 | 2.9887 | 2.9887
720 | feeder2_line69 | 2 | 99 | 2.5524e-06 | 6.6829e-07 | 2.5782e-06 | 6.7504e-07
720 | feeder2_line69 | 3 | 99 | 2.5561e-06 | 6.6898e-07 | 2.5819e-06 | 6.7574e-07
720 | feeder2_line70 | 1 | 354.6 | 89.1616 | 89.1595 | 25.1443 | 25.1437
720 | feeder2_line70 | 2 | 354.6 | 81.9353 | 81.9326 | 23.1064 | 23.1056
720 | feeder2_line70 | 3 | 354.6 | 79.5129 | 79.5173 | 22.4233 | 22.4245
720 | feeder2_line71 | 1 | 99 | 4.9992e-08 | 7.1957e-07 | 5.0497e-08 | 7.2684e-07
720 | feeder2_line71 | 2 | 99 | 1.248 | 1.248 | 1.2606 | 1.2606
720 | feeder2_line71 | 3 | 99 | 5.014e-08 | 7.1903e-07 | 5.0647e-08 | 7.2629e-07
720 | feeder2_line72 | 1 | 354.6 | 89.1617 | 89.1595 | 25.1443 | 25.1437
720 | feeder2_line72 | 2 | 354.6 | 82.5895 | 82.5867 | 23.2909 | 23.2901
720 | feeder2_line72 | 3 | 354.6 | 79.513 | 79.5173 | 22.4233 | 22.4245
720 | feeder2_line73 | 1 | 99 | 6.0124e-07 | 1.5421e-06 | 6.0731e-07 | 1.5576e-06
720 | feeder2_line73 | 2 | 99 | 1.3378 | 1.3378 | 1.3513 | 1.3513
720 | feeder2_line73 | 3 | 99 | 6.0101e-07 | 1.5414e-06 | 6.0708e-07 | 1.5569e-06
720 | feeder2_line74 | 1 | 99 | 4.9976e-08 | 4.5992e-07 | 5.0481e-08 | 4.6457e-07
720 | feeder2_line74 | 2 | 99 | 1.0858 | 1.0858 | 1.0968 | 1.0968
720 | feeder2_line74 | 3 | 99 | 5.0072e-08 | 4.5972e-07 | 5.0578e-08 | 4.6436e-07
720 | feeder2_line75 | 1 | 266.4 | 2.2341 | 2.2341 | 0.83861 | 0.83862
720 | feeder2_line75 | 2 | 266.4 | 0.089618 | 0.089649 | 0.03364 | 0.033652
720 | feeder2_line75 | 3 | 266.4 | 1.0851 | 1.0851 | 0.4073 | 0.40732
720 | feeder2_line76 | 1 | 99 | 2.2341 | 2.2341 | 2.2567 | 2.2567
720 | feeder2_line76 | 2 | 99 | 8.5046e-07 | 1.5882e-06 | 8.5905e-07 | 1.6043e-06
720 | feeder2_line76 | 3 | 99 | 8.5144e-07 | 1.59e-06 | 8.6004e-07 | 1.606e-06
720 | feeder2_line77 | 1 | 99 | 2.4988e-08 | 5.7797e-07 | 2.5241e-08 | 5.8381e-07
720 | feeder2_line77 | 2 | 99 | 2.5085e-08 | 5.7708e-07 | 2.5338e-08 | 5.8291e-07
720 | feeder2_line77 | 3 | 99 | 1.0851 | 1.0851 | 1.096 | 1.0961
720 | feeder2_line78 | 1 | 266.4 | 1.3632e-11 | 9.5846e-07 | 5.1171e-12 | 3.5978e-07
720 | feeder2_line78 | 2 | 266.4 | 0.08965 | 0.089649 | 0.033653 | 0.033652
720 | feeder2_line78 | 3 | 266.4 | 1.6186e-11 | 9.5811e-07 | 6.0758e-12 | 3.5965e-07
720 | feeder2_line79 | 1 | 354.6 | 2.4906 | 2.4903 | 0.70238 | 0.70227
720 | feeder2_line79 | 2 | 354.6 | 8.0244 | 8.0241 | 2.263 | 2.2629
720 | feeder2_line79 | 3 | 354.6 | 5.604 | 5.6037 | 1.5804 | 1.5803
720 | feeder2_line80 | 1 | 354.6 | 91.5739 | 91.5711 | 25.8246 | 25.8238
720 | feeder2_line80 | 2 | 354.6 | 90.2502 | 90.247 | 25.4513 | 25.4504
720 | feeder2_line80 | 3 | 354.6 | 84.6342 | 84.638 | 23.8675 | 23.8686
720 | feeder2_line81 | 1 | 354.6 | 91.5739 | 91.5711 | 25.8246 | 25.8238
720 | feeder2_line81 | 2 | 354.6 | 90.2502 | 90.247 | 25.4513 | 25.4504
720 | feeder2_line81 | 3 | 354.6 | 85.5717 | 85.5755 | 24.1319 | 24.133
720 | feeder2_line82 | 1 | 354.6 | 6.4778e-12 | 7.3852e-07 | 1.8268e-12 | 2.0827e-07
720 | feeder2_line82 | 2 | 354.6 | 1.9084e-11 | 7.372e-07 | 5.3819e-12 | 2.079e-07
720 | feeder2_line82 | 3 | 354.6 | 0.93779 | 0.9378 | 0.26446 | 0.26447
720 | feeder2_line83 | 1 | 354.6 | 91.574 | 91.5711 | 25.8246 | 25.8238
720 | feeder2_line83 | 2 | 354.6 | 91.522 | 91.5186 | 25.8099 | 25.809
720 | feeder2_line83 | 3 | 354.6 | 85.5719 | 85.5755 | 24.1319 | 24.133
720 | feeder2_line84 | 1 | 354.6 | 7.3736e-12 | 1.3055e-06 | 2.0794e-12 | 3.6815e-07
720 | feeder2_line84 | 2 | 354.6 | 2.2692 | 2.2692 | 0.63994 | 0.63994
720 | feeder2_line84 | 3 | 354.6 | 7.1968e-12 | 1.3042e-06 | 2.0296e-12 | 3.678e-07
720 | feeder2_line85 | 1 | 99 | 0.076674 | 0.076672 | 0.077448 | 0.077446
720 | feeder2_line85 | 2 | 99 | 5.0302e-08 | 4.6511e-07 | 5.081e-08 | 4.6981e-07
720 | feeder2_line85 | 3 | 99 | 5.0221e-08 | 4.6552e-07 | 5.0728e-08 | 4.7022e-07
720 | feeder2_line86 | 1 | 354.6 | 91.6506 | 91.6476 | 25.8462 | 25.8453
720 | feeder2_line86 | 2 | 354.6 | 91.5221 | 91.5186 | 25.81 | 25.809
720 | feeder2_line86 | 3 | 354.6 | 85.572 | 85.5755 | 24.132 | 24.133
720 | feeder2_line87 | 1 | 354.6 | 91.6508 | 91.6476 | 25.8463 | 25.8453
720 | feeder2_line87 | 2 | 354.6 | 91.8988 | 91.8951 | 25.9162 | 25.9151
720 | feeder2_line87 | 3 | 354.6 | 87.0894 | 87.0928 | 24.5599 | 24.5609
720 | feeder2_line88 | 1 | 354.6 | 0.00011507 | 3.3849e-06 | 3.245e-05 | 9.5457e-07
720 | feeder2_line88 | 2 | 354.6 | 0.37867 | 0.3785 | 0.10679 | 0.10674
720 | feeder2_line88 | 3 | 354.6 | 2.6275 | 2.6274 | 0.74097 | 0.74095
720 | feeder2_line89 | 1 | 354.6 | 91.6485 | 91.6476 | 25.8456 | 25.8453
720 | feeder2_line89 | 2 | 354.6 | 95.4244 | 95.4229 | 26.9104 | 26.91
720 | feeder2_line89 | 3 | 354.6 | 87.0872 | 87.0928 | 24.5593 | 24.5609
720 | feeder2_line90 | 1 | 354.6 | 0.00072925 | 2.0434e-06 | 0.00020566 | 5.7626e-07
720 | feeder2_line90 | 2 | 354.6 | 4.3172 | 4.3173 | 1.2175 | 1.2175
720 | feeder2_line90 | 3 | 354.6 | 0.00072777 | 2.042e-06 | 0.00020524 | 5.7587e-07
720 | feeder2_line91 | 1 | 354.6 | 91.6484 | 91.6476 | 25.8456 | 25.8453
720 | feeder2_line91 | 2 | 354.6 | 95.4243 | 95.4229 | 26.9104 | 26.91
720 | feeder2_line91 | 3 | 354.6 | 88.003 | 88.0088 | 24.8175 | 24.8192
720 | feeder2_line92 | 1 | 354.6 | 2.1879e-11 | 1.0309e-06 | 6.1702e-12 | 2.9073e-07
720 | feeder2_line92 | 2 | 354.6 | 1.9222e-12 | 1.0291e-06 | 5.4209e-13 | 2.902e-07
720 | feeder2_line92 | 3 | 354.6 | 0.91719 | 0.91719 | 0.25866 | 0.25865
720 | feeder2_line93 | 1 | 99 | 2.5028e-08 | 3.4416e-07 | 2.5281e-08 | 3.4763e-07
720 | feeder2_line93 | 2 | 99 | 2.27 | 2.27 | 2.2929 | 2.2929
720 | feeder2_line93 | 3 | 99 | 2.5135e-08 | 3.4373e-07 | 2.5389e-08 | 3.4721e-07
720 | feeder2_line94 | 1 | 354.6 | 2.5028e-06 | 1.6754e-06 | 7.058e-07 | 4.7247e-07
720 | feeder2_line94 | 2 | 354.6 | 2.3026 | 2.3026 | 0.64935 | 0.64935
720 | feeder2_line94 | 3 | 354.6 | 2.5134e-06 | 1.6736e-06 | 7.0879e-07 | 4.7196e-07
720 | feeder2_line95 | 1 | 99 | 3.5905e-06 | 2.625e-06 | 3.6268e-06 | 2.6515e-06
720 | feeder2_line95 | 2 | 99 | 0.37856 | 0.3785 | 0.38239 | 0.38232
720 | feeder2_line95 | 3 | 99 | 3.5835e-06 | 2.6219e-06 | 3.6197e-06 | 2.6484e-06
720 | feeder2_line96 | 1 | 354.6 | 0.00012184 | 6.2572e-07 | 3.436e-05 | 1.7646e-07
720 | feeder2_line96 | 2 | 354.6 | 0.00012156 | 6.2467e-07 | 3.4281e-05 | 1.7616e-07
720 | feeder2_line96 | 3 | 354.6 | 2.6274 | 2.6274 | 0.74095 | 0.74095
720 | feeder2_line97 | 1 | 354.6 | 92.7914 | 92.7905 | 26.1679 | 26.1676
720 | feeder2_line97 | 2 | 354.6 | 95.4244 | 95.4229 | 26.9104 | 26.91
720 | feeder2_line97 | 3 | 354.6 | 88.0032 | 88.0088 | 24.8176 | 24.8192
720 | feeder2_line98 | 1 | 354.6 | 1.1452 | 1.1435 | 0.32296 | 0.32248
720 | feeder2_line98 | 2 | 354.6 | 0.001706 | 6.2379e-07 | 0.00048109 | 1.7591e-07
720 | feeder2_line98 | 3 | 354.6 | 0.0017123 | 6.2406e-07 | 0.00048289 | 1.7599e-07
720 | feeder2_line99 | 1 | 99 | 2.5019e-08 | 4.4984e-07 | 2.5272e-08 | 4.5439e-07
720 | feeder2_line99 | 2 | 99 | 2.5154e-08 | 4.4894e-07 | 2.5408e-08 | 4.5348e-07
720 | feeder2_line99 | 3 | 99 | 2.6274 | 2.6274 | 2.654 | 2.654
720 | feeder2_line100 | 1 | 99 | 1.1435 | 1.1435 | 1.1551 | 1.1551
720 | feeder2_line100 | 2 | 99 | 2.5173e-08 | 6.1671e-07 | 2.5427e-08 | 6.2294e-07
720 | feeder2_line100 | 3 | 99 | 2.5144e-08 | 6.1715e-07 | 2.5398e-08 | 6.2339e-07
720 | feeder2_line101 | 1 | 354.6 | 2.3027 | 2.3023 | 0.64937 | 0.64927
720 | feeder2_line101 | 2 | 354.6 | 8.0244 | 8.0241 | 2.2629 | 2.2629
720 | feeder2_line101 | 3 | 354.6 | 5.604 | 5.6037 | 1.5804 | 1.5803
720 | feeder2_line102 | 1 | 99 | 0.20477 | 0.20477 | 0.20684 | 0.20684
720 | feeder2_line102 | 2 | 99 | 2.3405e-06 | 8.8114e-07 | 2.3641e-06 | 8.9004e-07
720 | feeder2_line102 | 3 | 99 | 2.3464e-06 | 8.8199e-07 | 2.3701e-06 | 8.909e-07
720 | feeder2_line103 | 1 | 99 | 5.5234e-07 | 8.0814e-07 | 5.5792e-07 | 8.1631e-07
720 | feeder2_line103 | 2 | 99 | 0.12395 | 0.12395 | 0.1252 | 0.1252
720 | feeder2_line103 | 3 | 99 | 5.5162e-07 | 8.0728e-07 | 5.572e-07 | 8.1543e-07
720 | feeder2_line104 | 1 | 354.6 | 2.3026 | 2.3023 | 0.64935 | 0.64927
720 | feeder2_line104 | 2 | 354.6 | 7.9129 | 7.9126 | 2.2315 | 2.2314
720 | feeder2_line104 | 3 | 354.6 | 5.6039 | 5.6037 | 1.5803 | 1.5803
720 | feeder2_line105 | 1 | 99 | 2.5617e-06 | 7.436e-07 | 2.5876e-06 | 7.5111e-07
720 | feeder2_line105 | 2 | 99 | 2.5539e-06 | 7.4205e-07 | 2.5797e-06 | 7.4955e-07
720 | feeder2_line105 | 3 | 99 | 0.82781 | 0.82783 | 0.83617 | 0.8362
720 | feeder2_line106 | 1 | 354.6 | 2.3025 | 2.3023 | 0.64933 | 0.64927
720 | feeder2_line106 | 2 | 354.6 | 7.9128 | 7.9126 | 2.2315 | 2.2314
720 | feeder2_line106 | 3 | 354.6 | 4.8693 | 4.8691 | 1.3732 | 1.3731
720 | feeder2_line107 | 1 | 99 | 3.2616e-07 | 9.0618e-07 | 3.2945e-07 | 9.1533e-07
720 | feeder2_line107 | 2 | 99 | 1.0492 | 1.0492 | 1.0598 | 1.0598
720 | feeder2_line107 | 3 | 99 | 3.2598e-07 | 9.0517e-07 | 3.2927e-07 | 9.1431e-07
720 | feeder2_line108 | 1 | 354.6 | 2.3025 | 2.3023 | 0.64933 | 0.64927
720 | feeder2_line108 | 2 | 354.6 | 7.1093 | 7.1091 | 2.0049 | 2.0048
720 | feeder2_line108 | 3 | 354.6 | 4.8693 | 4.8691 | 1.3732 | 1.3731
720 | feeder2_line109 | 1 | 354.6 | 94.8638 | 94.8616 | 26.7524 | 26.7517
720 | feeder2_line109 | 2 | 354.6 | 95.4256 | 95.4229 | 26.9108 | 26.91
720 | feeder2_line109 | 3 | 354.6 | 88.0044 | 88.0088 | 24.8179 | 24.8192
720 | feeder2_line110 | 1 | 99 | 2.3347 | 2.334 | 2.3583 | 2.3576
720 | feeder2_line110 | 2 | 99 | 0.00080755 | 9.1327e-07 | 0.00081571 | 9.225e-07
720 | feeder2_line110 | 3 | 99 | 0.00080833 | 9.1363e-07 | 0.00081649 | 9.2286e-07
720 | feeder2_line111 | 1 | 99 | 2.5017e-08 | 3.842e-07 | 2.527e-08 | 3.8808e-07
720 | feeder2_line111 | 2 | 99 | 0.045391 | 0.045371 | 0.04585 | 0.04583
720 | feeder2_line111 | 3 | 99 | 2.512e-08 | 3.8376e-07 | 2.5374e-08 | 3.8763e-07
720 | feeder2_line112 | 1 | 99 | 3.2647e-07 | 9.2325e-07 | 3.2977e-07 | 9.3258e-07
720 | feeder2_line112 | 2 | 99 | 0.33333 | 0.33329 | 0.3367 | 0.33666
720 | feeder2_line112 | 3 | 99 | 3.2628e-07 | 9.2218e-07 | 3.2958e-07 | 9.315e-07
720 | feeder2_line113 | 1 | 99 | 1.3471 | 1.3472 | 1.3607 | 1.3608
720 | feeder2_line113 | 2 | 99 | 3.2651e-07 | 9.0964e-07 | 3.2981e-07 | 9.1883e-07
720 | feeder2_line113 | 3 | 99 | 3.2665e-07 | 9.1024e-07 | 3.2995e-07 | 9.1943e-07
720 | feeder2_line114 | 1 | 99 | 0.12377 | 0.12377 | 0.12502 | 0.12502
720 | feeder2_line114 | 2 | 99 | 2.5139e-08 | 4.3815e-07 | 2.5393e-08 | 4.4258e-07
720 | feeder2_line114 | 3 | 99 | 2.5091e-08 | 4.3858e-07 | 2.5344e-08 | 4.4301e-07
720 | feeder2_line115 | 1 | 99 | 2.4986e-08 | 5.655e-07 | 2.5239e-08 | 5.7121e-07
720 | feeder2_line115 | 2 | 99 | 6.1612 | 6.1613 | 6.2235 | 6.2235
720 | feeder2_line115 | 3 | 99 | 2.5085e-08 | 5.6484e-07 | 2.5338e-08 | 5.7055e-07
720 | feeder2_line116 | 1 | 354.6 | 2.3025 | 2.3023 | 0.64933 | 0.64927
720 | feeder2_line116 | 2 | 354.6 | 1.3659 | 1.3658 | 0.38519 | 0.38516
720 | feeder2_line116 | 3 | 354.6 | 4.8693 | 4.8691 | 1.3732 | 1.3731
720 | feeder2_line117 | 1 | 99 | 5.011e-08 | 6.473e-07 | 5.0616e-08 | 6.5384e-07
720 | feeder2_line117 | 2 | 99 | 0.89976 | 0.89977 | 0.90885 | 0.90886
720 | feeder2_line117 | 3 | 99 | 5.035e-08 | 6.4642e-07 | 5.0859e-08 | 6.5295e-07
720 | feeder2_line118 | 1 | 354.6 | 94.8639 | 94.8616 | 26.7524 | 26.7517
720 | feeder2_line118 | 2 | 354.6 | 95.9847 | 95.9819 | 27.0684 | 27.0677
720 | feeder2_line118 | 3 | 354.6 | 88.0044 | 88.0088 | 24.8179 | 24.8192
720 | feeder2_line119 | 1 | 99 | 2.4994e-08 | 6.0849e-07 | 2.5246e-08 | 6.1464e-07
720 | feeder2_line119 | 2 | 99 | 2.5139e-08 | 6.0717e-07 | 2.5393e-08 | 6.1331e-07
720 | feeder2_line119 | 3 | 99 | 1.469 | 1.4689 | 1.4838 | 1.4838
720 | feeder2_line120 | 1 | 354.6 | 2.3025 | 2.3023 | 0.64933 | 0.64927
720 | feeder2_line120 | 2 | 354.6 | 1.3659 | 1.3658 | 0.38518 | 0.38516
720 | feeder2_line120 | 3 | 354.6 | 3.4005 | 3.4004 | 0.95898 | 0.95893
720 | feeder2_line121 | 1 | 99 | 3.2614e-07 | 9.4224e-07 | 3.2944e-07 | 9.5176e-07
720 | feeder2_line121 | 2 | 99 | 1.317 | 1.317 | 1.3303 | 1.3303
720 | feeder2_line121 | 3 | 99 | 3.2594e-07 | 9.4111e-07 | 3.2923e-07 | 9.5061e-07
720 | feeder2_line122 | 1 | 354.6 | 2.3025 | 2.3023 | 0.64933 | 0.64927
720 | feeder2_line122 | 2 | 354.6 | 0.089124 | 0.08888 | 0.025134 | 0.025065
720 | feeder2_line122 | 3 | 354.6 | 3.4005 | 3.4004 | 0.95897 | 0.95893
720 | feeder2_line123 | 1 | 99 | 5.773e-07 | 9.7637e-07 | 5.8314e-07 | 9.8623e-07
720 | feeder2_line123 | 2 | 99 | 5.7607e-07 | 9.7431e-07 | 5.8189e-07 | 9.8415e-07
720 | feeder2_line123 | 3 | 99 | 0.75695 | 0.75696 | 0.76459 | 0.76461
720 | feeder2_line124 | 1 | 354.6 | 2.3025 | 2.3023 | 0.64931 | 0.64927
720 | feeder2_line124 | 2 | 354.6 | 0.089027 | 0.08888 | 0.025106 | 0.025065
720 | feeder2_line124 | 3 | 354.6 | 2.7272 | 2.7271 | 0.76911 | 0.76907
720 | feeder2_line125 | 1 | 99 | 5.773e-07 | 9.0763e-07 | 5.8313e-07 | 9.1679e-07
720 | feeder2_line125 | 2 | 99 | 5.7607e-07 | 9.0573e-07 | 5.8189e-07 | 9.1488e-07
720 | feeder2_line125 | 3 | 99 | 1.1464 | 1.1464 | 1.1579 | 1.158
720 | feeder2_line126 | 1 | 354.6 | 2.3026 | 2.3023 | 0.64936 | 0.64927
720 | feeder2_line126 | 2 | 354.6 | 0.089184 | 0.088879 | 0.025151 | 0.025065
720 | feeder2_line126 | 3 | 354.6 | 1.7272 | 1.7269 | 0.48708 | 0.48699
720 | feeder2_line127 | 1 | 99 | 5.7729e-07 | 1.0866e-06 | 5.8312e-07 | 1.0975e-06
720 | feeder2_line127 | 2 | 99 | 5.7608e-07 | 1.0843e-06 | 5.819e-07 | 1.0953e-06
720 | feeder2_line127 | 3 | 99 | 0.076859 | 0.076864 | 0.077636 | 0.07764
720 | feeder2_line128 | 1 | 354.6 | 2.3026 | 2.3023 | 0.64934 | 0.64927
720 | feeder2_line128 | 2 | 354.6 | 0.089099 | 0.088879 | 0.025127 | 0.025065
720 | feeder2_line128 | 3 | 354.6 | 1.6687 | 1.6684 | 0.47059 | 0.47051
720 | feeder2_line129 | 1 | 99 | 5.5229e-07 | 8.8103e-07 | 5.5787e-07 | 8.8993e-07
720 | feeder2_line129 | 2 | 99 | 0.088882 | 0.088879 | 0.08978 | 0.089777
720 | feeder2_line129 | 3 | 99 | 5.5149e-07 | 8.7998e-07 | 5.5706e-07 | 8.8887e-07
720 | feeder2_line130 | 1 | 354.6 | 2.3026 | 2.3023 | 0.64935 | 0.64927
720 | feeder2_line130 | 2 | 354.6 | 0.0003096 | 4.653e-06 | 8.7311e-05 | 1.3122e-06
720 | feeder2_line130 | 3 | 354.6 | 1.6688 | 1.6684 | 0.4706 | 0.47051
720 | feeder2_line131 | 1 | 99 | 5.7727e-07 | 9.7647e-07 | 5.8311e-07 | 9.8633e-07
720 | feeder2_line131 | 2 | 99 | 5.7608e-07 | 9.7448e-07 | 5.819e-07 | 9.8433e-07
720 | feeder2_line131 | 3 | 99 | 1.6116 | 1.6116 | 1.6279 | 1.6279
720 | feeder2_line132 | 1 | 354.6 | 2.3024 | 2.3023 | 0.6493 | 0.64927
720 | feeder2_line132 | 2 | 354.6 | 0.00012603 | 2.9256e-06 | 3.5543e-05 | 8.2503e-07
720 | feeder2_line132 | 3 | 354.6 | 0.076929 | 0.076864 | 0.021695 | 0.021676
720 | feeder2_line133 | 1 | 99 | 2.3023 | 2.3023 | 2.3256 | 2.3256
720 | feeder2_line133 | 2 | 99 | 3.0061e-07 | 9.8227e-07 | 3.0364e-07 | 9.9219e-07
720 | feeder2_line133 | 3 | 99 | 3.0083e-07 | 9.831e-07 | 3.0387e-07 | 9.9303e-07
720 | feeder2_line134 | 1 | 354.6 | 5.0408e-12 | 1.7947e-06 | 1.4216e-12 | 5.0613e-07
720 | feeder2_line134 | 2 | 354.6 | 5.2997e-12 | 1.7914e-06 | 1.4945e-12 | 5.052e-07
720 | feeder2_line134 | 3 | 354.6 | 0.07686 | 0.076864 | 0.021675 | 0.021676
720 | feeder2_line135 | 1 | 99 | 1.2514 | 1.2513 | 1.264 | 1.264
720 | feeder2_line135 | 2 | 99 | 5.0429e-08 | 5.8901e-07 | 5.0938e-08 | 5.9496e-07
720 | feeder2_line135 | 3 | 99 | 5.0387e-08 | 5.8927e-07 | 5.0896e-08 | 5.9522e-07
720 | feeder2_line136 | 1 | 354.6 | 95.6044 | 95.6022 | 26.9612 | 26.9606
720 | feeder2_line136 | 2 | 354.6 | 95.9846 | 95.9819 | 27.0684 | 27.0677
720 | feeder2_line136 | 3 | 354.6 | 88.0044 | 88.0088 | 24.8179 | 24.8192
720 | feeder2_line137 | 1 | 99 | 1.0617 | 1.0617 | 1.0724 | 1.0724
720 | feeder2_line137 | 2 | 99 | 8.5484e-07 | 1.5866e-06 | 8.6347e-07 | 1.6026e-06
720 | feeder2_line137 | 3 | 99 | 8.552e-07 | 1.5873e-06 | 8.6384e-07 | 1.6033e-06
720 | feeder2_line138 | 1 | 354.6 | 96.5045 | 96.5022 | 27.215 | 27.2144
720 | feeder2_line138 | 2 | 354.6 | 95.9847 | 95.9819 | 27.0684 | 27.0677
720 | feeder2_line138 | 3 | 354.6 | 88.0044 | 88.0088 | 24.8179 | 24.8192
720 | feeder2_line139 | 1 | 99 | 5.0149e-08 | 4.9537e-07 | 5.0656e-08 | 5.0037e-07
720 | feeder2_line139 | 2 | 99 | 5.0431e-08 | 4.9444e-07 | 5.0941e-08 | 4.9943e-07
720 | feeder2_line139 | 3 | 99 | 9.4739 | 9.474 | 9.5696 | 9.5697
720 | feeder2_line140 | 1 | 354.6 | 96.5046 | 96.5022 | 27.2151 | 27.2144
720 | feeder2_line140 | 2 | 354.6 | 95.9848 | 95.9819 | 27.0685 | 27.0677
720 | feeder2_line140 | 3 | 354.6 | 97.4784 | 97.4827 | 27.4897 | 27.4909
720 | feeder2_line141 | 1 | 99 | 2.5471e-06 | 4.9011e-07 | 2.5729e-06 | 4.9506e-07
720 | feeder2_line141 | 2 | 99 | 1.4899 | 1.4899 | 1.505 | 1.505
720 | feeder2_line141 | 3 | 99 | 2.5408e-06 | 4.8935e-07 | 2.5665e-06 | 4.943e-07
720 | feeder2_line142 | 1 | 354.6 | 96.5044 | 96.5022 | 27.215 | 27.2144
720 | feeder2_line142 | 2 | 354.6 | 97.1881 | 97.1854 | 27.4078 | 27.407
720 | feeder2_line142 | 3 | 354.6 | 97.4782 | 97.4827 | 27.4896 | 27.4909
720 | feeder2_line143 | 1 | 99 | 8.5701e-07 | 1.7416e-06 | 8.6567e-07 | 1.7592e-06
720 | feeder2_line143 | 2 | 99 | 1.0505 | 1.0505 | 1.0611 | 1.0611
720 | feeder2_line143 | 3 | 99 | 8.5561e-07 | 1.739e-06 | 8.6425e-07 | 1.7566e-06
720 | feeder2_line144 | 1 | 354.6 | 96.5042 | 96.5022 | 27.2149 | 27.2144
720 | feeder2_line144 | 2 | 354.6 | 97.8549 | 97.8524 | 27.5959 | 27.5951
720 | feeder2_line144 | 3 | 354.6 | 97.478 | 97.4827 | 27.4896 | 27.4909
720 | feeder2_line145 | 1 | 99 | 2.5089e-08 | 4.8838e-07 | 2.5342e-08 | 4.9332e-07
720 | feeder2_line145 | 2 | 99 | 0.93623 | 0.93622 | 0.94569 | 0.94568
720 | feeder2_line145 | 3 | 99 | 2.5216e-08 | 4.8764e-07 | 2.5471e-08 | 4.9257e-07
720 | feeder2_line146 | 1 | 354.6 | 96.5041 | 96.5022 | 27.2149 | 27.2144
720 | feeder2_line146 | 2 | 354.6 | 98.7908 | 98.7884 | 27.8598 | 27.8591
720 | feeder2_line146 | 3 | 354.6 | 97.4779 | 97.4827 | 27.4895 | 27.4909
720 | feeder2_line147 | 1 | 99 | 1.2571 | 1.2571 | 1.2698 | 1.2698
720 | feeder2_line147 | 2 | 99 | 1.1574e-06 | 2.2486e-06 | 1.1691e-06 | 2.2713e-06
720 | feeder2_line147 | 3 | 99 | 1.1578e-06 | 2.2494e-06 | 1.1695e-06 | 2.2721e-06
720 | feeder2_line148 | 1 | 99 | 0.084258 | 0.084256 | 0.085109 | 0.085107
720 | feeder2_line148 | 2 | 99 | 6.0394e-07 | 1.5067e-06 | 6.1004e-07 | 1.5219e-06
720 | feeder2_line148 | 3 | 99 | 6.0414e-07 | 1.5073e-06 | 6.1025e-07 | 1.5225e-06
720 | feeder2_line149 | 1 | 354.6 | 97.845 | 97.8429 | 27.5931 | 27.5925
720 | feeder2_line149 | 2 | 354.6 | 98.791 | 98.7884 | 27.8598 | 27.8591
720 | feeder2_line149 | 3 | 354.6 | 97.4781 | 97.4827 | 27.4896 | 27.4909
720 | feeder2_line150 | 1 | 354.6 | 97.8451 | 97.8429 | 27.5931 | 27.5925
720 | feeder2_line150 | 2 | 354.6 | 99.0001 | 98.9974 | 27.9188 | 27.9181
720 | feeder2_line150 | 3 | 354.6 | 97.4782 | 97.4827 | 27.4896 | 27.4909
720 | feeder2_line151 | 1 | 99 | 9.8478e-06 | 1.7935e-06 | 9.9473e-06 | 1.8116e-06
720 | feeder2_line151 | 2 | 99 | 0.21233 | 0.21234 | 0.21448 | 0.21448
720 | feeder2_line151 | 3 | 99 | 9.8223e-06 | 1.7907e-06 | 9.9215e-06 | 1.8088e-06
720 | feeder2_line152 | 1 | 354.6 | 9.9805e-12 | 1.1954e-06 | 2.8146e-12 | 3.371e-07
720 | feeder2_line152 | 2 | 354.6 | 3.5958e-11 | 1.1934e-06 | 1.014e-11 | 3.3654e-07
720 | feeder2_line152 | 3 | 354.6 | 1.1886 | 1.1885 | 0.33518 | 0.33518
720 | feeder2_line153 | 1 | 99 | 1.3214 | 1.3214 | 1.3348 | 1.3348
720 | feeder2_line153 | 2 | 99 | 5.0512e-08 | 5.9704e-07 | 5.1022e-08 | 6.0307e-07
720 | feeder2_line153 | 3 | 99 | 5.0489e-08 | 5.9723e-07 | 5.0999e-08 | 6.0326e-07
720 | feeder2_line154 | 1 | 99 | 5.804e-07 | 8.9005e-07 | 5.8627e-07 | 8.9904e-07
720 | feeder2_line154 | 2 | 99 | 5.7932e-07 | 8.8841e-07 | 5.8517e-07 | 8.9738e-07
720 | feeder2_line154 | 3 | 99 | 1.2454 | 1.2454 | 1.258 | 1.258
720 | feeder2_line155 | 1 | 99 | 98.635 | 98.6329 | 99.6313 | 99.6292
720 | feeder2_line155 | 2 | 99 | 99 | 98.9974 | 100 | 99.9974
720 | feeder2_line155 | 3 | 99 | 98.9565 | 98.9612 | 99.9561 | 99.9608
720 | feeder2_line156 | 1 | 99 | 6.0524e-07 | 1.1711e-06 | 6.1135e-07 | 1.1829e-06
720 | feeder2_line156 | 2 | 99 | 0.12366 | 0.12365 | 0.1249 | 0.1249
720 | feeder2_line156 | 3 | 99 | 6.0447e-07 | 1.1693e-06 | 6.1058e-07 | 1.1811e-06
720 | feeder2_line157 | 1 | 99 | 2.5104e-08 | 2.5423e-07 | 2.5357e-08 | 2.568e-07
720 | feeder2_line157 | 2 | 99 | 0.089186 | 0.089184 | 0.090087 | 0.090085
720 | feeder2_line157 | 3 | 99 | 2.5232e-08 | 2.5385e-07 | 2.5487e-08 | 2.5642e-07
750 | feeder2_line1 | 1 | 354.6 | 44.8237 | 44.8358 | 12.6406 | 12.6441
750 | feeder2_line1 | 2 | 354.6 | 70.4185 | 70.4058 | 19.8586 | 19.855
750 | feeder2_line1 | 3 | 354.6 | 77.4519 | 77.4557 | 21.8421 | 21.8431
750 | feeder2_line2 | 1 | 354.6 | 45.2312 | 45.2431 | 12.7555 | 12.7589
750 | feeder2_line2 | 2 | 354.6 | 70.4186 | 70.4058 | 19.8586 | 19.855
750 | feeder2_line2 | 3 | 354.6 | 77.4521 | 77.4557 | 21.8421 | 21.8431
750 | feeder2_line3 | 1 | 80.1 | 1.2485 | 1.2486 | 1.5587 | 1.5588
750 | feeder2_line3 | 2 | 80.1 | 5.7211e-07 | 1.0572e-06 | 7.1424e-07 | 1.3199e-06
750 | feeder2_line3 | 3 | 80.1 | 5.7218e-07 | 1.0574e-06 | 7.1433e-07 | 1.3201e-06
750 | feeder2_line4 | 1 | 354.6 | 45.2313 | 45.2431 | 12.7556 | 12.7589
750 | feeder2_line4 | 2 | 354.6 | 71.1146 | 71.1016 | 20.0549 | 20.0512
750 | feeder2_line4 | 3 | 354.6 | 77.4523 | 77.4557 | 21.8421 | 21.8431
750 | feeder2_line5 | 1 | 80.1 | 5.7096e-07 | 9.963e-07 | 7.1281e-07 | 1.2438e-06
750 | feeder2_line5 | 2 | 80.1 | 0.71595 | 0.71595 | 0.89382 | 0.89382
750 | feeder2_line5 | 3 | 80.1 | 5.7223e-07 | 9.9848e-07 | 7.1439e-07 | 1.2465e-06
750 | feeder2_line6 | 1 | 80.1 | 5.7097e-07 | 1.172e-06 | 7.1282e-07 | 1.4632e-06
750 | feeder2_line6 | 2 | 80.1 | 5.7222e-07 | 1.1746e-06 | 7.1438e-07 | 1.4664e-06
750 | feeder2_line6 | 3 | 80.1 | 1.7444 | 1.7444 | 2.1778 | 2.1778
750 | feeder2_line7 | 1 | 354.6 | 45.2314 | 45.2431 | 12.7556 | 12.7589
750 | feeder2_line7 | 2 | 354.6 | 71.1148 | 71.1016 | 20.0549 | 20.0512
750 | feeder2_line7 | 3 | 354.6 | 78.804 | 78.8073 | 22.2234 | 22.2243
750 | feeder2_line8 | 1 | 80.1 | 0.52631 | 0.5263 | 0.65707 | 0.65706
750 | feeder2_line8 | 2 | 80.1 | 5.7243e-07 | 1.133e-06 | 7.1465e-07 | 1.4144e-06
750 | feeder2_line8 | 3 | 80.1 | 5.7252e-07 | 1.1331e-06 | 7.1475e-07 | 1.4147e-06
750 | feeder2_line9 | 1 | 354.6 | 45.6347 | 45.6463 | 12.8693 | 12.8726
750 | feeder2_line9 | 2 | 354.6 | 71.1148 | 71.1016 | 20.0549 | 20.0512
750 | feeder2_line9 | 3 | 354.6 | 78.8041 | 78.8073 | 22.2234 | 22.2243
750 | feeder2_line10 | 1 | 80.1 | 8.4397e-07 | 1.4922e-06 | 1.0536e-06 | 1.8629e-06
750 | feeder2_line10 | 2 | 80.1 | 0.52532 | 0.52531 | 0.65583 | 0.65582
750 | feeder2_line10 | 3 | 80.1 | 8.4639e-07 | 1.4963e-06 | 1.0567e-06 | 1.868e-06
750 | feeder2_line11 | 1 | 354.6 | 45.6347 | 45.6463 | 12.8693 | 12.8726
750 | feeder2_line11 | 2 | 354.6 | 71.5395 | 71.5264 | 20.1747 | 20.171
750 | feeder2_line11 | 3 | 354.6 | 78.804 | 78.8073 | 22.2234 | 22.2243
750 | feeder2_line12 | 1 | 80.1 | 5.4598e-07 | 9.8983e-07 | 6.8162e-07 | 1.2357e-06
750 | feeder2_line12 | 2 | 80.1 | 5.478e-07 | 9.9249e-07 | 6.839e-07 | 1.2391e-06
750 | feeder2_line12 | 3 | 80.1 | 0.96174 | 0.96176 | 1.2007 | 1.2007
750 | feeder2_line13 | 1 | 354.6 | 45.6347 | 45.6463 | 12.8693 | 12.8726
750 | feeder2_line13 | 2 | 354.6 | 71.5395 | 71.5264 | 20.1747 | 20.171
750 | feeder2_line13 | 3 | 354.6 | 79.1592 | 79.1625 | 22.3235 | 22.3244
750 | feeder2_line14 | 1 | 80.1 | 1.8165 | 1.8165 | 2.2678 | 2.2678
750 | feeder2_line14 | 2 | 80.1 | 2.9868e-07 | 6.4727e-07 | 3.7289e-07 | 8.0807e-07
750 | feeder2_line14 | 3 | 80.1 | 2.9878e-07 | 6.4738e-07 | 3.7301e-07 | 8.0822e-07
750 | feeder2_line15 | 1 | 354.6 | 46.4415 | 46.4531 | 13.0969 | 13.1001
750 | feeder2_line15 | 2 | 354.6 | 71.5395 | 71.5264 | 20.1747 | 20.171
750 | feeder2_line15 | 3 | 354.6 | 79.1592 | 79.1625 | 22.3235 | 22.3244
750 | feeder2_line16 | 1 | 80.1 | 5.71e-07 | 1.0287e-06 | 7.1286e-07 | 1.2843e-06
750 | feeder2_line16 | 2 | 80.1 | 0.94559 | 0.94559 | 1.1805 | 1.1805
750 | feeder2_line16 | 3 | 80.1 | 5.7283e-07 | 1.032e-06 | 7.1515e-07 | 1.2884e-06
750 | feeder2_line17 | 1 | 354.6 | 46.4415 | 46.4531 | 13.0969 | 13.1001
750 | feeder2_line17 | 2 | 354.6 | 72.4643 | 72.4511 | 20.4355 | 20.4318
750 | feeder2_line17 | 3 | 354.6 | 79.1592 | 79.1625 | 22.3235 | 22.3244
750 | feeder2_line18 | 1 | 80.1 | 5.4598e-07 | 7.3644e-07 | 6.8162e-07 | 9.194e-07
750 | feeder2_line18 | 2 | 80.1 | 5.4856e-07 | 7.3927e-07 | 6.8484e-07 | 9.2293e-07
750 | feeder2_line18 | 3 | 80.1 | 1.27 | 1.27 | 1.5856 | 1.5856
750 | feeder2_line19 | 1 | 354.6 | 46.4415 | 46.4531 | 13.0969 | 13.1001
750 | feeder2_line19 | 2 | 354.6 | 72.4643 | 72.4511 | 20.4355 | 20.4318
750 | feeder2_line19 | 3 | 354.6 | 79.8016 | 79.8048 | 22.5047 | 22.5056
750 | feeder2_line20 | 1 | 99 | 5.4598e-07 | 8.83e-07 | 5.5149e-07 | 8.9192e-07
750 | feeder2_line20 | 2 | 99 | 5.4876e-07 | 8.8664e-07 | 5.543e-07 | 8.956e-07
750 | feeder2_line20 | 3 | 99 | 0.085877 | 0.085864 | 0.086744 | 0.086731
750 | feeder2_line21 | 1 | 354.6 | 46.4416 | 46.4531 | 13.0969 | 13.1001
750 | feeder2_line21 | 2 | 354.6 | 72.4644 | 72.4511 | 20.4355 | 20.4318
750 | feeder2_line21 | 3 | 354.6 | 79.8863 | 79.8894 | 22.5286 | 22.5294
750 | feeder2_line22 | 1 | 99 | 5.7109e-07 | 1.0123e-06 | 5.7686e-07 | 1.0225e-06
750 | feeder2_line22 | 2 | 99 | 0.2952 | 0.29519 | 0.29818 | 0.29817
750 | feeder2_line22 | 3 | 99 | 5.7371e-07 | 1.0169e-06 | 5.7951e-07 | 1.0271e-06
750 | feeder2_line23 | 1 | 99 | 5.7109e-07 | 9.4757e-07 | 5.7686e-07 | 9.5714e-07
750 | feeder2_line23 | 2 | 99 | 5.736e-07 | 9.5167e-07 | 5.7939e-07 | 9.6128e-07
750 | feeder2_line23 | 3 | 99 | 0.081767 | 0.081768 | 0.082592 | 0.082594
750 | feeder2_line24 | 1 | 354.6 | 46.4417 | 46.4531 | 13.0969 | 13.1001
750 | feeder2_line24 | 2 | 354.6 | 72.7569 | 72.7435 | 20.518 | 20.5142
750 | feeder2_line24 | 3 | 354.6 | 79.9667 | 79.9697 | 22.5512 | 22.5521
750 | feeder2_line25 | 1 | 99 | 0.29735 | 0.29736 | 0.30035 | 0.30036
750 | feeder2_line25 | 2 | 99 | 4.9432e-08 | 6.9214e-07 | 4.9932e-08 | 6.9913e-07
750 | feeder2_line25 | 3 | 99 | 4.976e-08 | 6.923e-07 | 5.0262e-08 | 6.9929e-07
750 | feeder2_line26 | 1 | 99 | 0.085619 | 0.085624 | 0.086484 | 0.086489
750 | feeder2_line26 | 2 | 99 | 5.491e-07 | 8.5752e-07 | 5.5465e-07 | 8.6618e-07
750 | feeder2_line26 | 3 | 99 | 5.4906e-07 | 8.5772e-07 | 5.5461e-07 | 8.6638e-07
750 | feeder2_line27 | 1 | 354.6 | 46.8187 | 46.8301 | 13.2033 | 13.2065
750 | feeder2_line27 | 2 | 354.6 | 72.7569 | 72.7435 | 20.518 | 20.5142
750 | feeder2_line27 | 3 | 354.6 | 79.9667 | 79.9697 | 22.5512 | 22.5521
750 | feeder2_line28 | 1 | 99 | 2.5285e-06 | 7.0857e-07 | 2.554e-06 | 7.1573e-07
750 | feeder2_line28 | 2 | 99 | 0.076876 | 0.076871 | 0.077653 | 0.077648
750 | feeder2_line28 | 3 | 99 | 2.5481e-06 | 7.1244e-07 | 2.5738e-06 | 7.1964e-07
750 | feeder2_line29 | 1 | 354.6 | 46.8187 | 46.8301 | 13.2033 | 13.2065
750 | feeder2_line29 | 2 | 354.6 | 72.8327 | 72.8193 | 20.5394 | 20.5356
750 | feeder2_line29 | 3 | 354.6 | 79.9667 | 79.9697 | 22.5512 | 22.5521
750 | feeder2_line30 | 1 | 266.4 | 15.344 | 15.3439 | 5.7598 | 5.7597
750 | feeder2_line30 | 2 | 266.4 | 4.4584 | 4.4585 | 1.6736 | 1.6736
750 | feeder2_line30 | 3 | 266.4 | 10.6434 | 10.6433 | 3.9953 | 3.9952
750 | feeder2_line31 | 1 | 354.6 | 61.1343 | 61.1452 | 17.2404 | 17.2434
750 | feeder2_line31 | 2 | 354.6 | 75.6226 | 75.6086 | 21.3262 | 21.3222
750 | feeder2_line31 | 3 | 354.6 | 88.2239 | 88.2266 | 24.8798 | 24.8806
750 | feeder2_line32 | 1 | 354.6 | 61.1344 | 61.1452 | 17.2404 | 17.2434
750 | feeder2_line32 | 2 | 354.6 | 76.8223 | 76.8083 | 21.6645 | 21.6606
750 | feeder2_line32 | 3 | 354.6 | 88.2239 | 88.2266 | 24.8798 | 24.8806
750 | feeder2_line33 | 1 | 99 | 5.0503e-08 | 6.8381e-07 | 5.1013e-08 | 6.9072e-07
750 | feeder2_line33 | 2 | 99 | 1.2165 | 1.2165 | 1.2288 | 1.2288
750 | feeder2_line33 | 3 | 99 | 4.9791e-08 | 6.8832e-07 | 5.0294e-08 | 6.9527e-07
750 | feeder2_line34 | 1 | 354.6 | 61.1344 | 61.1452 | 17.2404 | 17.2434
750 | feeder2_line34 | 2 | 354.6 | 76.8223 | 76.8083 | 21.6645 | 21.6606
750 | feeder2_line34 | 3 | 354.6 | 88.3085 | 88.3111 | 24.9037 | 24.9044
750 | feeder2_line35 | 1 | 99 | 2.9833e-07 | 7.5731e-07 | 3.0134e-07 | 7.6496e-07
750 | feeder2_line35 | 2 | 99 | 2.9987e-07 | 7.6206e-07 | 3.029e-07 | 7.6976e-07
750 | feeder2_line35 | 3 | 99 | 0.085376 | 0.085379 | 0.086238 | 0.086241
750 | feeder2_line36 | 1 | 354.6 | 61.1624 | 61.1736 | 17.2483 | 17.2514
750 | feeder2_line36 | 2 | 354.6 | 76.8223 | 76.8083 | 21.6645 | 21.6606
750 | feeder2_line36 | 3 | 354.6 | 88.3084 | 88.3111 | 24.9037 | 24.9044
750 | feeder2_line37 | 1 | 99 | 0.028293 | 0.028553 | 0.028579 | 0.028842
750 | feeder2_line37 | 2 | 99 | 2.9993e-07 | 8.4339e-07 | 3.0296e-07 | 8.5191e-07
750 | feeder2_line37 | 3 | 99 | 3.0018e-07 | 8.4384e-07 | 3.0321e-07 | 8.5236e-07
750 | feeder2_line38 | 1 | 99 | 3.2342e-07 | 7.7295e-07 | 3.2669e-07 | 7.8076e-07
750 | feeder2_line38 | 2 | 99 | 1.3282 | 1.3283 | 1.3417 | 1.3417
750 | feeder2_line38 | 3 | 99 | 3.2474e-07 | 7.7784e-07 | 3.2802e-07 | 7.8569e-07
750 | feeder2_line39 | 1 | 266.4 | 15.344 | 15.3439 | 5.7598 | 5.7597
750 | feeder2_line39 | 2 | 266.4 | 3.1796 | 3.1796 | 1.1936 | 1.1936
750 | feeder2_line39 | 3 | 266.4 | 10.6434 | 10.6433 | 3.9953 | 3.9952
750 | feeder2_line40 | 1 | 354.6 | 61.4593 | 61.4703 | 17.332 | 17.3351
750 | feeder2_line40 | 2 | 354.6 | 76.8223 | 76.8083 | 21.6645 | 21.6606
750 | feeder2_line40 | 3 | 354.6 | 88.3085 | 88.3111 | 24.9037 | 24.9044
750 | feeder2_line41 | 1 | 99 | 0.29738 | 0.29739 | 0.30039 | 0.3004
750 | feeder2_line41 | 2 | 99 | 4.9404e-08 | 7.3706e-07 | 4.9903e-08 | 7.445e-07
750 | feeder2_line41 | 3 | 99 | 4.9803e-08 | 7.3748e-07 | 5.0306e-08 | 7.4492e-07
750 | feeder2_line42 | 1 | 99 | 2.9815e-07 | 7.4596e-07 | 3.0116e-07 | 7.5349e-07
750 | feeder2_line42 | 2 | 99 | 2.9968e-07 | 7.5061e-07 | 3.0271e-07 | 7.5819e-07
750 | feeder2_line42 | 3 | 99 | 1.2489 | 1.2489 | 1.2615 | 1.2615
750 | feeder2_line43 | 1 | 266.4 | 15.344 | 15.3439 | 5.7597 | 5.7597
750 | feeder2_line43 | 2 | 266.4 | 3.1797 | 3.1796 | 1.1936 | 1.1936
750 | feeder2_line43 | 3 | 266.4 | 9.5581 | 9.558 | 3.5879 | 3.5878
750 | feeder2_line44 | 1 | 354.6 | 61.4593 | 61.4703 | 17.332 | 17.3351
750 | feeder2_line44 | 2 | 354.6 | 76.8224 | 76.8083 | 21.6645 | 21.6606
750 | feeder2_line44 | 3 | 354.6 | 88.3938 | 88.3964 | 24.9277 | 24.9285
750 | feeder2_line45 | 1 | 99 | 5.0579e-08 | 5.7756e-07 | 5.109e-08 | 5.834e-07
750 | feeder2_line45 | 2 | 99 | 4.9402e-08 | 5.8134e-07 | 4.9901e-08 | 5.8721e-07
750 | feeder2_line45 | 3 | 99 | 0.085602 | 0.085579 | 0.086466 | 0.086443
750 | feeder2_line46 | 1 | 99 | 5.7106e-07 | 1.3523e-06 | 5.7683e-07 | 1.3659e-06
750 | feeder2_line46 | 2 | 99 | 5.7469e-07 | 1.3607e-06 | 5.8049e-07 | 1.3745e-06
750 | feeder2_line46 | 3 | 99 | 0.07212 | 0.072102 | 0.072849 | 0.072831
750 | feeder2_line47 | 1 | 266.4 | 15.344 | 15.3439 | 5.7598 | 5.7597
750 | feeder2_line47 | 2 | 266.4 | 3.1798 | 3.1796 | 1.1936 | 1.1936
750 | feeder2_line47 | 3 | 266.4 | 9.498 | 9.4978 | 3.5653 | 3.5653
750 | feeder2_line48 | 1 | 99 | 3.7912 | 3.7912 | 3.8295 | 3.8295
750 | feeder2_line48 | 2 | 99 | 4.9357e-08 | 7.3264e-07 | 4.9856e-08 | 7.4004e-07
750 | feeder2_line48 | 3 | 99 | 4.9776e-08 | 7.3272e-07 | 5.0279e-08 | 7.4012e-07
750 | feeder2_line49 | 1 | 266.4 | 12.2205 | 12.2203 | 4.5873 | 4.5872
750 | feeder2_line49 | 2 | 266.4 | 3.1798 | 3.1796 | 1.1936 | 1.1936
750 | feeder2_line49 | 3 | 266.4 | 9.498 | 9.4978 | 3.5653 | 3.5653
750 | feeder2_line50 | 1 | 99 | 5.7098e-07 | 1.2305e-06 | 5.7675e-07 | 1.2429e-06
750 | feeder2_line50 | 2 | 99 | 1.7411 | 1.741 | 1.7587 | 1.7586
750 | feeder2_line50 | 3 | 99 | 5.7471e-07 | 1.2385e-06 | 5.8052e-07 | 1.251e-06
750 | feeder2_line51 | 1 | 99 | 11.5369 | 11.537 | 11.6535 | 11.6535
750 | feeder2_line51 | 2 | 99 | 5.7466e-07 | 1.3444e-06 | 5.8047e-07 | 1.3579e-06
750 | feeder2_line51 | 3 | 99 | 5.7469e-07 | 1.3445e-06 | 5.805e-07 | 1.358e-06
750 | feeder2_line52 | 1 | 266.4 | 0.68451 | 0.68443 | 0.25695 | 0.25692
750 | feeder2_line52 | 2 | 266.4 | 1.5152 | 1.5153 | 0.56875 | 0.56879
750 | feeder2_line52 | 3 | 266.4 | 9.4979 | 9.4978 | 3.5653 | 3.5653
750 | feeder2_line53 | 1 | 99 | 5.4575e-07 | 7.5101e-07 | 5.5126e-07 | 7.5859e-07
750 | feeder2_line53 | 2 | 99 | 1.5152 | 1.5153 | 1.5305 | 1.5306
750 | feeder2_line53 | 3 | 99 | 5.4982e-07 | 7.5585e-07 | 5.5537e-07 | 7.6348e-07
750 | feeder2_line54 | 1 | 266.4 | 0.68433 | 0.68443 | 0.25688 | 0.25692
750 | feeder2_line54 | 2 | 266.4 | 8.5685e-05 | 4.6359e-06 | 3.2164e-05 | 1.7402e-06
750 | feeder2_line54 | 3 | 266.4 | 9.4978 | 9.4978 | 3.5652 | 3.5653
750 | feeder2_line55 | 1 | 99 | 0.34188 | 0.34188 | 0.34533 | 0.34533
750 | feeder2_line55 | 2 | 99 | 4.9412e-08 | 7.3282e-07 | 4.9911e-08 | 7.4023e-07
750 | feeder2_line55 | 3 | 99 | 4.9816e-08 | 7.3337e-07 | 5.0319e-08 | 7.4078e-07
750 | feeder2_line56 | 1 | 354.6 | 61.7985 | 61.8095 | 17.4277 | 17.4308
750 | feeder2_line56 | 2 | 354.6 | 76.8224 | 76.8083 | 21.6645 | 21.6606
750 | feeder2_line56 | 3 | 354.6 | 88.3938 | 88.3964 | 24.9277 | 24.9285
750 | feeder2_line57 | 1 | 99 | 7.5704e-07 | 1.5383e-06 | 7.6469e-07 | 1.5538e-06
750 | feeder2_line57 | 2 | 99 | 7.4012e-07 | 1.5482e-06 | 7.4759e-07 | 1.5638e-06
750 | feeder2_line57 | 3 | 99 | 9.4979 | 9.4978 | 9.5938 | 9.5938
750 | feeder2_line58 | 1 | 266.4 | 0.68439 | 0.68443 | 0.2569 | 0.25692
750 | feeder2_line58 | 2 | 266.4 | 1.8997e-05 | 2.6914e-06 | 7.1311e-06 | 1.0103e-06
750 | feeder2_line58 | 3 | 266.4 | 1.9015e-05 | 2.6917e-06 | 7.1377e-06 | 1.0104e-06
750 | feeder2_line59 | 1 | 99 | 5.0469e-08 | 5.3473e-07 | 5.0978e-08 | 5.4013e-07
750 | feeder2_line59 | 2 | 99 | 4.9341e-08 | 5.3814e-07 | 4.984e-08 | 5.4358e-07
750 | feeder2_line59 | 3 | 99 | 8.611 | 8.6109 | 8.6979 | 8.6979
750 | feeder2_line60 | 1 | 99 | 2.9811e-07 | 8.0814e-07 | 3.0112e-07 | 8.163e-07
750 | feeder2_line60 | 2 | 99 | 2.9968e-07 | 8.133e-07 | 3.0271e-07 | 8.2152e-07
750 | feeder2_line60 | 3 | 99 | 0.96293 | 0.96296 | 0.97266 | 0.97268
750 | feeder2_line61 | 1 | 266.4 | 11.3691 | 11.369 | 4.2677 | 4.2676
750 | feeder2_line61 | 2 | 266.4 | 2.5254 | 2.5255 | 0.94798 | 0.94801
750 | feeder2_line61 | 3 | 266.4 | 1.5637 | 1.5639 | 0.58697 | 0.58705
750 | feeder2_line62 | 1 | 354.6 | 73.0372 | 73.048 | 20.5971 | 20.6001
750 | feeder2_line62 | 2 | 354.6 | 79.1275 | 79.1135 | 22.3146 | 22.3106
750 | feeder2_line62 | 3 | 354.6 | 89.7071 | 89.7099 | 25.2981 | 25.2989
750 | feeder2_line63 | 1 | 99 | 0.089624 | 0.089634 | 0.090529 | 0.090539
750 | feeder2_line63 | 2 | 99 | 5.747e-07 | 1.2228e-06 | 5.8051e-07 | 1.2352e-06
750 | feeder2_line63 | 3 | 99 | 5.7468e-07 | 1.2228e-06 | 5.8048e-07 | 1.2351e-06
750 | feeder2_line64 | 1 | 99 | 0.59478 | 0.59479 | 0.60079 | 0.6008
750 | feeder2_line64 | 2 | 99 | 1.6175e-11 | 3.2212e-07 | 1.6338e-11 | 3.2537e-07
750 | feeder2_line64 | 3 | 99 | 6.9084e-12 | 3.2211e-07 | 6.9782e-12 | 3.2536e-07
750 | feeder2_line65 | 1 | 99 | 5.0742e-08 | 6.3962e-07 | 5.1254e-08 | 6.4608e-07
750 | feeder2_line65 | 2 | 99 | 0.72023 | 0.72024 | 0.72751 | 0.72751
750 | feeder2_line65 | 3 | 99 | 4.9839e-08 | 6.4485e-07 | 5.0343e-08 | 6.5136e-07
750 | feeder2_line66 | 1 | 354.6 | 73.0371 | 73.048 | 20.597 | 20.6001
750 | feeder2_line66 | 2 | 354.6 | 79.8382 | 79.8243 | 22.515 | 22.5111
750 | feeder2_line66 | 3 | 354.6 | 89.707 | 89.7099 | 25.2981 | 25.2989
750 | feeder2_line67 | 1 | 99 | 2.5348e-08 | 3.6145e-07 | 2.5604e-08 | 3.651e-07
750 | feeder2_line67 | 2 | 99 | 2.471e-08 | 3.6402e-07 | 2.4959e-08 | 3.677e-07
750 | feeder2_line67 | 3 | 99 | 0.29391 | 0.29392 | 0.29688 | 0.29689
750 | feeder2_line68 | 1 | 266.4 | 11.3692 | 11.369 | 4.2677 | 4.2676
750 | feeder2_line68 | 2 | 266.4 | 2.5255 | 2.5255 | 0.948 | 0.94801
750 | feeder2_line68 | 3 | 266.4 | 1.3131 | 1.3132 | 0.49289 | 0.49295
750 | feeder2_line69 | 1 | 99 | 0.66319 | 0.66329 | 0.66988 | 0.66999
750 | feeder2_line69 | 2 | 99 | 2.5604e-06 | 6.6891e-07 | 2.5862e-06 | 6.7567e-07
750 | feeder2_line69 | 3 | 99 | 2.5606e-06 | 6.6959e-07 | 2.5865e-06 | 6.7635e-07
750 | feeder2_line70 | 1 | 354.6 | 73.7002 | 73.7113 | 20.784 | 20.7872
750 | feeder2_line70 | 2 | 354.6 | 79.8382 | 79.8243 | 22.515 | 22.5111
750 | feeder2_line70 | 3 | 354.6 | 89.7069 | 89.7099 | 25.2981 | 25.2989
750 | feeder2_line71 | 1 | 99 | 5.0769e-08 | 7.1375e-07 | 5.1282e-08 | 7.2096e-07
750 | feeder2_line71 | 2 | 99 | 1.2829 | 1.2829 | 1.2959 | 1.2958
750 | feeder2_line71 | 3 | 99 | 4.9852e-08 | 7.1971e-07 | 5.0356e-08 | 7.2698e-07
750 | feeder2_line72 | 1 | 354.6 | 73.7003 | 73.7113 | 20.7841 | 20.7872
750 | feeder2_line72 | 2 | 354.6 | 80.4652 | 80.4512 | 22.6918 | 22.6879
750 | feeder2_line72 | 3 | 354.6 | 89.707 | 89.7099 | 25.2981 | 25.2989
750 | feeder2_line73 | 1 | 99 | 5.9707e-07 | 1.5301e-06 | 6.031e-07 | 1.5455e-06
750 | feeder2_line73 | 2 | 99 | 1.2153 | 1.2153 | 1.2276 | 1.2276
750 | feeder2_line73 | 3 | 99 | 6.0133e-07 | 1.5425e-06 | 6.0741e-07 | 1.5581e-06
750 | feeder2_line74 | 1 | 99 | 5.0701e-08 | 4.5635e-07 | 5.1213e-08 | 4.6096e-07
750 | feeder2_line74 | 2 | 99 | 1.3131 | 1.313 | 1.3263 | 1.3263
750 | feeder2_line74 | 3 | 99 | 4.9819e-08 | 4.6007e-07 | 5.0322e-08 | 4.6472e-07
750 | feeder2_line75 | 1 | 266.4 | 11.3692 | 11.369 | 4.2677 | 4.2676
750 | feeder2_line75 | 2 | 266.4 | 0.08936 | 0.089387 | 0.033544 | 0.033554
750 | feeder2_line75 | 3 | 266.4 | 1.3132 | 1.3132 | 0.49293 | 0.49295
750 | feeder2_line76 | 1 | 99 | 11.3693 | 11.369 | 11.4841 | 11.4838
750 | feeder2_line76 | 2 | 99 | 8.5152e-07 | 1.5898e-06 | 8.6012e-07 | 1.6058e-06
750 | feeder2_line76 | 3 | 99 | 8.5217e-07 | 1.5912e-06 | 8.6077e-07 | 1.6072e-06
750 | feeder2_line77 | 1 | 99 | 2.5356e-08 | 5.7344e-07 | 2.5612e-08 | 5.7923e-07
750 | feeder2_line77 | 2 | 99 | 2.4702e-08 | 5.7765e-07 | 2.4952e-08 | 5.8349e-07
750 | feeder2_line77 | 3 | 99 | 1.3132 | 1.3132 | 1.3265 | 1.3265
750 | feeder2_line78 | 1 | 266.4 | 1.1383e-11 | 9.5166e-07 | 4.2728e-12 | 3.5723e-07
750 | feeder2_line78 | 2 | 266.4 | 0.089393 | 0.089386 | 0.033556 | 0.033553
750 | feeder2_line78 | 3 | 266.4 | 3.4007e-12 | 9.5865e-07 | 1.2765e-12 | 3.5985e-07
750 | feeder2_line79 | 1 | 354.6 | 10.1691 | 10.1685 | 2.8678 | 2.8676
750 | feeder2_line79 | 2 | 354.6 | 2.7457 | 2.7454 | 0.7743 | 0.77422
750 | feeder2_line79 | 3 | 354.6 | 6.495 | 6.4949 | 1.8316 | 1.8316
750 | feeder2_line80 | 1 | 354.6 | 83.7895 | 83.7997 | 23.6293 | 23.6322
750 | feeder2_line80 | 2 | 354.6 | 82.1456 | 82.1309 | 23.1657 | 23.1616
750 | feeder2_line80 | 3 | 354.6 | 94.2203 | 94.2228 | 26.5709 | 26.5716
750 | feeder2_line81 | 1 | 354.6 | 83.7895 | 83.7997 | 23.6293 | 23.6322
750 | feeder2_line81 | 2 | 354.6 | 82.1456 | 82.1309 | 23.1657 | 23.1616
750 | feeder2_line81 | 3 | 354.6 | 95.1508 | 95.1533 | 26.8333 | 26.834
750 | feeder2_line82 | 1 | 354.6 | 3.2911e-11 | 7.3274e-07 | 9.2812e-12 | 2.0664e-07
750 | feeder2_line82 | 2 | 354.6 | 2.9208e-11 | 7.3746e-07 | 8.237e-12 | 2.0797e-07
750 | feeder2_line82 | 3 | 354.6 | 0.93648 | 0.93648 | 0.26409 | 0.2641
750 | feeder2_line83 | 1 | 354.6 | 83.7897 | 83.7997 | 23.6294 | 23.6322
750 | feeder2_line83 | 2 | 354.6 | 82.6658 | 82.6509 | 23.3124 | 23.3082
750 | feeder2_line83 | 3 | 354.6 | 95.151 | 95.1533 | 26.8333 | 26.834
750 | feeder2_line84 | 1 | 354.6 | 1.135e-11 | 1.2951e-06 | 3.2007e-12 | 3.6524e-07
750 | feeder2_line84 | 2 | 354.6 | 0.97754 | 0.9775 | 0.27568 | 0.27566
750 | feeder2_line84 | 3 | 354.6 | 4.7789e-12 | 1.3055e-06 | 1.3477e-12 | 3.6816e-07
750 | feeder2_line85 | 1 | 99 | 1.3247 | 1.3247 | 1.3381 | 1.3381
750 | feeder2_line85 | 2 | 99 | 4.9491e-08 | 4.6547e-07 | 4.9991e-08 | 4.7017e-07
750 | feeder2_line85 | 3 | 99 | 4.9879e-08 | 4.6608e-07 | 5.0382e-08 | 4.7079e-07
750 | feeder2_line86 | 1 | 354.6 | 84.4827 | 84.4925 | 23.8248 | 23.8276
750 | feeder2_line86 | 2 | 354.6 | 82.6659 | 82.6509 | 23.3124 | 23.3082
750 | feeder2_line86 | 3 | 354.6 | 95.1511 | 95.1533 | 26.8334 | 26.834
750 | feeder2_line87 | 1 | 354.6 | 84.4829 | 84.4925 | 23.8248 | 23.8276
750 | feeder2_line87 | 2 | 354.6 | 84.1387 | 84.1234 | 23.7278 | 23.7234
750 | feeder2_line87 | 3 | 354.6 | 95.2325 | 95.2345 | 26.8563 | 26.8569
750 | feeder2_line88 | 1 | 354.6 | 0.0001116 | 3.356e-06 | 3.1473e-05 | 9.4641e-07
750 | feeder2_line88 | 2 | 354.6 | 1.8839 | 1.8836 | 0.53127 | 0.53119
750 | feeder2_line88 | 3 | 354.6 | 0.081353 | 0.081215 | 0.022942 | 0.022903
750 | feeder2_line89 | 1 | 354.6 | 84.4806 | 84.4925 | 23.8242 | 23.8276
750 | feeder2_line89 | 2 | 354.6 | 94.7188 | 94.706 | 26.7114 | 26.7078
750 | feeder2_line89 | 3 | 354.6 | 95.2302 | 95.2345 | 26.8557 | 26.8569
750 | feeder2_line90 | 1 | 354.6 | 0.0007193 | 2.0254e-06 | 0.00020285 | 5.7117e-07
750 | feeder2_line90 | 2 | 354.6 | 10.727 | 10.7277 | 3.0251 | 3.0253
750 | feeder2_line90 | 3 | 354.6 | 0.00072922 | 2.0436e-06 | 0.00020565 | 5.7631e-07
750 | feeder2_line91 | 1 | 354.6 | 84.4805 | 84.4925 | 23.8242 | 23.8276
750 | feeder2_line91 | 2 | 354.6 | 94.7187 | 94.706 | 26.7114 | 26.7078
750 | feeder2_line91 | 3 | 354.6 | 95.7333 | 95.7378 | 26.9975 | 26.9988
750 | feeder2_line92 | 1 | 354.6 | 6.5716e-12 | 1.0226e-06 | 1.8533e-12 | 2.8837e-07
750 | feeder2_line92 | 2 | 354.6 | 1.8929e-11 | 1.0293e-06 | 5.3381e-12 | 2.9026e-07
750 | feeder2_line92 | 3 | 354.6 | 0.96516 | 0.96519 | 0.27218 | 0.27219
750 | feeder2_line93 | 1 | 99 | 2.5453e-08 | 3.4114e-07 | 2.571e-08 | 3.4459e-07
750 | feeder2_line93 | 2 | 99 | 0.97774 | 0.97769 | 0.98761 | 0.98757
750 | feeder2_line93 | 3 | 99 | 2.4949e-08 | 3.4419e-07 | 2.5201e-08 | 3.4767e-07
750 | feeder2_line94 | 1 | 354.6 | 2.5451e-06 | 1.6618e-06 | 7.1774e-07 | 4.6864e-07
750 | feeder2_line94 | 2 | 354.6 | 10.0828 | 10.0831 | 2.8434 | 2.8435
750 | feeder2_line94 | 3 | 354.6 | 2.4942e-06 | 1.6755e-06 | 7.034e-07 | 4.7249e-07
750 | feeder2_line95 | 1 | 99 | 3.5507e-06 | 2.6023e-06 | 3.5866e-06 | 2.6286e-06
750 | feeder2_line95 | 2 | 99 | 1.8838 | 1.8836 | 1.9029 | 1.9026
750 | feeder2_line95 | 3 | 99 | 3.5965e-06 | 2.6253e-06 | 3.6328e-06 | 2.6518e-06
750 | feeder2_line96 | 1 | 354.6 | 0.00012067 | 6.2049e-07 | 3.4029e-05 | 1.7498e-07
750 | feeder2_line96 | 2 | 354.6 | 0.00012177 | 6.2484e-07 | 3.434e-05 | 1.7621e-07
750 | feeder2_line96 | 3 | 354.6 | 0.081339 | 0.081215 | 0.022938 | 0.022903
750 | feeder2_line97 | 1 | 354.6 | 85.6323 | 85.6443 | 24.149 | 24.1524
750 | feeder2_line97 | 2 | 354.6 | 94.7189 | 94.706 | 26.7115 | 26.7078
750 | feeder2_line97 | 3 | 354.6 | 95.7335 | 95.7378 | 26.9976 | 26.9988
750 | feeder2_line98 | 1 | 354.6 | 1.1548 | 1.1532 | 0.32566 | 0.32522
750 | feeder2_line98 | 2 | 354.6 | 0.001727 | 6.2411e-07 | 0.00048704 | 1.76e-07
750 | feeder2_line98 | 3 | 354.6 | 0.0017064 | 6.2592e-07 | 0.00048121 | 1.7651e-07
750 | feeder2_line99 | 1 | 99 | 2.5445e-08 | 4.4596e-07 | 2.5702e-08 | 4.5046e-07
750 | feeder2_line99 | 2 | 99 | 2.4754e-08 | 4.4925e-07 | 2.5004e-08 | 4.5379e-07
750 | feeder2_line99 | 3 | 99 | 0.081247 | 0.081215 | 0.082068 | 0.082036
750 | feeder2_line100 | 1 | 99 | 1.1531 | 1.1532 | 1.1647 | 1.1649
750 | feeder2_line100 | 2 | 99 | 2.4767e-08 | 6.1707e-07 | 2.5018e-08 | 6.2331e-07
750 | feeder2_line100 | 3 | 99 | 2.4955e-08 | 6.1801e-07 | 2.5207e-08 | 6.2425e-07
750 | feeder2_line101 | 1 | 354.6 | 9.9354 | 9.9347 | 2.8019 | 2.8017
750 | feeder2_line101 | 2 | 354.6 | 2.7457 | 2.7454 | 0.7743 | 0.77422
750 | feeder2_line101 | 3 | 354.6 | 6.495 | 6.4949 | 1.8316 | 1.8316
750 | feeder2_line102 | 1 | 99 | 0.23845 | 0.23851 | 0.24085 | 0.24092
750 | feeder2_line102 | 2 | 99 | 2.358e-06 | 8.8201e-07 | 2.3819e-06 | 8.9092e-07
750 | feeder2_line102 | 3 | 99 | 2.3454e-06 | 8.8295e-07 | 2.3691e-06 | 8.9187e-07
750 | feeder2_line103 | 1 | 99 | 5.4692e-07 | 8.012e-07 | 5.5244e-07 | 8.0929e-07
750 | feeder2_line103 | 2 | 99 | 0.15617 | 0.15616 | 0.15775 | 0.15774
750 | feeder2_line103 | 3 | 99 | 5.5242e-07 | 8.0815e-07 | 5.58e-07 | 8.1632e-07
750 | feeder2_line104 | 1 | 354.6 | 9.9353 | 9.9347 | 2.8018 | 2.8017
750 | feeder2_line104 | 2 | 354.6 | 2.6682 | 2.6679 | 0.75244 | 0.75238
750 | feeder2_line104 | 3 | 354.6 | 6.495 | 6.4949 | 1.8316 | 1.8316
750 | feeder2_line105 | 1 | 99 | 2.5311e-06 | 7.3719e-07 | 2.5567e-06 | 7.4463e-07
750 | feeder2_line105 | 2 | 99 | 2.5627e-06 | 7.4286e-07 | 2.5886e-06 | 7.5036e-07
750 | feeder2_line105 | 3 | 99 | 1.2718 | 1.2718 | 1.2846 | 1.2846
750 | feeder2_line106 | 1 | 354.6 | 9.9352 | 9.9347 | 2.8018 | 2.8017
750 | feeder2_line106 | 2 | 354.6 | 2.6681 | 2.6679 | 0.75244 | 0.75238
750 | feeder2_line106 | 3 | 354.6 | 5.233 | 5.2329 | 1.4757 | 1.4757
750 | feeder2_line107 | 1 | 99 | 3.2426e-07 | 8.9828e-07 | 3.2753e-07 | 9.0736e-07
750 | feeder2_line107 | 2 | 99 | 1.1941 | 1.194 | 1.2061 | 1.2061
750 | feeder2_line107 | 3 | 99 | 3.2606e-07 | 9.0615e-07 | 3.2935e-07 | 9.153e-07
750 | feeder2_line108 | 1 | 354.6 | 9.9352 | 9.9347 | 2.8018 | 2.8017
750 | feeder2_line108 | 2 | 354.6 | 1.482 | 1.4818 | 0.41795 | 0.41789
750 | feeder2_line108 | 3 | 354.6 | 5.233 | 5.2329 | 1.4757 | 1.4757
750 | feeder2_line109 | 1 | 354.6 | 86.8846 | 86.8954 | 24.5021 | 24.5052
750 | feeder2_line109 | 2 | 354.6 | 94.7201 | 94.706 | 26.7118 | 26.7078
750 | feeder2_line109 | 3 | 354.6 | 95.7347 | 95.7378 | 26.9979 | 26.9988
750 | feeder2_line110 | 1 | 99 | 1.2557 | 1.255 | 1.2684 | 1.2676
750 | feeder2_line110 | 2 | 99 | 0.00081036 | 9.1376e-07 | 0.00081855 | 9.2299e-07
750 | feeder2_line110 | 3 | 99 | 0.00081075 | 9.1483e-07 | 0.00081894 | 9.2407e-07
750 | feeder2_line111 | 1 | 99 | 2.5433e-08 | 3.8088e-07 | 2.569e-08 | 3.8473e-07
750 | feeder2_line111 | 2 | 99 | 0.045305 | 0.045265 | 0.045762 | 0.045722
750 | feeder2_line111 | 3 | 99 | 2.4944e-08 | 3.8425e-07 | 2.5196e-08 | 3.8813e-07
750 | feeder2_line112 | 1 | 99 | 3.2457e-07 | 9.1528e-07 | 3.2785e-07 | 9.2452e-07
750 | feeder2_line112 | 2 | 99 | 1.8472 | 1.847 | 1.8658 | 1.8656
750 | feeder2_line112 | 3 | 99 | 3.2639e-07 | 9.2336e-07 | 3.2969e-07 | 9.3269e-07
750 | feeder2_line113 | 1 | 99 | 0.097927 | 0.097935 | 0.098916 | 0.098924
750 | feeder2_line113 | 2 | 99 | 3.2607e-07 | 9.1016e-07 | 3.2936e-07 | 9.1935e-07
750 | feeder2_line113 | 3 | 99 | 3.2678e-07 | 9.1154e-07 | 3.3008e-07 | 9.2074e-07
750 | feeder2_line114 | 1 | 99 | 0.15699 | 0.157 | 0.15858 | 0.15858
750 | feeder2_line114 | 2 | 99 | 2.4728e-08 | 4.3859e-07 | 2.4977e-08 | 4.4302e-07
750 | feeder2_line114 | 3 | 99 | 2.4936e-08 | 4.3906e-07 | 2.5188e-08 | 4.4349e-07
750 | feeder2_line115 | 1 | 99 | 2.5417e-08 | 5.6052e-07 | 2.5674e-08 | 5.6618e-07
750 | feeder2_line115 | 2 | 99 | 1.3848 | 1.3847 | 1.3987 | 1.3987
750 | feeder2_line115 | 3 | 99 | 2.4936e-08 | 5.6546e-07 | 2.5188e-08 | 5.7117e-07
750 | feeder2_line116 | 1 | 354.6 | 9.9352 | 9.9347 | 2.8018 | 2.8017
750 | feeder2_line116 | 2 | 354.6 | 0.15926 | 0.15899 | 0.044913 | 0.044837
750 | feeder2_line116 | 3 | 354.6 | 5.233 | 5.2329 | 1.4757 | 1.4757
750 | feeder2_line117 | 1 | 99 | 5.1001e-08 | 6.4142e-07 | 5.1516e-08 | 6.479e-07
750 | feeder2_line117 | 2 | 99 | 0.071582 | 0.071522 | 0.072305 | 0.072244
750 | feeder2_line117 | 3 | 99 | 4.9947e-08 | 6.4738e-07 | 5.0452e-08 | 6.5392e-07
750 | feeder2_line118 | 1 | 354.6 | 86.8846 | 86.8954 | 24.5022 | 24.5052
750 | feeder2_line118 | 2 | 354.6 | 94.7917 | 94.7775 | 26.732 | 26.728
750 | feeder2_line118 | 3 | 354.6 | 95.7347 | 95.7378 | 26.9979 | 26.9988
750 | feeder2_line119 | 1 | 99 | 2.5427e-08 | 6.0306e-07 | 2.5684e-08 | 6.0915e-07
750 | feeder2_line119 | 2 | 99 | 2.4691e-08 | 6.0796e-07 | 2.4941e-08 | 6.141e-07
750 | feeder2_line119 | 3 | 99 | 1.4136 | 1.4136 | 1.4278 | 1.4279
750 | feeder2_line120 | 1 | 354.6 | 9.9352 | 9.9347 | 2.8018 | 2.8017
750 | feeder2_line120 | 2 | 354.6 | 0.15926 | 0.15899 | 0.044914 | 0.044837
750 | feeder2_line120 | 3 | 354.6 | 3.8917 | 3.8916 | 1.0975 | 1.0975
750 | feeder2_line121 | 1 | 99 | 3.2417e-07 | 9.3373e-07 | 3.2744e-07 | 9.4317e-07
750 | feeder2_line121 | 2 | 99 | 0.070644 | 0.070639 | 0.071357 | 0.071353
750 | feeder2_line121 | 3 | 99 | 3.2603e-07 | 9.4217e-07 | 3.2932e-07 | 9.5168e-07
750 | feeder2_line122 | 1 | 354.6 | 9.9352 | 9.9347 | 2.8018 | 2.8017
750 | feeder2_line122 | 2 | 354.6 | 0.088768 | 0.088513 | 0.025033 | 0.024961
750 | feeder2_line122 | 3 | 354.6 | 3.8917 | 3.8916 | 1.0975 | 1.0975
750 | feeder2_line123 | 1 | 99 | 5.72e-07 | 9.675e-07 | 5.7778e-07 | 9.7727e-07
750 | feeder2_line123 | 2 | 99 | 5.7689e-07 | 9.7563e-07 | 5.8272e-07 | 9.8549e-07
750 | feeder2_line123 | 3 | 99 | 0.076546 | 0.076549 | 0.07732 | 0.077322
750 | feeder2_line124 | 1 | 354.6 | 9.9351 | 9.9347 | 2.8018 | 2.8017
750 | feeder2_line124 | 2 | 354.6 | 0.088672 | 0.088513 | 0.025006 | 0.024961
750 | feeder2_line124 | 3 | 354.6 | 3.829 | 3.8289 | 1.0798 | 1.0798
750 | feeder2_line125 | 1 | 99 | 5.7198e-07 | 8.9935e-07 | 5.7776e-07 | 9.0844e-07
750 | feeder2_line125 | 2 | 99 | 5.769e-07 | 9.0696e-07 | 5.8273e-07 | 9.1612e-07
750 | feeder2_line125 | 3 | 99 | 1.1447 | 1.1446 | 1.1562 | 1.1562
750 | feeder2_line126 | 1 | 354.6 | 9.9353 | 9.9347 | 2.8018 | 2.8017
750 | feeder2_line126 | 2 | 354.6 | 0.088829 | 0.088513 | 0.025051 | 0.024961
750 | feeder2_line126 | 3 | 354.6 | 2.9575 | 2.9573 | 0.83405 | 0.83398
750 | feeder2_line127 | 1 | 99 | 5.7194e-07 | 1.0766e-06 | 5.7772e-07 | 1.0875e-06
750 | feeder2_line127 | 2 | 99 | 5.7691e-07 | 1.0858e-06 | 5.8274e-07 | 1.0968e-06
750 | feeder2_line127 | 3 | 99 | 0.076699 | 0.076702 | 0.077474 | 0.077477
750 | feeder2_line128 | 1 | 354.6 | 9.9352 | 9.9347 | 2.8018 | 2.8017
750 | feeder2_line128 | 2 | 354.6 | 0.088743 | 0.088512 | 0.025026 | 0.024961
750 | feeder2_line128 | 3 | 354.6 | 2.9081 | 2.9079 | 0.82011 | 0.82004
750 | feeder2_line129 | 1 | 99 | 5.4648e-07 | 8.7293e-07 | 5.52e-07 | 8.8175e-07
750 | feeder2_line129 | 2 | 99 | 0.088525 | 0.088512 | 0.089419 | 0.089406
750 | feeder2_line129 | 3 | 99 | 5.5233e-07 | 8.8099e-07 | 5.5791e-07 | 8.8989e-07
750 | feeder2_line130 | 1 | 354.6 | 9.9352 | 9.9347 | 2.8018 | 2.8017
750 | feeder2_line130 | 2 | 354.6 | 0.00030871 | 4.6582e-06 | 8.7059e-05 | 1.3137e-06
750 | feeder2_line130 | 3 | 354.6 | 2.9081 | 2.9079 | 0.82012 | 0.82004
750 | feeder2_line131 | 1 | 99 | 5.7188e-07 | 9.6744e-07 | 5.7765e-07 | 9.7721e-07
750 | feeder2_line131 | 2 | 99 | 5.7693e-07 | 9.7585e-07 | 5.8276e-07 | 9.857e-07
750 | feeder2_line131 | 3 | 99 | 1.5977 | 1.5977 | 1.6138 | 1.6138
750 | feeder2_line132 | 1 | 354.6 | 9.935 | 9.9347 | 2.8018 | 2.8017
750 | feeder2_line132 | 2 | 354.6 | 0.00012646 | 2.9285e-06 | 3.5664e-05 | 8.2587e-07
750 | feeder2_line132 | 3 | 354.6 | 1.33 | 1.3299 | 0.37508 | 0.37504
750 | feeder2_line133 | 1 | 99 | 9.935 | 9.9347 | 10.0353 | 10.035
750 | feeder2_line133 | 2 | 99 | 3.0079e-07 | 9.8363e-07 | 3.0383e-07 | 9.9356e-07
750 | feeder2_line133 | 3 | 99 | 3.0108e-07 | 9.8422e-07 | 3.0413e-07 | 9.9416e-07
750 | feeder2_line134 | 1 | 354.6 | 1.1522e-11 | 1.7793e-06 | 3.2493e-12 | 5.0179e-07
750 | feeder2_line134 | 2 | 354.6 | 8.0347e-12 | 1.7931e-06 | 2.2658e-12 | 5.0566e-07
750 | feeder2_line134 | 3 | 354.6 | 1.3299 | 1.3299 | 0.37504 | 0.37504
750 | feeder2_line135 | 1 | 99 | 1.2786 | 1.2786 | 1.2915 | 1.2915
750 | feeder2_line135 | 2 | 99 | 4.9584e-08 | 5.8931e-07 | 5.0085e-08 | 5.9526e-07
750 | feeder2_line135 | 3 | 99 | 4.997e-08 | 5.9019e-07 | 5.0475e-08 | 5.9615e-07
750 | feeder2_line136 | 1 | 354.6 | 87.5892 | 87.6 | 24.7008 | 24.7039
750 | feeder2_line136 | 2 | 354.6 | 94.7917 | 94.7775 | 26.732 | 26.728
750 | feeder2_line136 | 3 | 354.6 | 95.7347 | 95.7378 | 26.9979 | 26.9988
750 | feeder2_line137 | 1 | 99 | 10.2492 | 10.2489 | 10.3527 | 10.3524
750 | feeder2_line137 | 2 | 99 | 8.5549e-07 | 1.5873e-06 | 8.6413e-07 | 1.6034e-06
750 | feeder2_line137 | 3 | 99 | 8.5668e-07 | 1.5897e-06 | 8.6533e-07 | 1.6058e-06
750 | feeder2_line138 | 1 | 354.6 | 97.6891 | 97.6995 | 27.5491 | 27.552
750 | feeder2_line138 | 2 | 354.6 | 94.7917 | 94.7775 | 26.732 | 26.728
750 | feeder2_line138 | 3 | 354.6 | 95.7348 | 95.7378 | 26.998 | 26.9988
750 | feeder2_line139 | 1 | 99 | 5.106e-08 | 4.9077e-07 | 5.1576e-08 | 4.9573e-07
750 | feeder2_line139 | 2 | 99 | 4.9599e-08 | 4.9467e-07 | 5.01e-08 | 4.9966e-07
750 | feeder2_line139 | 3 | 99 | 1.6587 | 1.6593 | 1.6755 | 1.6761
750 | feeder2_line140 | 1 | 354.6 | 97.6892 | 97.6995 | 27.5491 | 27.552
750 | feeder2_line140 | 2 | 354.6 | 94.7918 | 94.7775 | 26.732 | 26.728
750 | feeder2_line140 | 3 | 354.6 | 96.7163 | 96.7194 | 27.2748 | 27.2756
750 | feeder2_line141 | 1 | 99 | 2.5135e-06 | 4.8554e-07 | 2.5389e-06 | 4.9044e-07
750 | feeder2_line141 | 2 | 99 | 1.2532 | 1.2532 | 1.2659 | 1.2659
750 | feeder2_line141 | 3 | 99 | 2.5485e-06 | 4.9012e-07 | 2.5743e-06 | 4.9507e-07
750 | feeder2_line142 | 1 | 354.6 | 97.689 | 97.6995 | 27.5491 | 27.552
750 | feeder2_line142 | 2 | 354.6 | 96.0428 | 96.0287 | 27.0848 | 27.0808
750 | feeder2_line142 | 3 | 354.6 | 96.7162 | 96.7194 | 27.2747 | 27.2756
750 | feeder2_line143 | 1 | 99 | 8.486e-07 | 1.7254e-06 | 8.5717e-07 | 1.7428e-06
750 | feeder2_line143 | 2 | 99 | 1.1954 | 1.1954 | 1.2075 | 1.2074
750 | feeder2_line143 | 3 | 99 | 8.5711e-07 | 1.7417e-06 | 8.6577e-07 | 1.7593e-06
750 | feeder2_line144 | 1 | 354.6 | 97.6888 | 97.6995 | 27.549 | 27.552
750 | feeder2_line144 | 2 | 354.6 | 96.7031 | 96.689 | 27.271 | 27.2671
750 | feeder2_line144 | 3 | 354.6 | 96.716 | 96.7194 | 27.2747 | 27.2756
750 | feeder2_line145 | 1 | 99 | 2.5541e-08 | 4.8384e-07 | 2.5799e-08 | 4.8873e-07
750 | feeder2_line145 | 2 | 99 | 0.93448 | 0.93443 | 0.94391 | 0.94387
750 | feeder2_line145 | 3 | 99 | 2.5003e-08 | 4.884e-07 | 2.5256e-08 | 4.9334e-07
750 | feeder2_line146 | 1 | 354.6 | 97.6887 | 97.6995 | 27.549 | 27.552
750 | feeder2_line146 | 2 | 354.6 | 97.6353 | 97.6213 | 27.5339 | 27.53
750 | feeder2_line146 | 3 | 354.6 | 96.7158 | 96.7194 | 27.2746 | 27.2756
750 | feeder2_line147 | 1 | 99 | 1.1563 | 1.1563 | 1.168 | 1.168
750 | feeder2_line147 | 2 | 99 | 1.158e-06 | 2.2495e-06 | 1.1697e-06 | 2.2722e-06
750 | feeder2_line147 | 3 | 99 | 1.1597e-06 | 2.2529e-06 | 1.1714e-06 | 2.2756e-06
750 | feeder2_line148 | 1 | 99 | 0.085303 | 0.085318 | 0.086164 | 0.08618
750 | feeder2_line148 | 2 | 99 | 6.038e-07 | 1.5073e-06 | 6.099e-07 | 1.5226e-06
750 | feeder2_line148 | 3 | 99 | 6.0484e-07 | 1.5096e-06 | 6.1095e-07 | 1.5248e-06
750 | feeder2_line149 | 1 | 354.6 | 98.9293 | 98.9399 | 27.8988 | 27.9018
750 | feeder2_line149 | 2 | 354.6 | 97.6354 | 97.6213 | 27.534 | 27.53
750 | feeder2_line149 | 3 | 354.6 | 96.716 | 96.7194 | 27.2747 | 27.2756
750 | feeder2_line150 | 1 | 354.6 | 98.9294 | 98.9399 | 27.8989 | 27.9018
750 | feeder2_line150 | 2 | 354.6 | 97.8777 | 97.8634 | 27.6023 | 27.5983
750 | feeder2_line150 | 3 | 354.6 | 96.7161 | 96.7194 | 27.2747 | 27.2756
750 | feeder2_line151 | 1 | 99 | 9.7079e-06 | 1.7767e-06 | 9.8059e-06 | 1.7946e-06
750 | feeder2_line151 | 2 | 99 | 0.24394 | 0.24393 | 0.2464 | 0.24639
750 | feeder2_line151 | 3 | 99 | 9.8485e-06 | 1.7934e-06 | 9.948e-06 | 1.8115e-06
750 | feeder2_line152 | 1 | 354.6 | 1.9628e-11 | 1.185e-06 | 5.5354e-12 | 3.3418e-07
750 | feeder2_line152 | 2 | 354.6 | 1.9747e-11 | 1.1933e-06 | 5.5688e-12 | 3.3652e-07
750 | feeder2_line152 | 3 | 354.6 | 1.1898 | 1.1897 | 0.33552 | 0.33551
750 | feeder2_line153 | 1 | 99 | 0.071078 | 0.071084 | 0.071796 | 0.071802
750 | feeder2_line153 | 2 | 99 | 4.9663e-08 | 5.9724e-07 | 5.0164e-08 | 6.0328e-07
750 | feeder2_line153 | 3 | 99 | 5.0063e-08 | 5.981e-07 | 5.0568e-08 | 6.0414e-07
750 | feeder2_line154 | 1 | 99 | 5.7492e-07 | 8.8172e-07 | 5.8072e-07 | 8.9063e-07
750 | feeder2_line154 | 2 | 99 | 5.7955e-07 | 8.8873e-07 | 5.8541e-07 | 8.977e-07
750 | feeder2_line154 | 3 | 99 | 0.88615 | 0.88617 | 0.8951 | 0.89512
750 | feeder2_line155 | 1 | 99 | 99 | 99.0107 | 100 | 100.0108
750 | feeder2_line155 | 2 | 99 | 97.8776 | 97.8634 | 98.8663 | 98.852
750 | feeder2_line155 | 3 | 99 | 97.8351 | 97.8386 | 98.8234 | 98.8269
750 | feeder2_line156 | 1 | 99 | 6.0022e-07 | 1.1602e-06 | 6.0628e-07 | 1.1719e-06
750 | feeder2_line156 | 2 | 99 | 0.1559 | 0.15589 | 0.15748 | 0.15747
750 | feeder2_line156 | 3 | 99 | 6.0514e-07 | 1.1711e-06 | 6.1125e-07 | 1.1829e-06
750 | feeder2_line157 | 1 | 99 | 2.5554e-08 | 2.5185e-07 | 2.5812e-08 | 2.544e-07
750 | feeder2_line157 | 2 | 99 | 0.088967 | 0.088957 | 0.089866 | 0.089855
750 | feeder2_line157 | 3 | 99 | 2.5019e-08 | 2.5423e-07 | 2.5272e-08 | 2.568e-07
780 | feeder2_line1 | 1 | 354.6 | 59.7558 | 59.7504 | 16.8516 | 16.8501
780 | feeder2_line1 | 2 | 354.6 | 66.3459 | 66.3592 | 18.7101 | 18.7138
780 | feeder2_line1 | 3 | 354.6 | 63.2703 | 63.2609 | 17.8427 | 17.8401
780 | feeder2_line2 | 1 | 354.6 | 59.7869 | 59.7813 | 16.8604 | 16.8588
780 | feeder2_line2 | 2 | 354.6 | 66.346 | 66.3592 | 18.7101 | 18.7138
780 | feeder2_line2 | 3 | 354.6 | 63.2704 | 63.2609 | 17.8428 | 17.8401
780 | feeder2_line3 | 1 | 80.1 | 0.069575 | 0.06956 | 0.08686 | 0.086841
780 | feeder2_line3 | 2 | 80.1 | 5.6851e-07 | 1.0506e-06 | 7.0975e-07 | 1.3116e-06
780 | feeder2_line3 | 3 | 80.1 | 5.6973e-07 | 1.0528e-06 | 7.1128e-07 | 1.3144e-06
780 | feeder2_line4 | 1 | 354.6 | 59.787 | 59.7813 | 16.8604 | 16.8588
780 | feeder2_line4 | 2 | 354.6 | 67.1651 | 67.1812 | 18.9411 | 18.9456
780 | feeder2_line4 | 3 | 354.6 | 63.2705 | 63.2609 | 17.8428 | 17.8401
780 | feeder2_line5 | 1 | 80.1 | 5.6986e-07 | 9.9437e-07 | 7.1144e-07 | 1.2414e-06
780 | feeder2_line5 | 2 | 80.1 | 10.3905 | 10.3904 | 12.9719 | 12.9718
780 | feeder2_line5 | 3 | 80.1 | 5.697e-07 | 9.941e-07 | 7.1124e-07 | 1.2411e-06
780 | feeder2_line6 | 1 | 80.1 | 5.6987e-07 | 1.1698e-06 | 7.1145e-07 | 1.4604e-06
780 | feeder2_line6 | 2 | 80.1 | 5.6841e-07 | 1.1668e-06 | 7.0963e-07 | 1.4567e-06
780 | feeder2_line6 | 3 | 80.1 | 2.4916 | 2.4916 | 3.1107 | 3.1106
780 | feeder2_line7 | 1 | 354.6 | 59.787 | 59.7813 | 16.8604 | 16.8588
780 | feeder2_line7 | 2 | 354.6 | 67.1651 | 67.1812 | 18.9411 | 18.9456
780 | feeder2_line7 | 3 | 354.6 | 62.5649 | 62.5548 | 17.6438 | 17.6409
780 | feeder2_line8 | 1 | 80.1 | 1.4548 | 1.4548 | 1.8162 | 1.8162
780 | feeder2_line8 | 2 | 80.1 | 5.6828e-07 | 1.1248e-06 | 7.0946e-07 | 1.4042e-06
780 | feeder2_line8 | 3 | 80.1 | 5.6969e-07 | 1.1275e-06 | 7.1122e-07 | 1.4077e-06
780 | feeder2_line9 | 1 | 354.6 | 59.6978 | 59.6923 | 16.8353 | 16.8337
780 | feeder2_line9 | 2 | 354.6 | 67.165 | 67.1812 | 18.9411 | 18.9456
780 | feeder2_line9 | 3 | 354.6 | 62.5648 | 62.5548 | 17.6438 | 17.6409
780 | feeder2_line10 | 1 | 80.1 | 8.4239e-07 | 1.4892e-06 | 1.0517e-06 | 1.8592e-06
780 | feeder2_line10 | 2 | 80.1 | 1.4566 | 1.4566 | 1.8185 | 1.8185
780 | feeder2_line10 | 3 | 80.1 | 8.4218e-07 | 1.4888e-06 | 1.0514e-06 | 1.8587e-06
780 | feeder2_line11 | 1 | 354.6 | 59.6979 | 59.6923 | 16.8353 | 16.8337
780 | feeder2_line11 | 2 | 354.6 | 66.7835 | 66.7999 | 18.8335 | 18.8381
780 | feeder2_line11 | 3 | 354.6 | 62.5649 | 62.5548 | 17.6438 | 17.6409
780 | feeder2_line12 | 1 | 80.1 | 5.451e-07 | 9.878e-07 | 6.8053e-07 | 1.2332e-06
780 | feeder2_line12 | 2 | 80.1 | 5.4338e-07 | 9.85e-07 | 6.7838e-07 | 1.2297e-06
780 | feeder2_line12 | 3 | 80.1 | 0.061978 | 0.061976 | 0.077376 | 0.077374
780 | feeder2_line13 | 1 | 354.6 | 59.698 | 59.6923 | 16.8353 | 16.8337
780 | feeder2_line13 | 2 | 354.6 | 66.7836 | 66.7999 | 18.8335 | 18.8381
780 | feeder2_line13 | 3 | 354.6 | 62.5978 | 62.5876 | 17.6531 | 17.6502
780 | feeder2_line14 | 1 | 80.1 | 1.4665 | 1.4665 | 1.8308 | 1.8309
780 | feeder2_line14 | 2 | 80.1 | 2.9649e-07 | 6.4224e-07 | 3.7015e-07 | 8.018e-07
780 | feeder2_line14 | 3 | 80.1 | 2.9718e-07 | 6.4393e-07 | 3.7101e-07 | 8.0391e-07
780 | feeder2_line15 | 1 | 354.6 | 59.6509 | 59.6453 | 16.822 | 16.8204
780 | feeder2_line15 | 2 | 354.6 | 66.7836 | 66.7999 | 18.8335 | 18.8381
780 | feeder2_line15 | 3 | 354.6 | 62.5978 | 62.5876 | 17.6531 | 17.6502
780 | feeder2_line16 | 1 | 80.1 | 5.6982e-07 | 1.0265e-06 | 7.1138e-07 | 1.2816e-06
780 | feeder2_line16 | 2 | 80.1 | 0.40022 | 0.40022 | 0.49965 | 0.49966
780 | feeder2_line16 | 3 | 80.1 | 5.6965e-07 | 1.0262e-06 | 7.1117e-07 | 1.2812e-06
780 | feeder2_line17 | 1 | 354.6 | 59.6509 | 59.6453 | 16.822 | 16.8204
780 | feeder2_line17 | 2 | 354.6 | 66.8959 | 66.9123 | 18.8652 | 18.8698
780 | feeder2_line17 | 3 | 354.6 | 62.5979 | 62.5877 | 17.6531 | 17.6502
780 | feeder2_line18 | 1 | 80.1 | 5.4507e-07 | 7.3475e-07 | 6.8048e-07 | 9.173e-07
780 | feeder2_line18 | 2 | 80.1 | 5.429e-07 | 7.3215e-07 | 6.7778e-07 | 9.1404e-07
780 | feeder2_line18 | 3 | 80.1 | 8.6689 | 8.6691 | 10.8227 | 10.8229
780 | feeder2_line19 | 1 | 354.6 | 59.6509 | 59.6453 | 16.822 | 16.8204
780 | feeder2_line19 | 2 | 354.6 | 66.8959 | 66.9123 | 18.8652 | 18.8698
780 | feeder2_line19 | 3 | 354.6 | 67.0355 | 67.0241 | 18.9045 | 18.9013
780 | feeder2_line20 | 1 | 99 | 5.4506e-07 | 8.8091e-07 | 5.5057e-07 | 8.898e-07
780 | feeder2_line20 | 2 | 99 | 5.4276e-07 | 8.776e-07 | 5.4824e-07 | 8.8646e-07
780 | feeder2_line20 | 3 | 99 | 1.4001 | 1.4001 | 1.4143 | 1.4142
780 | feeder2_line21 | 1 | 354.6 | 59.651 | 59.6453 | 16.822 | 16.8204
780 | feeder2_line21 | 2 | 354.6 | 66.8959 | 66.9123 | 18.8652 | 18.8698
780 | feeder2_line21 | 3 | 354.6 | 66.623 | 66.6113 | 18.7882 | 18.7849
780 | feeder2_line22 | 1 | 99 | 5.6975e-07 | 1.0098e-06 | 5.755e-07 | 1.02e-06
780 | feeder2_line22 | 2 | 99 | 0.95676 | 0.95676 | 0.96642 | 0.96642
780 | feeder2_line22 | 3 | 99 | 5.696e-07 | 1.0096e-06 | 5.7535e-07 | 1.0198e-06
780 | feeder2_line23 | 1 | 99 | 5.6974e-07 | 9.4528e-07 | 5.755e-07 | 9.5483e-07
780 | feeder2_line23 | 2 | 99 | 5.6751e-07 | 9.4162e-07 | 5.7325e-07 | 9.5113e-07
780 | feeder2_line23 | 3 | 99 | 0.082225 | 0.082219 | 0.083055 | 0.083049
780 | feeder2_line24 | 1 | 354.6 | 59.651 | 59.6453 | 16.8221 | 16.8204
780 | feeder2_line24 | 2 | 354.6 | 67.1416 | 67.1582 | 18.9345 | 18.9391
780 | feeder2_line24 | 3 | 354.6 | 66.6758 | 66.664 | 18.8031 | 18.7998
780 | feeder2_line25 | 1 | 99 | 0.95554 | 0.95553 | 0.96519 | 0.96518
780 | feeder2_line25 | 2 | 99 | 4.9695e-08 | 6.844e-07 | 5.0197e-08 | 6.9131e-07
780 | feeder2_line25 | 3 | 99 | 4.9336e-08 | 6.8709e-07 | 4.9835e-08 | 6.9403e-07
780 | feeder2_line26 | 1 | 99 | 0.085627 | 0.085628 | 0.086492 | 0.086493
780 | feeder2_line26 | 2 | 99 | 5.4252e-07 | 8.4793e-07 | 5.48e-07 | 8.565e-07
780 | feeder2_line26 | 3 | 99 | 5.4495e-07 | 8.5126e-07 | 5.5046e-07 | 8.5986e-07
780 | feeder2_line27 | 1 | 354.6 | 60.1388 | 60.133 | 16.9596 | 16.958
780 | feeder2_line27 | 2 | 354.6 | 67.1416 | 67.1582 | 18.9345 | 18.9391
780 | feeder2_line27 | 3 | 354.6 | 66.6758 | 66.664 | 18.8031 | 18.7998
780 | feeder2_line28 | 1 | 99 | 2.5276e-06 | 7.0671e-07 | 2.5531e-06 | 7.1385e-07
780 | feeder2_line28 | 2 | 99 | 1.2524 | 1.2524 | 1.2651 | 1.2651
780 | feeder2_line28 | 3 | 99 | 2.5278e-06 | 7.0666e-07 | 2.5533e-06 | 7.138e-07
780 | feeder2_line29 | 1 | 354.6 | 60.1388 | 60.133 | 16.9596 | 16.958
780 | feeder2_line29 | 2 | 354.6 | 66.3452 | 66.362 | 18.7099 | 18.7146
780 | feeder2_line29 | 3 | 354.6 | 66.6758 | 66.664 | 18.8031 | 18.7998
780 | feeder2_line30 | 1 | 266.4 | 1.428 | 1.4277 | 0.53603 | 0.53592
780 | feeder2_line30 | 2 | 266.4 | 3.388 | 3.3881 | 1.2718 | 1.2718
780 | feeder2_line30 | 3 | 266.4 | 21.3477 | 21.3479 | 8.0134 | 8.0135
780 | feeder2_line31 | 1 | 354.6 | 60.8023 | 60.7955 | 17.1467 | 17.1448
780 | feeder2_line31 | 2 | 354.6 | 65.252 | 65.2689 | 18.4016 | 18.4064
780 | feeder2_line31 | 3 | 354.6 | 80.5902 | 80.5763 | 22.7271 | 22.7231
780 | feeder2_line32 | 1 | 354.6 | 60.8023 | 60.7955 | 17.1467 | 17.1448
780 | feeder2_line32 | 2 | 354.6 | 64.8783 | 64.8965 | 18.2962 | 18.3013
780 | feeder2_line32 | 3 | 354.6 | 80.5902 | 80.5763 | 22.7271 | 22.7231
780 | feeder2_line33 | 1 | 99 | 4.9351e-08 | 6.8167e-07 | 4.9849e-08 | 6.8855e-07
780 | feeder2_line33 | 2 | 99 | 5.0462 | 5.0462 | 5.0972 | 5.0972
780 | feeder2_line33 | 3 | 99 | 4.9241e-08 | 6.82e-07 | 4.9739e-08 | 6.8889e-07
780 | feeder2_line34 | 1 | 354.6 | 60.8023 | 60.7955 | 17.1467 | 17.1448
780 | feeder2_line34 | 2 | 354.6 | 64.8783 | 64.8965 | 18.2962 | 18.3013
780 | feeder2_line34 | 3 | 354.6 | 80.6565 | 80.6426 | 22.7458 | 22.7418
780 | feeder2_line35 | 1 | 99 | 2.9711e-07 | 7.5482e-07 | 3.0012e-07 | 7.6245e-07
780 | feeder2_line35 | 2 | 99 | 2.9572e-07 | 7.5088e-07 | 2.987e-07 | 7.5847e-07
780 | feeder2_line35 | 3 | 99 | 0.085983 | 0.085968 | 0.086852 | 0.086836
780 | feeder2_line36 | 1 | 354.6 | 59.681 | 59.674 | 16.8305 | 16.8285
780 | feeder2_line36 | 2 | 354.6 | 64.8783 | 64.8965 | 18.2962 | 18.3013
780 | feeder2_line36 | 3 | 354.6 | 80.6565 | 80.6426 | 22.7458 | 22.7418
780 | feeder2_line37 | 1 | 99 | 2.4472 | 2.4477 | 2.4719 | 2.4724
780 | feeder2_line37 | 2 | 99 | 2.9568e-07 | 8.3071e-07 | 2.9867e-07 | 8.391e-07
780 | feeder2_line37 | 3 | 99 | 2.9732e-07 | 8.3587e-07 | 3.0032e-07 | 8.4432e-07
780 | feeder2_line38 | 1 | 99 | 3.2182e-07 | 7.7085e-07 | 3.2507e-07 | 7.7864e-07
780 | feeder2_line38 | 2 | 99 | 0.078147 | 0.078159 | 0.078937 | 0.078948
780 | feeder2_line38 | 3 | 99 | 3.2178e-07 | 7.7082e-07 | 3.2503e-07 | 7.7861e-07
780 | feeder2_line39 | 1 | 266.4 | 1.428 | 1.4277 | 0.53604 | 0.53592
780 | feeder2_line39 | 2 | 266.4 | 3.327 | 3.3272 | 1.2489 | 1.2489
780 | feeder2_line39 | 3 | 266.4 | 21.3477 | 21.3479 | 8.0134 | 8.0135
780 | feeder2_line40 | 1 | 354.6 | 60.19 | 60.183 | 16.974 | 16.9721
780 | feeder2_line40 | 2 | 354.6 | 64.8783 | 64.8965 | 18.2962 | 18.3013
780 | feeder2_line40 | 3 | 354.6 | 80.6565 | 80.6426 | 22.7458 | 22.7418
780 | feeder2_line41 | 1 | 99 | 0.95563 | 0.95562 | 0.96528 | 0.96528
780 | feeder2_line41 | 2 | 99 | 4.9774e-08 | 7.2583e-07 | 5.0277e-08 | 7.3317e-07
780 | feeder2_line41 | 3 | 99 | 4.9198e-08 | 7.3046e-07 | 4.9695e-08 | 7.3784e-07
780 | feeder2_line42 | 1 | 99 | 2.9715e-07 | 7.4407e-07 | 3.0015e-07 | 7.5158e-07
780 | feeder2_line42 | 2 | 99 | 2.9583e-07 | 7.4037e-07 | 2.9881e-07 | 7.4785e-07
780 | feeder2_line42 | 3 | 99 | 11.0759 | 11.0762 | 11.1878 | 11.1881
780 | feeder2_line43 | 1 | 266.4 | 1.4279 | 1.4277 | 0.536 | 0.53592
780 | feeder2_line43 | 2 | 266.4 | 3.3271 | 3.3272 | 1.2489 | 1.2489
780 | feeder2_line43 | 3 | 266.4 | 10.2789 | 10.2789 | 3.8584 | 3.8584
780 | feeder2_line44 | 1 | 354.6 | 60.19 | 60.183 | 16.9741 | 16.9721
780 | feeder2_line44 | 2 | 354.6 | 64.8783 | 64.8965 | 18.2962 | 18.3013
780 | feeder2_line44 | 3 | 354.6 | 80.5786 | 80.5644 | 22.7238 | 22.7198
780 | feeder2_line45 | 1 | 99 | 4.9384e-08 | 5.7546e-07 | 4.9883e-08 | 5.8128e-07
780 | feeder2_line45 | 2 | 99 | 4.9778e-08 | 5.7235e-07 | 5.0281e-08 | 5.7814e-07
780 | feeder2_line45 | 3 | 99 | 1.4008 | 1.4008 | 1.415 | 1.4149
780 | feeder2_line46 | 1 | 99 | 5.6966e-07 | 1.3489e-06 | 5.7542e-07 | 1.3625e-06
780 | feeder2_line46 | 2 | 99 | 5.668e-07 | 1.3422e-06 | 5.7253e-07 | 1.3557e-06
780 | feeder2_line46 | 3 | 99 | 0.26173 | 0.2617 | 0.26438 | 0.26434
780 | feeder2_line47 | 1 | 266.4 | 1.4279 | 1.4277 | 0.536 | 0.53592
780 | feeder2_line47 | 2 | 266.4 | 3.3272 | 3.3272 | 1.2489 | 1.2489
780 | feeder2_line47 | 3 | 266.4 | 10.0177 | 10.0177 | 3.7604 | 3.7604
780 | feeder2_line48 | 1 | 99 | 0.082169 | 0.082172 | 0.082999 | 0.083002
780 | feeder2_line48 | 2 | 99 | 4.9722e-08 | 7.2264e-07 | 5.0225e-08 | 7.2994e-07
780 | feeder2_line48 | 3 | 99 | 4.9307e-08 | 7.2599e-07 | 4.9805e-08 | 7.3332e-07
780 | feeder2_line49 | 1 | 266.4 | 1.3458 | 1.3456 | 0.50517 | 0.50509
780 | feeder2_line49 | 2 | 266.4 | 3.3272 | 3.3272 | 1.2489 | 1.2489
780 | feeder2_line49 | 3 | 266.4 | 10.0177 | 10.0177 | 3.7604 | 3.7604
780 | feeder2_line50 | 1 | 99 | 5.6966e-07 | 1.2276e-06 | 5.7541e-07 | 1.24e-06
780 | feeder2_line50 | 2 | 99 | 2.4906 | 2.4907 | 2.5158 | 2.5158
780 | feeder2_line50 | 3 | 99 | 5.6943e-07 | 1.2271e-06 | 5.7518e-07 | 1.2395e-06
780 | feeder2_line51 | 1 | 99 | 0.74267 | 0.74272 | 0.75017 | 0.75022
780 | feeder2_line51 | 2 | 99 | 5.6679e-07 | 1.326e-06 | 5.7252e-07 | 1.3394e-06
780 | feeder2_line51 | 3 | 99 | 5.6943e-07 | 1.3321e-06 | 5.7518e-07 | 1.3456e-06
780 | feeder2_line52 | 1 | 266.4 | 0.60343 | 0.60333 | 0.22651 | 0.22647
780 | feeder2_line52 | 2 | 266.4 | 0.9454 | 0.94534 | 0.35488 | 0.35486
780 | feeder2_line52 | 3 | 266.4 | 10.0175 | 10.0177 | 3.7603 | 3.7604
780 | feeder2_line53 | 1 | 99 | 5.4502e-07 | 7.4922e-07 | 5.5053e-07 | 7.5679e-07
780 | feeder2_line53 | 2 | 99 | 0.94534 | 0.94534 | 0.95488 | 0.95489
780 | feeder2_line53 | 3 | 99 | 5.4477e-07 | 7.4889e-07 | 5.5027e-07 | 7.5646e-07
780 | feeder2_line54 | 1 | 266.4 | 0.60324 | 0.60333 | 0.22644 | 0.22647
780 | feeder2_line54 | 2 | 266.4 | 8.4592e-05 | 4.5736e-06 | 3.1754e-05 | 1.7168e-06
780 | feeder2_line54 | 3 | 266.4 | 10.0174 | 10.0177 | 3.7603 | 3.7604
780 | feeder2_line55 | 1 | 99 | 0.0457 | 0.045701 | 0.046161 | 0.046162
780 | feeder2_line55 | 2 | 99 | 4.9809e-08 | 7.2082e-07 | 5.0312e-08 | 7.281e-07
780 | feeder2_line55 | 3 | 99 | 4.9144e-08 | 7.2608e-07 | 4.9641e-08 | 7.3341e-07
780 | feeder2_line56 | 1 | 354.6 | 60.2143 | 60.2073 | 16.9809 | 16.9789
780 | feeder2_line56 | 2 | 354.6 | 64.8783 | 64.8965 | 18.2962 | 18.3013
780 | feeder2_line56 | 3 | 354.6 | 80.5786 | 80.5644 | 22.7238 | 22.7198
780 | feeder2_line57 | 1 | 99 | 7.3954e-07 | 1.5347e-06 | 7.4701e-07 | 1.5502e-06
780 | feeder2_line57 | 2 | 99 | 7.4573e-07 | 1.527e-06 | 7.5327e-07 | 1.5424e-06
780 | feeder2_line57 | 3 | 99 | 10.0175 | 10.0177 | 10.1186 | 10.1189
780 | feeder2_line58 | 1 | 266.4 | 0.6033 | 0.60333 | 0.22647 | 0.22647
780 | feeder2_line58 | 2 | 266.4 | 1.8724e-05 | 2.6554e-06 | 7.0285e-06 | 9.9679e-07
780 | feeder2_line58 | 3 | 266.4 | 1.8816e-05 | 2.6669e-06 | 7.063e-06 | 1.0011e-06
780 | feeder2_line59 | 1 | 99 | 4.9296e-08 | 5.3345e-07 | 4.9794e-08 | 5.3884e-07
780 | feeder2_line59 | 2 | 99 | 4.9705e-08 | 5.308e-07 | 5.0207e-08 | 5.3617e-07
780 | feeder2_line59 | 3 | 99 | 9.956 | 9.9563 | 10.0566 | 10.0568
780 | feeder2_line60 | 1 | 99 | 2.9716e-07 | 8.0621e-07 | 3.0016e-07 | 8.1436e-07
780 | feeder2_line60 | 2 | 99 | 2.9583e-07 | 8.022e-07 | 2.9881e-07 | 8.103e-07
780 | feeder2_line60 | 3 | 99 | 0.061996 | 0.061992 | 0.062622 | 0.062618
780 | feeder2_line61 | 1 | 266.4 | 0.48281 | 0.48298 | 0.18124 | 0.1813
780 | feeder2_line61 | 2 | 266.4 | 7.7368 | 7.7372 | 2.9042 | 2.9043
780 | feeder2_line61 | 3 | 266.4 | 1.9447 | 1.9448 | 0.72999 | 0.73002
780 | feeder2_line62 | 1 | 354.6 | 60.4673 | 60.4604 | 17.0523 | 17.0503
780 | feeder2_line62 | 2 | 354.6 | 64.9757 | 64.9955 | 18.3237 | 18.3292
780 | feeder2_line62 | 3 | 354.6 | 82.1019 | 82.0877 | 23.1534 | 23.1494
780 | feeder2_line63 | 1 | 99 | 0.089552 | 0.089554 | 0.090457 | 0.090458
780 | feeder2_line63 | 2 | 99 | 5.668e-07 | 1.2061e-06 | 5.7253e-07 | 1.2183e-06
780 | feeder2_line63 | 3 | 99 | 5.6939e-07 | 1.2115e-06 | 5.7514e-07 | 1.2238e-06
780 | feeder2_line64 | 1 | 99 | 0.51377 | 0.51378 | 0.51896 | 0.51896
780 | feeder2_line64 | 2 | 99 | 7.4377e-12 | 3.177e-07 | 7.5128e-12 | 3.2091e-07
780 | feeder2_line64 | 3 | 99 | 1.9129e-12 | 3.1914e-07 | 1.9323e-12 | 3.2237e-07
780 | feeder2_line65 | 1 | 99 | 4.9431e-08 | 6.3651e-07 | 4.993e-08 | 6.4294e-07
780 | feeder2_line65 | 2 | 99 | 10.3361 | 10.3357 | 10.4405 | 10.4401
780 | feeder2_line65 | 3 | 99 | 4.9065e-08 | 6.3809e-07 | 4.9561e-08 | 6.4453e-07
780 | feeder2_line66 | 1 | 354.6 | 60.4673 | 60.4604 | 17.0523 | 17.0503
780 | feeder2_line66 | 2 | 354.6 | 70.2037 | 70.2244 | 19.798 | 19.8038
780 | feeder2_line66 | 3 | 354.6 | 82.1019 | 82.0877 | 23.1534 | 23.1494
780 | feeder2_line67 | 1 | 99 | 2.4709e-08 | 3.5991e-07 | 2.4959e-08 | 3.6354e-07
780 | feeder2_line67 | 2 | 99 | 2.4911e-08 | 3.5778e-07 | 2.5163e-08 | 3.6139e-07
780 | feeder2_line67 | 3 | 99 | 0.95498 | 0.95495 | 0.96462 | 0.9646
780 | feeder2_line68 | 1 | 266.4 | 0.48285 | 0.48298 | 0.18125 | 0.1813
780 | feeder2_line68 | 2 | 266.4 | 7.7369 | 7.7372 | 2.9042 | 2.9043
780 | feeder2_line68 | 3 | 266.4 | 0.99055 | 0.99062 | 0.37183 | 0.37185
780 | feeder2_line69 | 1 | 99 | 10.8546 | 10.8545 | 10.9643 | 10.9641
780 | feeder2_line69 | 2 | 99 | 2.5055e-06 | 6.5684e-07 | 2.5308e-06 | 6.6347e-07
780 | feeder2_line69 | 3 | 99 | 2.5352e-06 | 6.625e-07 | 2.5608e-06 | 6.6919e-07
780 | feeder2_line70 | 1 | 354.6 | 66.5022 | 66.496 | 18.7541 | 18.7524
780 | feeder2_line70 | 2 | 354.6 | 70.2037 | 70.2244 | 19.798 | 19.8038
780 | feeder2_line70 | 3 | 354.6 | 82.1019 | 82.0877 | 23.1534 | 23.1494
780 | feeder2_line71 | 1 | 99 | 4.9452e-08 | 7.1003e-07 | 4.9952e-08 | 7.172e-07
780 | feeder2_line71 | 2 | 99 | 1.2734 | 1.2735 | 1.2863 | 1.2863
780 | feeder2_line71 | 3 | 99 | 4.9058e-08 | 7.1201e-07 | 4.9554e-08 | 7.192e-07
780 | feeder2_line72 | 1 | 354.6 | 66.5023 | 66.496 | 18.7542 | 18.7524
780 | feeder2_line72 | 2 | 354.6 | 69.8581 | 69.8789 | 19.7005 | 19.7064
780 | feeder2_line72 | 3 | 354.6 | 82.102 | 82.0877 | 23.1534 | 23.1494
780 | feeder2_line73 | 1 | 99 | 5.9407e-07 | 1.5237e-06 | 6.0007e-07 | 1.5391e-06
780 | feeder2_line73 | 2 | 99 | 5.0488 | 5.0488 | 5.0998 | 5.0998
780 | feeder2_line73 | 3 | 99 | 5.9508e-07 | 1.5267e-06 | 6.0109e-07 | 1.5421e-06
780 | feeder2_line74 | 1 | 99 | 4.9404e-08 | 4.5446e-07 | 4.9903e-08 | 4.5905e-07
780 | feeder2_line74 | 2 | 99 | 0.9987 | 0.99881 | 1.0088 | 1.0089
780 | feeder2_line74 | 3 | 99 | 4.9105e-08 | 4.5535e-07 | 4.9601e-08 | 4.5995e-07
780 | feeder2_line75 | 1 | 266.4 | 0.48295 | 0.48298 | 0.18129 | 0.1813
780 | feeder2_line75 | 2 | 266.4 | 1.8261 | 1.8262 | 0.68549 | 0.68551
780 | feeder2_line75 | 3 | 266.4 | 0.99065 | 0.99062 | 0.37187 | 0.37185
780 | feeder2_line76 | 1 | 99 | 0.48298 | 0.48298 | 0.48786 | 0.48786
780 | feeder2_line76 | 2 | 99 | 8.3645e-07 | 1.5624e-06 | 8.449e-07 | 1.5781e-06
780 | feeder2_line76 | 3 | 99 | 8.4352e-07 | 1.5749e-06 | 8.5204e-07 | 1.5908e-06
780 | feeder2_line77 | 1 | 99 | 2.4698e-08 | 5.711e-07 | 2.4948e-08 | 5.7687e-07
780 | feeder2_line77 | 2 | 99 | 2.4912e-08 | 5.6767e-07 | 2.5163e-08 | 5.734e-07
780 | feeder2_line77 | 3 | 99 | 0.99069 | 0.99062 | 1.0007 | 1.0006
780 | feeder2_line78 | 1 | 266.4 | 9.5366e-12 | 9.4709e-07 | 3.5798e-12 | 3.5551e-07
780 | feeder2_line78 | 2 | 266.4 | 1.8262 | 1.8262 | 0.6855 | 0.68551
780 | feeder2_line78 | 3 | 266.4 | 1.7589e-12 | 9.4869e-07 | 6.6026e-13 | 3.5611e-07
780 | feeder2_line79 | 1 | 354.6 | 10.5766 | 10.5761 | 2.9827 | 2.9826
780 | feeder2_line79 | 2 | 354.6 | 3.1142 | 3.114 | 0.87822 | 0.87816
780 | feeder2_line79 | 3 | 354.6 | 12.5564 | 12.5561 | 3.541 | 3.5409
780 | feeder2_line80 | 1 | 354.6 | 72.93 | 72.9239 | 20.5668 | 20.5651
780 | feeder2_line80 | 2 | 354.6 | 70.6946 | 70.7154 | 19.9364 | 19.9423
780 | feeder2_line80 | 3 | 354.6 | 90.8959 | 90.8807 | 25.6334 | 25.6291
780 | feeder2_line81 | 1 | 354.6 | 72.9299 | 72.9239 | 20.5668 | 20.5651
780 | feeder2_line81 | 2 | 354.6 | 70.6945 | 70.7154 | 19.9364 | 19.9423
780 | feeder2_line81 | 3 | 354.6 | 91.7116 | 91.6963 | 25.8634 | 25.8591
780 | feeder2_line82 | 1 | 354.6 | 1.7158e-11 | 7.2808e-07 | 4.8387e-12 | 2.0532e-07
780 | feeder2_line82 | 2 | 354.6 | 2.6009e-11 | 7.2394e-07 | 7.3348e-12 | 2.0416e-07
780 | feeder2_line82 | 3 | 354.6 | 1.7223 | 1.7222 | 0.48569 | 0.48568
780 | feeder2_line83 | 1 | 354.6 | 72.93 | 72.9239 | 20.5668 | 20.5651
780 | feeder2_line83 | 2 | 354.6 | 70.7562 | 70.7772 | 19.9538 | 19.9597
780 | feeder2_line83 | 3 | 354.6 | 91.7118 | 91.6963 | 25.8634 | 25.8591
780 | feeder2_line84 | 1 | 354.6 | 2.5288e-11 | 1.2867e-06 | 7.1315e-12 | 3.6287e-07
780 | feeder2_line84 | 2 | 354.6 | 0.090538 | 0.090638 | 0.025532 | 0.025561
780 | feeder2_line84 | 3 | 354.6 | 4.4798e-12 | 1.2907e-06 | 1.2633e-12 | 3.6398e-07
780 | feeder2_line85 | 1 | 99 | 0.077736 | 0.077737 | 0.078521 | 0.078522
780 | feeder2_line85 | 2 | 99 | 4.9882e-08 | 4.5643e-07 | 5.0385e-08 | 4.6104e-07
780 | feeder2_line85 | 3 | 99 | 4.9011e-08 | 4.6084e-07 | 4.9506e-08 | 4.655e-07
780 | feeder2_line86 | 1 | 354.6 | 72.9898 | 72.9836 | 20.5837 | 20.582
780 | feeder2_line86 | 2 | 354.6 | 70.7563 | 70.7772 | 19.9538 | 19.9597
780 | feeder2_line86 | 3 | 354.6 | 91.7118 | 91.6963 | 25.8635 | 25.8591
780 | feeder2_line87 | 1 | 354.6 | 72.9899 | 72.9836 | 20.5837 | 20.582
780 | feeder2_line87 | 2 | 354.6 | 78.9374 | 78.9588 | 22.261 | 22.267
780 | feeder2_line87 | 3 | 354.6 | 91.7841 | 91.7684 | 25.8838 | 25.8794
780 | feeder2_line88 | 1 | 354.6 | 0.00011189 | 3.3348e-06 | 3.1553e-05 | 9.4045e-07
780 | feeder2_line88 | 2 | 354.6 | 16.8154 | 16.8152 | 4.7421 | 4.742
780 | feeder2_line88 | 3 | 354.6 | 0.082025 | 0.081859 | 0.023132 | 0.023085
780 | feeder2_line89 | 1 | 354.6 | 72.9881 | 72.9836 | 20.5832 | 20.582
780 | feeder2_line89 | 2 | 354.6 | 86.2205 | 86.2436 | 24.3149 | 24.3214
780 | feeder2_line89 | 3 | 354.6 | 91.782 | 91.7684 | 25.8833 | 25.8794
780 | feeder2_line90 | 1 | 354.6 | 0.00071694 | 2.0134e-06 | 0.00020218 | 5.6778e-07
780 | feeder2_line90 | 2 | 354.6 | 9.8964 | 9.8965 | 2.7909 | 2.7909
780 | feeder2_line90 | 3 | 354.6 | 0.00072272 | 2.0207e-06 | 0.00020381 | 5.6985e-07
780 | feeder2_line91 | 1 | 354.6 | 72.9882 | 72.9836 | 20.5832 | 20.582
780 | feeder2_line91 | 2 | 354.6 | 86.2205 | 86.2436 | 24.3149 | 24.3214
780 | feeder2_line91 | 3 | 354.6 | 91.8365 | 91.8229 | 25.8986 | 25.8948
780 | feeder2_line92 | 1 | 354.6 | 1.4935e-11 | 1.0152e-06 | 4.2119e-12 | 2.863e-07
780 | feeder2_line92 | 2 | 354.6 | 1.4935e-11 | 1.0093e-06 | 4.2119e-12 | 2.8464e-07
780 | feeder2_line92 | 3 | 354.6 | 0.061748 | 0.061741 | 0.017413 | 0.017411
780 | feeder2_line93 | 1 | 99 | 2.4764e-08 | 3.3889e-07 | 2.5014e-08 | 3.4232e-07
780 | feeder2_line93 | 2 | 99 | 0.090545 | 0.090652 | 0.09146 | 0.091567
780 | feeder2_line93 | 3 | 99 | 2.4492e-08 | 3.4023e-07 | 2.4739e-08 | 3.4366e-07
780 | feeder2_line94 | 1 | 354.6 | 2.476e-06 | 1.65e-06 | 6.9824e-07 | 4.653e-07
780 | feeder2_line94 | 2 | 354.6 | 9.8075 | 9.8071 | 2.7658 | 2.7657
780 | feeder2_line94 | 3 | 354.6 | 2.4487e-06 | 1.6559e-06 | 6.9054e-07 | 4.6696e-07
780 | feeder2_line95 | 1 | 99 | 3.5399e-06 | 2.5859e-06 | 3.5756e-06 | 2.6121e-06
780 | feeder2_line95 | 2 | 99 | 16.8153 | 16.8152 | 16.9851 | 16.9851
780 | feeder2_line95 | 3 | 99 | 3.5506e-06 | 2.5954e-06 | 3.5864e-06 | 2.6216e-06
780 | feeder2_line96 | 1 | 354.6 | 0.00011999 | 6.1635e-07 | 3.3838e-05 | 1.7382e-07
780 | feeder2_line96 | 2 | 354.6 | 0.00011921 | 6.1274e-07 | 3.3617e-05 | 1.728e-07
780 | feeder2_line96 | 3 | 354.6 | 0.082007 | 0.081859 | 0.023127 | 0.023085
780 | feeder2_line97 | 1 | 354.6 | 73.6943 | 73.6897 | 20.7824 | 20.7811
780 | feeder2_line97 | 2 | 354.6 | 86.2207 | 86.2436 | 24.3149 | 24.3214
780 | feeder2_line97 | 3 | 354.6 | 91.8368 | 91.8229 | 25.8987 | 25.8948
780 | feeder2_line98 | 1 | 354.6 | 2.1455 | 2.1441 | 0.60505 | 0.60466
780 | feeder2_line98 | 2 | 354.6 | 0.0016731 | 6.1213e-07 | 0.00047183 | 1.7263e-07
780 | feeder2_line98 | 3 | 354.6 | 0.0017051 | 6.2036e-07 | 0.00048084 | 1.7495e-07
780 | feeder2_line99 | 1 | 99 | 2.4746e-08 | 4.4317e-07 | 2.4996e-08 | 4.4765e-07
780 | feeder2_line99 | 2 | 99 | 2.4946e-08 | 4.404e-07 | 2.5198e-08 | 4.4485e-07
780 | feeder2_line99 | 3 | 99 | 0.081917 | 0.081859 | 0.082744 | 0.082686
780 | feeder2_line100 | 1 | 99 | 2.1442 | 2.1441 | 2.1658 | 2.1658
780 | feeder2_line100 | 2 | 99 | 2.4956e-08 | 6.046e-07 | 2.5208e-08 | 6.1071e-07
780 | feeder2_line100 | 3 | 99 | 2.4489e-08 | 6.108e-07 | 2.4736e-08 | 6.1697e-07
780 | feeder2_line101 | 1 | 354.6 | 9.8695 | 9.8691 | 2.7833 | 2.7832
780 | feeder2_line101 | 2 | 354.6 | 3.1141 | 3.114 | 0.87821 | 0.87816
780 | feeder2_line101 | 3 | 354.6 | 12.5564 | 12.5561 | 3.541 | 3.5409
780 | feeder2_line102 | 1 | 99 | 0.7096 | 0.70957 | 0.71677 | 0.71673
780 | feeder2_line102 | 2 | 99 | 2.2967e-06 | 8.6539e-07 | 2.3199e-06 | 8.7414e-07
780 | feeder2_line102 | 3 | 99 | 2.3307e-06 | 8.7314e-07 | 2.3542e-06 | 8.8196e-07
780 | feeder2_line103 | 1 | 99 | 5.4444e-07 | 7.9671e-07 | 5.4994e-07 | 8.0476e-07
780 | feeder2_line103 | 2 | 99 | 0.63233 | 0.63236 | 0.63871 | 0.63875
780 | feeder2_line103 | 3 | 99 | 5.4641e-07 | 7.9915e-07 | 5.5193e-07 | 8.0722e-07
780 | feeder2_line104 | 1 | 354.6 | 9.8695 | 9.8691 | 2.7833 | 2.7832
780 | feeder2_line104 | 2 | 354.6 | 2.5347 | 2.5346 | 0.71481 | 0.71477
780 | feeder2_line104 | 3 | 354.6 | 12.5563 | 12.5561 | 3.541 | 3.5409
780 | feeder2_line105 | 1 | 99 | 2.5242e-06 | 7.3305e-07 | 2.5497e-06 | 7.4045e-07
780 | feeder2_line105 | 2 | 99 | 2.5054e-06 | 7.2885e-07 | 2.5307e-06 | 7.3621e-07
780 | feeder2_line105 | 3 | 99 | 8.7001 | 8.7005 | 8.788 | 8.7884
780 | feeder2_line106 | 1 | 354.6 | 9.8694 | 9.8691 | 2.7833 | 2.7832
780 | feeder2_line106 | 2 | 354.6 | 2.5347 | 2.5346 | 0.7148 | 0.71477
780 | feeder2_line106 | 3 | 354.6 | 4.1739 | 4.1735 | 1.1771 | 1.1769
780 | feeder2_line107 | 1 | 99 | 3.2165e-07 | 8.9327e-07 | 3.249e-07 | 9.0229e-07
780 | feeder2_line107 | 2 | 99 | 0.98097 | 0.98107 | 0.99088 | 0.99098
780 | feeder2_line107 | 3 | 99 | 3.2223e-07 | 8.9604e-07 | 3.2549e-07 | 9.0509e-07
780 | feeder2_line108 | 1 | 354.6 | 9.8694 | 9.8691 | 2.7832 | 2.7832
780 | feeder2_line108 | 2 | 354.6 | 1.7103 | 1.7102 | 0.48232 | 0.48228
780 | feeder2_line108 | 3 | 354.6 | 4.1739 | 4.1735 | 1.1771 | 1.1769
780 | feeder2_line109 | 1 | 354.6 | 81.9719 | 81.9672 | 23.1167 | 23.1154
780 | feeder2_line109 | 2 | 354.6 | 86.2217 | 86.2436 | 24.3152 | 24.3214
780 | feeder2_line109 | 3 | 354.6 | 91.8377 | 91.8229 | 25.899 | 25.8948
780 | feeder2_line110 | 1 | 99 | 10.9489 | 10.9481 | 11.0595 | 11.0587
780 | feeder2_line110 | 2 | 99 | 0.00079002 | 8.9512e-07 | 0.000798 | 9.0417e-07
780 | feeder2_line110 | 3 | 99 | 0.00080213 | 9.0405e-07 | 0.00081023 | 9.1318e-07
780 | feeder2_line111 | 1 | 99 | 2.4728e-08 | 3.7848e-07 | 2.4978e-08 | 3.823e-07
780 | feeder2_line111 | 2 | 99 | 15.2172 | 15.2168 | 15.3709 | 15.3706
780 | feeder2_line111 | 3 | 99 | 2.4485e-08 | 3.7987e-07 | 2.4733e-08 | 3.837e-07
780 | feeder2_line112 | 1 | 99 | 3.2173e-07 | 9.0951e-07 | 3.2498e-07 | 9.1869e-07
780 | feeder2_line112 | 2 | 99 | 1.6592 | 1.6595 | 1.676 | 1.6762
780 | feeder2_line112 | 3 | 99 | 3.2243e-07 | 9.1284e-07 | 3.2569e-07 | 9.2206e-07
780 | feeder2_line113 | 1 | 99 | 0.098242 | 0.098245 | 0.099235 | 0.099237
780 | feeder2_line113 | 2 | 99 | 3.204e-07 | 8.9154e-07 | 3.2364e-07 | 9.0055e-07
780 | feeder2_line113 | 3 | 99 | 3.2266e-07 | 9.0076e-07 | 3.2592e-07 | 9.0985e-07
780 | feeder2_line114 | 1 | 99 | 0.6275 | 0.62751 | 0.63384 | 0.63385
780 | feeder2_line114 | 2 | 99 | 2.4917e-08 | 4.3032e-07 | 2.5168e-08 | 4.3467e-07
780 | feeder2_line114 | 3 | 99 | 2.4521e-08 | 4.3418e-07 | 2.4769e-08 | 4.3856e-07
780 | feeder2_line115 | 1 | 99 | 2.4749e-08 | 5.5738e-07 | 2.4999e-08 | 5.6301e-07
780 | feeder2_line115 | 2 | 99 | 0.30876 | 0.30879 | 0.31188 | 0.31191
780 | feeder2_line115 | 3 | 99 | 2.4523e-08 | 5.5916e-07 | 2.477e-08 | 5.6481e-07
780 | feeder2_line116 | 1 | 354.6 | 9.8694 | 9.8691 | 2.7833 | 2.7832
780 | feeder2_line116 | 2 | 354.6 | 1.5066 | 1.5064 | 0.42487 | 0.42483
780 | feeder2_line116 | 3 | 354.6 | 4.1739 | 4.1735 | 1.1771 | 1.1769
780 | feeder2_line117 | 1 | 99 | 4.959e-08 | 6.3664e-07 | 5.0091e-08 | 6.4307e-07
780 | feeder2_line117 | 2 | 99 | 0.26146 | 0.26161 | 0.2641 | 0.26425
780 | feeder2_line117 | 3 | 99 | 4.8978e-08 | 6.3956e-07 | 4.9473e-08 | 6.4602e-07
780 | feeder2_line118 | 1 | 354.6 | 81.9719 | 81.9672 | 23.1167 | 23.1154
780 | feeder2_line118 | 2 | 354.6 | 86.4351 | 86.4571 | 24.3754 | 24.3816
780 | feeder2_line118 | 3 | 354.6 | 91.8378 | 91.8229 | 25.899 | 25.8948
780 | feeder2_line119 | 1 | 99 | 2.4743e-08 | 5.997e-07 | 2.4993e-08 | 6.0575e-07
780 | feeder2_line119 | 2 | 99 | 2.4896e-08 | 5.9647e-07 | 2.5148e-08 | 6.025e-07
780 | feeder2_line119 | 3 | 99 | 0.093954 | 0.093914 | 0.094903 | 0.094863
780 | feeder2_line120 | 1 | 354.6 | 9.8694 | 9.8691 | 2.7833 | 2.7832
780 | feeder2_line120 | 2 | 354.6 | 1.5066 | 1.5064 | 0.42487 | 0.42483
780 | feeder2_line120 | 3 | 354.6 | 4.0933 | 4.0929 | 1.1544 | 1.1542
780 | feeder2_line121 | 1 | 99 | 3.2157e-07 | 9.2853e-07 | 3.2482e-07 | 9.3791e-07
780 | feeder2_line121 | 2 | 99 | 0.071751 | 0.071758 | 0.072476 | 0.072482
780 | feeder2_line121 | 3 | 99 | 3.2221e-07 | 9.3168e-07 | 3.2547e-07 | 9.4109e-07
780 | feeder2_line122 | 1 | 354.6 | 9.8694 | 9.8691 | 2.7832 | 2.7832
780 | feeder2_line122 | 2 | 354.6 | 1.4707 | 1.4706 | 0.41475 | 0.41471
780 | feeder2_line122 | 3 | 354.6 | 4.0933 | 4.0929 | 1.1543 | 1.1542
780 | feeder2_line123 | 1 | 99 | 5.6886e-07 | 9.621e-07 | 5.7461e-07 | 9.7182e-07
780 | feeder2_line123 | 2 | 99 | 5.6592e-07 | 9.5717e-07 | 5.7163e-07 | 9.6683e-07
780 | feeder2_line123 | 3 | 99 | 1.256 | 1.256 | 1.2687 | 1.2687
780 | feeder2_line124 | 1 | 354.6 | 9.8693 | 9.8691 | 2.7832 | 2.7832
780 | feeder2_line124 | 2 | 354.6 | 1.4708 | 1.4706 | 0.41476 | 0.41471
780 | feeder2_line124 | 3 | 354.6 | 2.9896 | 2.9892 | 0.84309 | 0.84298
780 | feeder2_line125 | 1 | 99 | 5.6884e-07 | 8.9434e-07 | 5.7459e-07 | 9.0338e-07
780 | feeder2_line125 | 2 | 99 | 5.6592e-07 | 8.8979e-07 | 5.7164e-07 | 8.9878e-07
780 | feeder2_line125 | 3 | 99 | 2.1406 | 2.1404 | 2.1622 | 2.1621
780 | feeder2_line126 | 1 | 354.6 | 9.8695 | 9.8691 | 2.7833 | 2.7832
780 | feeder2_line126 | 2 | 354.6 | 1.4709 | 1.4706 | 0.4148 | 0.41471
780 | feeder2_line126 | 3 | 354.6 | 0.92671 | 0.92634 | 0.26134 | 0.26123
780 | feeder2_line127 | 1 | 99 | 5.688e-07 | 1.0706e-06 | 5.7455e-07 | 1.0814e-06
780 | feeder2_line127 | 2 | 99 | 5.6593e-07 | 1.0652e-06 | 5.7164e-07 | 1.076e-06
780 | feeder2_line127 | 3 | 99 | 0.07742 | 0.077402 | 0.078202 | 0.078184
780 | feeder2_line128 | 1 | 354.6 | 9.8694 | 9.8691 | 2.7832 | 2.7832
780 | feeder2_line128 | 2 | 354.6 | 1.4709 | 1.4706 | 0.41479 | 0.41472
780 | feeder2_line128 | 3 | 354.6 | 0.84939 | 0.84912 | 0.23954 | 0.23946
780 | feeder2_line129 | 1 | 99 | 5.4403e-07 | 8.6808e-07 | 5.4952e-07 | 8.7684e-07
780 | feeder2_line129 | 2 | 99 | 1.4706 | 1.4706 | 1.4855 | 1.4854
780 | feeder2_line129 | 3 | 99 | 5.4634e-07 | 8.712e-07 | 5.5186e-07 | 8.8e-07
780 | feeder2_line130 | 1 | 354.6 | 9.8694 | 9.8691 | 2.7833 | 2.7832
780 | feeder2_line130 | 2 | 354.6 | 0.00030388 | 4.5717e-06 | 8.5697e-05 | 1.2893e-06
780 | feeder2_line130 | 3 | 354.6 | 0.84941 | 0.84912 | 0.23954 | 0.23946
780 | feeder2_line131 | 1 | 99 | 5.6874e-07 | 9.6206e-07 | 5.7449e-07 | 9.7178e-07
780 | feeder2_line131 | 2 | 99 | 5.6593e-07 | 9.5735e-07 | 5.7165e-07 | 9.6702e-07
780 | feeder2_line131 | 3 | 99 | 0.77198 | 0.77194 | 0.77977 | 0.77974
780 | feeder2_line132 | 1 | 354.6 | 9.8692 | 9.8691 | 2.7832 | 2.7832
780 | feeder2_line132 | 2 | 354.6 | 0.0001237 | 2.8743e-06 | 3.4884e-05 | 8.1058e-07
780 | feeder2_line132 | 3 | 354.6 | 0.077486 | 0.0774 | 0.021852 | 0.021827
780 | feeder2_line133 | 1 | 99 | 9.8692 | 9.8691 | 9.9688 | 9.9688
780 | feeder2_line133 | 2 | 99 | 2.954e-07 | 9.6498e-07 | 2.9838e-07 | 9.7473e-07
780 | feeder2_line133 | 3 | 99 | 2.9768e-07 | 9.733e-07 | 3.0069e-07 | 9.8313e-07
780 | feeder2_line134 | 1 | 354.6 | 9.2058e-12 | 1.7685e-06 | 2.5961e-12 | 4.9872e-07
780 | feeder2_line134 | 2 | 354.6 | 2.257e-12 | 1.7603e-06 | 6.3651e-13 | 4.9641e-07
780 | feeder2_line134 | 3 | 354.6 | 0.077418 | 0.0774 | 0.021832 | 0.021827
780 | feeder2_line135 | 1 | 99 | 1.2767 | 1.2767 | 1.2895 | 1.2896
780 | feeder2_line135 | 2 | 99 | 4.9928e-08 | 5.7679e-07 | 5.0432e-08 | 5.8262e-07
780 | feeder2_line135 | 3 | 99 | 4.8976e-08 | 5.8289e-07 | 4.9471e-08 | 5.8878e-07
780 | feeder2_line136 | 1 | 354.6 | 82.0035 | 81.9988 | 23.1256 | 23.1243
780 | feeder2_line136 | 2 | 354.6 | 86.4351 | 86.4571 | 24.3754 | 24.3816
780 | feeder2_line136 | 3 | 354.6 | 91.8377 | 91.8229 | 25.899 | 25.8948
780 | feeder2_line137 | 1 | 99 | 7.6541 | 7.654 | 7.7314 | 7.7313
780 | feeder2_line137 | 2 | 99 | 8.368e-07 | 1.5535e-06 | 8.4526e-07 | 1.5692e-06
780 | feeder2_line137 | 3 | 99 | 8.4617e-07 | 1.57e-06 | 8.5471e-07 | 1.5859e-06
780 | feeder2_line138 | 1 | 354.6 | 88.2205 | 88.2161 | 24.8789 | 24.8776
780 | feeder2_line138 | 2 | 354.6 | 86.4351 | 86.4571 | 24.3754 | 24.3816
780 | feeder2_line138 | 3 | 354.6 | 91.8378 | 91.8229 | 25.899 | 25.8948
780 | feeder2_line139 | 1 | 99 | 4.9619e-08 | 4.8686e-07 | 5.012e-08 | 4.9177e-07
780 | feeder2_line139 | 2 | 99 | 4.9937e-08 | 4.8406e-07 | 5.0442e-08 | 4.8895e-07
780 | feeder2_line139 | 3 | 99 | 1.5715 | 1.5704 | 1.5873 | 1.5862
780 | feeder2_line140 | 1 | 354.6 | 88.2205 | 88.2161 | 24.8789 | 24.8776
780 | feeder2_line140 | 2 | 354.6 | 86.4352 | 86.4571 | 24.3754 | 24.3816
780 | feeder2_line140 | 3 | 354.6 | 92.736 | 92.7202 | 26.1523 | 26.1478
780 | feeder2_line141 | 1 | 99 | 2.5006e-06 | 4.816e-07 | 2.5258e-06 | 4.8646e-07
780 | feeder2_line141 | 2 | 99 | 10.9992 | 10.9986 | 11.1103 | 11.1097
780 | feeder2_line141 | 3 | 99 | 2.5192e-06 | 4.8395e-07 | 2.5446e-06 | 4.8883e-07
780 | feeder2_line142 | 1 | 354.6 | 88.2205 | 88.2161 | 24.8789 | 24.8776
780 | feeder2_line142 | 2 | 354.6 | 95.5653 | 95.5866 | 26.9502 | 26.9562
780 | feeder2_line142 | 3 | 354.6 | 92.7359 | 92.7202 | 26.1523 | 26.1478
780 | feeder2_line143 | 1 | 99 | 8.4199e-07 | 1.7113e-06 | 8.505e-07 | 1.7286e-06
780 | feeder2_line143 | 2 | 99 | 0.98131 | 0.98143 | 0.99122 | 0.99134
780 | feeder2_line143 | 3 | 99 | 8.4639e-07 | 1.7197e-06 | 8.5494e-07 | 1.7371e-06
780 | feeder2_line144 | 1 | 354.6 | 88.2202 | 88.2161 | 24.8788 | 24.8776
780 | feeder2_line144 | 2 | 354.6 | 96.3985 | 96.42 | 27.1851 | 27.1912
780 | feeder2_line144 | 3 | 354.6 | 92.7357 | 92.7202 | 26.1522 | 26.1478
780 | feeder2_line145 | 1 | 99 | 2.4814e-08 | 4.7985e-07 | 2.5065e-08 | 4.847e-07
780 | feeder2_line145 | 2 | 99 | 1.7285 | 1.7286 | 1.746 | 1.746
780 | feeder2_line145 | 3 | 99 | 2.4493e-08 | 4.8221e-07 | 2.474e-08 | 4.8708e-07
780 | feeder2_line146 | 1 | 354.6 | 88.2202 | 88.2161 | 24.8788 | 24.8776
780 | feeder2_line146 | 2 | 354.6 | 97.282 | 97.3037 | 27.4343 | 27.4404
780 | feeder2_line146 | 3 | 354.6 | 92.7356 | 92.7202 | 26.1522 | 26.1478
780 | feeder2_line147 | 1 | 99 | 10.8435 | 10.8435 | 10.953 | 10.953
780 | feeder2_line147 | 2 | 99 | 1.1326e-06 | 2.2006e-06 | 1.1441e-06 | 2.2228e-06
780 | feeder2_line147 | 3 | 99 | 1.1449e-06 | 2.2241e-06 | 1.1565e-06 | 2.2466e-06
780 | feeder2_line148 | 1 | 99 | 0.085698 | 0.0857 | 0.086564 | 0.086565
780 | feeder2_line148 | 2 | 99 | 5.9134e-07 | 1.4746e-06 | 5.9731e-07 | 1.4895e-06
780 | feeder2_line148 | 3 | 99 | 5.9697e-07 | 1.4904e-06 | 6.03e-07 | 1.5054e-06
780 | feeder2_line149 | 1 | 354.6 | 97.4467 | 97.4432 | 27.4807 | 27.4797
780 | feeder2_line149 | 2 | 354.6 | 97.2822 | 97.3037 | 27.4343 | 27.4404
780 | feeder2_line149 | 3 | 354.6 | 92.7358 | 92.7202 | 26.1522 | 26.1478
780 | feeder2_line150 | 1 | 354.6 | 97.4468 | 97.4432 | 27.4808 | 27.4797
780 | feeder2_line150 | 2 | 354.6 | 98.5334 | 98.5549 | 27.7872 | 27.7933
780 | feeder2_line150 | 3 | 354.6 | 92.7359 | 92.7202 | 26.1523 | 26.1478
780 | feeder2_line151 | 1 | 99 | 9.6568e-06 | 1.7615e-06 | 9.7543e-06 | 1.7793e-06
780 | feeder2_line151 | 2 | 99 | 2.3602 | 2.3603 | 2.3841 | 2.3841
780 | feeder2_line151 | 3 | 99 | 9.7414e-06 | 1.7701e-06 | 9.8398e-06 | 1.788e-06
780 | feeder2_line152 | 1 | 354.6 | 1.6816e-11 | 1.174e-06 | 4.7422e-12 | 3.3109e-07
780 | feeder2_line152 | 2 | 354.6 | 6.111e-12 | 1.1677e-06 | 1.7234e-12 | 3.2931e-07
780 | feeder2_line152 | 3 | 354.6 | 0.22625 | 0.22623 | 0.063805 | 0.063799
780 | feeder2_line153 | 1 | 99 | 0.071341 | 0.071341 | 0.072061 | 0.072061
780 | feeder2_line153 | 2 | 99 | 4.9971e-08 | 5.8403e-07 | 5.0476e-08 | 5.8993e-07
780 | feeder2_line153 | 3 | 99 | 4.9022e-08 | 5.9019e-07 | 4.9517e-08 | 5.9615e-07
780 | feeder2_line154 | 1 | 99 | 5.6993e-07 | 8.7402e-07 | 5.7569e-07 | 8.8285e-07
780 | feeder2_line154 | 2 | 99 | 5.6666e-07 | 8.6905e-07 | 5.7239e-07 | 8.7783e-07
780 | feeder2_line154 | 3 | 99 | 5.2811 | 5.2807 | 5.3345 | 5.3341
780 | feeder2_line155 | 1 | 99 | 97.5134 | 97.5098 | 98.4984 | 98.4948
780 | feeder2_line155 | 2 | 99 | 98.5334 | 98.5549 | 99.5287 | 99.5504
780 | feeder2_line155 | 3 | 99 | 97.0728 | 97.0566 | 98.0533 | 98.037
780 | feeder2_line156 | 1 | 99 | 5.9462e-07 | 1.1503e-06 | 6.0062e-07 | 1.1619e-06
780 | feeder2_line156 | 2 | 99 | 0.63175 | 0.6318 | 0.63813 | 0.63818
780 | feeder2_line156 | 3 | 99 | 5.9711e-07 | 1.1559e-06 | 6.0314e-07 | 1.1675e-06
780 | feeder2_line157 | 1 | 99 | 2.4834e-08 | 2.4971e-07 | 2.5085e-08 | 2.5223e-07
780 | feeder2_line157 | 2 | 99 | 1.8261 | 1.8261 | 1.8446 | 1.8446
780 | feeder2_line157 | 3 | 99 | 2.4503e-08 | 2.5093e-07 | 2.475e-08 | 2.5347e-07
810 | feeder2_line1 | 1 | 354.6 | 60.7497 | 60.7527 | 17.1319 | 17.1327
810 | feeder2_line1 | 2 | 354.6 | 42.114 | 42.1216 | 11.8765 | 11.8786
810 | feeder2_line1 | 3 | 354.6 | 73.1365 | 73.1281 | 20.6251 | 20.6227
810 | feeder2_line2 | 1 | 354.6 | 60.6537 | 60.6565 | 17.1048 | 17.1056
810 | feeder2_line2 | 2 | 354.6 | 42.1141 | 42.1216 | 11.8765 | 11.8786
810 | feeder2_line2 | 3 | 354.6 | 73.1367 | 73.1281 | 20.6251 | 20.6227
810 | feeder2_line3 | 1 | 80.1 | 1.3919 | 1.3919 | 1.7377 | 1.7377
810 | feeder2_line3 | 2 | 80.1 | 5.6923e-07 | 1.0519e-06 | 7.1065e-07 | 1.3133e-06
810 | feeder2_line3 | 3 | 80.1 | 5.7168e-07 | 1.0564e-06 | 7.1371e-07 | 1.3189e-06
810 | feeder2_line4 | 1 | 354.6 | 60.6538 | 60.6565 | 17.1049 | 17.1056
810 | feeder2_line4 | 2 | 354.6 | 42.3019 | 42.3095 | 11.9295 | 11.9316
810 | feeder2_line4 | 3 | 354.6 | 73.1368 | 73.1281 | 20.6252 | 20.6227
810 | feeder2_line5 | 1 | 80.1 | 5.7097e-07 | 9.9631e-07 | 7.1283e-07 | 1.2438e-06
810 | feeder2_line5 | 2 | 80.1 | 1.2158 | 1.2158 | 1.5178 | 1.5178
810 | feeder2_line5 | 3 | 80.1 | 5.7173e-07 | 9.9759e-07 | 7.1377e-07 | 1.2454e-06
810 | feeder2_line6 | 1 | 80.1 | 5.7101e-07 | 1.1721e-06 | 7.1287e-07 | 1.4633e-06
810 | feeder2_line6 | 2 | 80.1 | 5.6914e-07 | 1.1683e-06 | 7.1053e-07 | 1.4585e-06
810 | feeder2_line6 | 3 | 80.1 | 0.50288 | 0.50286 | 0.62781 | 0.62779
810 | feeder2_line7 | 1 | 354.6 | 60.6539 | 60.6565 | 17.1049 | 17.1056
810 | feeder2_line7 | 2 | 354.6 | 42.3019 | 42.3095 | 11.9295 | 11.9316
810 | feeder2_line7 | 3 | 354.6 | 73.5832 | 73.5744 | 20.751 | 20.7486
810 | feeder2_line8 | 1 | 80.1 | 0.072782 | 0.072783 | 0.090864 | 0.090865
810 | feeder2_line8 | 2 | 80.1 | 5.6897e-07 | 1.1262e-06 | 7.1033e-07 | 1.4059e-06
810 | feeder2_line8 | 3 | 80.1 | 5.7201e-07 | 1.1321e-06 | 7.1411e-07 | 1.4134e-06
810 | feeder2_line9 | 1 | 354.6 | 60.7128 | 60.7154 | 17.1215 | 17.1222
810 | feeder2_line9 | 2 | 354.6 | 42.3019 | 42.3095 | 11.9295 | 11.9316
810 | feeder2_line9 | 3 | 354.6 | 73.5832 | 73.5744 | 20.751 | 20.7486
810 | feeder2_line10 | 1 | 80.1 | 8.4422e-07 | 1.4925e-06 | 1.054e-06 | 1.8633e-06
810 | feeder2_line10 | 2 | 80.1 | 0.07315 | 0.07315 | 0.091323 | 0.091324
810 | feeder2_line10 | 3 | 80.1 | 8.4573e-07 | 1.4949e-06 | 1.0558e-06 | 1.8663e-06
810 | feeder2_line11 | 1 | 354.6 | 60.7129 | 60.7154 | 17.1215 | 17.1222
810 | feeder2_line11 | 2 | 354.6 | 42.331 | 42.3385 | 11.9377 | 11.9398
810 | feeder2_line11 | 3 | 354.6 | 73.5832 | 73.5744 | 20.7511 | 20.7486
810 | feeder2_line12 | 1 | 80.1 | 5.4628e-07 | 9.9007e-07 | 6.82e-07 | 1.236e-06
810 | feeder2_line12 | 2 | 80.1 | 5.4392e-07 | 9.8619e-07 | 6.7905e-07 | 1.2312e-06
810 | feeder2_line12 | 3 | 80.1 | 0.81866 | 0.81868 | 1.022 | 1.0221
810 | feeder2_line13 | 1 | 354.6 | 60.7129 | 60.7154 | 17.1215 | 17.1222
810 | feeder2_line13 | 2 | 354.6 | 42.3311 | 42.3385 | 11.9377 | 11.9398
810 | feeder2_line13 | 3 | 354.6 | 73.7401 | 73.7313 | 20.7953 | 20.7928
810 | feeder2_line14 | 1 | 80.1 | 0.086103 | 0.086105 | 0.10749 | 0.1075
810 | feeder2_line14 | 2 | 80.1 | 2.969e-07 | 6.4301e-07 | 3.7066e-07 | 8.0276e-07
810 | feeder2_line14 | 3 | 80.1 | 2.984e-07 | 6.4677e-07 | 3.7254e-07 | 8.0746e-07
810 | feeder2_line15 | 1 | 354.6 | 60.7823 | 60.7848 | 17.1411 | 17.1418
810 | feeder2_line15 | 2 | 354.6 | 42.3311 | 42.3385 | 11.9377 | 11.9398
810 | feeder2_line15 | 3 | 354.6 | 73.7402 | 73.7313 | 20.7953 | 20.7928
810 | feeder2_line16 | 1 | 80.1 | 5.7121e-07 | 1.0291e-06 | 7.1312e-07 | 1.2847e-06
810 | feeder2_line16 | 2 | 80.1 | 1.5959 | 1.5959 | 1.9924 | 1.9924
810 | feeder2_line16 | 3 | 80.1 | 5.7231e-07 | 1.031e-06 | 7.1449e-07 | 1.2871e-06
810 | feeder2_line17 | 1 | 354.6 | 60.7823 | 60.7848 | 17.1411 | 17.1418
810 | feeder2_line17 | 2 | 354.6 | 42.2186 | 42.2263 | 11.906 | 11.9081
810 | feeder2_line17 | 3 | 354.6 | 73.7402 | 73.7313 | 20.7953 | 20.7928
810 | feeder2_line18 | 1 | 80.1 | 5.4656e-07 | 7.3688e-07 | 6.8235e-07 | 9.1995e-07
810 | feeder2_line18 | 2 | 80.1 | 5.4331e-07 | 7.3295e-07 | 6.7829e-07 | 9.1505e-07
810 | feeder2_line18 | 3 | 80.1 | 0.0401 | 0.040078 | 0.050063 | 0.050035
810 | feeder2_line19 | 1 | 354.6 | 60.7823 | 60.7848 | 17.1411 | 17.1418
810 | feeder2_line19 | 2 | 354.6 | 42.2187 | 42.2263 | 11.906 | 11.9081
810 | feeder2_line19 | 3 | 354.6 | 73.7765 | 73.7675 | 20.8056 | 20.803
810 | feeder2_line20 | 1 | 99 | 5.4663e-07 | 8.836e-07 | 5.5216e-07 | 8.9253e-07
810 | feeder2_line20 | 2 | 99 | 5.4314e-07 | 8.7855e-07 | 5.4863e-07 | 8.8742e-07
810 | feeder2_line20 | 3 | 99 | 0.085819 | 0.085794 | 0.086686 | 0.086661
810 | feeder2_line21 | 1 | 354.6 | 60.7824 | 60.7848 | 17.1411 | 17.1418
810 | feeder2_line21 | 2 | 354.6 | 42.2187 | 42.2263 | 11.906 | 11.9081
810 | feeder2_line21 | 3 | 354.6 | 73.8561 | 73.847 | 20.828 | 20.8254
810 | feeder2_line22 | 1 | 99 | 5.7153e-07 | 1.013e-06 | 5.773e-07 | 1.0233e-06
810 | feeder2_line22 | 2 | 99 | 5.1262 | 5.1262 | 5.178 | 5.178
810 | feeder2_line22 | 3 | 99 | 5.7313e-07 | 1.0158e-06 | 5.7892e-07 | 1.0261e-06
810 | feeder2_line23 | 1 | 99 | 5.7154e-07 | 9.4828e-07 | 5.7731e-07 | 9.5786e-07
810 | feeder2_line23 | 2 | 99 | 5.6811e-07 | 9.4263e-07 | 5.7384e-07 | 9.5215e-07
810 | feeder2_line23 | 3 | 99 | 0.08171 | 0.081707 | 0.082535 | 0.082532
810 | feeder2_line24 | 1 | 354.6 | 60.7825 | 60.7848 | 17.1411 | 17.1418
810 | feeder2_line24 | 2 | 354.6 | 42.5244 | 42.5323 | 11.9922 | 11.9944
810 | feeder2_line24 | 3 | 354.6 | 73.9315 | 73.9224 | 20.8493 | 20.8467
810 | feeder2_line25 | 1 | 99 | 5.1152 | 5.1152 | 5.1669 | 5.1669
810 | feeder2_line25 | 2 | 99 | 5.0175e-08 | 6.8516e-07 | 5.0682e-08 | 6.9208e-07
810 | feeder2_line25 | 3 | 99 | 4.9036e-08 | 6.9155e-07 | 4.9531e-08 | 6.9853e-07
810 | feeder2_line26 | 1 | 99 | 0.085412 | 0.085415 | 0.086275 | 0.086277
810 | feeder2_line26 | 2 | 99 | 5.429e-07 | 8.4887e-07 | 5.4838e-07 | 8.5745e-07
810 | feeder2_line26 | 3 | 99 | 5.4882e-07 | 8.5679e-07 | 5.5437e-07 | 8.6545e-07
810 | feeder2_line27 | 1 | 354.6 | 63.463 | 63.4655 | 17.8971 | 17.8978
810 | feeder2_line27 | 2 | 354.6 | 42.5244 | 42.5323 | 11.9922 | 11.9944
810 | feeder2_line27 | 3 | 354.6 | 73.9315 | 73.9224 | 20.8493 | 20.8467
810 | feeder2_line28 | 1 | 99 | 2.5356e-06 | 7.0931e-07 | 2.5613e-06 | 7.1647e-07
810 | feeder2_line28 | 2 | 99 | 0.07794 | 0.077942 | 0.078727 | 0.078729
810 | feeder2_line28 | 3 | 99 | 2.5499e-06 | 7.1161e-07 | 2.5757e-06 | 7.188e-07
810 | feeder2_line29 | 1 | 354.6 | 63.463 | 63.4655 | 17.8971 | 17.8978
810 | feeder2_line29 | 2 | 354.6 | 42.5655 | 42.5733 | 12.0038 | 12.006
810 | feeder2_line29 | 3 | 354.6 | 73.9315 | 73.9224 | 20.8493 | 20.8467
810 | feeder2_line30 | 1 | 266.4 | 1.2599 | 1.2602 | 0.47295 | 0.47306
810 | feeder2_line30 | 2 | 266.4 | 10.5825 | 10.5821 | 3.9724 | 3.9723
810 | feeder2_line30 | 3 | 266.4 | 4.6251 | 4.6251 | 1.7362 | 1.7361
810 | feeder2_line31 | 1 | 354.6 | 63.7919 | 63.794 | 17.9898 | 17.9904
810 | feeder2_line31 | 2 | 354.6 | 48.4 | 48.4076 | 13.6492 | 13.6513
810 | feeder2_line31 | 3 | 354.6 | 76.741 | 76.7312 | 21.6416 | 21.6388
810 | feeder2_line32 | 1 | 354.6 | 63.792 | 63.794 | 17.9898 | 17.9904
810 | feeder2_line32 | 2 | 354.6 | 49.1637 | 49.1713 | 13.8645 | 13.8667
810 | feeder2_line32 | 3 | 354.6 | 76.741 | 76.7312 | 21.6416 | 21.6388
810 | feeder2_line33 | 1 | 99 | 4.9765e-08 | 6.8474e-07 | 5.0268e-08 | 6.9165e-07
810 | feeder2_line33 | 2 | 99 | 1.1696 | 1.1696 | 1.1814 | 1.1814
810 | feeder2_line33 | 3 | 99 | 4.8894e-08 | 6.8736e-07 | 4.9388e-08 | 6.943e-07
810 | feeder2_line34 | 1 | 354.6 | 63.7919 | 63.794 | 17.9898 | 17.9904
810 | feeder2_line34 | 2 | 354.6 | 49.1637 | 49.1713 | 13.8645 | 13.8667
810 | feeder2_line34 | 3 | 354.6 | 76.8201 | 76.8103 | 21.6639 | 21.6611
810 | feeder2_line35 | 1 | 99 | 2.9854e-07 | 7.5833e-07 | 3.0155e-07 | 7.6599e-07
810 | feeder2_line35 | 2 | 99 | 2.9627e-07 | 7.5195e-07 | 2.9926e-07 | 7.5955e-07
810 | feeder2_line35 | 3 | 99 | 0.0853 | 0.085291 | 0.086161 | 0.086153
810 | feeder2_line36 | 1 | 354.6 | 63.8581 | 63.8602 | 18.0085 | 18.0091
810 | feeder2_line36 | 2 | 354.6 | 49.1637 | 49.1713 | 13.8645 | 13.8667
810 | feeder2_line36 | 3 | 354.6 | 76.8201 | 76.8103 | 21.6639 | 21.6611
810 | feeder2_line37 | 1 | 99 | 2.4515 | 2.4517 | 2.4762 | 2.4765
810 | feeder2_line37 | 2 | 99 | 2.9626e-07 | 8.3194e-07 | 2.9925e-07 | 8.4034e-07
810 | feeder2_line37 | 3 | 99 | 2.9952e-07 | 8.4256e-07 | 3.0255e-07 | 8.5107e-07
810 | feeder2_line38 | 1 | 99 | 3.2332e-07 | 7.7408e-07 | 3.2659e-07 | 7.819e-07
810 | feeder2_line38 | 2 | 99 | 0.078188 | 0.078192 | 0.078978 | 0.078982
810 | feeder2_line38 | 3 | 99 | 3.2375e-07 | 7.7687e-07 | 3.2702e-07 | 7.8472e-07
810 | feeder2_line39 | 1 | 266.4 | 1.2599 | 1.2602 | 0.47295 | 0.47306
810 | feeder2_line39 | 2 | 266.4 | 10.5047 | 10.5043 | 3.9432 | 3.943
810 | feeder2_line39 | 3 | 266.4 | 4.6251 | 4.6251 | 1.7362 | 1.7361
810 | feeder2_line40 | 1 | 354.6 | 67.0089 | 67.0112 | 18.897 | 18.8977
810 | feeder2_line40 | 2 | 354.6 | 49.1637 | 49.1713 | 13.8645 | 13.8667
810 | feeder2_line40 | 3 | 354.6 | 76.8201 | 76.8103 | 21.6639 | 21.6611
810 | feeder2_line41 | 1 | 99 | 5.1136 | 5.1136 | 5.1652 | 5.1653
810 | feeder2_line41 | 2 | 99 | 5.0439e-08 | 7.2693e-07 | 5.0949e-08 | 7.3428e-07
810 | feeder2_line41 | 3 | 99 | 4.8854e-08 | 7.3633e-07 | 4.9347e-08 | 7.4377e-07
810 | feeder2_line42 | 1 | 99 | 2.9845e-07 | 7.4718e-07 | 3.0147e-07 | 7.5473e-07
810 | feeder2_line42 | 2 | 99 | 2.9627e-07 | 7.4115e-07 | 2.9926e-07 | 7.4863e-07
810 | feeder2_line42 | 3 | 99 | 0.52818 | 0.52818 | 0.53351 | 0.53352
810 | feeder2_line43 | 1 | 266.4 | 1.26 | 1.2602 | 0.47297 | 0.47306
810 | feeder2_line43 | 2 | 266.4 | 10.5046 | 10.5043 | 3.9432 | 3.943
810 | feeder2_line43 | 3 | 266.4 | 4.099 | 4.099 | 1.5387 | 1.5387
810 | feeder2_line44 | 1 | 354.6 | 67.0089 | 67.0112 | 18.897 | 18.8977
810 | feeder2_line44 | 2 | 354.6 | 49.1637 | 49.1713 | 13.8645 | 13.8667
810 | feeder2_line44 | 3 | 354.6 | 76.9009 | 76.891 | 21.6867 | 21.6839
810 | feeder2_line45 | 1 | 99 | 4.9781e-08 | 5.7836e-07 | 5.0284e-08 | 5.842e-07
810 | feeder2_line45 | 2 | 99 | 5.0458e-08 | 5.7325e-07 | 5.0968e-08 | 5.7904e-07
810 | feeder2_line45 | 3 | 99 | 0.085527 | 0.085486 | 0.086391 | 0.08635
810 | feeder2_line46 | 1 | 99 | 5.7203e-07 | 1.3545e-06 | 5.7781e-07 | 1.3682e-06
810 | feeder2_line46 | 2 | 99 | 5.6736e-07 | 1.3436e-06 | 5.7309e-07 | 1.3571e-06
810 | feeder2_line46 | 3 | 99 | 1.878 | 1.878 | 1.897 | 1.897
810 | feeder2_line47 | 1 | 266.4 | 1.2601 | 1.2602 | 0.47302 | 0.47306
810 | feeder2_line47 | 2 | 266.4 | 10.5046 | 10.5043 | 3.9432 | 3.943
810 | feeder2_line47 | 3 | 266.4 | 2.2882 | 2.288 | 0.85893 | 0.85886
810 | feeder2_line48 | 1 | 99 | 0.081943 | 0.081945 | 0.082771 | 0.082773
810 | feeder2_line48 | 2 | 99 | 5.0355e-08 | 7.2336e-07 | 5.0864e-08 | 7.3067e-07
810 | feeder2_line48 | 3 | 99 | 4.891e-08 | 7.3188e-07 | 4.9404e-08 | 7.3927e-07
810 | feeder2_line49 | 1 | 266.4 | 1.202 | 1.2021 | 0.4512 | 0.45126
810 | feeder2_line49 | 2 | 266.4 | 10.5046 | 10.5043 | 3.9432 | 3.943
810 | feeder2_line49 | 3 | 266.4 | 2.2882 | 2.288 | 0.85892 | 0.85886
810 | feeder2_line50 | 1 | 99 | 5.7204e-07 | 1.2327e-06 | 5.7782e-07 | 1.2452e-06
810 | feeder2_line50 | 2 | 99 | 0.50896 | 0.50901 | 0.5141 | 0.51415
810 | feeder2_line50 | 3 | 99 | 5.741e-07 | 1.2371e-06 | 5.799e-07 | 1.2496e-06
810 | feeder2_line51 | 1 | 99 | 0.20645 | 0.20654 | 0.20854 | 0.20863
810 | feeder2_line51 | 2 | 99 | 5.6732e-07 | 1.3273e-06 | 5.7305e-07 | 1.3407e-06
810 | feeder2_line51 | 3 | 99 | 5.741e-07 | 1.343e-06 | 5.799e-07 | 1.3566e-06
810 | feeder2_line52 | 1 | 266.4 | 1.0669 | 1.067 | 0.40049 | 0.40051
810 | feeder2_line52 | 2 | 266.4 | 9.9955 | 9.9953 | 3.7521 | 3.752
810 | feeder2_line52 | 3 | 266.4 | 2.288 | 2.288 | 0.85887 | 0.85886
810 | feeder2_line53 | 1 | 99 | 5.4716e-07 | 7.5234e-07 | 5.5269e-07 | 7.5994e-07
810 | feeder2_line53 | 2 | 99 | 9.9954 | 9.9953 | 10.0964 | 10.0963
810 | feeder2_line53 | 3 | 99 | 5.4964e-07 | 7.55e-07 | 5.5519e-07 | 7.6263e-07
810 | feeder2_line54 | 1 | 266.4 | 1.0669 | 1.067 | 0.40049 | 0.40051
810 | feeder2_line54 | 2 | 266.4 | 8.4756e-05 | 4.5785e-06 | 3.1815e-05 | 1.7186e-06
810 | feeder2_line54 | 3 | 266.4 | 2.2879 | 2.288 | 0.85883 | 0.85886
810 | feeder2_line55 | 1 | 99 | 0.045557 | 0.04556 | 0.046018 | 0.04602
810 | feeder2_line55 | 2 | 99 | 5.0515e-08 | 7.2204e-07 | 5.1026e-08 | 7.2934e-07
810 | feeder2_line55 | 3 | 99 | 4.8826e-08 | 7.3206e-07 | 4.9319e-08 | 7.3945e-07
810 | feeder2_line56 | 1 | 354.6 | 67.0499 | 67.0521 | 18.9086 | 18.9092
810 | feeder2_line56 | 2 | 354.6 | 49.1637 | 49.1713 | 13.8646 | 13.8667
810 | feeder2_line56 | 3 | 354.6 | 76.9009 | 76.891 | 21.6867 | 21.6839
810 | feeder2_line57 | 1 | 99 | 7.4616e-07 | 1.541e-06 | 7.537e-07 | 1.5566e-06
810 | feeder2_line57 | 2 | 99 | 7.5535e-07 | 1.5285e-06 | 7.6298e-07 | 1.5439e-06
810 | feeder2_line57 | 3 | 99 | 2.288 | 2.288 | 2.3111 | 2.3111
810 | feeder2_line58 | 1 | 266.4 | 1.067 | 1.067 | 0.40051 | 0.40051
810 | feeder2_line58 | 2 | 266.4 | 1.8715e-05 | 2.6584e-06 | 7.025e-06 | 9.9788e-07
810 | feeder2_line58 | 3 | 266.4 | 1.8986e-05 | 2.6882e-06 | 7.1268e-06 | 1.0091e-06
810 | feeder2_line59 | 1 | 99 | 4.9747e-08 | 5.3567e-07 | 5.025e-08 | 5.4108e-07
810 | feeder2_line59 | 2 | 99 | 5.0359e-08 | 5.313e-07 | 5.0868e-08 | 5.3667e-07
810 | feeder2_line59 | 3 | 99 | 1.6657 | 1.6657 | 1.6825 | 1.6825
810 | feeder2_line60 | 1 | 99 | 2.9845e-07 | 8.0957e-07 | 3.0146e-07 | 8.1775e-07
810 | feeder2_line60 | 2 | 99 | 2.9624e-07 | 8.0294e-07 | 2.9924e-07 | 8.1105e-07
810 | feeder2_line60 | 3 | 99 | 0.81991 | 0.81993 | 0.82819 | 0.82821
810 | feeder2_line61 | 1 | 266.4 | 2.0969 | 2.0971 | 0.78714 | 0.78721
810 | feeder2_line61 | 2 | 266.4 | 14.0308 | 14.0309 | 5.2668 | 5.2668
810 | feeder2_line61 | 3 | 266.4 | 6.4391 | 6.4392 | 2.4171 | 2.4171
810 | feeder2_line62 | 1 | 354.6 | 68.1542 | 68.1568 | 19.22 | 19.2207
810 | feeder2_line62 | 2 | 354.6 | 59.2052 | 59.2128 | 16.6963 | 16.6985
810 | feeder2_line62 | 3 | 354.6 | 81.8872 | 81.8774 | 23.0928 | 23.0901
810 | feeder2_line63 | 1 | 99 | 0.089272 | 0.089276 | 0.090174 | 0.090177
810 | feeder2_line63 | 2 | 99 | 5.6731e-07 | 1.2072e-06 | 5.7304e-07 | 1.2194e-06
810 | feeder2_line63 | 3 | 99 | 5.741e-07 | 1.2215e-06 | 5.799e-07 | 1.2338e-06
810 | feeder2_line64 | 1 | 99 | 1.0161 | 1.0161 | 1.0264 | 1.0264
810 | feeder2_line64 | 2 | 99 | 3.8869e-12 | 3.1801e-07 | 3.9262e-12 | 3.2122e-07
810 | feeder2_line64 | 3 | 99 | 6.0584e-12 | 3.2176e-07 | 6.1196e-12 | 3.2501e-07
810 | feeder2_line65 | 1 | 99 | 4.9801e-08 | 6.4055e-07 | 5.0305e-08 | 6.4702e-07
810 | feeder2_line65 | 2 | 99 | 1.2152 | 1.2152 | 1.2275 | 1.2275
810 | feeder2_line65 | 3 | 99 | 4.8789e-08 | 6.4352e-07 | 4.9282e-08 | 6.5002e-07
810 | feeder2_line66 | 1 | 354.6 | 68.1542 | 68.1568 | 19.22 | 19.2207
810 | feeder2_line66 | 2 | 354.6 | 60.0219 | 60.0295 | 16.9267 | 16.9288
810 | feeder2_line66 | 3 | 354.6 | 81.8872 | 81.8774 | 23.0928 | 23.0901
810 | feeder2_line67 | 1 | 99 | 2.489e-08 | 3.6204e-07 | 2.5141e-08 | 3.6569e-07
810 | feeder2_line67 | 2 | 99 | 2.5281e-08 | 3.5842e-07 | 2.5536e-08 | 3.6204e-07
810 | feeder2_line67 | 3 | 99 | 5.1025 | 5.1024 | 5.154 | 5.154
810 | feeder2_line68 | 1 | 266.4 | 2.097 | 2.0971 | 0.78716 | 0.78721
810 | feeder2_line68 | 2 | 266.4 | 14.0308 | 14.0309 | 5.2668 | 5.2668
810 | feeder2_line68 | 3 | 266.4 | 1.4163 | 1.4164 | 0.53165 | 0.53169
810 | feeder2_line69 | 1 | 99 | 11.4103 | 11.4101 | 11.5255 | 11.5254
810 | feeder2_line69 | 2 | 99 | 2.5061e-06 | 6.5818e-07 | 2.5314e-06 | 6.6483e-07
810 | feeder2_line69 | 3 | 99 | 2.5616e-06 | 6.6817e-07 | 2.5875e-06 | 6.7492e-07
810 | feeder2_line70 | 1 | 354.6 | 78.4493 | 78.4521 | 22.1233 | 22.1241
810 | feeder2_line70 | 2 | 354.6 | 60.0219 | 60.0295 | 16.9266 | 16.9288
810 | feeder2_line70 | 3 | 354.6 | 81.8871 | 81.8774 | 23.0928 | 23.0901
810 | feeder2_line71 | 1 | 99 | 4.9807e-08 | 7.1478e-07 | 5.031e-08 | 7.22e-07
810 | feeder2_line71 | 2 | 99 | 0.88102 | 0.88108 | 0.88992 | 0.88998
810 | feeder2_line71 | 3 | 99 | 4.8782e-08 | 7.1815e-07 | 4.9275e-08 | 7.254e-07
810 | feeder2_line72 | 1 | 354.6 | 78.4494 | 78.4521 | 22.1234 | 22.1241
810 | feeder2_line72 | 2 | 354.6 | 60.7133 | 60.7209 | 17.1216 | 17.1238
810 | feeder2_line72 | 3 | 354.6 | 81.8872 | 81.8774 | 23.0928 | 23.0901
810 | feeder2_line73 | 1 | 99 | 5.9763e-07 | 1.5327e-06 | 6.0366e-07 | 1.5482e-06
810 | feeder2_line73 | 2 | 99 | 1.1687 | 1.1687 | 1.1806 | 1.1806
810 | feeder2_line73 | 3 | 99 | 5.9972e-07 | 1.5395e-06 | 6.0577e-07 | 1.555e-06
810 | feeder2_line74 | 1 | 99 | 4.978e-08 | 4.5714e-07 | 5.0283e-08 | 4.6176e-07
810 | feeder2_line74 | 2 | 99 | 1.4212 | 1.4212 | 1.4356 | 1.4356
810 | feeder2_line74 | 3 | 99 | 4.879e-08 | 4.5916e-07 | 4.9283e-08 | 4.6379e-07
810 | feeder2_line75 | 1 | 266.4 | 2.0971 | 2.0971 | 0.7872 | 0.78722
810 | feeder2_line75 | 2 | 266.4 | 11.4413 | 11.4412 | 4.2948 | 4.2947
810 | feeder2_line75 | 3 | 266.4 | 1.4164 | 1.4164 | 0.53169 | 0.53169
810 | feeder2_line76 | 1 | 99 | 2.0971 | 2.0971 | 2.1183 | 2.1183
810 | feeder2_line76 | 2 | 99 | 8.3766e-07 | 1.565e-06 | 8.4612e-07 | 1.5808e-06
810 | feeder2_line76 | 3 | 99 | 8.5079e-07 | 1.5881e-06 | 8.5939e-07 | 1.6041e-06
810 | feeder2_line77 | 1 | 99 | 2.4892e-08 | 5.7447e-07 | 2.5144e-08 | 5.8027e-07
810 | feeder2_line77 | 2 | 99 | 2.5295e-08 | 5.6862e-07 | 2.5551e-08 | 5.7436e-07
810 | feeder2_line77 | 3 | 99 | 1.4165 | 1.4164 | 1.4308 | 1.4307
810 | feeder2_line78 | 1 | 266.4 | 7.391e-12 | 9.527e-07 | 2.7744e-12 | 3.5762e-07
810 | feeder2_line78 | 2 | 266.4 | 11.4413 | 11.4412 | 4.2948 | 4.2947
810 | feeder2_line78 | 3 | 266.4 | 8.8838e-12 | 9.5617e-07 | 3.3347e-12 | 3.5892e-07
810 | feeder2_line79 | 1 | 354.6 | 10.1434 | 10.143 | 2.8605 | 2.8604
810 | feeder2_line79 | 2 | 354.6 | 7.2614 | 7.2612 | 2.0478 | 2.0477
810 | feeder2_line79 | 3 | 354.6 | 12.0386 | 12.0383 | 3.395 | 3.3949
810 | feeder2_line80 | 1 | 354.6 | 86.5516 | 86.5539 | 24.4082 | 24.4089
810 | feeder2_line80 | 2 | 354.6 | 63.96 | 63.9671 | 18.0372 | 18.0392
810 | feeder2_line80 | 3 | 354.6 | 93.2109 | 93.2006 | 26.2862 | 26.2833
810 | feeder2_line81 | 1 | 354.6 | 86.5515 | 86.5539 | 24.4082 | 24.4089
810 | feeder2_line81 | 2 | 354.6 | 63.9599 | 63.9671 | 18.0372 | 18.0392
810 | feeder2_line81 | 3 | 354.6 | 94.5992 | 94.589 | 26.6777 | 26.6748
810 | feeder2_line82 | 1 | 354.6 | 1.7898e-11 | 7.3341e-07 | 5.0474e-12 | 2.0683e-07
810 | feeder2_line82 | 2 | 354.6 | 1.6736e-11 | 7.2575e-07 | 4.7198e-12 | 2.0467e-07
810 | feeder2_line82 | 3 | 354.6 | 1.9195 | 1.9195 | 0.54131 | 0.5413
810 | feeder2_line83 | 1 | 354.6 | 86.5517 | 86.5539 | 24.4083 | 24.4089
810 | feeder2_line83 | 2 | 354.6 | 64.1327 | 64.1397 | 18.0859 | 18.0879
810 | feeder2_line83 | 3 | 354.6 | 94.5994 | 94.589 | 26.6778 | 26.6748
810 | feeder2_line84 | 1 | 354.6 | 8.1907e-12 | 1.2964e-06 | 2.3098e-12 | 3.6559e-07
810 | feeder2_line84 | 2 | 354.6 | 1.3273 | 1.3273 | 0.37432 | 0.37432
810 | feeder2_line84 | 3 | 354.6 | 1.82e-11 | 1.3018e-06 | 5.1326e-12 | 3.6711e-07
810 | feeder2_line85 | 1 | 99 | 0.07719 | 0.077194 | 0.07797 | 0.077974
810 | feeder2_line85 | 2 | 99 | 5.0746e-08 | 4.5746e-07 | 5.1258e-08 | 4.6208e-07
810 | feeder2_line85 | 3 | 99 | 4.8767e-08 | 4.6496e-07 | 4.9259e-08 | 4.6966e-07
810 | feeder2_line86 | 1 | 354.6 | 86.6267 | 86.6288 | 24.4294 | 24.43
810 | feeder2_line86 | 2 | 354.6 | 64.1328 | 64.1397 | 18.086 | 18.0879
810 | feeder2_line86 | 3 | 354.6 | 94.5995 | 94.589 | 26.6778 | 26.6748
810 | feeder2_line87 | 1 | 354.6 | 86.6269 | 86.6288 | 24.4295 | 24.43
810 | feeder2_line87 | 2 | 354.6 | 75.556 | 75.5625 | 21.3074 | 21.3092
810 | feeder2_line87 | 3 | 354.6 | 95.0596 | 95.0488 | 26.8076 | 26.8045
810 | feeder2_line88 | 1 | 354.6 | 0.00011181 | 3.361e-06 | 3.153e-05 | 9.4782e-07
810 | feeder2_line88 | 2 | 354.6 | 13.4131 | 13.413 | 3.7826 | 3.7826
810 | feeder2_line88 | 3 | 354.6 | 1.3344 | 1.3344 | 0.37631 | 0.3763
810 | feeder2_line89 | 1 | 354.6 | 86.6246 | 86.6288 | 24.4288 | 24.43
810 | feeder2_line89 | 2 | 354.6 | 82.448 | 82.4565 | 23.251 | 23.2534
810 | feeder2_line89 | 3 | 354.6 | 95.0573 | 95.0488 | 26.8069 | 26.8045
810 | feeder2_line90 | 1 | 354.6 | 0.00072254 | 2.0291e-06 | 0.00020376 | 5.7223e-07
810 | feeder2_line90 | 2 | 354.6 | 8.3736 | 8.374 | 2.3614 | 2.3615
810 | feeder2_line90 | 3 | 354.6 | 0.00073162 | 2.0388e-06 | 0.00020632 | 5.7496e-07
810 | feeder2_line91 | 1 | 354.6 | 86.6246 | 86.6288 | 24.4288 | 24.43
810 | feeder2_line91 | 2 | 354.6 | 82.448 | 82.4565 | 23.251 | 23.2534
810 | feeder2_line91 | 3 | 354.6 | 95.3581 | 95.3496 | 26.8917 | 26.8893
810 | feeder2_line92 | 1 | 354.6 | 1.8596e-11 | 1.0235e-06 | 5.2442e-12 | 2.8863e-07
810 | feeder2_line92 | 2 | 354.6 | 2.8285e-12 | 1.0121e-06 | 7.9766e-13 | 2.8543e-07
810 | feeder2_line92 | 3 | 354.6 | 0.82146 | 0.82149 | 0.23166 | 0.23167
810 | feeder2_line93 | 1 | 99 | 2.4925e-08 | 3.4166e-07 | 2.5177e-08 | 3.4511e-07
810 | feeder2_line93 | 2 | 99 | 1.3273 | 1.3273 | 1.3407 | 1.3407
810 | feeder2_line93 | 3 | 99 | 2.438e-08 | 3.4334e-07 | 2.4626e-08 | 3.468e-07
810 | feeder2_line94 | 1 | 354.6 | 2.4919e-06 | 1.6633e-06 | 7.0273e-07 | 4.6907e-07
810 | feeder2_line94 | 2 | 354.6 | 7.4025 | 7.4024 | 2.0876 | 2.0875
810 | feeder2_line94 | 3 | 354.6 | 2.4376e-06 | 1.6704e-06 | 6.8743e-07 | 4.7107e-07
810 | feeder2_line95 | 1 | 99 | 3.5721e-06 | 2.6062e-06 | 3.6081e-06 | 2.6325e-06
810 | feeder2_line95 | 2 | 99 | 13.413 | 13.413 | 13.5485 | 13.5485
810 | feeder2_line95 | 3 | 99 | 3.5844e-06 | 2.6188e-06 | 3.6206e-06 | 2.6452e-06
810 | feeder2_line96 | 1 | 354.6 | 0.0001209 | 6.2111e-07 | 3.4095e-05 | 1.7516e-07
810 | feeder2_line96 | 2 | 354.6 | 0.00011942 | 6.1425e-07 | 3.3677e-05 | 1.7322e-07
810 | feeder2_line96 | 3 | 354.6 | 1.3344 | 1.3344 | 0.3763 | 0.3763
810 | feeder2_line97 | 1 | 354.6 | 87.4331 | 87.4371 | 24.6568 | 24.6579
810 | feeder2_line97 | 2 | 354.6 | 82.4482 | 82.4565 | 23.251 | 23.2534
810 | feeder2_line97 | 3 | 354.6 | 95.3584 | 95.3496 | 26.8918 | 26.8893
810 | feeder2_line98 | 1 | 354.6 | 0.85165 | 0.84999 | 0.24017 | 0.2397
810 | feeder2_line98 | 2 | 354.6 | 0.0016723 | 6.0942e-07 | 0.00047159 | 1.7186e-07
810 | feeder2_line98 | 3 | 354.6 | 0.0017337 | 6.2401e-07 | 0.00048892 | 1.7598e-07
810 | feeder2_line99 | 1 | 99 | 2.4911e-08 | 4.4663e-07 | 2.5162e-08 | 4.5114e-07
810 | feeder2_line99 | 2 | 99 | 2.5389e-08 | 4.4142e-07 | 2.5645e-08 | 4.4588e-07
810 | feeder2_line99 | 3 | 99 | 1.3344 | 1.3344 | 1.3479 | 1.3479
810 | feeder2_line100 | 1 | 99 | 0.84999 | 0.84999 | 0.85858 | 0.85858
810 | feeder2_line100 | 2 | 99 | 2.5418e-08 | 6.0607e-07 | 2.5675e-08 | 6.1219e-07
810 | feeder2_line100 | 3 | 99 | 2.4382e-08 | 6.1643e-07 | 2.4628e-08 | 6.2266e-07
810 | feeder2_line101 | 1 | 354.6 | 7.4833 | 7.4828 | 2.1103 | 2.1102
810 | feeder2_line101 | 2 | 354.6 | 7.2614 | 7.2612 | 2.0478 | 2.0477
810 | feeder2_line101 | 3 | 354.6 | 12.0385 | 12.0383 | 3.395 | 3.3949
810 | feeder2_line102 | 1 | 99 | 3.1269 | 3.1269 | 3.1585 | 3.1585
810 | feeder2_line102 | 2 | 99 | 2.2959e-06 | 8.6716e-07 | 2.3191e-06 | 8.7591e-07
810 | feeder2_line102 | 3 | 99 | 2.3615e-06 | 8.8085e-07 | 2.3853e-06 | 8.8974e-07
810 | feeder2_line103 | 1 | 99 | 5.4841e-07 | 8.0248e-07 | 5.5395e-07 | 8.1059e-07
810 | feeder2_line103 | 2 | 99 | 1.7712 | 1.7712 | 1.789 | 1.7891
810 | feeder2_line103 | 3 | 99 | 5.5162e-07 | 8.0621e-07 | 5.5719e-07 | 8.1435e-07
810 | feeder2_line104 | 1 | 354.6 | 7.4832 | 7.4828 | 2.1103 | 2.1102
810 | feeder2_line104 | 2 | 354.6 | 5.5001 | 5.4999 | 1.5511 | 1.551
810 | feeder2_line104 | 3 | 354.6 | 12.0384 | 12.0383 | 3.3949 | 3.3949
810 | feeder2_line105 | 1 | 99 | 2.543e-06 | 7.3838e-07 | 2.5687e-06 | 7.4584e-07
810 | feeder2_line105 | 2 | 99 | 2.5054e-06 | 7.303e-07 | 2.5307e-06 | 7.3767e-07
810 | feeder2_line105 | 3 | 99 | 0.039806 | 0.039755 | 0.040208 | 0.040157
810 | feeder2_line106 | 1 | 354.6 | 7.4831 | 7.4828 | 2.1103 | 2.1102
810 | feeder2_line106 | 2 | 354.6 | 5.5 | 5.4999 | 1.551 | 1.551
810 | feeder2_line106 | 3 | 354.6 | 11.9986 | 11.9985 | 3.3837 | 3.3837
810 | feeder2_line107 | 1 | 99 | 3.2396e-07 | 8.998e-07 | 3.2723e-07 | 9.0889e-07
810 | feeder2_line107 | 2 | 99 | 1.9035 | 1.9036 | 1.9228 | 1.9228
810 | feeder2_line107 | 3 | 99 | 3.2455e-07 | 9.0389e-07 | 3.2783e-07 | 9.1302e-07
810 | feeder2_line108 | 1 | 354.6 | 7.4831 | 7.4828 | 2.1103 | 2.1102
810 | feeder2_line108 | 2 | 354.6 | 3.7997 | 3.7995 | 1.0715 | 1.0715
810 | feeder2_line108 | 3 | 354.6 | 11.9986 | 11.9985 | 3.3837 | 3.3837
810 | feeder2_line109 | 1 | 354.6 | 89.1455 | 89.1484 | 25.1397 | 25.1405
810 | feeder2_line109 | 2 | 354.6 | 82.4492 | 82.4565 | 23.2513 | 23.2534
810 | feeder2_line109 | 3 | 354.6 | 95.3595 | 95.3496 | 26.8921 | 26.8893
810 | feeder2_line110 | 1 | 99 | 1.863 | 1.8622 | 1.8818 | 1.881
810 | feeder2_line110 | 2 | 99 | 0.00078976 | 8.9756e-07 | 0.00079773 | 9.0662e-07
810 | feeder2_line110 | 3 | 99 | 0.00081146 | 9.1264e-07 | 0.00081965 | 9.2186e-07
810 | feeder2_line111 | 1 | 99 | 2.4908e-08 | 3.8144e-07 | 2.5159e-08 | 3.853e-07
810 | feeder2_line111 | 2 | 99 | 1.7933 | 1.7933 | 1.8114 | 1.8114
810 | feeder2_line111 | 3 | 99 | 2.4369e-08 | 3.8329e-07 | 2.4615e-08 | 3.8716e-07
810 | feeder2_line112 | 1 | 99 | 3.2419e-07 | 9.1663e-07 | 3.2747e-07 | 9.2589e-07
810 | feeder2_line112 | 2 | 99 | 11.785 | 11.7849 | 11.904 | 11.9039
810 | feeder2_line112 | 3 | 99 | 3.2481e-07 | 9.2105e-07 | 3.2809e-07 | 9.3035e-07
810 | feeder2_line113 | 1 | 99 | 0.09752 | 0.097523 | 0.098505 | 0.098508
810 | feeder2_line113 | 2 | 99 | 3.2179e-07 | 8.9374e-07 | 3.2504e-07 | 9.0277e-07
810 | feeder2_line113 | 3 | 99 | 3.2518e-07 | 9.0916e-07 | 3.2846e-07 | 9.1835e-07
810 | feeder2_line114 | 1 | 99 | 1.7634 | 1.7634 | 1.7812 | 1.7812
810 | feeder2_line114 | 2 | 99 | 2.5341e-08 | 4.312e-07 | 2.5597e-08 | 4.3556e-07
810 | feeder2_line114 | 3 | 99 | 2.4387e-08 | 4.3801e-07 | 2.4633e-08 | 4.4243e-07
810 | feeder2_line115 | 1 | 99 | 2.489e-08 | 5.615e-07 | 2.5142e-08 | 5.6717e-07
810 | feeder2_line115 | 2 | 99 | 0.8165 | 0.81651 | 0.82475 | 0.82475
810 | feeder2_line115 | 3 | 99 | 2.4398e-08 | 5.6401e-07 | 2.4644e-08 | 5.697e-07
810 | feeder2_line116 | 1 | 354.6 | 7.4831 | 7.4828 | 2.1103 | 2.1102
810 | feeder2_line116 | 2 | 354.6 | 3.3277 | 3.3275 | 0.93843 | 0.93839
810 | feeder2_line116 | 3 | 354.6 | 11.9986 | 11.9985 | 3.3837 | 3.3837
810 | feeder2_line117 | 1 | 99 | 4.9886e-08 | 6.4233e-07 | 5.039e-08 | 6.4882e-07
810 | feeder2_line117 | 2 | 99 | 1.8833 | 1.8833 | 1.9023 | 1.9024
810 | feeder2_line117 | 3 | 99 | 4.8775e-08 | 6.4565e-07 | 4.9267e-08 | 6.5217e-07
810 | feeder2_line118 | 1 | 354.6 | 89.1455 | 89.1484 | 25.1397 | 25.1405
810 | feeder2_line118 | 2 | 354.6 | 83.4228 | 83.43 | 23.5259 | 23.5279
810 | feeder2_line118 | 3 | 354.6 | 95.3595 | 95.3496 | 26.8921 | 26.8893
810 | feeder2_line119 | 1 | 99 | 2.4881e-08 | 6.0417e-07 | 2.5132e-08 | 6.1027e-07
810 | feeder2_line119 | 2 | 99 | 2.533e-08 | 5.9763e-07 | 2.5586e-08 | 6.0367e-07
810 | feeder2_line119 | 3 | 99 | 0.093156 | 0.093134 | 0.094097 | 0.094075
810 | feeder2_line120 | 1 | 354.6 | 7.4831 | 7.4828 | 2.1103 | 2.1102
810 | feeder2_line120 | 2 | 354.6 | 3.3277 | 3.3275 | 0.93842 | 0.93839
810 | feeder2_line120 | 3 | 354.6 | 11.9056 | 11.9055 | 3.3575 | 3.3575
810 | feeder2_line121 | 1 | 99 | 3.239e-07 | 9.3552e-07 | 3.2717e-07 | 9.4497e-07
810 | feeder2_line121 | 2 | 99 | 2.1435 | 2.1435 | 2.1651 | 2.1651
810 | feeder2_line121 | 3 | 99 | 3.2446e-07 | 9.3954e-07 | 3.2774e-07 | 9.4903e-07
810 | feeder2_line122 | 1 | 354.6 | 7.4831 | 7.4828 | 2.1103 | 2.1102
810 | feeder2_line122 | 2 | 354.6 | 1.1858 | 1.1857 | 0.3344 | 0.33438
810 | feeder2_line122 | 3 | 354.6 | 11.9056 | 11.9055 | 3.3575 | 3.3575
810 | feeder2_line123 | 1 | 99 | 5.7318e-07 | 9.694e-07 | 5.7896e-07 | 9.7919e-07
810 | feeder2_line123 | 2 | 99 | 5.6698e-07 | 9.5901e-07 | 5.7271e-07 | 9.687e-07
810 | feeder2_line123 | 3 | 99 | 0.076552 | 0.076546 | 0.077325 | 0.077319
810 | feeder2_line124 | 1 | 354.6 | 7.483 | 7.4828 | 2.1103 | 2.1102
810 | feeder2_line124 | 2 | 354.6 | 1.1858 | 1.1857 | 0.33441 | 0.33438
810 | feeder2_line124 | 3 | 354.6 | 11.8291 | 11.8292 | 3.3359 | 3.3359
810 | feeder2_line125 | 1 | 99 | 5.7317e-07 | 9.0114e-07 | 5.7896e-07 | 9.1024e-07
810 | feeder2_line125 | 2 | 99 | 5.6699e-07 | 8.9151e-07 | 5.7271e-07 | 9.0052e-07
810 | feeder2_line125 | 3 | 99 | 0.84489 | 0.84482 | 0.85342 | 0.85335
810 | feeder2_line126 | 1 | 354.6 | 7.4832 | 7.4828 | 2.1103 | 2.1102
810 | feeder2_line126 | 2 | 354.6 | 1.186 | 1.1857 | 0.33445 | 0.33438
810 | feeder2_line126 | 3 | 354.6 | 10.9846 | 10.9845 | 3.0977 | 3.0977
810 | feeder2_line127 | 1 | 99 | 5.7315e-07 | 1.0788e-06 | 5.7894e-07 | 1.0897e-06
810 | feeder2_line127 | 2 | 99 | 5.67e-07 | 1.0673e-06 | 5.7273e-07 | 1.0781e-06
810 | feeder2_line127 | 3 | 99 | 0.076714 | 0.076704 | 0.077489 | 0.077478
810 | feeder2_line128 | 1 | 354.6 | 7.4831 | 7.4828 | 2.1103 | 2.1102
810 | feeder2_line128 | 2 | 354.6 | 1.1859 | 1.1857 | 0.33444 | 0.33438
810 | feeder2_line128 | 3 | 354.6 | 10.9081 | 10.9081 | 3.0762 | 3.0762
810 | feeder2_line129 | 1 | 99 | 5.4827e-07 | 8.7471e-07 | 5.5381e-07 | 8.8355e-07
810 | feeder2_line129 | 2 | 99 | 1.1857 | 1.1857 | 1.1977 | 1.1977
810 | feeder2_line129 | 3 | 99 | 5.5117e-07 | 8.7837e-07 | 5.5673e-07 | 8.8724e-07
810 | feeder2_line130 | 1 | 354.6 | 7.4831 | 7.4828 | 2.1103 | 2.1102
810 | feeder2_line130 | 2 | 354.6 | 0.0003046 | 4.5817e-06 | 8.5899e-05 | 1.2921e-06
810 | feeder2_line130 | 3 | 354.6 | 10.9081 | 10.9081 | 3.0762 | 3.0762
810 | feeder2_line131 | 1 | 99 | 5.731e-07 | 9.6943e-07 | 5.7889e-07 | 9.7922e-07
810 | feeder2_line131 | 2 | 99 | 5.6701e-07 | 9.5921e-07 | 5.7274e-07 | 9.689e-07
810 | feeder2_line131 | 3 | 99 | 10.8315 | 10.8318 | 10.9409 | 10.9412
810 | feeder2_line132 | 1 | 354.6 | 7.4829 | 7.4828 | 2.1103 | 2.1102
810 | feeder2_line132 | 2 | 354.6 | 0.00012373 | 2.881e-06 | 3.4892e-05 | 8.1245e-07
810 | feeder2_line132 | 3 | 354.6 | 0.076792 | 0.076712 | 0.021656 | 0.021633
810 | feeder2_line133 | 1 | 99 | 7.4829 | 7.4828 | 7.5584 | 7.5584
810 | feeder2_line133 | 2 | 99 | 2.9616e-07 | 9.6688e-07 | 2.9915e-07 | 9.7665e-07
810 | feeder2_line133 | 3 | 99 | 2.9997e-07 | 9.8124e-07 | 3.03e-07 | 9.9115e-07
810 | feeder2_line134 | 1 | 354.6 | 6.9057e-12 | 1.7819e-06 | 1.9475e-12 | 5.0251e-07
810 | feeder2_line134 | 2 | 354.6 | 7.4693e-12 | 1.7644e-06 | 2.1064e-12 | 4.9758e-07
810 | feeder2_line134 | 3 | 354.6 | 0.076722 | 0.076712 | 0.021636 | 0.021633
810 | feeder2_line135 | 1 | 99 | 0.872 | 0.87199 | 0.88081 | 0.8808
810 | feeder2_line135 | 2 | 99 | 5.0915e-08 | 5.7832e-07 | 5.1429e-08 | 5.8416e-07
810 | feeder2_line135 | 3 | 99 | 4.8782e-08 | 5.8856e-07 | 4.9274e-08 | 5.9451e-07
810 | feeder2_line136 | 1 | 354.6 | 89.9732 | 89.9761 | 25.3732 | 25.374
810 | feeder2_line136 | 2 | 354.6 | 83.4227 | 83.43 | 23.5259 | 23.5279
810 | feeder2_line136 | 3 | 354.6 | 95.3595 | 95.3496 | 26.8921 | 26.8893
810 | feeder2_line137 | 1 | 99 | 4.5159 | 4.5158 | 4.5615 | 4.5615
810 | feeder2_line137 | 2 | 99 | 8.388e-07 | 1.5577e-06 | 8.4727e-07 | 1.5734e-06
810 | feeder2_line137 | 3 | 99 | 8.5466e-07 | 1.5854e-06 | 8.6329e-07 | 1.6014e-06
810 | feeder2_line138 | 1 | 354.6 | 94.2737 | 94.2765 | 26.5859 | 26.5867
810 | feeder2_line138 | 2 | 354.6 | 83.4228 | 83.43 | 23.5259 | 23.5279
810 | feeder2_line138 | 3 | 354.6 | 95.3596 | 95.3496 | 26.8922 | 26.8893
810 | feeder2_line139 | 1 | 99 | 4.993e-08 | 4.9143e-07 | 5.0435e-08 | 4.9639e-07
810 | feeder2_line139 | 2 | 99 | 5.0943e-08 | 4.8537e-07 | 5.1457e-08 | 4.9028e-07
810 | feeder2_line139 | 3 | 99 | 1.0545 | 1.0541 | 1.0651 | 1.0647
810 | feeder2_line140 | 1 | 354.6 | 94.2738 | 94.2765 | 26.5859 | 26.5867
810 | feeder2_line140 | 2 | 354.6 | 83.4229 | 83.43 | 23.5259 | 23.5279
810 | feeder2_line140 | 3 | 354.6 | 95.855 | 95.8444 | 27.0319 | 27.0289
810 | feeder2_line141 | 1 | 99 | 2.5257e-06 | 4.8617e-07 | 2.5512e-06 | 4.9108e-07
810 | feeder2_line141 | 2 | 99 | 0.53234 | 0.53236 | 0.53772 | 0.53774
810 | feeder2_line141 | 3 | 99 | 2.5491e-06 | 4.8875e-07 | 2.5748e-06 | 4.9368e-07
810 | feeder2_line142 | 1 | 354.6 | 94.2736 | 94.2765 | 26.5859 | 26.5867
810 | feeder2_line142 | 2 | 354.6 | 83.8193 | 83.8266 | 23.6377 | 23.6397
810 | feeder2_line142 | 3 | 354.6 | 95.8549 | 95.8444 | 27.0318 | 27.0289
810 | feeder2_line143 | 1 | 99 | 8.5007e-07 | 1.7276e-06 | 8.5865e-07 | 1.7451e-06
810 | feeder2_line143 | 2 | 99 | 1.9043 | 1.9043 | 1.9235 | 1.9236
810 | feeder2_line143 | 3 | 99 | 8.5502e-07 | 1.7368e-06 | 8.6365e-07 | 1.7543e-06
810 | feeder2_line144 | 1 | 354.6 | 94.2734 | 94.2765 | 26.5858 | 26.5867
810 | feeder2_line144 | 2 | 354.6 | 85.5485 | 85.556 | 24.1254 | 24.1275
810 | feeder2_line144 | 3 | 354.6 | 95.8547 | 95.8444 | 27.0318 | 27.0289
810 | feeder2_line145 | 1 | 99 | 2.4963e-08 | 4.8444e-07 | 2.5215e-08 | 4.8933e-07
810 | feeder2_line145 | 2 | 99 | 1.9297 | 1.9297 | 1.9492 | 1.9492
810 | feeder2_line145 | 3 | 99 | 2.4396e-08 | 4.8702e-07 | 2.4642e-08 | 4.9194e-07
810 | feeder2_line146 | 1 | 354.6 | 94.2733 | 94.2765 | 26.5858 | 26.5867
810 | feeder2_line146 | 2 | 354.6 | 86.9384 | 86.946 | 24.5173 | 24.5195
810 | feeder2_line146 | 3 | 354.6 | 95.8546 | 95.8444 | 27.0318 | 27.0289
810 | feeder2_line147 | 1 | 99 | 1.7652 | 1.7652 | 1.7831 | 1.7831
810 | feeder2_line147 | 2 | 99 | 1.1358e-06 | 2.2067e-06 | 1.1472e-06 | 2.229e-06
810 | feeder2_line147 | 3 | 99 | 1.1565e-06 | 2.2465e-06 | 1.1682e-06 | 2.2692e-06
810 | feeder2_line148 | 1 | 99 | 0.084911 | 0.084916 | 0.085768 | 0.085774
810 | feeder2_line148 | 2 | 99 | 5.9338e-07 | 1.4787e-06 | 5.9937e-07 | 1.4936e-06
810 | feeder2_line148 | 3 | 99 | 6.0263e-07 | 1.5053e-06 | 6.0872e-07 | 1.5205e-06
810 | feeder2_line149 | 1 | 354.6 | 95.9934 | 95.9964 | 27.0709 | 27.0718
810 | feeder2_line149 | 2 | 354.6 | 86.9386 | 86.946 | 24.5174 | 24.5195
810 | feeder2_line149 | 3 | 354.6 | 95.8548 | 95.8444 | 27.0318 | 27.0289
810 | feeder2_line150 | 1 | 354.6 | 95.9935 | 95.9964 | 27.0709 | 27.0718
810 | feeder2_line150 | 2 | 354.6 | 99.0001 | 99.007 | 27.9188 | 27.9208
810 | feeder2_line150 | 3 | 354.6 | 95.8549 | 95.8444 | 27.0318 | 27.0289
810 | feeder2_line151 | 1 | 99 | 9.7532e-06 | 1.7787e-06 | 9.8518e-06 | 1.7967e-06
810 | feeder2_line151 | 2 | 99 | 12.9615 | 12.9613 | 13.0925 | 13.0923
810 | feeder2_line151 | 3 | 99 | 9.8699e-06 | 1.7882e-06 | 9.9696e-06 | 1.8063e-06
810 | feeder2_line152 | 1 | 354.6 | 1.9359e-11 | 1.1855e-06 | 5.4593e-12 | 3.3431e-07
810 | feeder2_line152 | 2 | 354.6 | 2.9295e-11 | 1.1716e-06 | 8.2614e-12 | 3.3041e-07
810 | feeder2_line152 | 3 | 354.6 | 0.4504 | 0.45038 | 0.12702 | 0.12701
810 | feeder2_line153 | 1 | 99 | 2.149 | 2.149 | 2.1707 | 2.1707
810 | feeder2_line153 | 2 | 99 | 5.1024e-08 | 5.8571e-07 | 5.1539e-08 | 5.9162e-07
810 | feeder2_line153 | 3 | 99 | 4.8819e-08 | 5.9633e-07 | 4.9312e-08 | 6.0235e-07
810 | feeder2_line154 | 1 | 99 | 5.7556e-07 | 8.8263e-07 | 5.8137e-07 | 8.9155e-07
810 | feeder2_line154 | 2 | 99 | 5.6827e-07 | 8.7156e-07 | 5.7401e-07 | 8.8036e-07
810 | feeder2_line154 | 3 | 99 | 0.040396 | 0.040345 | 0.040804 | 0.040752
810 | feeder2_line155 | 1 | 99 | 96.9326 | 96.9358 | 97.9117 | 97.9149
810 | feeder2_line155 | 2 | 99 | 99 | 99.007 | 100 | 100.0071
810 | feeder2_line155 | 3 | 99 | 96.3379 | 96.3274 | 97.311 | 97.3004
810 | feeder2_line156 | 1 | 99 | 6.0031e-07 | 1.1615e-06 | 6.0637e-07 | 1.1732e-06
810 | feeder2_line156 | 2 | 99 | 1.7706 | 1.7706 | 1.7885 | 1.7885
810 | feeder2_line156 | 3 | 99 | 6.0288e-07 | 1.1677e-06 | 6.0897e-07 | 1.1795e-06
810 | feeder2_line157 | 1 | 99 | 2.4971e-08 | 2.5216e-07 | 2.5224e-08 | 2.5471e-07
810 | feeder2_line157 | 2 | 99 | 11.4519 | 11.4516 | 11.5675 | 11.5673
810 | feeder2_line157 | 3 | 99 | 2.4398e-08 | 2.535e-07 | 2.4645e-08 | 2.5606e-07
840 | feeder2_line1 | 1 | 354.6 | 38.3367 | 38.3367 | 10.8113 | 10.8112
840 | feeder2_line1 | 2 | 354.6 | 45.2048 | 45.2094 | 12.7481 | 12.7494
840 | feeder2_line1 | 3 | 354.6 | 70.3417 | 70.34 | 19.8369 | 19.8364
840 | feeder2_line2 | 1 | 354.6 | 38.5915 | 38.5913 | 10.8831 | 10.883
840 | feeder2_line2 | 2 | 354.6 | 45.205 | 45.2094 | 12.7482 | 12.7494
840 | feeder2_line2 | 3 | 354.6 | 70.3418 | 70.34 | 19.837 | 19.8364
840 | feeder2_line3 | 1 | 80.1 | 0.51925 | 0.51925 | 0.64825 | 0.64825
840 | feeder2_line3 | 2 | 80.1 | 5.7023e-07 | 1.0538e-06 | 7.119e-07 | 1.3156e-06
840 | feeder2_line3 | 3 | 80.1 | 5.7167e-07 | 1.0564e-06 | 7.137e-07 | 1.3189e-06
840 | feeder2_line4 | 1 | 354.6 | 38.5915 | 38.5913 | 10.8831 | 10.883
840 | feeder2_line4 | 2 | 354.6 | 45.268 | 45.2724 | 12.7659 | 12.7672
840 | feeder2_line4 | 3 | 354.6 | 70.342 | 70.3401 | 19.837 | 19.8365
840 | feeder2_line5 | 1 | 80.1 | 5.6997e-07 | 9.9457e-07 | 7.1157e-07 | 1.2417e-06
840 | feeder2_line5 | 2 | 80.1 | 2.731 | 2.7311 | 3.4095 | 3.4096
840 | feeder2_line5 | 3 | 80.1 | 5.7171e-07 | 9.9757e-07 | 7.1375e-07 | 1.2454e-06
840 | feeder2_line6 | 1 | 80.1 | 5.6995e-07 | 1.1699e-06 | 7.1154e-07 | 1.4606e-06
840 | feeder2_line6 | 2 | 80.1 | 5.7023e-07 | 1.1705e-06 | 7.119e-07 | 1.4613e-06
840 | feeder2_line6 | 3 | 80.1 | 0.79983 | 0.79983 | 0.99854 | 0.99854
840 | feeder2_line7 | 1 | 354.6 | 38.5916 | 38.5913 | 10.8831 | 10.883
840 | feeder2_line7 | 2 | 354.6 | 45.2681 | 45.2724 | 12.7659 | 12.7672
840 | feeder2_line7 | 3 | 354.6 | 71.0377 | 71.0357 | 20.0332 | 20.0326
840 | feeder2_line8 | 1 | 80.1 | 0.073013 | 0.073013 | 0.091152 | 0.091152
840 | feeder2_line8 | 2 | 80.1 | 5.7023e-07 | 1.1286e-06 | 7.119e-07 | 1.409e-06
840 | feeder2_line8 | 3 | 80.1 | 5.7198e-07 | 1.132e-06 | 7.1408e-07 | 1.4133e-06
840 | feeder2_line9 | 1 | 354.6 | 38.6324 | 38.6322 | 10.8946 | 10.8946
840 | feeder2_line9 | 2 | 354.6 | 45.268 | 45.2724 | 12.7659 | 12.7672
840 | feeder2_line9 | 3 | 354.6 | 71.0377 | 71.0357 | 20.0332 | 20.0326
840 | feeder2_line10 | 1 | 80.1 | 8.4229e-07 | 1.4893e-06 | 1.0516e-06 | 1.8593e-06
840 | feeder2_line10 | 2 | 80.1 | 0.072877 | 0.072877 | 0.090982 | 0.090983
840 | feeder2_line10 | 3 | 80.1 | 8.4565e-07 | 1.4948e-06 | 1.0557e-06 | 1.8662e-06
840 | feeder2_line11 | 1 | 354.6 | 38.6325 | 38.6322 | 10.8947 | 10.8946
840 | feeder2_line11 | 2 | 354.6 | 45.3215 | 45.3258 | 12.781 | 12.7822
840 | feeder2_line11 | 3 | 354.6 | 71.0377 | 71.0357 | 20.0332 | 20.0326
840 | feeder2_line12 | 1 | 80.1 | 5.4485e-07 | 9.878e-07 | 6.8021e-07 | 1.2332e-06
840 | feeder2_line12 | 2 | 80.1 | 5.4545e-07 | 9.8849e-07 | 6.8096e-07 | 1.2341e-06
840 | feeder2_line12 | 3 | 80.1 | 0.81853 | 0.81855 | 1.0219 | 1.0219
840 | feeder2_line13 | 1 | 354.6 | 38.6325 | 38.6322 | 10.8947 | 10.8946
840 | feeder2_line13 | 2 | 354.6 | 45.3216 | 45.3258 | 12.781 | 12.7822
840 | feeder2_line13 | 3 | 354.6 | 71.1592 | 71.1571 | 20.0674 | 20.0669
840 | feeder2_line14 | 1 | 80.1 | 1.4725 | 1.4724 | 1.8383 | 1.8382
840 | feeder2_line14 | 2 | 80.1 | 2.975e-07 | 6.4457e-07 | 3.7141e-07 | 8.0471e-07
840 | feeder2_line14 | 3 | 80.1 | 2.9842e-07 | 6.4673e-07 | 3.7256e-07 | 8.0741e-07
840 | feeder2_line15 | 1 | 354.6 | 38.0895 | 38.0892 | 10.7415 | 10.7414
840 | feeder2_line15 | 2 | 354.6 | 45.3216 | 45.3258 | 12.781 | 12.7822
840 | feeder2_line15 | 3 | 354.6 | 71.1592 | 71.1571 | 20.0674 | 20.0669
840 | feeder2_line16 | 1 | 80.1 | 5.6973e-07 | 1.0264e-06 | 7.1128e-07 | 1.2815e-06
840 | feeder2_line16 | 2 | 80.1 | 1.3213 | 1.3213 | 1.6495 | 1.6495
840 | feeder2_line16 | 3 | 80.1 | 5.7226e-07 | 1.0309e-06 | 7.1443e-07 | 1.2871e-06
840 | feeder2_line17 | 1 | 354.6 | 38.0895 | 38.0892 | 10.7415 | 10.7414
840 | feeder2_line17 | 2 | 354.6 | 46.2287 | 46.2329 | 13.0369 | 13.0381
840 | feeder2_line17 | 3 | 354.6 | 71.1592 | 71.1571 | 20.0675 | 20.0669
840 | feeder2_line18 | 1 | 80.1 | 5.4451e-07 | 7.3448e-07 | 6.7979e-07 | 9.1695e-07
840 | feeder2_line18 | 2 | 80.1 | 5.4546e-07 | 7.3536e-07 | 6.8098e-07 | 9.1805e-07
840 | feeder2_line18 | 3 | 80.1 | 1.0975 | 1.0974 | 1.3701 | 1.3701
840 | feeder2_line19 | 1 | 354.6 | 38.0895 | 38.0892 | 10.7415 | 10.7414
840 | feeder2_line19 | 2 | 354.6 | 46.2287 | 46.2329 | 13.0369 | 13.0381
840 | feeder2_line19 | 3 | 354.6 | 71.2975 | 71.2953 | 20.1065 | 20.1058
840 | feeder2_line20 | 1 | 99 | 5.4441e-07 | 8.8049e-07 | 5.4991e-07 | 8.8938e-07
840 | feeder2_line20 | 2 | 99 | 5.4546e-07 | 8.8165e-07 | 5.5097e-07 | 8.9056e-07
840 | feeder2_line20 | 3 | 99 | 0.085871 | 0.085865 | 0.086738 | 0.086733
840 | feeder2_line21 | 1 | 354.6 | 38.0896 | 38.0892 | 10.7416 | 10.7414
840 | feeder2_line21 | 2 | 354.6 | 46.2288 | 46.2329 | 13.0369 | 13.0381
840 | feeder2_line21 | 3 | 354.6 | 71.3762 | 71.3739 | 20.1287 | 20.128
840 | feeder2_line22 | 1 | 99 | 5.6939e-07 | 1.0093e-06 | 5.7514e-07 | 1.0195e-06
840 | feeder2_line22 | 2 | 99 | 13.7782 | 13.7781 | 13.9174 | 13.9173
840 | feeder2_line22 | 3 | 99 | 5.7303e-07 | 1.0157e-06 | 5.7882e-07 | 1.0259e-06
840 | feeder2_line23 | 1 | 99 | 5.6941e-07 | 9.4478e-07 | 5.7517e-07 | 9.5432e-07
840 | feeder2_line23 | 2 | 99 | 5.7024e-07 | 9.4611e-07 | 5.76e-07 | 9.5567e-07
840 | feeder2_line23 | 3 | 99 | 1.4023 | 1.4023 | 1.4164 | 1.4165
840 | feeder2_line24 | 1 | 354.6 | 38.0897 | 38.0892 | 10.7416 | 10.7414
840 | feeder2_line24 | 2 | 354.6 | 56.4885 | 56.4925 | 15.9302 | 15.9313
840 | feeder2_line24 | 3 | 354.6 | 71.6074 | 71.605 | 20.1939 | 20.1932
840 | feeder2_line25 | 1 | 99 | 13.7412 | 13.7411 | 13.88 | 13.8799
840 | feeder2_line25 | 2 | 99 | 4.9536e-08 | 6.8792e-07 | 5.0036e-08 | 6.9487e-07
840 | feeder2_line25 | 3 | 99 | 4.9246e-08 | 6.9144e-07 | 4.9744e-08 | 6.9842e-07
840 | feeder2_line26 | 1 | 99 | 0.085871 | 0.085871 | 0.086738 | 0.086739
840 | feeder2_line26 | 2 | 99 | 5.4554e-07 | 8.5231e-07 | 5.5105e-07 | 8.6092e-07
840 | feeder2_line26 | 3 | 99 | 5.4862e-07 | 8.5666e-07 | 5.5416e-07 | 8.6531e-07
840 | feeder2_line27 | 1 | 354.6 | 46.6748 | 46.6744 | 13.1627 | 13.1626
840 | feeder2_line27 | 2 | 354.6 | 56.4885 | 56.4925 | 15.9302 | 15.9313
840 | feeder2_line27 | 3 | 354.6 | 71.6074 | 71.605 | 20.1939 | 20.1932
840 | feeder2_line28 | 1 | 99 | 2.5201e-06 | 7.0624e-07 | 2.5456e-06 | 7.1337e-07
840 | feeder2_line28 | 2 | 99 | 0.75507 | 0.75509 | 0.7627 | 0.76272
840 | feeder2_line28 | 3 | 99 | 2.5477e-06 | 7.1146e-07 | 2.5734e-06 | 7.1865e-07
840 | feeder2_line29 | 1 | 354.6 | 46.6748 | 46.6744 | 13.1627 | 13.1626
840 | feeder2_line29 | 2 | 354.6 | 56.5477 | 56.5517 | 15.9469 | 15.948
840 | feeder2_line29 | 3 | 354.6 | 71.6074 | 71.605 | 20.1939 | 20.1932
840 | feeder2_line30 | 1 | 266.4 | 3.4599 | 3.4598 | 1.2988 | 1.2987
840 | feeder2_line30 | 2 | 266.4 | 3.8429 | 3.8429 | 1.4425 | 1.4425
840 | feeder2_line30 | 3 | 266.4 | 7.6026 | 7.6026 | 2.8538 | 2.8538
840 | feeder2_line31 | 1 | 354.6 | 48.4392 | 48.4381 | 13.6602 | 13.6599
840 | feeder2_line31 | 2 | 354.6 | 58.6913 | 58.6948 | 16.5514 | 16.5524
840 | feeder2_line31 | 3 | 354.6 | 76.1919 | 76.1888 | 21.4867 | 21.4859
840 | feeder2_line32 | 1 | 354.6 | 48.4392 | 48.4381 | 13.6602 | 13.6599
840 | feeder2_line32 | 2 | 354.6 | 59.5408 | 59.5442 | 16.791 | 16.7919
840 | feeder2_line32 | 3 | 354.6 | 76.192 | 76.1888 | 21.4867 | 21.4859
840 | feeder2_line33 | 1 | 99 | 5.0303e-08 | 6.8127e-07 | 5.0811e-08 | 6.8815e-07
840 | feeder2_line33 | 2 | 99 | 0.98512 | 0.98512 | 0.99507 | 0.99507
840 | feeder2_line33 | 3 | 99 | 4.919e-08 | 6.8716e-07 | 4.9687e-08 | 6.941e-07
840 | feeder2_line34 | 1 | 354.6 | 48.4392 | 48.4381 | 13.6602 | 13.6599
840 | feeder2_line34 | 2 | 354.6 | 59.5408 | 59.5442 | 16.791 | 16.7919
840 | feeder2_line34 | 3 | 354.6 | 76.2719 | 76.2688 | 21.5093 | 21.5084
840 | feeder2_line35 | 1 | 99 | 2.9718e-07 | 7.5441e-07 | 3.0018e-07 | 7.6203e-07
840 | feeder2_line35 | 2 | 99 | 2.9772e-07 | 7.5632e-07 | 3.0073e-07 | 7.6396e-07
840 | feeder2_line35 | 3 | 99 | 0.085384 | 0.085381 | 0.086247 | 0.086244
840 | feeder2_line36 | 1 | 354.6 | 48.4618 | 48.4608 | 13.6666 | 13.6663
840 | feeder2_line36 | 2 | 354.6 | 59.5408 | 59.5442 | 16.791 | 16.7919
840 | feeder2_line36 | 3 | 354.6 | 76.2719 | 76.2688 | 21.5093 | 21.5084
840 | feeder2_line37 | 1 | 99 | 0.028405 | 0.028405 | 0.028692 | 0.028692
840 | feeder2_line37 | 2 | 99 | 2.9775e-07 | 8.3689e-07 | 3.0076e-07 | 8.4535e-07
840 | feeder2_line37 | 3 | 99 | 2.9952e-07 | 8.4233e-07 | 3.0254e-07 | 8.5084e-07
840 | feeder2_line38 | 1 | 99 | 3.2231e-07 | 7.7032e-07 | 3.2556e-07 | 7.781e-07
840 | feeder2_line38 | 2 | 99 | 0.07757 | 0.077572 | 0.078354 | 0.078356
840 | feeder2_line38 | 3 | 99 | 3.2387e-07 | 7.7662e-07 | 3.2714e-07 | 7.8446e-07
840 | feeder2_line39 | 1 | 266.4 | 3.4599 | 3.4598 | 1.2988 | 1.2987
840 | feeder2_line39 | 2 | 266.4 | 3.7745 | 3.7744 | 1.4169 | 1.4168
840 | feeder2_line39 | 3 | 266.4 | 7.6026 | 7.6026 | 2.8538 | 2.8538
840 | feeder2_line40 | 1 | 354.6 | 59.5271 | 59.5261 | 16.7871 | 16.7868
840 | feeder2_line40 | 2 | 354.6 | 59.5408 | 59.5442 | 16.791 | 16.7919
840 | feeder2_line40 | 3 | 354.6 | 76.2719 | 76.2688 | 21.5093 | 21.5084
840 | feeder2_line41 | 1 | 99 | 13.7317 | 13.7316 | 13.8704 | 13.8703
840 | feeder2_line41 | 2 | 99 | 4.9559e-08 | 7.3131e-07 | 5.0059e-08 | 7.387e-07
840 | feeder2_line41 | 3 | 99 | 4.916e-08 | 7.3613e-07 | 4.9656e-08 | 7.4356e-07
840 | feeder2_line42 | 1 | 99 | 2.9717e-07 | 7.4352e-07 | 3.0017e-07 | 7.5103e-07
840 | feeder2_line42 | 2 | 99 | 2.9765e-07 | 7.4522e-07 | 3.0066e-07 | 7.5275e-07
840 | feeder2_line42 | 3 | 99 | 2.5154 | 2.5153 | 2.5408 | 2.5407
840 | feeder2_line43 | 1 | 266.4 | 3.4598 | 3.4598 | 1.2987 | 1.2987
840 | feeder2_line43 | 2 | 266.4 | 3.7745 | 3.7744 | 1.4168 | 1.4168
840 | feeder2_line43 | 3 | 266.4 | 5.1521 | 5.1521 | 1.934 | 1.934
840 | feeder2_line44 | 1 | 354.6 | 59.5272 | 59.5261 | 16.7871 | 16.7868
840 | feeder2_line44 | 2 | 354.6 | 59.5408 | 59.5442 | 16.791 | 16.7919
840 | feeder2_line44 | 3 | 354.6 | 76.3536 | 76.3504 | 21.5323 | 21.5314
840 | feeder2_line45 | 1 | 99 | 5.0364e-08 | 5.7523e-07 | 5.0873e-08 | 5.8104e-07
840 | feeder2_line45 | 2 | 99 | 4.9579e-08 | 5.7676e-07 | 5.008e-08 | 5.8259e-07
840 | feeder2_line45 | 3 | 99 | 0.085615 | 0.085607 | 0.08648 | 0.086472
840 | feeder2_line46 | 1 | 99 | 5.692e-07 | 1.3479e-06 | 5.7495e-07 | 1.3615e-06
840 | feeder2_line46 | 2 | 99 | 5.7053e-07 | 1.351e-06 | 5.7629e-07 | 1.3646e-06
840 | feeder2_line46 | 3 | 99 | 1.989 | 1.989 | 2.0091 | 2.0091
840 | feeder2_line47 | 1 | 266.4 | 3.4599 | 3.4598 | 1.2988 | 1.2987
840 | feeder2_line47 | 2 | 266.4 | 3.7746 | 3.7744 | 1.4169 | 1.4168
840 | feeder2_line47 | 3 | 266.4 | 3.1632 | 3.1631 | 1.1874 | 1.1873
840 | feeder2_line48 | 1 | 99 | 1.1841 | 1.1841 | 1.1961 | 1.1961
840 | feeder2_line48 | 2 | 99 | 4.9544e-08 | 7.2737e-07 | 5.0045e-08 | 7.3472e-07
840 | feeder2_line48 | 3 | 99 | 4.9208e-08 | 7.316e-07 | 4.9705e-08 | 7.3899e-07
840 | feeder2_line49 | 1 | 266.4 | 2.5624 | 2.5622 | 0.96187 | 0.96179
840 | feeder2_line49 | 2 | 266.4 | 3.7746 | 3.7744 | 1.4169 | 1.4168
840 | feeder2_line49 | 3 | 266.4 | 3.1632 | 3.1631 | 1.1874 | 1.1873
840 | feeder2_line50 | 1 | 99 | 5.6919e-07 | 1.2266e-06 | 5.7493e-07 | 1.239e-06
840 | feeder2_line50 | 2 | 99 | 0.8008 | 0.80082 | 0.80889 | 0.80891
840 | feeder2_line50 | 3 | 99 | 5.7386e-07 | 1.2366e-06 | 5.7966e-07 | 1.2491e-06
840 | feeder2_line51 | 1 | 99 | 1.2759 | 1.2759 | 1.2888 | 1.2888
840 | feeder2_line51 | 2 | 99 | 5.7052e-07 | 1.3347e-06 | 5.7628e-07 | 1.3482e-06
840 | feeder2_line51 | 3 | 99 | 5.7386e-07 | 1.3425e-06 | 5.7966e-07 | 1.356e-06
840 | feeder2_line52 | 1 | 266.4 | 1.2949 | 1.2948 | 0.48607 | 0.48604
840 | feeder2_line52 | 2 | 266.4 | 3.0606 | 3.0606 | 1.1489 | 1.1489
840 | feeder2_line52 | 3 | 266.4 | 3.1631 | 3.1631 | 1.1873 | 1.1873
840 | feeder2_line53 | 1 | 99 | 5.4405e-07 | 7.4864e-07 | 5.4955e-07 | 7.562e-07
840 | feeder2_line53 | 2 | 99 | 3.0606 | 3.0606 | 3.0915 | 3.0915
840 | feeder2_line53 | 3 | 99 | 5.4926e-07 | 7.5471e-07 | 5.5481e-07 | 7.6233e-07
840 | feeder2_line54 | 1 | 266.4 | 1.2947 | 1.2948 | 0.48601 | 0.48604
840 | feeder2_line54 | 2 | 266.4 | 8.5131e-05 | 4.6029e-06 | 3.1956e-05 | 1.7278e-06
840 | feeder2_line54 | 3 | 266.4 | 3.163 | 3.1631 | 1.1873 | 1.1873
840 | feeder2_line55 | 1 | 99 | 0.69706 | 0.69706 | 0.7041 | 0.7041
840 | feeder2_line55 | 2 | 99 | 4.9602e-08 | 7.2673e-07 | 5.0103e-08 | 7.3407e-07
840 | feeder2_line55 | 3 | 99 | 4.9152e-08 | 7.3186e-07 | 4.9648e-08 | 7.3926e-07
840 | feeder2_line56 | 1 | 354.6 | 60.1241 | 60.123 | 16.9555 | 16.9552
840 | feeder2_line56 | 2 | 354.6 | 59.5409 | 59.5442 | 16.791 | 16.7919
840 | feeder2_line56 | 3 | 354.6 | 76.3536 | 76.3504 | 21.5323 | 21.5314
840 | feeder2_line57 | 1 | 99 | 7.5389e-07 | 1.5334e-06 | 7.615e-07 | 1.5489e-06
840 | feeder2_line57 | 2 | 99 | 7.4309e-07 | 1.537e-06 | 7.506e-07 | 1.5525e-06
840 | feeder2_line57 | 3 | 99 | 3.1631 | 3.1631 | 3.195 | 3.195
840 | feeder2_line58 | 1 | 266.4 | 1.2948 | 1.2948 | 0.48603 | 0.48604
840 | feeder2_line58 | 2 | 266.4 | 1.8841e-05 | 2.6724e-06 | 7.0725e-06 | 1.0031e-06
840 | feeder2_line58 | 3 | 266.4 | 1.8992e-05 | 2.6874e-06 | 7.1292e-06 | 1.0088e-06
840 | feeder2_line59 | 1 | 99 | 5.0259e-08 | 5.3304e-07 | 5.0767e-08 | 5.3842e-07
840 | feeder2_line59 | 2 | 99 | 4.9539e-08 | 5.3426e-07 | 5.004e-08 | 5.3966e-07
840 | feeder2_line59 | 3 | 99 | 2.4779 | 2.4779 | 2.503 | 2.503
840 | feeder2_line60 | 1 | 99 | 2.9716e-07 | 8.0558e-07 | 3.0016e-07 | 8.1372e-07
840 | feeder2_line60 | 2 | 99 | 2.9764e-07 | 8.0743e-07 | 3.0065e-07 | 8.1558e-07
840 | feeder2_line60 | 3 | 99 | 0.81955 | 0.81957 | 0.82783 | 0.82785
840 | feeder2_line61 | 1 | 266.4 | 0.086391 | 0.086558 | 0.032429 | 0.032492
840 | feeder2_line61 | 2 | 266.4 | 2.9921 | 2.9923 | 1.1232 | 1.1232
840 | feeder2_line61 | 3 | 266.4 | 15.5175 | 15.5177 | 5.8249 | 5.8249
840 | feeder2_line62 | 1 | 354.6 | 60.2017 | 60.2008 | 16.9774 | 16.9771
840 | feeder2_line62 | 2 | 354.6 | 62.1532 | 62.1567 | 17.5277 | 17.5287
840 | feeder2_line62 | 3 | 354.6 | 90.8111 | 90.8081 | 25.6094 | 25.6086
840 | feeder2_line63 | 1 | 99 | 0.089869 | 0.089869 | 0.090777 | 0.090777
840 | feeder2_line63 | 2 | 99 | 5.7052e-07 | 1.214e-06 | 5.7629e-07 | 1.2262e-06
840 | feeder2_line63 | 3 | 99 | 5.7386e-07 | 1.221e-06 | 5.7965e-07 | 1.2333e-06
840 | feeder2_line64 | 1 | 99 | 1.2066 | 1.2066 | 1.2188 | 1.2188
840 | feeder2_line64 | 2 | 99 | 9.2287e-12 | 3.1978e-07 | 9.3219e-12 | 3.2301e-07
840 | feeder2_line64 | 3 | 99 | 1.288e-12 | 3.2163e-07 | 1.301e-12 | 3.2488e-07
840 | feeder2_line65 | 1 | 99 | 5.0463e-08 | 6.3674e-07 | 5.0973e-08 | 6.4317e-07
840 | feeder2_line65 | 2 | 99 | 2.731 | 2.731 | 2.7586 | 2.7586
840 | feeder2_line65 | 3 | 99 | 4.9114e-08 | 6.4345e-07 | 4.961e-08 | 6.4995e-07
840 | feeder2_line66 | 1 | 354.6 | 60.2017 | 60.2008 | 16.9773 | 16.9771
840 | feeder2_line66 | 2 | 354.6 | 63.1596 | 63.1632 | 17.8115 | 17.8125
840 | feeder2_line66 | 3 | 354.6 | 90.8111 | 90.8081 | 25.6094 | 25.6086
840 | feeder2_line67 | 1 | 99 | 2.5203e-08 | 3.5994e-07 | 2.5458e-08 | 3.6358e-07
840 | feeder2_line67 | 2 | 99 | 2.4806e-08 | 3.6088e-07 | 2.5057e-08 | 3.6453e-07
840 | feeder2_line67 | 3 | 99 | 13.9015 | 13.9015 | 14.0419 | 14.0419
840 | feeder2_line68 | 1 | 266.4 | 0.086429 | 0.086558 | 0.032443 | 0.032492
840 | feeder2_line68 | 2 | 266.4 | 2.9922 | 2.9923 | 1.1232 | 1.1232
840 | feeder2_line68 | 3 | 266.4 | 1.6164 | 1.6165 | 0.60676 | 0.60681
840 | feeder2_line69 | 1 | 99 | 15.1754 | 15.1754 | 15.3287 | 15.3287
840 | feeder2_line69 | 2 | 99 | 2.5325e-06 | 6.6277e-07 | 2.5581e-06 | 6.6947e-07
840 | feeder2_line69 | 3 | 99 | 2.5593e-06 | 6.6814e-07 | 2.5852e-06 | 6.7489e-07
840 | feeder2_line70 | 1 | 354.6 | 73.6628 | 73.6621 | 20.7735 | 20.7733
840 | feeder2_line70 | 2 | 354.6 | 63.1596 | 63.1632 | 17.8115 | 17.8125
840 | feeder2_line70 | 3 | 354.6 | 90.811 | 90.8081 | 25.6094 | 25.6086
840 | feeder2_line71 | 1 | 99 | 5.0498e-08 | 7.1044e-07 | 5.1008e-08 | 7.1762e-07
840 | feeder2_line71 | 2 | 99 | 1.0917 | 1.0917 | 1.1027 | 1.1027
840 | feeder2_line71 | 3 | 99 | 4.9096e-08 | 7.1816e-07 | 4.9592e-08 | 7.2541e-07
840 | feeder2_line72 | 1 | 354.6 | 73.6629 | 73.6621 | 20.7735 | 20.7733
840 | feeder2_line72 | 2 | 354.6 | 64.1262 | 64.1298 | 18.0841 | 18.0851
840 | feeder2_line72 | 3 | 354.6 | 90.8111 | 90.8081 | 25.6094 | 25.6086
840 | feeder2_line73 | 1 | 99 | 5.9463e-07 | 1.5239e-06 | 6.0063e-07 | 1.5393e-06
840 | feeder2_line73 | 2 | 99 | 0.98527 | 0.98526 | 0.99522 | 0.99522
840 | feeder2_line73 | 3 | 99 | 5.9968e-07 | 1.5389e-06 | 6.0573e-07 | 1.5545e-06
840 | feeder2_line74 | 1 | 99 | 5.0417e-08 | 4.545e-07 | 5.0926e-08 | 4.591e-07
840 | feeder2_line74 | 2 | 99 | 1.6159 | 1.6159 | 1.6322 | 1.6322
840 | feeder2_line74 | 3 | 99 | 4.9143e-08 | 4.5899e-07 | 4.9639e-08 | 4.6363e-07
840 | feeder2_line75 | 1 | 266.4 | 0.086525 | 0.086558 | 0.032479 | 0.032492
840 | feeder2_line75 | 2 | 266.4 | 0.39341 | 0.39344 | 0.14768 | 0.14769
840 | feeder2_line75 | 3 | 266.4 | 1.6165 | 1.6165 | 0.6068 | 0.60681
840 | feeder2_line76 | 1 | 99 | 0.086557 | 0.086557 | 0.087431 | 0.087432
840 | feeder2_line76 | 2 | 99 | 8.4397e-07 | 1.576e-06 | 8.5249e-07 | 1.5919e-06
840 | feeder2_line76 | 3 | 99 | 8.5037e-07 | 1.5875e-06 | 8.5896e-07 | 1.6035e-06
840 | feeder2_line77 | 1 | 99 | 2.5211e-08 | 5.7117e-07 | 2.5466e-08 | 5.7694e-07
840 | feeder2_line77 | 2 | 99 | 2.4809e-08 | 5.7263e-07 | 2.506e-08 | 5.7841e-07
840 | feeder2_line77 | 3 | 99 | 1.6166 | 1.6165 | 1.6329 | 1.6329
840 | feeder2_line78 | 1 | 266.4 | 9.0353e-13 | 9.4782e-07 | 3.3916e-13 | 3.5579e-07
840 | feeder2_line78 | 2 | 266.4 | 0.39344 | 0.39344 | 0.14769 | 0.14769
840 | feeder2_line78 | 3 | 266.4 | 1.1635e-11 | 9.5606e-07 | 4.3673e-12 | 3.5888e-07
840 | feeder2_line79 | 1 | 354.6 | 3.8327 | 3.8323 | 1.0808 | 1.0807
840 | feeder2_line79 | 2 | 354.6 | 14.5697 | 14.5692 | 4.1088 | 4.1086
840 | feeder2_line79 | 3 | 354.6 | 5.3968 | 5.3965 | 1.5219 | 1.5219
840 | feeder2_line80 | 1 | 354.6 | 76.4928 | 76.4916 | 21.5716 | 21.5712
840 | feeder2_line80 | 2 | 354.6 | 76.8701 | 76.8731 | 21.678 | 21.6788
840 | feeder2_line80 | 3 | 354.6 | 93.4502 | 93.4465 | 26.3537 | 26.3526
840 | feeder2_line81 | 1 | 354.6 | 76.4928 | 76.4916 | 21.5716 | 21.5712
840 | feeder2_line81 | 2 | 354.6 | 76.87 | 76.8731 | 21.6779 | 21.6788
840 | feeder2_line81 | 3 | 354.6 | 94.5708 | 94.5672 | 26.6697 | 26.6687
840 | feeder2_line82 | 1 | 354.6 | 7.0105e-12 | 7.2922e-07 | 1.977e-12 | 2.0564e-07
840 | feeder2_line82 | 2 | 354.6 | 2.1231e-11 | 7.3053e-07 | 5.9873e-12 | 2.0602e-07
840 | feeder2_line82 | 3 | 354.6 | 1.1634 | 1.1634 | 0.32808 | 0.32807
840 | feeder2_line83 | 1 | 354.6 | 76.4929 | 76.4916 | 21.5716 | 21.5712
840 | feeder2_line83 | 2 | 354.6 | 77.1774 | 77.1803 | 21.7646 | 21.7655
840 | feeder2_line83 | 3 | 354.6 | 94.571 | 94.5672 | 26.6698 | 26.6687
840 | feeder2_line84 | 1 | 354.6 | 5.0122e-12 | 1.2888e-06 | 1.4135e-12 | 3.6345e-07
840 | feeder2_line84 | 2 | 354.6 | 0.97442 | 0.97443 | 0.27479 | 0.2748
840 | feeder2_line84 | 3 | 354.6 | 1.133e-11 | 1.3022e-06 | 3.1951e-12 | 3.6723e-07
840 | feeder2_line85 | 1 | 99 | 0.077882 | 0.077882 | 0.078669 | 0.078669
840 | feeder2_line85 | 2 | 99 | 4.9743e-08 | 4.6086e-07 | 5.0245e-08 | 4.6551e-07
840 | feeder2_line85 | 3 | 99 | 4.9071e-08 | 4.6506e-07 | 4.9567e-08 | 4.6976e-07
840 | feeder2_line86 | 1 | 354.6 | 76.5674 | 76.566 | 21.5926 | 21.5922
840 | feeder2_line86 | 2 | 354.6 | 77.1775 | 77.1803 | 21.7647 | 21.7655
840 | feeder2_line86 | 3 | 354.6 | 94.5711 | 94.5672 | 26.6698 | 26.6687
840 | feeder2_line87 | 1 | 354.6 | 76.5676 | 76.566 | 21.5927 | 21.5922
840 | feeder2_line87 | 2 | 354.6 | 80.0254 | 80.0281 | 22.5678 | 22.5685
840 | feeder2_line87 | 3 | 354.6 | 94.9839 | 94.9798 | 26.7862 | 26.785
840 | feeder2_line88 | 1 | 354.6 | 0.00010991 | 3.339e-06 | 3.0995e-05 | 9.4163e-07
840 | feeder2_line88 | 2 | 354.6 | 3.3999 | 3.3999 | 0.95881 | 0.9588
840 | feeder2_line88 | 3 | 354.6 | 1.0466 | 1.0465 | 0.29514 | 0.29511
840 | feeder2_line89 | 1 | 354.6 | 76.5654 | 76.566 | 21.592 | 21.5922
840 | feeder2_line89 | 2 | 354.6 | 82.3809 | 82.3859 | 23.2321 | 23.2335
840 | feeder2_line89 | 3 | 354.6 | 94.9816 | 94.9798 | 26.7856 | 26.785
840 | feeder2_line90 | 1 | 354.6 | 0.00071507 | 2.017e-06 | 0.00020166 | 5.6881e-07
840 | feeder2_line90 | 2 | 354.6 | 3.2464 | 3.2467 | 0.91552 | 0.91559
840 | feeder2_line90 | 3 | 354.6 | 0.00072999 | 2.038e-06 | 0.00020586 | 5.7473e-07
840 | feeder2_line91 | 1 | 354.6 | 76.5654 | 76.566 | 21.592 | 21.5922
840 | feeder2_line91 | 2 | 354.6 | 82.3809 | 82.3859 | 23.2321 | 23.2335
840 | feeder2_line91 | 3 | 354.6 | 95.31 | 95.3082 | 26.8782 | 26.8777
840 | feeder2_line92 | 1 | 354.6 | 1.3984e-11 | 1.0172e-06 | 3.9436e-12 | 2.8687e-07
840 | feeder2_line92 | 2 | 354.6 | 1.0142e-11 | 1.0192e-06 | 2.8602e-12 | 2.8742e-07
840 | feeder2_line92 | 3 | 354.6 | 0.8213 | 0.82132 | 0.23161 | 0.23162
840 | feeder2_line93 | 1 | 99 | 2.5309e-08 | 3.3937e-07 | 2.5565e-08 | 3.428e-07
840 | feeder2_line93 | 2 | 99 | 0.97452 | 0.97453 | 0.98436 | 0.98437
840 | feeder2_line93 | 3 | 99 | 2.4531e-08 | 3.4343e-07 | 2.4779e-08 | 3.469e-07
840 | feeder2_line94 | 1 | 354.6 | 2.5307e-06 | 1.6531e-06 | 7.1368e-07 | 4.662e-07
840 | feeder2_line94 | 2 | 354.6 | 2.4058 | 2.4058 | 0.67846 | 0.67847
840 | feeder2_line94 | 3 | 354.6 | 2.453e-06 | 1.6711e-06 | 6.9177e-07 | 4.7126e-07
840 | feeder2_line95 | 1 | 99 | 3.5372e-06 | 2.5892e-06 | 3.5729e-06 | 2.6153e-06
840 | feeder2_line95 | 2 | 99 | 3.3998 | 3.3999 | 3.4342 | 3.4343
840 | feeder2_line95 | 3 | 99 | 3.5906e-06 | 2.6195e-06 | 3.6269e-06 | 2.6459e-06
840 | feeder2_line96 | 1 | 354.6 | 0.00012003 | 6.1723e-07 | 3.385e-05 | 1.7406e-07
840 | feeder2_line96 | 2 | 354.6 | 0.00012049 | 6.1893e-07 | 3.398e-05 | 1.7454e-07
840 | feeder2_line96 | 3 | 354.6 | 1.0465 | 1.0465 | 0.29512 | 0.29511
840 | feeder2_line97 | 1 | 354.6 | 77.4216 | 77.422 | 21.8335 | 21.8336
840 | feeder2_line97 | 2 | 354.6 | 82.3811 | 82.3859 | 23.2321 | 23.2335
840 | feeder2_line97 | 3 | 354.6 | 95.3103 | 95.3082 | 26.8782 | 26.8777
840 | feeder2_line98 | 1 | 354.6 | 0.9129 | 0.91124 | 0.25745 | 0.25698
840 | feeder2_line98 | 2 | 354.6 | 0.0017057 | 6.1806e-07 | 0.00048101 | 1.743e-07
840 | feeder2_line98 | 3 | 354.6 | 0.0017155 | 6.2494e-07 | 0.00048378 | 1.7624e-07
840 | feeder2_line99 | 1 | 99 | 2.5294e-08 | 4.4371e-07 | 2.5549e-08 | 4.4819e-07
840 | feeder2_line99 | 2 | 99 | 2.4874e-08 | 4.4477e-07 | 2.5125e-08 | 4.4926e-07
840 | feeder2_line99 | 3 | 99 | 1.0465 | 1.0465 | 1.0571 | 1.057
840 | feeder2_line100 | 1 | 99 | 0.91125 | 0.91124 | 0.92045 | 0.92044
840 | feeder2_line100 | 2 | 99 | 2.4898e-08 | 6.1075e-07 | 2.5149e-08 | 6.1692e-07
840 | feeder2_line100 | 3 | 99 | 2.453e-08 | 6.1663e-07 | 2.4778e-08 | 6.2286e-07
840 | feeder2_line101 | 1 | 354.6 | 2.4052 | 2.4048 | 0.67828 | 0.67817
840 | feeder2_line101 | 2 | 354.6 | 14.5696 | 14.5692 | 4.1088 | 4.1086
840 | feeder2_line101 | 3 | 354.6 | 5.3968 | 5.3965 | 1.5219 | 1.5219
840 | feeder2_line102 | 1 | 99 | 1.445 | 1.445 | 1.4596 | 1.4596
840 | feeder2_line102 | 2 | 99 | 2.329e-06 | 8.7328e-07 | 2.3525e-06 | 8.821e-07
840 | feeder2_line102 | 3 | 99 | 2.3508e-06 | 8.8109e-07 | 2.3745e-06 | 8.8999e-07
840 | feeder2_line103 | 1 | 99 | 5.4447e-07 | 7.9754e-07 | 5.4997e-07 | 8.056e-07
840 | feeder2_line103 | 2 | 99 | 0.76272 | 0.76273 | 0.77042 | 0.77043
840 | feeder2_line103 | 3 | 99 | 5.5164e-07 | 8.0646e-07 | 5.5722e-07 | 8.146e-07
840 | feeder2_line104 | 1 | 354.6 | 2.4051 | 2.4048 | 0.67826 | 0.67817
840 | feeder2_line104 | 2 | 354.6 | 13.8095 | 13.8092 | 3.8944 | 3.8943
840 | feeder2_line104 | 3 | 354.6 | 5.3967 | 5.3965 | 1.5219 | 1.5219
840 | feeder2_line105 | 1 | 99 | 2.5203e-06 | 7.3385e-07 | 2.5457e-06 | 7.4126e-07
840 | feeder2_line105 | 2 | 99 | 2.5317e-06 | 7.354e-07 | 2.5573e-06 | 7.4283e-07
840 | feeder2_line105 | 3 | 99 | 1.1006 | 1.1006 | 1.1117 | 1.1117
840 | feeder2_line106 | 1 | 354.6 | 2.4051 | 2.4048 | 0.67824 | 0.67817
840 | feeder2_line106 | 2 | 354.6 | 13.8095 | 13.8092 | 3.8944 | 3.8943
840 | feeder2_line106 | 3 | 354.6 | 4.3182 | 4.318 | 1.2178 | 1.2177
840 | feeder2_line107 | 1 | 99 | 3.2274e-07 | 8.9429e-07 | 3.26e-07 | 9.0333e-07
840 | feeder2_line107 | 2 | 99 | 11.9943 | 11.9943 | 12.1155 | 12.1154
840 | feeder2_line107 | 3 | 99 | 3.2485e-07 | 9.0426e-07 | 3.2813e-07 | 9.1339e-07
840 | feeder2_line108 | 1 | 354.6 | 2.405 | 2.4048 | 0.67824 | 0.67817
840 | feeder2_line108 | 2 | 354.6 | 1.8165 | 1.8162 | 0.51226 | 0.51219
840 | feeder2_line108 | 3 | 354.6 | 4.3182 | 4.318 | 1.2178 | 1.2177
840 | feeder2_line109 | 1 | 354.6 | 80.7987 | 80.7982 | 22.7859 | 22.7857
840 | feeder2_line109 | 2 | 354.6 | 82.3822 | 82.3859 | 23.2324 | 23.2335
840 | feeder2_line109 | 3 | 354.6 | 95.3114 | 95.3082 | 26.8786 | 26.8777
840 | feeder2_line110 | 1 | 99 | 5.2772 | 5.2765 | 5.3305 | 5.3298
840 | feeder2_line110 | 2 | 99 | 0.00079981 | 9.0411e-07 | 0.00080789 | 9.1324e-07
840 | feeder2_line110 | 3 | 99 | 0.00081099 | 9.1286e-07 | 0.00081918 | 9.2208e-07
840 | feeder2_line111 | 1 | 99 | 2.5291e-08 | 3.7895e-07 | 2.5546e-08 | 3.8278e-07
840 | feeder2_line111 | 2 | 99 | 2.302 | 2.302 | 2.3252 | 2.3253
840 | feeder2_line111 | 3 | 99 | 2.4531e-08 | 3.834e-07 | 2.4779e-08 | 3.8727e-07
840 | feeder2_line112 | 1 | 99 | 3.2291e-07 | 9.1067e-07 | 3.2618e-07 | 9.1986e-07
840 | feeder2_line112 | 2 | 99 | 1.1323 | 1.1323 | 1.1437 | 1.1437
840 | feeder2_line112 | 3 | 99 | 3.2515e-07 | 9.2132e-07 | 3.2843e-07 | 9.3062e-07
840 | feeder2_line113 | 1 | 99 | 1.4112 | 1.4111 | 1.4254 | 1.4254
840 | feeder2_line113 | 2 | 99 | 3.2323e-07 | 9.0066e-07 | 3.2649e-07 | 9.0975e-07
840 | feeder2_line113 | 3 | 99 | 3.255e-07 | 9.095e-07 | 3.2879e-07 | 9.1869e-07
840 | feeder2_line114 | 1 | 99 | 0.76649 | 0.76649 | 0.77423 | 0.77423
840 | feeder2_line114 | 2 | 99 | 2.4863e-08 | 4.3424e-07 | 2.5114e-08 | 4.3863e-07
840 | feeder2_line114 | 3 | 99 | 2.4531e-08 | 4.3813e-07 | 2.4779e-08 | 4.4255e-07
840 | feeder2_line115 | 1 | 99 | 2.526e-08 | 5.5808e-07 | 2.5515e-08 | 5.6371e-07
840 | feeder2_line115 | 2 | 99 | 0.6271 | 0.6271 | 0.63343 | 0.63344
840 | feeder2_line115 | 3 | 99 | 2.4524e-08 | 5.6429e-07 | 2.4772e-08 | 5.6999e-07
840 | feeder2_line116 | 1 | 354.6 | 2.4051 | 2.4048 | 0.67824 | 0.67817
840 | feeder2_line116 | 2 | 354.6 | 1.3574 | 1.3572 | 0.3828 | 0.38274
840 | feeder2_line116 | 3 | 354.6 | 4.3182 | 4.318 | 1.2178 | 1.2177
840 | feeder2_line117 | 1 | 99 | 5.0696e-08 | 6.3786e-07 | 5.1208e-08 | 6.443e-07
840 | feeder2_line117 | 2 | 99 | 1.9919 | 1.9919 | 2.012 | 2.012
840 | feeder2_line117 | 3 | 99 | 4.9057e-08 | 6.4592e-07 | 4.9553e-08 | 6.5245e-07
840 | feeder2_line118 | 1 | 354.6 | 80.7987 | 80.7982 | 22.7859 | 22.7857
840 | feeder2_line118 | 2 | 354.6 | 83.9072 | 83.9108 | 23.6625 | 23.6635
840 | feeder2_line118 | 3 | 354.6 | 95.3114 | 95.3082 | 26.8786 | 26.8777
840 | feeder2_line119 | 1 | 99 | 2.5263e-08 | 6.005e-07 | 2.5518e-08 | 6.0657e-07
840 | feeder2_line119 | 2 | 99 | 2.4859e-08 | 6.0173e-07 | 2.511e-08 | 6.0781e-07
840 | feeder2_line119 | 3 | 99 | 1.4136 | 1.4136 | 1.4279 | 1.4279
840 | feeder2_line120 | 1 | 354.6 | 2.4051 | 2.4048 | 0.67824 | 0.67818
840 | feeder2_line120 | 2 | 354.6 | 1.3574 | 1.3572 | 0.3828 | 0.38274
840 | feeder2_line120 | 3 | 354.6 | 2.9448 | 2.9446 | 0.83047 | 0.83041
840 | feeder2_line121 | 1 | 99 | 3.2273e-07 | 9.2986e-07 | 3.2599e-07 | 9.3925e-07
840 | feeder2_line121 | 2 | 99 | 1.2781 | 1.2781 | 1.291 | 1.291
840 | feeder2_line121 | 3 | 99 | 3.2483e-07 | 9.4021e-07 | 3.2811e-07 | 9.497e-07
840 | feeder2_line122 | 1 | 354.6 | 2.405 | 2.4048 | 0.67824 | 0.67818
840 | feeder2_line122 | 2 | 354.6 | 0.089829 | 0.089591 | 0.025332 | 0.025265
840 | feeder2_line122 | 3 | 354.6 | 2.9448 | 2.9446 | 0.83046 | 0.83041
840 | feeder2_line123 | 1 | 99 | 5.6967e-07 | 9.6354e-07 | 5.7542e-07 | 9.7327e-07
840 | feeder2_line123 | 2 | 99 | 5.7091e-07 | 9.6558e-07 | 5.7668e-07 | 9.7533e-07
840 | feeder2_line123 | 3 | 99 | 0.7574 | 0.75742 | 0.76505 | 0.76507
840 | feeder2_line124 | 1 | 354.6 | 2.405 | 2.4048 | 0.67823 | 0.67818
840 | feeder2_line124 | 2 | 354.6 | 0.089733 | 0.089591 | 0.025305 | 0.025265
840 | feeder2_line124 | 3 | 354.6 | 2.221 | 2.2208 | 0.62633 | 0.62627
840 | feeder2_line125 | 1 | 99 | 5.6966e-07 | 8.9569e-07 | 5.7542e-07 | 9.0474e-07
840 | feeder2_line125 | 2 | 99 | 5.7092e-07 | 8.9761e-07 | 5.7668e-07 | 9.0667e-07
840 | feeder2_line125 | 3 | 99 | 0.89714 | 0.89712 | 0.9062 | 0.90619
840 | feeder2_line126 | 1 | 354.6 | 2.4051 | 2.4048 | 0.67827 | 0.67818
840 | feeder2_line126 | 2 | 354.6 | 0.089889 | 0.089591 | 0.025349 | 0.025265
840 | feeder2_line126 | 3 | 354.6 | 1.5474 | 1.5471 | 0.43638 | 0.4363
840 | feeder2_line127 | 1 | 99 | 5.6965e-07 | 1.0723e-06 | 5.7541e-07 | 1.0831e-06
840 | feeder2_line127 | 2 | 99 | 5.7092e-07 | 1.0746e-06 | 5.7668e-07 | 1.0854e-06
840 | feeder2_line127 | 3 | 99 | 1.4737 | 1.4738 | 1.4886 | 1.4886
840 | feeder2_line128 | 1 | 354.6 | 2.4051 | 2.4048 | 0.67825 | 0.67818
840 | feeder2_line128 | 2 | 354.6 | 0.089803 | 0.089591 | 0.025325 | 0.025265
840 | feeder2_line128 | 3 | 354.6 | 0.12604 | 0.12582 | 0.035545 | 0.035482
840 | feeder2_line129 | 1 | 99 | 5.4439e-07 | 8.6945e-07 | 5.4989e-07 | 8.7823e-07
840 | feeder2_line129 | 2 | 99 | 0.089588 | 0.08959 | 0.090493 | 0.090495
840 | feeder2_line129 | 3 | 99 | 5.5156e-07 | 8.7915e-07 | 5.5713e-07 | 8.8803e-07
840 | feeder2_line130 | 1 | 354.6 | 2.4051 | 2.4048 | 0.67826 | 0.67818
840 | feeder2_line130 | 2 | 354.6 | 0.00030563 | 4.6112e-06 | 8.6189e-05 | 1.3004e-06
840 | feeder2_line130 | 3 | 354.6 | 0.12606 | 0.12582 | 0.035549 | 0.035482
840 | feeder2_line131 | 1 | 99 | 5.6964e-07 | 9.6363e-07 | 5.7539e-07 | 9.7337e-07
840 | feeder2_line131 | 2 | 99 | 5.7092e-07 | 9.6575e-07 | 5.7669e-07 | 9.755e-07
840 | feeder2_line131 | 3 | 99 | 0.049227 | 0.049225 | 0.049724 | 0.049722
840 | feeder2_line132 | 1 | 354.6 | 2.4049 | 2.4048 | 0.67821 | 0.67818
840 | feeder2_line132 | 2 | 354.6 | 0.00012491 | 2.899e-06 | 3.5225e-05 | 8.1755e-07
840 | feeder2_line132 | 3 | 354.6 | 0.076762 | 0.07669 | 0.021648 | 0.021627
840 | feeder2_line133 | 1 | 99 | 2.4048 | 2.4048 | 2.4291 | 2.4291
840 | feeder2_line133 | 2 | 99 | 2.9788e-07 | 9.7345e-07 | 3.0089e-07 | 9.8328e-07
840 | feeder2_line133 | 3 | 99 | 3.003e-07 | 9.8218e-07 | 3.0334e-07 | 9.921e-07
840 | feeder2_line134 | 1 | 354.6 | 1.7767e-12 | 1.7722e-06 | 5.0104e-13 | 4.9978e-07
840 | feeder2_line134 | 2 | 354.6 | 5.915e-12 | 1.7753e-06 | 1.6681e-12 | 5.0064e-07
840 | feeder2_line134 | 3 | 354.6 | 0.076693 | 0.076689 | 0.021628 | 0.021627
840 | feeder2_line135 | 1 | 99 | 1.0932 | 1.0932 | 1.1043 | 1.1043
840 | feeder2_line135 | 2 | 99 | 4.9861e-08 | 5.8286e-07 | 5.0364e-08 | 5.8875e-07
840 | feeder2_line135 | 3 | 99 | 4.906e-08 | 5.8884e-07 | 4.9555e-08 | 5.9479e-07
840 | feeder2_line136 | 1 | 354.6 | 81.831 | 81.8305 | 23.077 | 23.0768
840 | feeder2_line136 | 2 | 354.6 | 83.9071 | 83.9108 | 23.6625 | 23.6635
840 | feeder2_line136 | 3 | 354.6 | 95.3114 | 95.3082 | 26.8786 | 26.8777
840 | feeder2_line137 | 1 | 99 | 2.2505 | 2.2505 | 2.2732 | 2.2732
840 | feeder2_line137 | 2 | 99 | 8.4588e-07 | 1.57e-06 | 8.5443e-07 | 1.5858e-06
840 | feeder2_line137 | 3 | 99 | 8.5499e-07 | 1.5861e-06 | 8.6363e-07 | 1.6022e-06
840 | feeder2_line138 | 1 | 354.6 | 82.9751 | 82.9746 | 23.3996 | 23.3995
840 | feeder2_line138 | 2 | 354.6 | 83.9072 | 83.9108 | 23.6625 | 23.6635
840 | feeder2_line138 | 3 | 354.6 | 95.3115 | 95.3082 | 26.8786 | 26.8777
840 | feeder2_line139 | 1 | 99 | 5.0756e-08 | 4.8792e-07 | 5.1269e-08 | 4.9285e-07
840 | feeder2_line139 | 2 | 99 | 4.9872e-08 | 4.892e-07 | 5.0376e-08 | 4.9414e-07
840 | feeder2_line139 | 3 | 99 | 1.6147 | 1.6144 | 1.631 | 1.6307
840 | feeder2_line140 | 1 | 354.6 | 82.9752 | 82.9746 | 23.3997 | 23.3995
840 | feeder2_line140 | 2 | 354.6 | 83.9073 | 83.9108 | 23.6625 | 23.6635
840 | feeder2_line140 | 3 | 354.6 | 96.5114 | 96.5079 | 27.217 | 27.216
840 | feeder2_line141 | 1 | 99 | 2.4987e-06 | 4.8267e-07 | 2.524e-06 | 4.8755e-07
840 | feeder2_line141 | 2 | 99 | 2.5157 | 2.5156 | 2.5411 | 2.541
840 | feeder2_line141 | 3 | 99 | 2.5486e-06 | 4.8901e-07 | 2.5743e-06 | 4.9395e-07
840 | feeder2_line142 | 1 | 354.6 | 82.9751 | 82.9746 | 23.3996 | 23.3995
840 | feeder2_line142 | 2 | 354.6 | 85.3642 | 85.3677 | 24.0734 | 24.0744
840 | feeder2_line142 | 3 | 354.6 | 96.5112 | 96.5079 | 27.2169 | 27.216
840 | feeder2_line143 | 1 | 99 | 8.4353e-07 | 1.7151e-06 | 8.5205e-07 | 1.7324e-06
840 | feeder2_line143 | 2 | 99 | 12.014 | 12.0139 | 12.1353 | 12.1353
840 | feeder2_line143 | 3 | 99 | 8.5536e-07 | 1.7377e-06 | 8.64e-07 | 1.7552e-06
840 | feeder2_line144 | 1 | 354.6 | 82.9749 | 82.9746 | 23.3996 | 23.3995
840 | feeder2_line144 | 2 | 354.6 | 96.7301 | 96.7338 | 27.2787 | 27.2797
840 | feeder2_line144 | 3 | 354.6 | 96.511 | 96.5079 | 27.2169 | 27.216
840 | feeder2_line145 | 1 | 99 | 2.5392e-08 | 4.8095e-07 | 2.5649e-08 | 4.8581e-07
840 | feeder2_line145 | 2 | 99 | 1.1679 | 1.1679 | 1.1797 | 1.1797
840 | feeder2_line145 | 3 | 99 | 2.4533e-08 | 4.8729e-07 | 2.4781e-08 | 4.9221e-07
840 | feeder2_line146 | 1 | 354.6 | 82.9748 | 82.9746 | 23.3995 | 23.3995
840 | feeder2_line146 | 2 | 354.6 | 97.8677 | 97.8715 | 27.5995 | 27.6005
840 | feeder2_line146 | 3 | 354.6 | 96.5109 | 96.5079 | 27.2168 | 27.216
840 | feeder2_line147 | 1 | 99 | 4.0038 | 4.0037 | 4.0442 | 4.0442
840 | feeder2_line147 | 2 | 99 | 1.145e-06 | 2.2244e-06 | 1.1566e-06 | 2.2469e-06
840 | feeder2_line147 | 3 | 99 | 1.1571e-06 | 2.2477e-06 | 1.1687e-06 | 2.2704e-06
840 | feeder2_line148 | 1 | 99 | 0.085772 | 0.085772 | 0.086638 | 0.086638
840 | feeder2_line148 | 2 | 99 | 5.9744e-07 | 1.4905e-06 | 6.0347e-07 | 1.5056e-06
840 | feeder2_line148 | 3 | 99 | 6.0308e-07 | 1.5061e-06 | 6.0917e-07 | 1.5214e-06
840 | feeder2_line149 | 1 | 354.6 | 86.1888 | 86.1885 | 24.3059 | 24.3058
840 | feeder2_line149 | 2 | 354.6 | 97.8679 | 97.8715 | 27.5995 | 27.6005
840 | feeder2_line149 | 3 | 354.6 | 96.5111 | 96.5079 | 27.2169 | 27.216
840 | feeder2_line150 | 1 | 354.6 | 86.1889 | 86.1885 | 24.3059 | 24.3058
840 | feeder2_line150 | 2 | 354.6 | 99.0001 | 99.0036 | 27.9188 | 27.9198
840 | feeder2_line150 | 3 | 354.6 | 96.5112 | 96.5079 | 27.2169 | 27.216
840 | feeder2_line151 | 1 | 99 | 9.6415e-06 | 1.7656e-06 | 9.7389e-06 | 1.7834e-06
840 | feeder2_line151 | 2 | 99 | 1.1508 | 1.1508 | 1.1624 | 1.1624
840 | feeder2_line151 | 3 | 99 | 9.8578e-06 | 1.7893e-06 | 9.9573e-06 | 1.8073e-06
840 | feeder2_line152 | 1 | 354.6 | 1.1505e-11 | 1.1774e-06 | 3.2445e-12 | 3.3203e-07
840 | feeder2_line152 | 2 | 354.6 | 1.3095e-11 | 1.1804e-06 | 3.6928e-12 | 3.3287e-07
840 | feeder2_line152 | 3 | 354.6 | 1.3962 | 1.3962 | 0.39374 | 0.39373
840 | feeder2_line153 | 1 | 99 | 1.2785 | 1.2785 | 1.2914 | 1.2914
840 | feeder2_line153 | 2 | 99 | 4.9918e-08 | 5.9054e-07 | 5.0422e-08 | 5.965e-07
840 | feeder2_line153 | 3 | 99 | 4.9099e-08 | 5.967e-07 | 4.9595e-08 | 6.0272e-07
840 | feeder2_line154 | 1 | 99 | 5.7122e-07 | 8.7605e-07 | 5.7699e-07 | 8.849e-07
840 | feeder2_line154 | 2 | 99 | 5.7301e-07 | 8.7874e-07 | 5.788e-07 | 8.8762e-07
840 | feeder2_line154 | 3 | 99 | 0.22237 | 0.22237 | 0.22462 | 0.22461
840 | feeder2_line155 | 1 | 99 | 87.1697 | 87.1694 | 88.0502 | 88.0499
840 | feeder2_line155 | 2 | 99 | 99 | 99.0036 | 100 | 100.0037
840 | feeder2_line155 | 3 | 99 | 97.5982 | 97.595 | 98.5841 | 98.5808
840 | feeder2_line156 | 1 | 99 | 5.9648e-07 | 1.1529e-06 | 6.0251e-07 | 1.1646e-06
840 | feeder2_line156 | 2 | 99 | 0.76048 | 0.76049 | 0.76816 | 0.76817
840 | feeder2_line156 | 3 | 99 | 6.0336e-07 | 1.1684e-06 | 6.0945e-07 | 1.1802e-06
840 | feeder2_line157 | 1 | 99 | 2.5414e-08 | 2.5029e-07 | 2.5671e-08 | 2.5282e-07
840 | feeder2_line157 | 2 | 99 | 0.3924 | 0.39241 | 0.39637 | 0.39637
840 | feeder2_line157 | 3 | 99 | 2.4542e-08 | 2.5365e-07 | 2.479e-08 | 2.5621e-07
870 | feeder2_line1 | 1 | 354.6 | 52.9869 | 52.9928 | 14.9427 | 14.9444
870 | feeder2_line1 | 2 | 354.6 | 59.7904 | 59.7888 | 16.8614 | 16.8609
870 | feeder2_line1 | 3 | 354.6 | 83.8556 | 83.8545 | 23.6479 | 23.6476
870 | feeder2_line2 | 1 | 354.6 | 52.3861 | 52.3921 | 14.7733 | 14.775
870 | feeder2_line2 | 2 | 354.6 | 59.7906 | 59.7888 | 16.8614 | 16.8609
870 | feeder2_line2 | 3 | 354.6 | 83.8558 | 83.8545 | 23.648 | 23.6476
870 | feeder2_line3 | 1 | 80.1 | 3.8343 | 3.8344 | 4.7869 | 4.787
870 | feeder2_line3 | 2 | 80.1 | 5.6982e-07 | 1.053e-06 | 7.1138e-07 | 1.3146e-06
870 | feeder2_line3 | 3 | 80.1 | 5.7155e-07 | 1.0562e-06 | 7.1355e-07 | 1.3186e-06
870 | feeder2_line4 | 1 | 354.6 | 52.3861 | 52.3921 | 14.7733 | 14.775
870 | feeder2_line4 | 2 | 354.6 | 59.8473 | 59.8455 | 16.8774 | 16.8769
870 | feeder2_line4 | 3 | 354.6 | 83.8559 | 83.8545 | 23.648 | 23.6476
870 | feeder2_line5 | 1 | 80.1 | 5.6936e-07 | 9.9351e-07 | 7.1081e-07 | 1.2403e-06
870 | feeder2_line5 | 2 | 80.1 | 0.090352 | 0.09035 | 0.1128 | 0.1128
870 | feeder2_line5 | 3 | 80.1 | 5.7161e-07 | 9.9738e-07 | 7.1361e-07 | 1.2452e-06
870 | feeder2_line6 | 1 | 80.1 | 5.6932e-07 | 1.1687e-06 | 7.1076e-07 | 1.459e-06
870 | feeder2_line6 | 2 | 80.1 | 5.698e-07 | 1.1696e-06 | 7.1136e-07 | 1.4602e-06
870 | feeder2_line6 | 3 | 80.1 | 1.2748 | 1.2748 | 1.5915 | 1.5915
870 | feeder2_line7 | 1 | 354.6 | 52.3862 | 52.3921 | 14.7733 | 14.775
870 | feeder2_line7 | 2 | 354.6 | 59.8473 | 59.8455 | 16.8774 | 16.8769
870 | feeder2_line7 | 3 | 354.6 | 84.9116 | 84.9101 | 23.9457 | 23.9453
870 | feeder2_line8 | 1 | 80.1 | 0.073113 | 0.073114 | 0.091277 | 0.091278
870 | feeder2_line8 | 2 | 80.1 | 5.6976e-07 | 1.1277e-06 | 7.1131e-07 | 1.4079e-06
870 | feeder2_line8 | 3 | 80.1 | 5.7188e-07 | 1.1319e-06 | 7.1396e-07 | 1.4131e-06
870 | feeder2_line9 | 1 | 354.6 | 52.4209 | 52.4269 | 14.7831 | 14.7848
870 | feeder2_line9 | 2 | 354.6 | 59.8473 | 59.8455 | 16.8774 | 16.8769
870 | feeder2_line9 | 3 | 354.6 | 84.9116 | 84.9101 | 23.9457 | 23.9453
870 | feeder2_line10 | 1 | 80.1 | 8.4131e-07 | 1.4876e-06 | 1.0503e-06 | 1.8571e-06
870 | feeder2_line10 | 2 | 80.1 | 0.072939 | 0.072938 | 0.091059 | 0.091059
870 | feeder2_line10 | 3 | 80.1 | 8.4553e-07 | 1.4946e-06 | 1.0556e-06 | 1.8659e-06
870 | feeder2_line11 | 1 | 354.6 | 52.421 | 52.4269 | 14.7831 | 14.7848
870 | feeder2_line11 | 2 | 354.6 | 59.8932 | 59.8913 | 16.8904 | 16.8898
870 | feeder2_line11 | 3 | 354.6 | 84.9116 | 84.9101 | 23.9457 | 23.9453
870 | feeder2_line12 | 1 | 80.1 | 5.4418e-07 | 9.8665e-07 | 6.7937e-07 | 1.2318e-06
870 | feeder2_line12 | 2 | 80.1 | 5.4499e-07 | 9.8765e-07 | 6.8038e-07 | 1.233e-06
870 | feeder2_line12 | 3 | 80.1 | 0.06176 | 0.06176 | 0.077104 | 0.077104
870 | feeder2_line13 | 1 | 354.6 | 52.4211 | 52.4269 | 14.7832 | 14.7848
870 | feeder2_line13 | 2 | 354.6 | 59.8933 | 59.8913 | 16.8904 | 16.8898
870 | feeder2_line13 | 3 | 354.6 | 84.9652 | 84.9637 | 23.9608 | 23.9604
870 | feeder2_line14 | 1 | 80.1 | 0.086441 | 0.086444 | 0.10792 | 0.10792
870 | feeder2_line14 | 2 | 80.1 | 2.9724e-07 | 6.4401e-07 | 3.7109e-07 | 8.04e-07
870 | feeder2_line14 | 3 | 80.1 | 2.9836e-07 | 6.4664e-07 | 3.7249e-07 | 8.0729e-07
870 | feeder2_line15 | 1 | 354.6 | 52.4618 | 52.4676 | 14.7946 | 14.7963
870 | feeder2_line15 | 2 | 354.6 | 59.8933 | 59.8913 | 16.8904 | 16.8898
870 | feeder2_line15 | 3 | 354.6 | 84.9652 | 84.9637 | 23.9608 | 23.9604
870 | feeder2_line16 | 1 | 80.1 | 5.6904e-07 | 1.0252e-06 | 7.1041e-07 | 1.2799e-06
870 | feeder2_line16 | 2 | 80.1 | 1.7074 | 1.7074 | 2.1316 | 2.1316
870 | feeder2_line16 | 3 | 80.1 | 5.7218e-07 | 1.0308e-06 | 7.1434e-07 | 1.2869e-06
870 | feeder2_line17 | 1 | 354.6 | 52.4618 | 52.4676 | 14.7946 | 14.7963
870 | feeder2_line17 | 2 | 354.6 | 60.8836 | 60.8815 | 17.1696 | 17.1691
870 | feeder2_line17 | 3 | 354.6 | 84.9652 | 84.9637 | 23.9609 | 23.9604
870 | feeder2_line18 | 1 | 80.1 | 5.4373e-07 | 7.3348e-07 | 6.7881e-07 | 9.1571e-07
870 | feeder2_line18 | 2 | 80.1 | 5.4488e-07 | 7.3459e-07 | 6.8025e-07 | 9.1709e-07
870 | feeder2_line18 | 3 | 80.1 | 0.040121 | 0.040111 | 0.050088 | 0.050076
870 | feeder2_line19 | 1 | 354.6 | 52.4618 | 52.4676 | 14.7946 | 14.7963
870 | feeder2_line19 | 2 | 354.6 | 60.8836 | 60.8815 | 17.1696 | 17.1691
870 | feeder2_line19 | 3 | 354.6 | 84.9991 | 84.9976 | 23.9704 | 23.97
870 | feeder2_line20 | 1 | 99 | 5.436e-07 | 8.7924e-07 | 5.4909e-07 | 8.8812e-07
870 | feeder2_line20 | 2 | 99 | 5.4485e-07 | 8.8068e-07 | 5.5036e-07 | 8.8958e-07
870 | feeder2_line20 | 3 | 99 | 0.085855 | 0.085842 | 0.086723 | 0.086709
870 | feeder2_line21 | 1 | 354.6 | 52.4619 | 52.4676 | 14.7947 | 14.7963
870 | feeder2_line21 | 2 | 354.6 | 60.8837 | 60.8815 | 17.1697 | 17.1691
870 | feeder2_line21 | 3 | 354.6 | 85.0741 | 85.0724 | 23.9916 | 23.9911
870 | feeder2_line22 | 1 | 99 | 5.6858e-07 | 1.0078e-06 | 5.7433e-07 | 1.018e-06
870 | feeder2_line22 | 2 | 99 | 1.9255 | 1.9255 | 1.9449 | 1.945
870 | feeder2_line22 | 3 | 99 | 5.7301e-07 | 1.0156e-06 | 5.788e-07 | 1.0258e-06
870 | feeder2_line23 | 1 | 99 | 5.6859e-07 | 9.4342e-07 | 5.7433e-07 | 9.5295e-07
870 | feeder2_line23 | 2 | 99 | 5.6959e-07 | 9.4504e-07 | 5.7534e-07 | 9.5459e-07
870 | feeder2_line23 | 3 | 99 | 2.1916 | 2.1916 | 2.2137 | 2.2137
870 | feeder2_line24 | 1 | 354.6 | 52.4619 | 52.4676 | 14.7947 | 14.7963
870 | feeder2_line24 | 2 | 354.6 | 62.0606 | 62.0583 | 17.5016 | 17.5009
870 | feeder2_line24 | 3 | 354.6 | 85.1912 | 85.1895 | 24.0246 | 24.0241
870 | feeder2_line25 | 1 | 99 | 1.9286 | 1.9286 | 1.948 | 1.9481
870 | feeder2_line25 | 2 | 99 | 4.9519e-08 | 6.8704e-07 | 5.002e-08 | 6.9398e-07
870 | feeder2_line25 | 3 | 99 | 4.9135e-08 | 6.9142e-07 | 4.9631e-08 | 6.984e-07
870 | feeder2_line26 | 1 | 99 | 0.086006 | 0.086009 | 0.086875 | 0.086878
870 | feeder2_line26 | 2 | 99 | 5.4481e-07 | 8.512e-07 | 5.5031e-07 | 8.5979e-07
870 | feeder2_line26 | 3 | 99 | 5.4866e-07 | 8.5663e-07 | 5.542e-07 | 8.6528e-07
870 | feeder2_line27 | 1 | 354.6 | 53.3611 | 53.3669 | 15.0482 | 15.0499
870 | feeder2_line27 | 2 | 354.6 | 62.0606 | 62.0583 | 17.5016 | 17.5009
870 | feeder2_line27 | 3 | 354.6 | 85.1912 | 85.1895 | 24.0246 | 24.0241
870 | feeder2_line28 | 1 | 99 | 2.5151e-06 | 7.0503e-07 | 2.5405e-06 | 7.1215e-07
870 | feeder2_line28 | 2 | 99 | 1.9694 | 1.9694 | 1.9893 | 1.9893
870 | feeder2_line28 | 3 | 99 | 2.5489e-06 | 7.1151e-07 | 2.5746e-06 | 7.187e-07
870 | feeder2_line29 | 1 | 354.6 | 53.3611 | 53.3669 | 15.0482 | 15.0499
870 | feeder2_line29 | 2 | 354.6 | 61.545 | 61.5426 | 17.3562 | 17.3555
870 | feeder2_line29 | 3 | 354.6 | 85.1912 | 85.1895 | 24.0246 | 24.0241
870 | feeder2_line30 | 1 | 266.4 | 3.7506 | 3.7506 | 1.4079 | 1.4079
870 | feeder2_line30 | 2 | 266.4 | 3.6929 | 3.6928 | 1.3862 | 1.3862
870 | feeder2_line30 | 3 | 266.4 | 3.1676 | 3.1673 | 1.1891 | 1.1889
870 | feeder2_line31 | 1 | 354.6 | 54.1723 | 54.178 | 15.277 | 15.2786
870 | feeder2_line31 | 2 | 354.6 | 63.0966 | 63.0934 | 17.7937 | 17.7928
870 | feeder2_line31 | 3 | 354.6 | 88.001 | 87.9987 | 24.817 | 24.8163
870 | feeder2_line32 | 1 | 354.6 | 54.1723 | 54.178 | 15.277 | 15.2786
870 | feeder2_line32 | 2 | 354.6 | 64.2852 | 64.2819 | 18.1289 | 18.128
870 | feeder2_line32 | 3 | 354.6 | 88.001 | 87.9987 | 24.817 | 24.8163
870 | feeder2_line33 | 1 | 99 | 5.0346e-08 | 6.7975e-07 | 5.0855e-08 | 6.8662e-07
870 | feeder2_line33 | 2 | 99 | 1.7494 | 1.7494 | 1.7671 | 1.7671
870 | feeder2_line33 | 3 | 99 | 4.8974e-08 | 6.8734e-07 | 4.9469e-08 | 6.9428e-07
870 | feeder2_line34 | 1 | 354.6 | 54.1723 | 54.178 | 15.277 | 15.2786
870 | feeder2_line34 | 2 | 354.6 | 64.2852 | 64.2819 | 18.1289 | 18.128
870 | feeder2_line34 | 3 | 354.6 | 88.0754 | 88.0731 | 24.838 | 24.8373
870 | feeder2_line35 | 1 | 99 | 2.9653e-07 | 7.5266e-07 | 2.9952e-07 | 7.6026e-07
870 | feeder2_line35 | 2 | 99 | 2.9713e-07 | 7.5475e-07 | 3.0013e-07 | 7.6237e-07
870 | feeder2_line35 | 3 | 99 | 0.085318 | 0.085317 | 0.086179 | 0.086178
870 | feeder2_line36 | 1 | 354.6 | 54.1879 | 54.1937 | 15.2814 | 15.2831
870 | feeder2_line36 | 2 | 354.6 | 64.2852 | 64.2819 | 18.1289 | 18.128
870 | feeder2_line36 | 3 | 354.6 | 88.0754 | 88.0731 | 24.8379 | 24.8373
870 | feeder2_line37 | 1 | 99 | 0.028489 | 0.028632 | 0.028777 | 0.028921
870 | feeder2_line37 | 2 | 99 | 2.9713e-07 | 8.3511e-07 | 3.0013e-07 | 8.4355e-07
870 | feeder2_line37 | 3 | 99 | 2.9955e-07 | 8.4257e-07 | 3.0257e-07 | 8.5108e-07
870 | feeder2_line38 | 1 | 99 | 3.2174e-07 | 7.6873e-07 | 3.2499e-07 | 7.765e-07
870 | feeder2_line38 | 2 | 99 | 1.3237 | 1.3237 | 1.337 | 1.337
870 | feeder2_line38 | 3 | 99 | 3.238e-07 | 7.7682e-07 | 3.2707e-07 | 7.8467e-07
870 | feeder2_line39 | 1 | 266.4 | 3.7506 | 3.7506 | 1.4079 | 1.4079
870 | feeder2_line39 | 2 | 266.4 | 2.7447 | 2.7444 | 1.0303 | 1.0302
870 | feeder2_line39 | 3 | 266.4 | 3.1676 | 3.1673 | 1.1891 | 1.1889
870 | feeder2_line40 | 1 | 354.6 | 55.2213 | 55.2272 | 15.5728 | 15.5745
870 | feeder2_line40 | 2 | 354.6 | 64.2852 | 64.2819 | 18.1289 | 18.128
870 | feeder2_line40 | 3 | 354.6 | 88.0754 | 88.0731 | 24.838 | 24.8373
870 | feeder2_line41 | 1 | 99 | 1.9302 | 1.9302 | 1.9497 | 1.9497
870 | feeder2_line41 | 2 | 99 | 4.9543e-08 | 7.2973e-07 | 5.0044e-08 | 7.371e-07
870 | feeder2_line41 | 3 | 99 | 4.893e-08 | 7.3634e-07 | 4.9424e-08 | 7.4378e-07
870 | feeder2_line42 | 1 | 99 | 2.9658e-07 | 7.4198e-07 | 2.9958e-07 | 7.4948e-07
870 | feeder2_line42 | 2 | 99 | 2.9711e-07 | 7.4383e-07 | 3.0011e-07 | 7.5134e-07
870 | feeder2_line42 | 3 | 99 | 0.07692 | 0.076919 | 0.077697 | 0.077696
870 | feeder2_line43 | 1 | 266.4 | 3.7506 | 3.7506 | 1.4079 | 1.4079
870 | feeder2_line43 | 2 | 266.4 | 2.7446 | 2.7444 | 1.0303 | 1.0302
870 | feeder2_line43 | 3 | 266.4 | 3.0906 | 3.0903 | 1.1601 | 1.16
870 | feeder2_line44 | 1 | 354.6 | 55.2213 | 55.2272 | 15.5728 | 15.5745
870 | feeder2_line44 | 2 | 354.6 | 64.2852 | 64.2819 | 18.1289 | 18.128
870 | feeder2_line44 | 3 | 354.6 | 88.152 | 88.1496 | 24.8596 | 24.8589
870 | feeder2_line45 | 1 | 99 | 5.0423e-08 | 5.7376e-07 | 5.0932e-08 | 5.7955e-07
870 | feeder2_line45 | 2 | 99 | 4.9544e-08 | 5.7549e-07 | 5.0044e-08 | 5.813e-07
870 | feeder2_line45 | 3 | 99 | 0.085539 | 0.085517 | 0.086403 | 0.086381
870 | feeder2_line46 | 1 | 99 | 5.6801e-07 | 1.3451e-06 | 5.7375e-07 | 1.3587e-06
870 | feeder2_line46 | 2 | 99 | 5.6946e-07 | 1.3484e-06 | 5.7521e-07 | 1.362e-06
870 | feeder2_line46 | 3 | 99 | 1.9248 | 1.9248 | 1.9442 | 1.9442
870 | feeder2_line47 | 1 | 266.4 | 3.7506 | 3.7506 | 1.4079 | 1.4079
870 | feeder2_line47 | 2 | 266.4 | 2.7446 | 2.7444 | 1.0303 | 1.0302
870 | feeder2_line47 | 3 | 266.4 | 1.1702 | 1.17 | 0.43927 | 0.43918
870 | feeder2_line48 | 1 | 99 | 1.1833 | 1.1833 | 1.1953 | 1.1952
870 | feeder2_line48 | 2 | 99 | 4.9539e-08 | 7.2601e-07 | 5.004e-08 | 7.3334e-07
870 | feeder2_line48 | 3 | 99 | 4.9004e-08 | 7.3184e-07 | 4.9499e-08 | 7.3924e-07
870 | feeder2_line49 | 1 | 266.4 | 2.8743 | 2.8742 | 1.0789 | 1.0789
870 | feeder2_line49 | 2 | 266.4 | 2.7446 | 2.7444 | 1.0303 | 1.0302
870 | feeder2_line49 | 3 | 266.4 | 1.1702 | 1.17 | 0.43926 | 0.43918
870 | feeder2_line50 | 1 | 99 | 5.68e-07 | 1.2241e-06 | 5.7374e-07 | 1.2365e-06
870 | feeder2_line50 | 2 | 99 | 1.2766 | 1.2766 | 1.2895 | 1.2895
870 | feeder2_line50 | 3 | 99 | 5.7407e-07 | 1.237e-06 | 5.7987e-07 | 1.2495e-06
870 | feeder2_line51 | 1 | 99 | 1.1688 | 1.169 | 1.1806 | 1.1808
870 | feeder2_line51 | 2 | 99 | 5.6945e-07 | 1.3322e-06 | 5.752e-07 | 1.3456e-06
870 | feeder2_line51 | 3 | 99 | 5.7407e-07 | 1.3429e-06 | 5.7987e-07 | 1.3565e-06
870 | feeder2_line52 | 1 | 266.4 | 1.7113 | 1.7113 | 0.64239 | 0.64237
870 | feeder2_line52 | 2 | 266.4 | 1.468 | 1.4679 | 0.55107 | 0.55102
870 | feeder2_line52 | 3 | 266.4 | 1.1701 | 1.17 | 0.43921 | 0.43918
870 | feeder2_line53 | 1 | 99 | 5.4285e-07 | 7.4708e-07 | 5.4834e-07 | 7.5463e-07
870 | feeder2_line53 | 2 | 99 | 1.4679 | 1.4679 | 1.4828 | 1.4828
870 | feeder2_line53 | 3 | 99 | 5.4957e-07 | 7.5497e-07 | 5.5512e-07 | 7.626e-07
870 | feeder2_line54 | 1 | 266.4 | 1.7112 | 1.7113 | 0.64233 | 0.64237
870 | feeder2_line54 | 2 | 266.4 | 8.4988e-05 | 4.5944e-06 | 3.1903e-05 | 1.7246e-06
870 | feeder2_line54 | 3 | 266.4 | 1.1699 | 1.17 | 0.43915 | 0.43918
870 | feeder2_line55 | 1 | 99 | 1.7008 | 1.7008 | 1.7179 | 1.7179
870 | feeder2_line55 | 2 | 99 | 4.9546e-08 | 7.2503e-07 | 5.0047e-08 | 7.3235e-07
870 | feeder2_line55 | 3 | 99 | 4.8873e-08 | 7.3214e-07 | 4.9367e-08 | 7.3953e-07
870 | feeder2_line56 | 1 | 354.6 | 56.2441 | 56.2501 | 15.8613 | 15.863
870 | feeder2_line56 | 2 | 354.6 | 64.2853 | 64.2819 | 18.129 | 18.128
870 | feeder2_line56 | 3 | 354.6 | 88.152 | 88.1496 | 24.8596 | 24.8589
870 | feeder2_line57 | 1 | 99 | 7.5446e-07 | 1.5302e-06 | 7.6208e-07 | 1.5457e-06
870 | feeder2_line57 | 2 | 99 | 7.4303e-07 | 1.5341e-06 | 7.5053e-07 | 1.5496e-06
870 | feeder2_line57 | 3 | 99 | 1.17 | 1.17 | 1.1818 | 1.1818
870 | feeder2_line58 | 1 | 266.4 | 1.7112 | 1.7113 | 0.64235 | 0.64237
870 | feeder2_line58 | 2 | 266.4 | 1.8799e-05 | 2.6674e-06 | 7.0568e-06 | 1.0013e-06
870 | feeder2_line58 | 3 | 266.4 | 1.9005e-05 | 2.6882e-06 | 7.134e-06 | 1.0091e-06
870 | feeder2_line59 | 1 | 99 | 5.0299e-08 | 5.3193e-07 | 5.0807e-08 | 5.3731e-07
870 | feeder2_line59 | 2 | 99 | 4.954e-08 | 5.3326e-07 | 5.004e-08 | 5.3865e-07
870 | feeder2_line59 | 3 | 99 | 1.1086 | 1.1086 | 1.1198 | 1.1198
870 | feeder2_line60 | 1 | 99 | 2.9657e-07 | 8.0391e-07 | 2.9957e-07 | 8.1203e-07
870 | feeder2_line60 | 2 | 99 | 2.9711e-07 | 8.0592e-07 | 3.0011e-07 | 8.1406e-07
870 | feeder2_line60 | 3 | 99 | 0.061535 | 0.061534 | 0.062156 | 0.062156
870 | feeder2_line61 | 1 | 266.4 | 0.086689 | 0.08686 | 0.032541 | 0.032605
870 | feeder2_line61 | 2 | 266.4 | 3.7902 | 3.7903 | 1.4227 | 1.4228
870 | feeder2_line61 | 3 | 266.4 | 3.8531 | 3.8533 | 1.4463 | 1.4464
870 | feeder2_line62 | 1 | 354.6 | 56.2977 | 56.3038 | 15.8764 | 15.8781
870 | feeder2_line62 | 2 | 354.6 | 66.5253 | 66.5219 | 18.7606 | 18.7597
870 | feeder2_line62 | 3 | 354.6 | 91.178 | 91.1758 | 25.7129 | 25.7123
870 | feeder2_line63 | 1 | 99 | 0.090075 | 0.090081 | 0.090985 | 0.090991
870 | feeder2_line63 | 2 | 99 | 5.6945e-07 | 1.2117e-06 | 5.752e-07 | 1.2239e-06
870 | feeder2_line63 | 3 | 99 | 5.7407e-07 | 1.2214e-06 | 5.7987e-07 | 1.2338e-06
870 | feeder2_line64 | 1 | 99 | 1.6221 | 1.6221 | 1.6385 | 1.6385
870 | feeder2_line64 | 2 | 99 | 6.4044e-12 | 3.1918e-07 | 6.4691e-12 | 3.2241e-07
870 | feeder2_line64 | 3 | 99 | 1.9148e-12 | 3.2175e-07 | 1.9342e-12 | 3.25e-07
870 | feeder2_line65 | 1 | 99 | 5.0587e-08 | 6.3441e-07 | 5.1098e-08 | 6.4082e-07
870 | feeder2_line65 | 2 | 99 | 0.090398 | 0.090392 | 0.091311 | 0.091306
870 | feeder2_line65 | 3 | 99 | 4.8799e-08 | 6.4367e-07 | 4.9292e-08 | 6.5018e-07
870 | feeder2_line66 | 1 | 354.6 | 56.2977 | 56.3038 | 15.8764 | 15.8781
870 | feeder2_line66 | 2 | 354.6 | 66.5949 | 66.5915 | 18.7803 | 18.7793
870 | feeder2_line66 | 3 | 354.6 | 91.1779 | 91.1758 | 25.7129 | 25.7123
870 | feeder2_line67 | 1 | 99 | 2.5259e-08 | 3.5875e-07 | 2.5514e-08 | 3.6237e-07
870 | feeder2_line67 | 2 | 99 | 2.4778e-08 | 3.5999e-07 | 2.5028e-08 | 3.6362e-07
870 | feeder2_line67 | 3 | 99 | 1.9155 | 1.9155 | 1.9349 | 1.9349
870 | feeder2_line68 | 1 | 266.4 | 0.086727 | 0.08686 | 0.032555 | 0.032605
870 | feeder2_line68 | 2 | 266.4 | 3.7902 | 3.7903 | 1.4228 | 1.4228
870 | feeder2_line68 | 3 | 266.4 | 1.9843 | 1.9844 | 0.74484 | 0.7449
870 | feeder2_line69 | 1 | 99 | 16.298 | 16.2979 | 16.4626 | 16.4625
870 | feeder2_line69 | 2 | 99 | 2.5258e-06 | 6.6106e-07 | 2.5513e-06 | 6.6774e-07
870 | feeder2_line69 | 3 | 99 | 2.5624e-06 | 6.6835e-07 | 2.5883e-06 | 6.751e-07
870 | feeder2_line70 | 1 | 354.6 | 64.035 | 64.0417 | 18.0584 | 18.0603
870 | feeder2_line70 | 2 | 354.6 | 66.5949 | 66.5915 | 18.7803 | 18.7793
870 | feeder2_line70 | 3 | 354.6 | 91.1779 | 91.1758 | 25.7129 | 25.7123
870 | feeder2_line71 | 1 | 99 | 5.0624e-08 | 7.0768e-07 | 5.1135e-08 | 7.1483e-07
870 | feeder2_line71 | 2 | 99 | 2.0776 | 2.0776 | 2.0986 | 2.0985
870 | feeder2_line71 | 3 | 99 | 4.8774e-08 | 7.1836e-07 | 4.9266e-08 | 7.2561e-07
870 | feeder2_line72 | 1 | 354.6 | 64.0351 | 64.0417 | 18.0584 | 18.0603
870 | feeder2_line72 | 2 | 354.6 | 67.2946 | 67.2911 | 18.9776 | 18.9766
870 | feeder2_line72 | 3 | 354.6 | 91.178 | 91.1758 | 25.7129 | 25.7123
870 | feeder2_line73 | 1 | 99 | 5.9276e-07 | 1.5188e-06 | 5.9875e-07 | 1.5341e-06
870 | feeder2_line73 | 2 | 99 | 1.7493 | 1.7493 | 1.767 | 1.767
870 | feeder2_line73 | 3 | 99 | 5.9982e-07 | 1.5397e-06 | 6.0588e-07 | 1.5553e-06
870 | feeder2_line74 | 1 | 99 | 5.0529e-08 | 4.5298e-07 | 5.1039e-08 | 4.5756e-07
870 | feeder2_line74 | 2 | 99 | 1.9917 | 1.9917 | 2.0118 | 2.0118
870 | feeder2_line74 | 3 | 99 | 4.8837e-08 | 4.5923e-07 | 4.933e-08 | 4.6386e-07
870 | feeder2_line75 | 1 | 266.4 | 0.086823 | 0.08686 | 0.032591 | 0.032605
870 | feeder2_line75 | 2 | 266.4 | 0.090333 | 0.090363 | 0.033909 | 0.03392
870 | feeder2_line75 | 3 | 266.4 | 1.9844 | 1.9844 | 0.74488 | 0.7449
870 | feeder2_line76 | 1 | 99 | 0.086854 | 0.08686 | 0.087732 | 0.087737
870 | feeder2_line76 | 2 | 99 | 8.4185e-07 | 1.5721e-06 | 8.5035e-07 | 1.588e-06
870 | feeder2_line76 | 3 | 99 | 8.509e-07 | 1.5883e-06 | 8.595e-07 | 1.6043e-06
870 | feeder2_line77 | 1 | 99 | 2.5265e-08 | 5.6925e-07 | 2.552e-08 | 5.75e-07
870 | feeder2_line77 | 2 | 99 | 2.4778e-08 | 5.712e-07 | 2.5028e-08 | 5.7697e-07
870 | feeder2_line77 | 3 | 99 | 1.9844 | 1.9844 | 2.0044 | 2.0045
870 | feeder2_line78 | 1 | 266.4 | 1.0155e-11 | 9.4483e-07 | 3.812e-12 | 3.5467e-07
870 | feeder2_line78 | 2 | 266.4 | 0.090365 | 0.090363 | 0.033921 | 0.03392
870 | feeder2_line78 | 3 | 266.4 | 7.2721e-12 | 9.5634e-07 | 2.7298e-12 | 3.5899e-07
870 | feeder2_line79 | 1 | 354.6 | 3.2034 | 3.203 | 0.90338 | 0.90328
870 | feeder2_line79 | 2 | 354.6 | 18.6765 | 18.6762 | 5.2669 | 5.2668
870 | feeder2_line79 | 3 | 354.6 | 6.315 | 6.3147 | 1.7809 | 1.7808
870 | feeder2_line80 | 1 | 354.6 | 66.4235 | 66.4297 | 18.732 | 18.7337
870 | feeder2_line80 | 2 | 354.6 | 79.429 | 79.4244 | 22.3996 | 22.3983
870 | feeder2_line80 | 3 | 354.6 | 93.1707 | 93.168 | 26.2749 | 26.2741
870 | feeder2_line81 | 1 | 354.6 | 66.4234 | 66.4297 | 18.7319 | 18.7337
870 | feeder2_line81 | 2 | 354.6 | 79.4289 | 79.4244 | 22.3996 | 22.3983
870 | feeder2_line81 | 3 | 354.6 | 94.0795 | 94.0769 | 26.5312 | 26.5304
870 | feeder2_line82 | 1 | 354.6 | 1.9272e-11 | 7.2617e-07 | 5.435e-12 | 2.0479e-07
870 | feeder2_line82 | 2 | 354.6 | 7.8088e-12 | 7.2859e-07 | 2.2022e-12 | 2.0547e-07
870 | feeder2_line82 | 3 | 354.6 | 0.991 | 0.991 | 0.27947 | 0.27947
870 | feeder2_line83 | 1 | 354.6 | 66.4235 | 66.4297 | 18.732 | 18.7337
870 | feeder2_line83 | 2 | 354.6 | 79.581 | 79.5763 | 22.4425 | 22.4411
870 | feeder2_line83 | 3 | 354.6 | 94.0797 | 94.0769 | 26.5312 | 26.5304
870 | feeder2_line84 | 1 | 354.6 | 6.9639e-12 | 1.2833e-06 | 1.9639e-12 | 3.6191e-07
870 | feeder2_line84 | 2 | 354.6 | 1.0451 | 1.0451 | 0.29474 | 0.29473
870 | feeder2_line84 | 3 | 354.6 | 1.0515e-11 | 1.3021e-06 | 2.9654e-12 | 3.6721e-07
870 | feeder2_line85 | 1 | 99 | 1.3205 | 1.3205 | 1.3339 | 1.3339
870 | feeder2_line85 | 2 | 99 | 4.9592e-08 | 4.596e-07 | 5.0093e-08 | 4.6424e-07
870 | feeder2_line85 | 3 | 99 | 4.8729e-08 | 4.651e-07 | 4.9222e-08 | 4.698e-07
870 | feeder2_line86 | 1 | 354.6 | 66.379 | 66.3851 | 18.7194 | 18.7211
870 | feeder2_line86 | 2 | 354.6 | 79.5811 | 79.5763 | 22.4425 | 22.4412
870 | feeder2_line86 | 3 | 354.6 | 94.0798 | 94.0769 | 26.5312 | 26.5304
870 | feeder2_line87 | 1 | 354.6 | 66.3791 | 66.3851 | 18.7194 | 18.7211
870 | feeder2_line87 | 2 | 354.6 | 82.0966 | 82.0916 | 23.1519 | 23.1505
870 | feeder2_line87 | 3 | 354.6 | 95.061 | 95.0579 | 26.8079 | 26.8071
870 | feeder2_line88 | 1 | 354.6 | 0.00010827 | 3.3237e-06 | 3.0532e-05 | 9.373e-07
870 | feeder2_line88 | 2 | 354.6 | 3.6433 | 3.6432 | 1.0274 | 1.0274
870 | feeder2_line88 | 3 | 354.6 | 1.9071 | 1.907 | 0.53781 | 0.5378
870 | feeder2_line89 | 1 | 354.6 | 66.3772 | 66.3851 | 18.7189 | 18.7211
870 | feeder2_line89 | 2 | 354.6 | 83.6937 | 83.6908 | 23.6023 | 23.6015
870 | feeder2_line89 | 3 | 354.6 | 95.0588 | 95.0579 | 26.8073 | 26.8071
870 | feeder2_line90 | 1 | 354.6 | 0.00071028 | 2.0054e-06 | 0.0002003 | 5.6555e-07
870 | feeder2_line90 | 2 | 354.6 | 2.3112 | 2.3115 | 0.65179 | 0.65187
870 | feeder2_line90 | 3 | 354.6 | 0.00073084 | 2.0381e-06 | 0.0002061 | 5.7476e-07
870 | feeder2_line91 | 1 | 354.6 | 66.3772 | 66.3851 | 18.7189 | 18.7211
870 | feeder2_line91 | 2 | 354.6 | 83.6937 | 83.6908 | 23.6023 | 23.6015
870 | feeder2_line91 | 3 | 354.6 | 95.1162 | 95.1154 | 26.8235 | 26.8233
870 | feeder2_line92 | 1 | 354.6 | 2.9673e-12 | 1.0125e-06 | 8.368e-13 | 2.8552e-07
870 | feeder2_line92 | 2 | 354.6 | 2.9673e-12 | 1.0164e-06 | 8.368e-13 | 2.8662e-07
870 | feeder2_line92 | 3 | 354.6 | 0.061238 | 0.061237 | 0.01727 | 0.017269
870 | feeder2_line93 | 1 | 99 | 2.539e-08 | 3.3772e-07 | 2.5647e-08 | 3.4113e-07
870 | feeder2_line93 | 2 | 99 | 1.0453 | 1.0452 | 1.0558 | 1.0558
870 | feeder2_line93 | 3 | 99 | 2.4355e-08 | 3.4343e-07 | 2.4601e-08 | 3.469e-07
870 | feeder2_line94 | 1 | 354.6 | 2.5391e-06 | 1.6454e-06 | 7.1605e-07 | 4.6402e-07
870 | feeder2_line94 | 2 | 354.6 | 1.5378 | 1.5377 | 0.43366 | 0.43366
870 | feeder2_line94 | 3 | 354.6 | 2.4354e-06 | 1.6708e-06 | 6.8682e-07 | 4.7118e-07
870 | feeder2_line95 | 1 | 99 | 3.5193e-06 | 2.5772e-06 | 3.5549e-06 | 2.6032e-06
870 | feeder2_line95 | 2 | 99 | 3.6432 | 3.6432 | 3.68 | 3.68
870 | feeder2_line95 | 3 | 99 | 3.594e-06 | 2.6196e-06 | 3.6303e-06 | 2.646e-06
870 | feeder2_line96 | 1 | 354.6 | 0.00011943 | 6.1443e-07 | 3.3679e-05 | 1.7327e-07
870 | feeder2_line96 | 2 | 354.6 | 0.00012018 | 6.1723e-07 | 3.3893e-05 | 1.7406e-07
870 | feeder2_line96 | 3 | 354.6 | 1.907 | 1.907 | 0.5378 | 0.5378
870 | feeder2_line97 | 1 | 354.6 | 67.2744 | 67.2822 | 18.9719 | 18.9741
870 | feeder2_line97 | 2 | 354.6 | 83.694 | 83.6908 | 23.6024 | 23.6015
870 | feeder2_line97 | 3 | 354.6 | 95.1165 | 95.1154 | 26.8236 | 26.8233
870 | feeder2_line98 | 1 | 354.6 | 1.1237 | 1.1221 | 0.31689 | 0.31645
870 | feeder2_line98 | 2 | 354.6 | 0.0017066 | 6.1287e-07 | 0.00048127 | 1.7283e-07
870 | feeder2_line98 | 3 | 354.6 | 0.0017163 | 6.2412e-07 | 0.00048402 | 1.7601e-07
870 | feeder2_line99 | 1 | 99 | 2.5367e-08 | 4.4165e-07 | 2.5623e-08 | 4.4611e-07
870 | feeder2_line99 | 2 | 99 | 2.4798e-08 | 4.4356e-07 | 2.5048e-08 | 4.4804e-07
870 | feeder2_line99 | 3 | 99 | 1.907 | 1.907 | 1.9263 | 1.9263
870 | feeder2_line100 | 1 | 99 | 1.1221 | 1.1221 | 1.1334 | 1.1335
870 | feeder2_line100 | 2 | 99 | 2.4795e-08 | 6.0905e-07 | 2.5045e-08 | 6.152e-07
870 | feeder2_line100 | 3 | 99 | 2.4352e-08 | 6.166e-07 | 2.4598e-08 | 6.2282e-07
870 | feeder2_line101 | 1 | 354.6 | 1.5373 | 1.5369 | 0.43354 | 0.43343
870 | feeder2_line101 | 2 | 354.6 | 18.6765 | 18.6762 | 5.2669 | 5.2668
870 | feeder2_line101 | 3 | 354.6 | 6.315 | 6.3147 | 1.7809 | 1.7808
870 | feeder2_line102 | 1 | 99 | 1.6713 | 1.6714 | 1.6882 | 1.6883
870 | feeder2_line102 | 2 | 99 | 2.3249e-06 | 8.7088e-07 | 2.3484e-06 | 8.7968e-07
870 | feeder2_line102 | 3 | 99 | 2.3536e-06 | 8.8121e-07 | 2.3773e-06 | 8.9011e-07
870 | feeder2_line103 | 1 | 99 | 5.4204e-07 | 7.9425e-07 | 5.4752e-07 | 8.0227e-07
870 | feeder2_line103 | 2 | 99 | 1.5841 | 1.5841 | 1.6001 | 1.6001
870 | feeder2_line103 | 3 | 99 | 5.5189e-07 | 8.0656e-07 | 5.5747e-07 | 8.1471e-07
870 | feeder2_line104 | 1 | 354.6 | 1.5372 | 1.5369 | 0.43351 | 0.43343
870 | feeder2_line104 | 2 | 354.6 | 17.1146 | 17.1144 | 4.8264 | 4.8264
870 | feeder2_line104 | 3 | 354.6 | 6.3149 | 6.3148 | 1.7809 | 1.7808
870 | feeder2_line105 | 1 | 99 | 2.5077e-06 | 7.3083e-07 | 2.533e-06 | 7.3821e-07
870 | feeder2_line105 | 2 | 99 | 2.5246e-06 | 7.3334e-07 | 2.5501e-06 | 7.4075e-07
870 | feeder2_line105 | 3 | 99 | 0.039778 | 0.039754 | 0.04018 | 0.040156
870 | feeder2_line106 | 1 | 354.6 | 1.5372 | 1.5369 | 0.43349 | 0.43343
870 | feeder2_line106 | 2 | 354.6 | 17.1145 | 17.1144 | 4.8264 | 4.8264
870 | feeder2_line106 | 3 | 354.6 | 6.2872 | 6.2871 | 1.773 | 1.773
870 | feeder2_line107 | 1 | 99 | 3.2165e-07 | 8.9063e-07 | 3.2489e-07 | 8.9963e-07
870 | feeder2_line107 | 2 | 99 | 13.1096 | 13.1097 | 13.242 | 13.2421
870 | feeder2_line107 | 3 | 99 | 3.2464e-07 | 9.0435e-07 | 3.2791e-07 | 9.1348e-07
870 | feeder2_line108 | 1 | 354.6 | 1.5372 | 1.5369 | 0.43349 | 0.43343
870 | feeder2_line108 | 2 | 354.6 | 4.2156 | 4.2154 | 1.1888 | 1.1888
870 | feeder2_line108 | 3 | 354.6 | 6.2872 | 6.2871 | 1.773 | 1.773
870 | feeder2_line109 | 1 | 354.6 | 78.1806 | 78.1875 | 22.0476 | 22.0495
870 | feeder2_line109 | 2 | 354.6 | 83.695 | 83.6908 | 23.6027 | 23.6015
870 | feeder2_line109 | 3 | 354.6 | 95.1176 | 95.1154 | 26.8239 | 26.8233
870 | feeder2_line110 | 1 | 99 | 14.0028 | 14.0018 | 14.1442 | 14.1433
870 | feeder2_line110 | 2 | 99 | 0.00079782 | 9.0211e-07 | 0.00080588 | 9.1122e-07
870 | feeder2_line110 | 3 | 99 | 0.00081188 | 9.1263e-07 | 0.00082008 | 9.2185e-07
870 | feeder2_line111 | 1 | 99 | 2.537e-08 | 3.772e-07 | 2.5626e-08 | 3.8101e-07
870 | feeder2_line111 | 2 | 99 | 1.4718 | 1.4718 | 1.4866 | 1.4866
870 | feeder2_line111 | 3 | 99 | 2.4359e-08 | 3.8341e-07 | 2.4605e-08 | 3.8728e-07
870 | feeder2_line112 | 1 | 99 | 3.2169e-07 | 9.0644e-07 | 3.2494e-07 | 9.1559e-07
870 | feeder2_line112 | 2 | 99 | 2.2896 | 2.2895 | 2.3127 | 2.3127
870 | feeder2_line112 | 3 | 99 | 3.2491e-07 | 9.2136e-07 | 3.2819e-07 | 9.3066e-07
870 | feeder2_line113 | 1 | 99 | 0.098888 | 0.098892 | 0.099887 | 0.099891
870 | feeder2_line113 | 2 | 99 | 3.2227e-07 | 8.9815e-07 | 3.2552e-07 | 9.0722e-07
870 | feeder2_line113 | 3 | 99 | 3.252e-07 | 9.094e-07 | 3.2849e-07 | 9.1859e-07
870 | feeder2_line114 | 1 | 99 | 1.5894 | 1.5894 | 1.6054 | 1.6055
870 | feeder2_line114 | 2 | 99 | 2.4793e-08 | 4.3306e-07 | 2.5043e-08 | 4.3743e-07
870 | feeder2_line114 | 3 | 99 | 2.4367e-08 | 4.3819e-07 | 2.4613e-08 | 4.4262e-07
870 | feeder2_line115 | 1 | 99 | 2.5318e-08 | 5.558e-07 | 2.5574e-08 | 5.6141e-07
870 | feeder2_line115 | 2 | 99 | 1.8329 | 1.8329 | 1.8514 | 1.8514
870 | feeder2_line115 | 3 | 99 | 2.4363e-08 | 5.6433e-07 | 2.4609e-08 | 5.7003e-07
870 | feeder2_line116 | 1 | 354.6 | 1.5372 | 1.5369 | 0.43349 | 0.43343
870 | feeder2_line116 | 2 | 354.6 | 2.3827 | 2.3825 | 0.67194 | 0.67188
870 | feeder2_line116 | 3 | 354.6 | 6.2872 | 6.2871 | 1.7731 | 1.773
870 | feeder2_line117 | 1 | 99 | 5.0883e-08 | 6.3443e-07 | 5.1397e-08 | 6.4083e-07
870 | feeder2_line117 | 2 | 99 | 1.9242 | 1.9242 | 1.9436 | 1.9436
870 | feeder2_line117 | 3 | 99 | 4.8688e-08 | 6.4579e-07 | 4.918e-08 | 6.5231e-07
870 | feeder2_line118 | 1 | 354.6 | 78.1807 | 78.1875 | 22.0476 | 22.0495
870 | feeder2_line118 | 2 | 354.6 | 85.4978 | 85.4935 | 24.111 | 24.1099
870 | feeder2_line118 | 3 | 354.6 | 95.1176 | 95.1154 | 26.8239 | 26.8233
870 | feeder2_line119 | 1 | 99 | 2.532e-08 | 5.9807e-07 | 2.5576e-08 | 6.0411e-07
870 | feeder2_line119 | 2 | 99 | 2.4796e-08 | 6.0002e-07 | 2.5046e-08 | 6.0608e-07
870 | feeder2_line119 | 3 | 99 | 0.093086 | 0.093083 | 0.094026 | 0.094023
870 | feeder2_line120 | 1 | 354.6 | 1.5372 | 1.5369 | 0.43349 | 0.43343
870 | feeder2_line120 | 2 | 354.6 | 2.3827 | 2.3825 | 0.67194 | 0.67188
870 | feeder2_line120 | 3 | 354.6 | 6.2244 | 6.2242 | 1.7553 | 1.7553
870 | feeder2_line121 | 1 | 99 | 3.2165e-07 | 9.261e-07 | 3.249e-07 | 9.3545e-07
870 | feeder2_line121 | 2 | 99 | 1.169 | 1.169 | 1.1808 | 1.1808
870 | feeder2_line121 | 3 | 99 | 3.246e-07 | 9.4019e-07 | 3.2787e-07 | 9.4969e-07
870 | feeder2_line122 | 1 | 354.6 | 1.5372 | 1.5369 | 0.43349 | 0.43343
870 | feeder2_line122 | 2 | 354.6 | 1.474 | 1.4739 | 0.41567 | 0.41565
870 | feeder2_line122 | 3 | 354.6 | 6.2243 | 6.2242 | 1.7553 | 1.7553
870 | feeder2_line123 | 1 | 99 | 5.6736e-07 | 9.5965e-07 | 5.7309e-07 | 9.6934e-07
870 | feeder2_line123 | 2 | 99 | 5.693e-07 | 9.6284e-07 | 5.7505e-07 | 9.7257e-07
870 | feeder2_line123 | 3 | 99 | 1.9804 | 1.9803 | 2.0004 | 2.0003
870 | feeder2_line124 | 1 | 354.6 | 1.5371 | 1.5369 | 0.43346 | 0.43343
870 | feeder2_line124 | 2 | 354.6 | 1.474 | 1.4739 | 0.41569 | 0.41565
870 | feeder2_line124 | 3 | 354.6 | 4.2798 | 4.2796 | 1.2069 | 1.2069
870 | feeder2_line125 | 1 | 99 | 5.6735e-07 | 8.9208e-07 | 5.7308e-07 | 9.0109e-07
870 | feeder2_line125 | 2 | 99 | 5.693e-07 | 8.9507e-07 | 5.7505e-07 | 9.0411e-07
870 | feeder2_line125 | 3 | 99 | 1.1041 | 1.104 | 1.1152 | 1.1152
870 | feeder2_line126 | 1 | 354.6 | 1.5372 | 1.5369 | 0.43351 | 0.43343
870 | feeder2_line126 | 2 | 354.6 | 1.4741 | 1.4739 | 0.41572 | 0.41565
870 | feeder2_line126 | 3 | 354.6 | 3.5522 | 3.5519 | 1.0017 | 1.0017
870 | feeder2_line127 | 1 | 99 | 5.6735e-07 | 1.068e-06 | 5.7308e-07 | 1.0787e-06
870 | feeder2_line127 | 2 | 99 | 5.693e-07 | 1.0715e-06 | 5.7505e-07 | 1.0824e-06
870 | feeder2_line127 | 3 | 99 | 0.97082 | 0.97081 | 0.98062 | 0.98061
870 | feeder2_line128 | 1 | 354.6 | 1.5371 | 1.5369 | 0.43348 | 0.43343
870 | feeder2_line128 | 2 | 354.6 | 1.4741 | 1.4739 | 0.41572 | 0.41565
870 | feeder2_line128 | 3 | 354.6 | 2.5816 | 2.5814 | 0.72804 | 0.72798
870 | feeder2_line129 | 1 | 99 | 5.4203e-07 | 8.6595e-07 | 5.4751e-07 | 8.747e-07
870 | feeder2_line129 | 2 | 99 | 1.4739 | 1.4739 | 1.4888 | 1.4888
870 | feeder2_line129 | 3 | 99 | 5.5168e-07 | 8.7908e-07 | 5.5725e-07 | 8.8796e-07
870 | feeder2_line130 | 1 | 354.6 | 1.5371 | 1.5369 | 0.43349 | 0.43343
870 | feeder2_line130 | 2 | 354.6 | 0.00030445 | 4.5981e-06 | 8.5858e-05 | 1.2967e-06
870 | feeder2_line130 | 3 | 354.6 | 2.5817 | 2.5814 | 0.72805 | 0.72798
870 | feeder2_line131 | 1 | 99 | 5.6734e-07 | 9.5976e-07 | 5.7307e-07 | 9.6946e-07
870 | feeder2_line131 | 2 | 99 | 5.6931e-07 | 9.6301e-07 | 5.7506e-07 | 9.7274e-07
870 | feeder2_line131 | 3 | 99 | 1.2512 | 1.2512 | 1.2638 | 1.2639
870 | feeder2_line132 | 1 | 354.6 | 1.537 | 1.5369 | 0.43344 | 0.43343
870 | feeder2_line132 | 2 | 354.6 | 0.00012455 | 2.8909e-06 | 3.5123e-05 | 8.1526e-07
870 | feeder2_line132 | 3 | 354.6 | 1.3304 | 1.3303 | 0.37519 | 0.37516
870 | feeder2_line133 | 1 | 99 | 1.5369 | 1.5369 | 1.5524 | 1.5525
870 | feeder2_line133 | 2 | 99 | 2.9704e-07 | 9.7071e-07 | 3.0004e-07 | 9.8051e-07
870 | feeder2_line133 | 3 | 99 | 3.002e-07 | 9.8209e-07 | 3.0324e-07 | 9.9201e-07
870 | feeder2_line134 | 1 | 354.6 | 4.6625e-12 | 1.7654e-06 | 1.3149e-12 | 4.9785e-07
870 | feeder2_line134 | 2 | 354.6 | 5.6603e-12 | 1.7703e-06 | 1.5963e-12 | 4.9923e-07
870 | feeder2_line134 | 3 | 354.6 | 1.3303 | 1.3303 | 0.37516 | 0.37516
870 | feeder2_line135 | 1 | 99 | 2.0813 | 2.0813 | 2.1023 | 2.1023
870 | feeder2_line135 | 2 | 99 | 4.9624e-08 | 5.8117e-07 | 5.0126e-08 | 5.8704e-07
870 | feeder2_line135 | 3 | 99 | 4.8684e-08 | 5.8866e-07 | 4.9176e-08 | 5.9461e-07
870 | feeder2_line136 | 1 | 354.6 | 79.282 | 79.2889 | 22.3582 | 22.3601
870 | feeder2_line136 | 2 | 354.6 | 85.4977 | 85.4935 | 24.111 | 24.1099
870 | feeder2_line136 | 3 | 354.6 | 95.1176 | 95.1154 | 26.8239 | 26.8233
870 | feeder2_line137 | 1 | 99 | 5.3489 | 5.3489 | 5.4029 | 5.4029
870 | feeder2_line137 | 2 | 99 | 8.4343e-07 | 1.5654e-06 | 8.5195e-07 | 1.5812e-06
870 | feeder2_line137 | 3 | 99 | 8.548e-07 | 1.5856e-06 | 8.6343e-07 | 1.6016e-06
870 | feeder2_line138 | 1 | 354.6 | 82.241 | 82.2479 | 23.1926 | 23.1946
870 | feeder2_line138 | 2 | 354.6 | 85.4978 | 85.4935 | 24.1111 | 24.1099
870 | feeder2_line138 | 3 | 354.6 | 95.1177 | 95.1154 | 26.8239 | 26.8233
870 | feeder2_line139 | 1 | 99 | 5.0943e-08 | 4.8517e-07 | 5.1458e-08 | 4.9007e-07
870 | feeder2_line139 | 2 | 99 | 4.9628e-08 | 4.8777e-07 | 5.0129e-08 | 4.927e-07
870 | feeder2_line139 | 3 | 99 | 2.0694 | 2.0694 | 2.0903 | 2.0903
870 | feeder2_line140 | 1 | 354.6 | 82.2411 | 82.2479 | 23.1926 | 23.1946
870 | feeder2_line140 | 2 | 354.6 | 85.4979 | 85.4936 | 24.1111 | 24.1099
870 | feeder2_line140 | 3 | 354.6 | 96.3118 | 96.3092 | 27.1607 | 27.16
870 | feeder2_line141 | 1 | 99 | 2.4812e-06 | 4.7994e-07 | 2.5062e-06 | 4.8479e-07
870 | feeder2_line141 | 2 | 99 | 0.077522 | 0.077516 | 0.078305 | 0.078299
870 | feeder2_line141 | 3 | 99 | 2.5501e-06 | 4.888e-07 | 2.5759e-06 | 4.9374e-07
870 | feeder2_line142 | 1 | 354.6 | 82.241 | 82.2479 | 23.1926 | 23.1946
870 | feeder2_line142 | 2 | 354.6 | 85.5696 | 85.5654 | 24.1313 | 24.1301
870 | feeder2_line142 | 3 | 354.6 | 96.3116 | 96.3092 | 27.1606 | 27.16
870 | feeder2_line143 | 1 | 99 | 8.3857e-07 | 1.7053e-06 | 8.4704e-07 | 1.7226e-06
870 | feeder2_line143 | 2 | 99 | 13.1276 | 13.1277 | 13.2602 | 13.2603
870 | feeder2_line143 | 3 | 99 | 8.551e-07 | 1.7369e-06 | 8.6374e-07 | 1.7545e-06
870 | feeder2_line144 | 1 | 354.6 | 82.2408 | 82.2479 | 23.1925 | 23.1946
870 | feeder2_line144 | 2 | 354.6 | 96.5482 | 96.5441 | 27.2273 | 27.2262
870 | feeder2_line144 | 3 | 354.6 | 96.3114 | 96.3092 | 27.1606 | 27.16
870 | feeder2_line145 | 1 | 99 | 2.5483e-08 | 4.7819e-07 | 2.5741e-08 | 4.8302e-07
870 | feeder2_line145 | 2 | 99 | 0.99932 | 0.99931 | 1.0094 | 1.0094
870 | feeder2_line145 | 3 | 99 | 2.4344e-08 | 4.8707e-07 | 2.459e-08 | 4.9199e-07
870 | feeder2_line146 | 1 | 354.6 | 82.2407 | 82.2479 | 23.1925 | 23.1946
870 | feeder2_line146 | 2 | 354.6 | 97.4865 | 97.4826 | 27.492 | 27.4909
870 | feeder2_line146 | 3 | 354.6 | 96.3113 | 96.3092 | 27.1606 | 27.16
870 | feeder2_line147 | 1 | 99 | 13.8915 | 13.8913 | 14.0318 | 14.0316
870 | feeder2_line147 | 2 | 99 | 1.1414e-06 | 2.2176e-06 | 1.153e-06 | 2.24e-06
870 | feeder2_line147 | 3 | 99 | 1.1565e-06 | 2.2466e-06 | 1.1682e-06 | 2.2693e-06
870 | feeder2_line148 | 1 | 99 | 0.086337 | 0.086346 | 0.087209 | 0.087218
870 | feeder2_line148 | 2 | 99 | 5.9558e-07 | 1.486e-06 | 6.016e-07 | 1.501e-06
870 | feeder2_line148 | 3 | 99 | 6.0263e-07 | 1.5054e-06 | 6.0872e-07 | 1.5206e-06
870 | feeder2_line149 | 1 | 354.6 | 94.5053 | 94.5121 | 26.6512 | 26.6532
870 | feeder2_line149 | 2 | 354.6 | 97.4867 | 97.4826 | 27.492 | 27.4909
870 | feeder2_line149 | 3 | 354.6 | 96.3115 | 96.3092 | 27.1606 | 27.16
870 | feeder2_line150 | 1 | 354.6 | 94.5054 | 94.5121 | 26.6513 | 26.6532
870 | feeder2_line150 | 2 | 354.6 | 99.0001 | 98.9958 | 27.9188 | 27.9176
870 | feeder2_line150 | 3 | 354.6 | 96.3116 | 96.3092 | 27.1606 | 27.16
870 | feeder2_line151 | 1 | 99 | 9.5692e-06 | 1.7555e-06 | 9.6658e-06 | 1.7732e-06
870 | feeder2_line151 | 2 | 99 | 1.6714 | 1.6714 | 1.6883 | 1.6883
870 | feeder2_line151 | 3 | 99 | 9.8628e-06 | 1.7882e-06 | 9.9625e-06 | 1.8063e-06
870 | feeder2_line152 | 1 | 354.6 | 2.0053e-11 | 1.1709e-06 | 5.6552e-12 | 3.3021e-07
870 | feeder2_line152 | 2 | 354.6 | 2.1555e-11 | 1.1765e-06 | 6.0786e-12 | 3.3179e-07
870 | feeder2_line152 | 3 | 354.6 | 1.4378 | 1.4378 | 0.40546 | 0.40547
870 | feeder2_line153 | 1 | 99 | 1.1649 | 1.1649 | 1.1766 | 1.1766
870 | feeder2_line153 | 2 | 99 | 4.9671e-08 | 5.8865e-07 | 5.0173e-08 | 5.946e-07
870 | feeder2_line153 | 3 | 99 | 4.8723e-08 | 5.9628e-07 | 4.9215e-08 | 6.023e-07
870 | feeder2_line154 | 1 | 99 | 5.6794e-07 | 8.7105e-07 | 5.7367e-07 | 8.7985e-07
870 | feeder2_line154 | 2 | 99 | 5.7119e-07 | 8.7593e-07 | 5.7696e-07 | 8.8478e-07
870 | feeder2_line154 | 3 | 99 | 1.2472 | 1.2472 | 1.2598 | 1.2598
870 | feeder2_line155 | 1 | 99 | 95.5758 | 95.5826 | 96.5412 | 96.5481
870 | feeder2_line155 | 2 | 99 | 99 | 98.9958 | 100 | 99.9958
870 | feeder2_line155 | 3 | 99 | 97.2869 | 97.2847 | 98.2696 | 98.2673
870 | feeder2_line156 | 1 | 99 | 5.9327e-07 | 1.1463e-06 | 5.9927e-07 | 1.1579e-06
870 | feeder2_line156 | 2 | 99 | 1.5821 | 1.582 | 1.598 | 1.598
870 | feeder2_line156 | 3 | 99 | 6.0283e-07 | 1.1677e-06 | 6.0892e-07 | 1.1795e-06
870 | feeder2_line157 | 1 | 99 | 2.5495e-08 | 2.4887e-07 | 2.5753e-08 | 2.5138e-07
870 | feeder2_line157 | 2 | 99 | 0.090163 | 0.09016 | 0.091074 | 0.091071
870 | feeder2_line157 | 3 | 99 | 2.4353e-08 | 2.5349e-07 | 2.4599e-08 | 2.5605e-07
900 | feeder2_line1 | 1 | 354.6 | 29.7929 | 29.7775 | 8.4018 | 8.3975
900 | feeder2_line1 | 2 | 354.6 | 43.1754 | 43.1828 | 12.1758 | 12.1779
900 | feeder2_line1 | 3 | 354.6 | 58.1568 | 58.1638 | 16.4007 | 16.4027
900 | feeder2_line2 | 1 | 354.6 | 31.0921 | 31.0765 | 8.7682 | 8.7638
900 | feeder2_line2 | 2 | 354.6 | 43.1756 | 43.1828 | 12.1759 | 12.1779
900 | feeder2_line2 | 3 | 354.6 | 58.157 | 58.1638 | 16.4007 | 16.4027
900 | feeder2_line3 | 1 | 80.1 | 1.3308 | 1.3308 | 1.6614 | 1.6614
900 | feeder2_line3 | 2 | 80.1 | 5.713e-07 | 1.0557e-06 | 7.1323e-07 | 1.318e-06
900 | feeder2_line3 | 3 | 80.1 | 5.7216e-07 | 1.0573e-06 | 7.1431e-07 | 1.32e-06
900 | feeder2_line4 | 1 | 354.6 | 31.0922 | 31.0765 | 8.7683 | 8.7638
900 | feeder2_line4 | 2 | 354.6 | 43.2619 | 43.2689 | 12.2002 | 12.2022
900 | feeder2_line4 | 3 | 354.6 | 58.1571 | 58.1638 | 16.4008 | 16.4027
900 | feeder2_line5 | 1 | 80.1 | 5.7126e-07 | 9.9681e-07 | 7.1319e-07 | 1.2445e-06
900 | feeder2_line5 | 2 | 80.1 | 0.090156 | 0.090159 | 0.11255 | 0.11256
900 | feeder2_line5 | 3 | 80.1 | 5.722e-07 | 9.9844e-07 | 7.1436e-07 | 1.2465e-06
900 | feeder2_line6 | 1 | 80.1 | 5.7127e-07 | 1.1726e-06 | 7.132e-07 | 1.464e-06
900 | feeder2_line6 | 2 | 80.1 | 5.7133e-07 | 1.1728e-06 | 7.1327e-07 | 1.4641e-06
900 | feeder2_line6 | 3 | 80.1 | 5.0505 | 5.0505 | 6.3052 | 6.3053
900 | feeder2_line7 | 1 | 354.6 | 31.0923 | 31.0765 | 8.7683 | 8.7638
900 | feeder2_line7 | 2 | 354.6 | 43.262 | 43.2689 | 12.2002 | 12.2022
900 | feeder2_line7 | 3 | 354.6 | 62.3702 | 62.3767 | 17.5889 | 17.5907
900 | feeder2_line8 | 1 | 80.1 | 0.072781 | 0.072779 | 0.090863 | 0.09086
900 | feeder2_line8 | 2 | 80.1 | 5.7142e-07 | 1.131e-06 | 7.1338e-07 | 1.4119e-06
900 | feeder2_line8 | 3 | 80.1 | 5.7248e-07 | 1.1331e-06 | 7.1471e-07 | 1.4146e-06
900 | feeder2_line9 | 1 | 354.6 | 31.1646 | 31.1486 | 8.7886 | 8.7842
900 | feeder2_line9 | 2 | 354.6 | 43.262 | 43.2689 | 12.2002 | 12.2022
900 | feeder2_line9 | 3 | 354.6 | 62.3703 | 62.3767 | 17.5889 | 17.5907
900 | feeder2_line10 | 1 | 80.1 | 8.4452e-07 | 1.4931e-06 | 1.0543e-06 | 1.864e-06
900 | feeder2_line10 | 2 | 80.1 | 0.072718 | 0.07272 | 0.090785 | 0.090786
900 | feeder2_line10 | 3 | 80.1 | 8.4635e-07 | 1.4962e-06 | 1.0566e-06 | 1.8679e-06
900 | feeder2_line11 | 1 | 354.6 | 31.1645 | 31.1486 | 8.7886 | 8.7842
900 | feeder2_line11 | 2 | 354.6 | 43.3315 | 43.3384 | 12.2198 | 12.2218
900 | feeder2_line11 | 3 | 354.6 | 62.3703 | 62.3767 | 17.5889 | 17.5907
900 | feeder2_line12 | 1 | 80.1 | 5.4641e-07 | 9.9044e-07 | 6.8216e-07 | 1.2365e-06
900 | feeder2_line12 | 2 | 80.1 | 5.4664e-07 | 9.9062e-07 | 6.8244e-07 | 1.2367e-06
900 | feeder2_line12 | 3 | 80.1 | 0.061751 | 0.061752 | 0.077093 | 0.077094
900 | feeder2_line13 | 1 | 354.6 | 31.1645 | 31.1486 | 8.7886 | 8.7842
900 | feeder2_line13 | 2 | 354.6 | 43.3315 | 43.3384 | 12.2198 | 12.2218
900 | feeder2_line13 | 3 | 354.6 | 62.4319 | 62.4384 | 17.6063 | 17.6081
900 | feeder2_line14 | 1 | 80.1 | 2.4761 | 2.4761 | 3.0912 | 3.0913
900 | feeder2_line14 | 2 | 80.1 | 2.9815e-07 | 6.4599e-07 | 3.7222e-07 | 8.0648e-07
900 | feeder2_line14 | 3 | 80.1 | 2.9874e-07 | 6.4733e-07 | 3.7296e-07 | 8.0815e-07
900 | feeder2_line15 | 1 | 354.6 | 32.2656 | 32.2496 | 9.0992 | 9.0946
900 | feeder2_line15 | 2 | 354.6 | 43.3315 | 43.3384 | 12.2198 | 12.2218
900 | feeder2_line15 | 3 | 354.6 | 62.4319 | 62.4384 | 17.6063 | 17.6081
900 | feeder2_line16 | 1 | 80.1 | 5.7139e-07 | 1.0294e-06 | 7.1334e-07 | 1.2851e-06
900 | feeder2_line16 | 2 | 80.1 | 0.80772 | 0.80771 | 1.0084 | 1.0084
900 | feeder2_line16 | 3 | 80.1 | 5.7278e-07 | 1.0319e-06 | 7.1508e-07 | 1.2883e-06
900 | feeder2_line17 | 1 | 354.6 | 32.2656 | 32.2496 | 9.0992 | 9.0946
900 | feeder2_line17 | 2 | 354.6 | 44.0858 | 44.0927 | 12.4325 | 12.4345
900 | feeder2_line17 | 3 | 354.6 | 62.432 | 62.4384 | 17.6063 | 17.6081
900 | feeder2_line18 | 1 | 80.1 | 5.4655e-07 | 7.3703e-07 | 6.8233e-07 | 9.2014e-07
900 | feeder2_line18 | 2 | 80.1 | 5.4688e-07 | 7.3727e-07 | 6.8275e-07 | 9.2044e-07
900 | feeder2_line18 | 3 | 80.1 | 0.040126 | 0.040156 | 0.050094 | 0.050133
900 | feeder2_line19 | 1 | 354.6 | 32.2656 | 32.2496 | 9.0992 | 9.0946
900 | feeder2_line19 | 2 | 354.6 | 44.0858 | 44.0927 | 12.4325 | 12.4345
900 | feeder2_line19 | 3 | 354.6 | 62.472 | 62.4784 | 17.6176 | 17.6194
900 | feeder2_line20 | 1 | 99 | 5.4659e-07 | 8.8373e-07 | 5.5211e-07 | 8.9266e-07
900 | feeder2_line20 | 2 | 99 | 5.4695e-07 | 8.8405e-07 | 5.5247e-07 | 8.9298e-07
900 | feeder2_line20 | 3 | 99 | 0.11303 | 0.11307 | 0.11417 | 0.11421
900 | feeder2_line21 | 1 | 354.6 | 32.2658 | 32.2496 | 9.0992 | 9.0946
900 | feeder2_line21 | 2 | 354.6 | 44.0859 | 44.0927 | 12.4326 | 12.4345
900 | feeder2_line21 | 3 | 354.6 | 62.585 | 62.5914 | 17.6495 | 17.6513
900 | feeder2_line22 | 1 | 99 | 5.7159e-07 | 1.0131e-06 | 5.7737e-07 | 1.0234e-06
900 | feeder2_line22 | 2 | 99 | 5.784 | 5.7839 | 5.8424 | 5.8423
900 | feeder2_line22 | 3 | 99 | 5.736e-07 | 1.0167e-06 | 5.7939e-07 | 1.0269e-06
900 | feeder2_line23 | 1 | 99 | 5.716e-07 | 9.4839e-07 | 5.7738e-07 | 9.5797e-07
900 | feeder2_line23 | 2 | 99 | 5.7183e-07 | 9.4876e-07 | 5.7761e-07 | 9.5834e-07
900 | feeder2_line23 | 3 | 99 | 0.82929 | 0.82927 | 0.83766 | 0.83765
900 | feeder2_line24 | 1 | 354.6 | 32.2658 | 32.2496 | 9.0992 | 9.0946
900 | feeder2_line24 | 2 | 354.6 | 49.5075 | 49.5143 | 13.9615 | 13.9634
900 | feeder2_line24 | 3 | 354.6 | 63.0359 | 63.0422 | 17.7766 | 17.7784
900 | feeder2_line25 | 1 | 99 | 5.7789 | 5.7789 | 5.8372 | 5.8373
900 | feeder2_line25 | 2 | 99 | 4.968e-08 | 6.8989e-07 | 5.0182e-08 | 6.9686e-07
900 | feeder2_line25 | 3 | 99 | 4.9648e-08 | 6.9214e-07 | 5.0149e-08 | 6.9913e-07
900 | feeder2_line26 | 1 | 99 | 0.085471 | 0.085463 | 0.086334 | 0.086326
900 | feeder2_line26 | 2 | 99 | 5.471e-07 | 8.5474e-07 | 5.5263e-07 | 8.6337e-07
900 | feeder2_line26 | 3 | 99 | 5.4898e-07 | 8.5752e-07 | 5.5453e-07 | 8.6618e-07
900 | feeder2_line27 | 1 | 354.6 | 38.0776 | 38.0615 | 10.7382 | 10.7336
900 | feeder2_line27 | 2 | 354.6 | 49.5075 | 49.5143 | 13.9615 | 13.9634
900 | feeder2_line27 | 3 | 354.6 | 63.0359 | 63.0422 | 17.7766 | 17.7784
900 | feeder2_line28 | 1 | 99 | 2.5337e-06 | 7.0932e-07 | 2.5592e-06 | 7.1649e-07
900 | feeder2_line28 | 2 | 99 | 0.077218 | 0.077221 | 0.077998 | 0.078001
900 | feeder2_line28 | 3 | 99 | 2.5479e-06 | 7.1222e-07 | 2.5736e-06 | 7.1941e-07
900 | feeder2_line29 | 1 | 354.6 | 38.0777 | 38.0615 | 10.7382 | 10.7336
900 | feeder2_line29 | 2 | 354.6 | 49.5821 | 49.5889 | 13.9825 | 13.9845
900 | feeder2_line29 | 3 | 354.6 | 63.0359 | 63.0422 | 17.7766 | 17.7784
900 | feeder2_line30 | 1 | 266.4 | 3.2405 | 3.24 | 1.2164 | 1.2162
900 | feeder2_line30 | 2 | 266.4 | 6.1254 | 6.1253 | 2.2993 | 2.2993
900 | feeder2_line30 | 3 | 266.4 | 3.7985 | 3.7983 | 1.4259 | 1.4258
900 | feeder2_line31 | 1 | 354.6 | 41.0844 | 41.0675 | 11.5861 | 11.5814
900 | feeder2_line31 | 2 | 354.6 | 54.4961 | 54.503 | 15.3683 | 15.3703
900 | feeder2_line31 | 3 | 354.6 | 66.5958 | 66.6017 | 18.7806 | 18.7822
900 | feeder2_line32 | 1 | 354.6 | 41.0845 | 41.0675 | 11.5861 | 11.5814
900 | feeder2_line32 | 2 | 354.6 | 54.9741 | 54.9811 | 15.5031 | 15.5051
900 | feeder2_line32 | 3 | 354.6 | 66.5959 | 66.6017 | 18.7806 | 18.7822
900 | feeder2_line33 | 1 | 99 | 5.0111e-08 | 6.8465e-07 | 5.0617e-08 | 6.9157e-07
900 | feeder2_line33 | 2 | 99 | 1.1834 | 1.1834 | 1.1953 | 1.1953
900 | feeder2_line33 | 3 | 99 | 4.9678e-08 | 6.8795e-07 | 5.018e-08 | 6.949e-07
900 | feeder2_line34 | 1 | 354.6 | 41.0845 | 41.0675 | 11.5861 | 11.5814
900 | feeder2_line34 | 2 | 354.6 | 54.9741 | 54.9811 | 15.5031 | 15.5051
900 | feeder2_line34 | 3 | 354.6 | 66.6811 | 66.687 | 18.8046 | 18.8063
900 | feeder2_line35 | 1 | 99 | 2.9859e-07 | 7.5823e-07 | 3.016e-07 | 7.6589e-07
900 | feeder2_line35 | 2 | 99 | 2.9872e-07 | 7.5882e-07 | 3.0173e-07 | 7.6649e-07
900 | feeder2_line35 | 3 | 99 | 0.085399 | 0.085406 | 0.086262 | 0.086268
900 | feeder2_line36 | 1 | 354.6 | 41.1126 | 41.0953 | 11.5941 | 11.5892
900 | feeder2_line36 | 2 | 354.6 | 54.9741 | 54.9811 | 15.5031 | 15.5051
900 | feeder2_line36 | 3 | 354.6 | 66.6811 | 66.687 | 18.8046 | 18.8063
900 | feeder2_line37 | 1 | 99 | 0.028218 | 0.027831 | 0.028503 | 0.028112
900 | feeder2_line37 | 2 | 99 | 2.9876e-07 | 8.3973e-07 | 3.0178e-07 | 8.4822e-07
900 | feeder2_line37 | 3 | 99 | 2.9997e-07 | 8.433e-07 | 3.03e-07 | 8.5181e-07
900 | feeder2_line38 | 1 | 99 | 3.2354e-07 | 7.7401e-07 | 3.2681e-07 | 7.8183e-07
900 | feeder2_line38 | 2 | 99 | 0.077356 | 0.077361 | 0.078137 | 0.078142
900 | feeder2_line38 | 3 | 99 | 3.2454e-07 | 7.7753e-07 | 3.2782e-07 | 7.8538e-07
900 | feeder2_line39 | 1 | 266.4 | 3.2405 | 3.24 | 1.2164 | 1.2162
900 | feeder2_line39 | 2 | 266.4 | 6.0554 | 6.0554 | 2.273 | 2.273
900 | feeder2_line39 | 3 | 266.4 | 3.7985 | 3.7983 | 1.4259 | 1.4258
900 | feeder2_line40 | 1 | 354.6 | 46.8726 | 46.8553 | 13.2184 | 13.2136
900 | feeder2_line40 | 2 | 354.6 | 54.9741 | 54.9811 | 15.5031 | 15.5051
900 | feeder2_line40 | 3 | 354.6 | 66.6812 | 66.687 | 18.8046 | 18.8063
900 | feeder2_line41 | 1 | 99 | 5.7814 | 5.7815 | 5.8398 | 5.8399
900 | feeder2_line41 | 2 | 99 | 4.9725e-08 | 7.3383e-07 | 5.0227e-08 | 7.4125e-07
900 | feeder2_line41 | 3 | 99 | 4.9683e-08 | 7.3698e-07 | 5.0185e-08 | 7.4442e-07
900 | feeder2_line42 | 1 | 99 | 2.985e-07 | 7.4708e-07 | 3.0151e-07 | 7.5463e-07
900 | feeder2_line42 | 2 | 99 | 2.9857e-07 | 7.4752e-07 | 3.0159e-07 | 7.5507e-07
900 | feeder2_line42 | 3 | 99 | 0.07699 | 0.076995 | 0.077768 | 0.077772
900 | feeder2_line43 | 1 | 266.4 | 3.2405 | 3.24 | 1.2164 | 1.2162
900 | feeder2_line43 | 2 | 266.4 | 6.0554 | 6.0554 | 2.273 | 2.273
900 | feeder2_line43 | 3 | 266.4 | 3.726 | 3.7258 | 1.3986 | 1.3986
900 | feeder2_line44 | 1 | 354.6 | 46.8726 | 46.8553 | 13.2184 | 13.2136
900 | feeder2_line44 | 2 | 354.6 | 54.9742 | 54.9811 | 15.5032 | 15.5051
900 | feeder2_line44 | 3 | 354.6 | 66.7937 | 66.7996 | 18.8363 | 18.838
900 | feeder2_line45 | 1 | 99 | 5.0164e-08 | 5.7826e-07 | 5.067e-08 | 5.841e-07
900 | feeder2_line45 | 2 | 99 | 4.9733e-08 | 5.7877e-07 | 5.0235e-08 | 5.8462e-07
900 | feeder2_line45 | 3 | 99 | 0.11278 | 0.11285 | 0.11392 | 0.11399
900 | feeder2_line46 | 1 | 99 | 5.7194e-07 | 1.3543e-06 | 5.7772e-07 | 1.368e-06
900 | feeder2_line46 | 2 | 99 | 5.7228e-07 | 1.3551e-06 | 5.7806e-07 | 1.3688e-06
900 | feeder2_line46 | 3 | 99 | 2.8864 | 2.8864 | 2.9156 | 2.9156
900 | feeder2_line47 | 1 | 266.4 | 3.2406 | 3.24 | 1.2164 | 1.2162
900 | feeder2_line47 | 2 | 266.4 | 6.0555 | 6.0554 | 2.2731 | 2.273
900 | feeder2_line47 | 3 | 266.4 | 0.87366 | 0.87342 | 0.32795 | 0.32786
900 | feeder2_line48 | 1 | 99 | 0.082023 | 0.082016 | 0.082851 | 0.082844
900 | feeder2_line48 | 2 | 99 | 4.9715e-08 | 7.2959e-07 | 5.0217e-08 | 7.3696e-07
900 | feeder2_line48 | 3 | 99 | 4.9666e-08 | 7.325e-07 | 5.0168e-08 | 7.399e-07
900 | feeder2_line49 | 1 | 266.4 | 3.1637 | 3.1631 | 1.1876 | 1.1873
900 | feeder2_line49 | 2 | 266.4 | 6.0554 | 6.0554 | 2.2731 | 2.273
900 | feeder2_line49 | 3 | 266.4 | 0.87364 | 0.87342 | 0.32794 | 0.32786
900 | feeder2_line50 | 1 | 99 | 5.7192e-07 | 1.2325e-06 | 5.777e-07 | 1.245e-06
900 | feeder2_line50 | 2 | 99 | 5.0507 | 5.0508 | 5.1017 | 5.1018
900 | feeder2_line50 | 3 | 99 | 5.7456e-07 | 1.2381e-06 | 5.8036e-07 | 1.2506e-06
900 | feeder2_line51 | 1 | 99 | 0.97341 | 0.973 | 0.98324 | 0.98283
900 | feeder2_line51 | 2 | 99 | 5.7225e-07 | 1.3388e-06 | 5.7803e-07 | 1.3523e-06
900 | feeder2_line51 | 3 | 99 | 5.7456e-07 | 1.3441e-06 | 5.8037e-07 | 1.3577e-06
900 | feeder2_line52 | 1 | 266.4 | 2.262 | 2.262 | 0.84911 | 0.84909
900 | feeder2_line52 | 2 | 266.4 | 1.1065 | 1.1064 | 0.41536 | 0.41532
900 | feeder2_line52 | 3 | 266.4 | 0.87351 | 0.87342 | 0.32789 | 0.32786
900 | feeder2_line53 | 1 | 99 | 5.469e-07 | 7.5223e-07 | 5.5242e-07 | 7.5983e-07
900 | feeder2_line53 | 2 | 99 | 1.1064 | 1.1064 | 1.1176 | 1.1176
900 | feeder2_line53 | 3 | 99 | 5.4973e-07 | 7.5565e-07 | 5.5528e-07 | 7.6329e-07
900 | feeder2_line54 | 1 | 266.4 | 2.2619 | 2.262 | 0.84907 | 0.84909
900 | feeder2_line54 | 2 | 266.4 | 8.5372e-05 | 4.6169e-06 | 3.2047e-05 | 1.7331e-06
900 | feeder2_line54 | 3 | 266.4 | 0.87333 | 0.87342 | 0.32783 | 0.32786
900 | feeder2_line55 | 1 | 99 | 2.2417 | 2.2417 | 2.2644 | 2.2644
900 | feeder2_line55 | 2 | 99 | 4.9749e-08 | 7.2941e-07 | 5.0252e-08 | 7.3678e-07
900 | feeder2_line55 | 3 | 99 | 4.97e-08 | 7.3273e-07 | 5.0202e-08 | 7.4013e-07
900 | feeder2_line56 | 1 | 354.6 | 48.9315 | 48.9141 | 13.7991 | 13.7942
900 | feeder2_line56 | 2 | 354.6 | 54.9742 | 54.9811 | 15.5032 | 15.5051
900 | feeder2_line56 | 3 | 354.6 | 66.7937 | 66.7996 | 18.8363 | 18.838
900 | feeder2_line57 | 1 | 99 | 7.5115e-07 | 1.5408e-06 | 7.5874e-07 | 1.5563e-06
900 | feeder2_line57 | 2 | 99 | 7.4573e-07 | 1.5416e-06 | 7.5327e-07 | 1.5572e-06
900 | feeder2_line57 | 3 | 99 | 0.87341 | 0.87342 | 0.88224 | 0.88224
900 | feeder2_line58 | 1 | 266.4 | 2.262 | 2.262 | 0.8491 | 0.84909
900 | feeder2_line58 | 2 | 266.4 | 1.8907e-05 | 2.6805e-06 | 7.0972e-06 | 1.0062e-06
900 | feeder2_line58 | 3 | 266.4 | 1.9001e-05 | 2.6911e-06 | 7.1327e-06 | 1.0102e-06
900 | feeder2_line59 | 1 | 99 | 5.0082e-08 | 5.356e-07 | 5.0588e-08 | 5.4101e-07
900 | feeder2_line59 | 2 | 99 | 4.9715e-08 | 5.3589e-07 | 5.0217e-08 | 5.4131e-07
900 | feeder2_line59 | 3 | 99 | 0.81213 | 0.81213 | 0.82033 | 0.82033
900 | feeder2_line60 | 1 | 99 | 2.9848e-07 | 8.0945e-07 | 3.015e-07 | 8.1763e-07
900 | feeder2_line60 | 2 | 99 | 2.9855e-07 | 8.0989e-07 | 3.0157e-07 | 8.1807e-07
900 | feeder2_line60 | 3 | 99 | 0.061578 | 0.06158 | 0.0622 | 0.062202
900 | feeder2_line61 | 1 | 266.4 | 0.085902 | 0.086057 | 0.032245 | 0.032304
900 | feeder2_line61 | 2 | 266.4 | 4.6841 | 4.6842 | 1.7583 | 1.7583
900 | feeder2_line61 | 3 | 266.4 | 7.6541 | 7.6542 | 2.8732 | 2.8732
900 | feeder2_line62 | 1 | 354.6 | 49.0173 | 49.0002 | 13.8233 | 13.8184
900 | feeder2_line62 | 2 | 354.6 | 57.6378 | 57.6453 | 16.2543 | 16.2564
900 | feeder2_line62 | 3 | 354.6 | 74.2483 | 74.2543 | 20.9386 | 20.9403
900 | feeder2_line63 | 1 | 99 | 0.089376 | 0.08936 | 0.090279 | 0.090262
900 | feeder2_line63 | 2 | 99 | 5.7226e-07 | 1.2176e-06 | 5.7804e-07 | 1.2299e-06
900 | feeder2_line63 | 3 | 99 | 5.7457e-07 | 1.2225e-06 | 5.8037e-07 | 1.2349e-06
900 | feeder2_line64 | 1 | 99 | 2.1832 | 2.1832 | 2.2053 | 2.2052
900 | feeder2_line64 | 2 | 99 | 3.7466e-12 | 3.2076e-07 | 3.7844e-12 | 3.24e-07
900 | feeder2_line64 | 3 | 99 | 9.2698e-12 | 3.2204e-07 | 9.3634e-12 | 3.2529e-07
900 | feeder2_line65 | 1 | 99 | 5.0262e-08 | 6.4035e-07 | 5.0769e-08 | 6.4682e-07
900 | feeder2_line65 | 2 | 99 | 0.089896 | 0.089905 | 0.090805 | 0.090813
900 | feeder2_line65 | 3 | 99 | 4.9718e-08 | 6.4418e-07 | 5.0221e-08 | 6.5069e-07
900 | feeder2_line66 | 1 | 354.6 | 49.0172 | 49.0002 | 13.8232 | 13.8184
900 | feeder2_line66 | 2 | 354.6 | 57.7273 | 57.7348 | 16.2795 | 16.2817
900 | feeder2_line66 | 3 | 354.6 | 74.2483 | 74.2543 | 20.9386 | 20.9403
900 | feeder2_line67 | 1 | 99 | 2.5105e-08 | 3.6194e-07 | 2.5359e-08 | 3.656e-07
900 | feeder2_line67 | 2 | 99 | 2.4884e-08 | 3.6226e-07 | 2.5135e-08 | 3.6592e-07
900 | feeder2_line67 | 3 | 99 | 5.8168 | 5.8167 | 5.8755 | 5.8754
900 | feeder2_line68 | 1 | 266.4 | 0.08594 | 0.086057 | 0.03226 | 0.032304
900 | feeder2_line68 | 2 | 266.4 | 4.6841 | 4.6842 | 1.7583 | 1.7583
900 | feeder2_line68 | 3 | 266.4 | 2.087 | 2.0871 | 0.7834 | 0.78345
900 | feeder2_line69 | 1 | 99 | 1.8246 | 1.8245 | 1.843 | 1.8429
900 | feeder2_line69 | 2 | 99 | 2.5433e-06 | 6.6551e-07 | 2.569e-06 | 6.7223e-07
900 | feeder2_line69 | 3 | 99 | 2.5584e-06 | 6.6889e-07 | 2.5842e-06 | 6.7565e-07
900 | feeder2_line70 | 1 | 354.6 | 50.8413 | 50.8242 | 14.3377 | 14.3328
900 | feeder2_line70 | 2 | 354.6 | 57.7272 | 57.7348 | 16.2795 | 16.2817
900 | feeder2_line70 | 3 | 354.6 | 74.2482 | 74.2543 | 20.9386 | 20.9403
900 | feeder2_line71 | 1 | 99 | 5.0272e-08 | 7.145e-07 | 5.078e-08 | 7.2172e-07
900 | feeder2_line71 | 2 | 99 | 14.2866 | 14.2865 | 14.4309 | 14.4308
900 | feeder2_line71 | 3 | 99 | 4.9709e-08 | 7.1894e-07 | 5.0211e-08 | 7.262e-07
900 | feeder2_line72 | 1 | 354.6 | 50.8414 | 50.8242 | 14.3377 | 14.3328
900 | feeder2_line72 | 2 | 354.6 | 71.6889 | 71.6966 | 20.2168 | 20.219
900 | feeder2_line72 | 3 | 354.6 | 74.2483 | 74.2543 | 20.9386 | 20.9403
900 | feeder2_line73 | 1 | 99 | 5.9769e-07 | 1.5323e-06 | 6.0373e-07 | 1.5478e-06
900 | feeder2_line73 | 2 | 99 | 1.1838 | 1.1838 | 1.1957 | 1.1957
900 | feeder2_line73 | 3 | 99 | 6.0066e-07 | 1.5408e-06 | 6.0673e-07 | 1.5564e-06
900 | feeder2_line74 | 1 | 99 | 5.0209e-08 | 4.5703e-07 | 5.0716e-08 | 4.6164e-07
900 | feeder2_line74 | 2 | 99 | 2.0882 | 2.0882 | 2.1093 | 2.1093
900 | feeder2_line74 | 3 | 99 | 4.9719e-08 | 4.5956e-07 | 5.0221e-08 | 4.642e-07
900 | feeder2_line75 | 1 | 266.4 | 0.086037 | 0.086057 | 0.032296 | 0.032304
900 | feeder2_line75 | 2 | 266.4 | 1.4776 | 1.4776 | 0.55465 | 0.55466
900 | feeder2_line75 | 3 | 266.4 | 2.0871 | 2.0871 | 0.78344 | 0.78345
900 | feeder2_line76 | 1 | 99 | 0.08607 | 0.086057 | 0.086939 | 0.086926
900 | feeder2_line76 | 2 | 99 | 8.4719e-07 | 1.582e-06 | 8.5575e-07 | 1.598e-06
900 | feeder2_line76 | 3 | 99 | 8.5125e-07 | 1.5894e-06 | 8.5985e-07 | 1.6055e-06
900 | feeder2_line77 | 1 | 99 | 2.5103e-08 | 5.7433e-07 | 2.5356e-08 | 5.8013e-07
900 | feeder2_line77 | 2 | 99 | 2.4881e-08 | 5.7481e-07 | 2.5132e-08 | 5.8062e-07
900 | feeder2_line77 | 3 | 99 | 2.0871 | 2.0871 | 2.1082 | 2.1082
900 | feeder2_line78 | 1 | 266.4 | 5.9335e-12 | 9.5276e-07 | 2.2273e-12 | 3.5764e-07
900 | feeder2_line78 | 2 | 266.4 | 1.4776 | 1.4776 | 0.55466 | 0.55466
900 | feeder2_line78 | 3 | 266.4 | 1.6613e-11 | 9.5755e-07 | 6.2362e-12 | 3.5944e-07
900 | feeder2_line79 | 1 | 354.6 | 5.8552 | 5.8547 | 1.6512 | 1.6511
900 | feeder2_line79 | 2 | 354.6 | 8.9694 | 8.9691 | 2.5294 | 2.5294
900 | feeder2_line79 | 3 | 354.6 | 3.2118 | 3.2116 | 0.90576 | 0.90571
900 | feeder2_line80 | 1 | 354.6 | 56.2256 | 56.2078 | 15.8561 | 15.851
900 | feeder2_line80 | 2 | 354.6 | 79.9414 | 79.9488 | 22.5441 | 22.5462
900 | feeder2_line80 | 3 | 354.6 | 76.8515 | 76.857 | 21.6727 | 21.6743
900 | feeder2_line81 | 1 | 354.6 | 56.2255 | 56.2078 | 15.856 | 15.851
900 | feeder2_line81 | 2 | 354.6 | 79.9413 | 79.9488 | 22.5441 | 22.5462
900 | feeder2_line81 | 3 | 354.6 | 77.8437 | 77.8493 | 21.9525 | 21.9541
900 | feeder2_line82 | 1 | 354.6 | 1.7817e-11 | 7.3313e-07 | 5.0246e-12 | 2.0675e-07
900 | feeder2_line82 | 2 | 354.6 | 9.4845e-12 | 7.3392e-07 | 2.6747e-12 | 2.0697e-07
900 | feeder2_line82 | 3 | 354.6 | 0.99224 | 0.99226 | 0.27982 | 0.27983
900 | feeder2_line83 | 1 | 354.6 | 56.2257 | 56.2078 | 15.8561 | 15.851
900 | feeder2_line83 | 2 | 354.6 | 80.6898 | 80.6971 | 22.7552 | 22.7572
900 | feeder2_line83 | 3 | 354.6 | 77.8439 | 77.8493 | 21.9526 | 21.9541
900 | feeder2_line84 | 1 | 354.6 | 1.8536e-11 | 1.2958e-06 | 5.2274e-12 | 3.6542e-07
900 | feeder2_line84 | 2 | 354.6 | 1.3339 | 1.3339 | 0.37618 | 0.37618
900 | feeder2_line84 | 3 | 354.6 | 9.2207e-12 | 1.3039e-06 | 2.6003e-12 | 3.6772e-07
900 | feeder2_line85 | 1 | 99 | 0.077384 | 0.077367 | 0.078165 | 0.078148
900 | feeder2_line85 | 2 | 99 | 4.9798e-08 | 4.6313e-07 | 5.0301e-08 | 4.6781e-07
900 | feeder2_line85 | 3 | 99 | 4.9766e-08 | 4.6551e-07 | 5.0269e-08 | 4.7022e-07
900 | feeder2_line86 | 1 | 354.6 | 56.303 | 56.2849 | 15.8779 | 15.8728
900 | feeder2_line86 | 2 | 354.6 | 80.6899 | 80.6971 | 22.7552 | 22.7572
900 | feeder2_line86 | 3 | 354.6 | 77.844 | 77.8493 | 21.9526 | 21.9541
900 | feeder2_line87 | 1 | 354.6 | 56.3032 | 56.2849 | 15.8779 | 15.8728
900 | feeder2_line87 | 2 | 354.6 | 85.117 | 85.1241 | 24.0037 | 24.0057
900 | feeder2_line87 | 3 | 354.6 | 89.0596 | 89.0644 | 25.1155 | 25.1169
900 | feeder2_line88 | 1 | 354.6 | 0.0001123 | 3.3577e-06 | 3.1669e-05 | 9.4689e-07
900 | feeder2_line88 | 2 | 354.6 | 4.8272 | 4.8271 | 1.3613 | 1.3613
900 | feeder2_line88 | 3 | 354.6 | 11.2899 | 11.2897 | 3.1838 | 3.1838
900 | feeder2_line89 | 1 | 354.6 | 56.3009 | 56.2849 | 15.8773 | 15.8728
900 | feeder2_line89 | 2 | 354.6 | 88.0994 | 88.1089 | 24.8447 | 24.8474
900 | feeder2_line89 | 3 | 354.6 | 89.0573 | 89.0644 | 25.1148 | 25.1169
900 | feeder2_line90 | 1 | 354.6 | 0.00072071 | 2.0269e-06 | 0.00020325 | 5.7161e-07
900 | feeder2_line90 | 2 | 354.6 | 3.1918 | 3.1921 | 0.90011 | 0.9002
900 | feeder2_line90 | 3 | 354.6 | 0.00072881 | 2.042e-06 | 0.00020553 | 5.7587e-07
900 | feeder2_line91 | 1 | 354.6 | 56.3008 | 56.2849 | 15.8773 | 15.8728
900 | feeder2_line91 | 2 | 354.6 | 88.0993 | 88.1089 | 24.8447 | 24.8474
900 | feeder2_line91 | 3 | 354.6 | 89.1184 | 89.1257 | 25.1321 | 25.1341
900 | feeder2_line92 | 1 | 354.6 | 1.2912e-11 | 1.0227e-06 | 3.6413e-12 | 2.884e-07
900 | feeder2_line92 | 2 | 354.6 | 1.6365e-11 | 1.0245e-06 | 4.6149e-12 | 2.8892e-07
900 | feeder2_line92 | 3 | 354.6 | 0.061332 | 0.061335 | 0.017296 | 0.017297
900 | feeder2_line93 | 1 | 99 | 2.5225e-08 | 3.4127e-07 | 2.548e-08 | 3.4472e-07
900 | feeder2_line93 | 2 | 99 | 1.3344 | 1.3344 | 1.3478 | 1.3479
900 | feeder2_line93 | 3 | 99 | 2.4895e-08 | 3.4377e-07 | 2.5146e-08 | 3.4724e-07
900 | feeder2_line94 | 1 | 354.6 | 2.5225e-06 | 1.662e-06 | 7.1136e-07 | 4.6868e-07
900 | feeder2_line94 | 2 | 354.6 | 2.1974 | 2.1974 | 0.61969 | 0.61969
900 | feeder2_line94 | 3 | 354.6 | 2.4893e-06 | 1.6733e-06 | 7.0202e-07 | 4.7189e-07
900 | feeder2_line95 | 1 | 99 | 3.5574e-06 | 2.6037e-06 | 3.5933e-06 | 2.63e-06
900 | feeder2_line95 | 2 | 99 | 4.8271 | 4.8271 | 4.8759 | 4.8759
900 | feeder2_line95 | 3 | 99 | 3.5891e-06 | 2.6219e-06 | 3.6254e-06 | 2.6484e-06
900 | feeder2_line96 | 1 | 354.6 | 0.00012078 | 6.2072e-07 | 3.406e-05 | 1.7505e-07
900 | feeder2_line96 | 2 | 354.6 | 0.0001211 | 6.2191e-07 | 3.4151e-05 | 1.7538e-07
900 | feeder2_line96 | 3 | 354.6 | 11.2899 | 11.2897 | 3.1838 | 3.1838
900 | feeder2_line97 | 1 | 354.6 | 57.3699 | 57.3538 | 16.1788 | 16.1742
900 | feeder2_line97 | 2 | 354.6 | 88.0995 | 88.1089 | 24.8448 | 24.8474
900 | feeder2_line97 | 3 | 354.6 | 89.1186 | 89.1257 | 25.1321 | 25.1341
900 | feeder2_line98 | 1 | 354.6 | 1.0707 | 1.0689 | 0.30195 | 0.30145
900 | feeder2_line98 | 2 | 354.6 | 0.0017108 | 6.2324e-07 | 0.00048245 | 1.7576e-07
900 | feeder2_line98 | 3 | 354.6 | 0.0017107 | 6.2589e-07 | 0.00048243 | 1.7651e-07
900 | feeder2_line99 | 1 | 99 | 2.5197e-08 | 4.4621e-07 | 2.5452e-08 | 4.5072e-07
900 | feeder2_line99 | 2 | 99 | 2.4897e-08 | 4.4703e-07 | 2.5149e-08 | 4.5155e-07
900 | feeder2_line99 | 3 | 99 | 11.2898 | 11.2897 | 11.4038 | 11.4037
900 | feeder2_line100 | 1 | 99 | 1.0691 | 1.0689 | 1.0799 | 1.0797
900 | feeder2_line100 | 2 | 99 | 2.4904e-08 | 6.1409e-07 | 2.5155e-08 | 6.2029e-07
900 | feeder2_line100 | 3 | 99 | 2.4899e-08 | 6.1726e-07 | 2.515e-08 | 6.2349e-07
900 | feeder2_line101 | 1 | 354.6 | 2.1939 | 2.1935 | 0.61871 | 0.61859
900 | feeder2_line101 | 2 | 354.6 | 8.9694 | 8.9691 | 2.5294 | 2.5294
900 | feeder2_line101 | 3 | 354.6 | 3.2118 | 3.2116 | 0.90575 | 0.90571
900 | feeder2_line102 | 1 | 99 | 3.8999 | 3.8998 | 3.9393 | 3.9392
900 | feeder2_line102 | 2 | 99 | 2.3374e-06 | 8.7736e-07 | 2.361e-06 | 8.8622e-07
900 | feeder2_line102 | 3 | 99 | 2.3478e-06 | 8.8201e-07 | 2.3715e-06 | 8.9092e-07
900 | feeder2_line103 | 1 | 99 | 5.4779e-07 | 8.0203e-07 | 5.5332e-07 | 8.1013e-07
900 | feeder2_line103 | 2 | 99 | 2.6141 | 2.6141 | 2.6405 | 2.6405
900 | feeder2_line103 | 3 | 99 | 5.5189e-07 | 8.0731e-07 | 5.5746e-07 | 8.1546e-07
900 | feeder2_line104 | 1 | 354.6 | 2.1938 | 2.1935 | 0.61868 | 0.61859
900 | feeder2_line104 | 2 | 354.6 | 6.3738 | 6.3736 | 1.7975 | 1.7974
900 | feeder2_line104 | 3 | 354.6 | 3.2118 | 3.2116 | 0.90574 | 0.90571
900 | feeder2_line105 | 1 | 99 | 2.5376e-06 | 7.3798e-07 | 2.5633e-06 | 7.4543e-07
900 | feeder2_line105 | 2 | 99 | 2.5446e-06 | 7.3887e-07 | 2.5703e-06 | 7.4633e-07
900 | feeder2_line105 | 3 | 99 | 0.039859 | 0.039932 | 0.040261 | 0.040335
900 | feeder2_line106 | 1 | 354.6 | 2.1938 | 2.1935 | 0.61867 | 0.61859
900 | feeder2_line106 | 2 | 354.6 | 6.3738 | 6.3736 | 1.7975 | 1.7974
900 | feeder2_line106 | 3 | 354.6 | 3.1791 | 3.179 | 0.89654 | 0.8965
900 | feeder2_line107 | 1 | 99 | 3.2421e-07 | 8.9932e-07 | 3.2748e-07 | 9.0841e-07
900 | feeder2_line107 | 2 | 99 | 3.9879 | 3.988 | 4.0282 | 4.0282
900 | feeder2_line107 | 3 | 99 | 3.2566e-07 | 9.0521e-07 | 3.2895e-07 | 9.1436e-07
900 | feeder2_line108 | 1 | 354.6 | 2.1938 | 2.1935 | 0.61866 | 0.61859
900 | feeder2_line108 | 2 | 354.6 | 2.3926 | 2.3924 | 0.67474 | 0.67467
900 | feeder2_line108 | 3 | 354.6 | 3.1791 | 3.179 | 0.89654 | 0.8965
900 | feeder2_line109 | 1 | 354.6 | 69.3871 | 69.3704 | 19.5677 | 19.563
900 | feeder2_line109 | 2 | 354.6 | 88.1007 | 88.1089 | 24.8451 | 24.8474
900 | feeder2_line109 | 3 | 354.6 | 89.1198 | 89.1257 | 25.1325 | 25.1341
900 | feeder2_line110 | 1 | 99 | 12.069 | 12.0687 | 12.1909 | 12.1906
900 | feeder2_line110 | 2 | 99 | 0.00080513 | 9.0818e-07 | 0.00081327 | 9.1735e-07
900 | feeder2_line110 | 3 | 99 | 0.00080993 | 9.1398e-07 | 0.00081811 | 9.2321e-07
900 | feeder2_line111 | 1 | 99 | 2.5193e-08 | 3.811e-07 | 2.5448e-08 | 3.8495e-07
900 | feeder2_line111 | 2 | 99 | 1.9363 | 1.9363 | 1.9559 | 1.9559
900 | feeder2_line111 | 3 | 99 | 2.4886e-08 | 3.8375e-07 | 2.5138e-08 | 3.8763e-07
900 | feeder2_line112 | 1 | 99 | 3.2438e-07 | 9.1578e-07 | 3.2765e-07 | 9.2503e-07
900 | feeder2_line112 | 2 | 99 | 3.2496 | 3.2496 | 3.2824 | 3.2824
900 | feeder2_line112 | 3 | 99 | 3.2594e-07 | 9.2217e-07 | 3.2923e-07 | 9.3149e-07
900 | feeder2_line113 | 1 | 99 | 1.3423 | 1.3424 | 1.3559 | 1.3559
900 | feeder2_line113 | 2 | 99 | 3.2486e-07 | 9.0579e-07 | 3.2814e-07 | 9.1494e-07
900 | feeder2_line113 | 3 | 99 | 3.2635e-07 | 9.1046e-07 | 3.2965e-07 | 9.1966e-07
900 | feeder2_line114 | 1 | 99 | 2.6166 | 2.6165 | 2.643 | 2.643
900 | feeder2_line114 | 2 | 99 | 2.4898e-08 | 4.3628e-07 | 2.5149e-08 | 4.4068e-07
900 | feeder2_line114 | 3 | 99 | 2.4864e-08 | 4.3859e-07 | 2.5115e-08 | 4.4302e-07
900 | feeder2_line115 | 1 | 99 | 2.5161e-08 | 5.6122e-07 | 2.5415e-08 | 5.6689e-07
900 | feeder2_line115 | 2 | 99 | 0.30972 | 0.30972 | 0.31285 | 0.31285
900 | feeder2_line115 | 3 | 99 | 2.4864e-08 | 5.6488e-07 | 2.5115e-08 | 5.7059e-07
900 | feeder2_line116 | 1 | 354.6 | 2.1938 | 2.1935 | 0.61866 | 0.61859
900 | feeder2_line116 | 2 | 354.6 | 2.1958 | 2.1955 | 0.61923 | 0.61916
900 | feeder2_line116 | 3 | 354.6 | 3.1791 | 3.179 | 0.89654 | 0.8965
900 | feeder2_line117 | 1 | 99 | 5.0569e-08 | 6.4138e-07 | 5.108e-08 | 6.4786e-07
900 | feeder2_line117 | 2 | 99 | 2.8862 | 2.8862 | 2.9154 | 2.9153
900 | feeder2_line117 | 3 | 99 | 4.9829e-08 | 6.4663e-07 | 5.0333e-08 | 6.5316e-07
900 | feeder2_line118 | 1 | 354.6 | 69.3871 | 69.3704 | 19.5677 | 19.563
900 | feeder2_line118 | 2 | 354.6 | 90.8063 | 90.8144 | 25.6081 | 25.6104
900 | feeder2_line118 | 3 | 354.6 | 89.1198 | 89.1257 | 25.1325 | 25.1341
900 | feeder2_line119 | 1 | 99 | 2.516e-08 | 6.0388e-07 | 2.5414e-08 | 6.0998e-07
900 | feeder2_line119 | 2 | 99 | 2.4897e-08 | 6.046e-07 | 2.5148e-08 | 6.1071e-07
900 | feeder2_line119 | 3 | 99 | 0.093228 | 0.093246 | 0.09417 | 0.094188
900 | feeder2_line120 | 1 | 354.6 | 2.1938 | 2.1935 | 0.61867 | 0.61859
900 | feeder2_line120 | 2 | 354.6 | 2.1958 | 2.1955 | 0.61923 | 0.61916
900 | feeder2_line120 | 3 | 354.6 | 3.1047 | 3.1046 | 0.87555 | 0.87551
900 | feeder2_line121 | 1 | 99 | 3.242e-07 | 9.3511e-07 | 3.2747e-07 | 9.4456e-07
900 | feeder2_line121 | 2 | 99 | 2.1132 | 2.1132 | 2.1346 | 2.1345
900 | feeder2_line121 | 3 | 99 | 3.2564e-07 | 9.412e-07 | 3.2892e-07 | 9.5071e-07
900 | feeder2_line122 | 1 | 354.6 | 2.1938 | 2.1935 | 0.61866 | 0.61859
900 | feeder2_line122 | 2 | 354.6 | 0.089403 | 0.089169 | 0.025212 | 0.025146
900 | feeder2_line122 | 3 | 354.6 | 3.1047 | 3.1046 | 0.87554 | 0.87551
900 | feeder2_line123 | 1 | 99 | 5.7291e-07 | 9.6898e-07 | 5.787e-07 | 9.7876e-07
900 | feeder2_line123 | 2 | 99 | 5.7363e-07 | 9.7018e-07 | 5.7943e-07 | 9.7998e-07
900 | feeder2_line123 | 3 | 99 | 0.076601 | 0.076605 | 0.077375 | 0.077379
900 | feeder2_line124 | 1 | 354.6 | 2.1937 | 2.1935 | 0.61864 | 0.61859
900 | feeder2_line124 | 2 | 354.6 | 0.089307 | 0.089169 | 0.025185 | 0.025146
900 | feeder2_line124 | 3 | 354.6 | 3.0448 | 3.0447 | 0.85867 | 0.85863
900 | feeder2_line125 | 1 | 99 | 5.729e-07 | 9.0075e-07 | 5.7869e-07 | 9.0985e-07
900 | feeder2_line125 | 2 | 99 | 5.7364e-07 | 9.0188e-07 | 5.7943e-07 | 9.1099e-07
900 | feeder2_line125 | 3 | 99 | 1.0641 | 1.0642 | 1.0749 | 1.075
900 | feeder2_line126 | 1 | 354.6 | 2.1938 | 2.1935 | 0.61868 | 0.61859
900 | feeder2_line126 | 2 | 354.6 | 0.089463 | 0.089169 | 0.025229 | 0.025146
900 | feeder2_line126 | 3 | 354.6 | 2.2622 | 2.262 | 0.63797 | 0.63789
900 | feeder2_line127 | 1 | 99 | 5.7289e-07 | 1.0783e-06 | 5.7868e-07 | 1.0892e-06
900 | feeder2_line127 | 2 | 99 | 5.7364e-07 | 1.0797e-06 | 5.7944e-07 | 1.0906e-06
900 | feeder2_line127 | 3 | 99 | 0.97031 | 0.97028 | 0.98011 | 0.98008
900 | feeder2_line128 | 1 | 354.6 | 2.1938 | 2.1935 | 0.61866 | 0.61859
900 | feeder2_line128 | 2 | 354.6 | 0.089378 | 0.089169 | 0.025205 | 0.025146
900 | feeder2_line128 | 3 | 354.6 | 1.292 | 1.2917 | 0.36434 | 0.36427
900 | feeder2_line129 | 1 | 99 | 5.4772e-07 | 8.7436e-07 | 5.5326e-07 | 8.8319e-07
900 | feeder2_line129 | 2 | 99 | 0.089161 | 0.089168 | 0.090062 | 0.090069
900 | feeder2_line129 | 3 | 99 | 5.5179e-07 | 8.8006e-07 | 5.5736e-07 | 8.8895e-07
900 | feeder2_line130 | 1 | 354.6 | 2.1938 | 2.1935 | 0.61866 | 0.61859
900 | feeder2_line130 | 2 | 354.6 | 0.00030758 | 4.633e-06 | 8.6739e-05 | 1.3065e-06
900 | feeder2_line130 | 3 | 354.6 | 1.292 | 1.2917 | 0.36435 | 0.36427
900 | feeder2_line131 | 1 | 99 | 5.7288e-07 | 9.6908e-07 | 5.7867e-07 | 9.7887e-07
900 | feeder2_line131 | 2 | 99 | 5.7365e-07 | 9.7035e-07 | 5.7944e-07 | 9.8015e-07
900 | feeder2_line131 | 3 | 99 | 1.2503 | 1.2504 | 1.263 | 1.263
900 | feeder2_line132 | 1 | 354.6 | 2.1936 | 2.1935 | 0.61862 | 0.61859
900 | feeder2_line132 | 2 | 354.6 | 0.00012556 | 2.9126e-06 | 3.5408e-05 | 8.2138e-07
900 | feeder2_line132 | 3 | 354.6 | 0.076826 | 0.076764 | 0.021665 | 0.021648
900 | feeder2_line133 | 1 | 99 | 2.1935 | 2.1935 | 2.2157 | 2.2157
900 | feeder2_line133 | 2 | 99 | 2.9927e-07 | 9.781e-07 | 3.0229e-07 | 9.8798e-07
900 | feeder2_line133 | 3 | 99 | 3.0076e-07 | 9.832e-07 | 3.038e-07 | 9.9313e-07
900 | feeder2_line134 | 1 | 354.6 | 1.0141e-11 | 1.7818e-06 | 2.8598e-12 | 5.0248e-07
900 | feeder2_line134 | 2 | 354.6 | 1.0141e-11 | 1.7836e-06 | 2.8598e-12 | 5.0299e-07
900 | feeder2_line134 | 3 | 354.6 | 0.076756 | 0.076764 | 0.021646 | 0.021648
900 | feeder2_line135 | 1 | 99 | 14.2823 | 14.2823 | 14.4266 | 14.4266
900 | feeder2_line135 | 2 | 99 | 4.98e-08 | 5.8651e-07 | 5.0303e-08 | 5.9243e-07
900 | feeder2_line135 | 3 | 99 | 4.9846e-08 | 5.895e-07 | 5.035e-08 | 5.9546e-07
900 | feeder2_line136 | 1 | 354.6 | 83.6464 | 83.6298 | 23.589 | 23.5843
900 | feeder2_line136 | 2 | 354.6 | 90.8063 | 90.8144 | 25.6081 | 25.6104
900 | feeder2_line136 | 3 | 354.6 | 89.1198 | 89.1257 | 25.1325 | 25.1341
900 | feeder2_line137 | 1 | 99 | 1.5406 | 1.5405 | 1.5561 | 1.556
900 | feeder2_line137 | 2 | 99 | 8.5133e-07 | 1.5799e-06 | 8.5993e-07 | 1.5958e-06
900 | feeder2_line137 | 3 | 99 | 8.5573e-07 | 1.5879e-06 | 8.6437e-07 | 1.604e-06
900 | feeder2_line138 | 1 | 354.6 | 85.1826 | 85.1658 | 24.0222 | 24.0174
900 | feeder2_line138 | 2 | 354.6 | 90.8063 | 90.8144 | 25.6081 | 25.6104
900 | feeder2_line138 | 3 | 354.6 | 89.1198 | 89.1257 | 25.1325 | 25.1341
900 | feeder2_line139 | 1 | 99 | 5.0648e-08 | 4.9067e-07 | 5.116e-08 | 4.9562e-07
900 | feeder2_line139 | 2 | 99 | 4.9816e-08 | 4.9234e-07 | 5.0319e-08 | 4.9731e-07
900 | feeder2_line139 | 3 | 99 | 0.94411 | 0.94465 | 0.95365 | 0.95419
900 | feeder2_line140 | 1 | 354.6 | 85.1827 | 85.1658 | 24.0222 | 24.0174
900 | feeder2_line140 | 2 | 354.6 | 90.8064 | 90.8144 | 25.6081 | 25.6104
900 | feeder2_line140 | 3 | 354.6 | 90.0639 | 90.0701 | 25.3987 | 25.4005
900 | feeder2_line141 | 1 | 99 | 2.5158e-06 | 4.8542e-07 | 2.5412e-06 | 4.9033e-07
900 | feeder2_line141 | 2 | 99 | 0.076811 | 0.076819 | 0.077587 | 0.077595
900 | feeder2_line141 | 3 | 99 | 2.5459e-06 | 4.8955e-07 | 2.5716e-06 | 4.945e-07
900 | feeder2_line142 | 1 | 354.6 | 85.1825 | 85.1658 | 24.0221 | 24.0174
900 | feeder2_line142 | 2 | 354.6 | 90.8829 | 90.8911 | 25.6297 | 25.632
900 | feeder2_line142 | 3 | 354.6 | 90.0637 | 90.0701 | 25.3987 | 25.4005
900 | feeder2_line143 | 1 | 99 | 8.4851e-07 | 1.725e-06 | 8.5708e-07 | 1.7424e-06
900 | feeder2_line143 | 2 | 99 | 3.9871 | 3.9872 | 4.0274 | 4.0275
900 | feeder2_line143 | 3 | 99 | 8.5611e-07 | 1.7397e-06 | 8.6476e-07 | 1.7572e-06
900 | feeder2_line144 | 1 | 354.6 | 85.1823 | 85.1658 | 24.0221 | 24.0174
900 | feeder2_line144 | 2 | 354.6 | 94.6846 | 94.693 | 26.7018 | 26.7042
900 | feeder2_line144 | 3 | 354.6 | 90.0635 | 90.0701 | 25.3986 | 25.4005
900 | feeder2_line145 | 1 | 99 | 2.534e-08 | 4.8371e-07 | 2.5595e-08 | 4.886e-07
900 | feeder2_line145 | 2 | 99 | 0.99316 | 0.99319 | 1.0032 | 1.0032
900 | feeder2_line145 | 3 | 99 | 2.4947e-08 | 4.8784e-07 | 2.5199e-08 | 4.9276e-07
900 | feeder2_line146 | 1 | 354.6 | 85.1822 | 85.1658 | 24.022 | 24.0174
900 | feeder2_line146 | 2 | 354.6 | 95.6768 | 95.6854 | 26.9816 | 26.9841
900 | feeder2_line146 | 3 | 354.6 | 90.0634 | 90.0701 | 25.3986 | 25.4005
900 | feeder2_line147 | 1 | 99 | 11.1857 | 11.1863 | 11.2987 | 11.2993
900 | feeder2_line147 | 2 | 99 | 1.1524e-06 | 2.2389e-06 | 1.1641e-06 | 2.2615e-06
900 | feeder2_line147 | 3 | 99 | 1.1583e-06 | 2.2502e-06 | 1.17e-06 | 2.2729e-06
900 | feeder2_line148 | 1 | 99 | 0.085228 | 0.085206 | 0.086089 | 0.086066
900 | feeder2_line148 | 2 | 99 | 6.0118e-07 | 1.5003e-06 | 6.0725e-07 | 1.5155e-06
900 | feeder2_line148 | 3 | 99 | 6.0412e-07 | 1.5078e-06 | 6.1022e-07 | 1.5231e-06
900 | feeder2_line149 | 1 | 354.6 | 96.4517 | 96.4357 | 27.2001 | 27.1956
900 | feeder2_line149 | 2 | 354.6 | 95.677 | 95.6854 | 26.9817 | 26.9841
900 | feeder2_line149 | 3 | 354.6 | 90.0635 | 90.0701 | 25.3986 | 25.4005
900 | feeder2_line150 | 1 | 354.6 | 96.4518 | 96.4357 | 27.2002 | 27.1956
900 | feeder2_line150 | 2 | 354.6 | 99.0001 | 99.0086 | 27.9188 | 27.9212
900 | feeder2_line150 | 3 | 354.6 | 90.0636 | 90.0701 | 25.3987 | 25.4005
900 | feeder2_line151 | 1 | 99 | 9.7185e-06 | 1.7762e-06 | 9.8167e-06 | 1.7942e-06
900 | feeder2_line151 | 2 | 99 | 3.9689 | 3.9689 | 4.009 | 4.009
900 | feeder2_line151 | 3 | 99 | 9.8405e-06 | 1.7913e-06 | 9.9399e-06 | 1.8094e-06
900 | feeder2_line152 | 1 | 354.6 | 2.6363e-12 | 1.1844e-06 | 7.4345e-13 | 3.3402e-07
900 | feeder2_line152 | 2 | 354.6 | 1.9083e-11 | 1.1881e-06 | 5.3816e-12 | 3.3505e-07
900 | feeder2_line152 | 3 | 354.6 | 9.2053 | 9.2056 | 2.596 | 2.596
900 | feeder2_line153 | 1 | 99 | 2.1132 | 2.1132 | 2.1346 | 2.1345
900 | feeder2_line153 | 2 | 99 | 4.9866e-08 | 5.9451e-07 | 5.037e-08 | 6.0052e-07
900 | feeder2_line153 | 3 | 99 | 4.9961e-08 | 5.9736e-07 | 5.0466e-08 | 6.0339e-07
900 | feeder2_line154 | 1 | 99 | 5.748e-07 | 8.8151e-07 | 5.8061e-07 | 8.9042e-07
900 | feeder2_line154 | 2 | 99 | 5.7689e-07 | 8.8467e-07 | 5.8272e-07 | 8.936e-07
900 | feeder2_line154 | 3 | 99 | 0.040444 | 0.040538 | 0.040852 | 0.040947
900 | feeder2_line155 | 1 | 99 | 98.4689 | 98.4529 | 99.4636 | 99.4474
900 | feeder2_line155 | 2 | 99 | 99 | 99.0086 | 100 | 100.0087
900 | feeder2_line155 | 3 | 99 | 98.4905 | 98.4972 | 99.4854 | 99.4921
900 | feeder2_line156 | 1 | 99 | 5.9988e-07 | 1.1599e-06 | 6.0594e-07 | 1.1716e-06
900 | feeder2_line156 | 2 | 99 | 2.6097 | 2.6097 | 2.6361 | 2.6361
900 | feeder2_line156 | 3 | 99 | 6.044e-07 | 1.1697e-06 | 6.105e-07 | 1.1815e-06
900 | feeder2_line157 | 1 | 99 | 2.5353e-08 | 2.518e-07 | 2.5609e-08 | 2.5434e-07
900 | feeder2_line157 | 2 | 99 | 1.4809 | 1.4808 | 1.4958 | 1.4958
900 | feeder2_line157 | 3 | 99 | 2.4967e-08 | 2.5393e-07 | 2.5219e-08 | 2.565e-07
930 | feeder2_line1 | 1 | 354.6 | 52.0899 | 52.0872 | 14.6898 | 14.689
930 | feeder2_line1 | 2 | 354.6 | 64.9555 | 64.9598 | 18.318 | 18.3192
930 | feeder2_line1 | 3 | 354.6 | 68.6481 | 68.6485 | 19.3593 | 19.3594
930 | feeder2_line2 | 1 | 354.6 | 54.2293 | 54.2263 | 15.2931 | 15.2923
930 | feeder2_line2 | 2 | 354.6 | 64.9557 | 64.9598 | 18.318 | 18.3192
930 | feeder2_line2 | 3 | 354.6 | 68.6482 | 68.6485 | 19.3593 | 19.3594
930 | feeder2_line3 | 1 | 80.1 | 2.4481 | 2.448 | 3.0563 | 3.0562
930 | feeder2_line3 | 2 | 80.1 | 5.722e-07 | 1.0574e-06 | 7.1435e-07 | 1.3201e-06
930 | feeder2_line3 | 3 | 80.1 | 5.7242e-07 | 1.0578e-06 | 7.1464e-07 | 1.3206e-06
930 | feeder2_line4 | 1 | 354.6 | 54.2295 | 54.2263 | 15.2931 | 15.2923
930 | feeder2_line4 | 2 | 354.6 | 65.0458 | 65.0498 | 18.3434 | 18.3445
930 | feeder2_line4 | 3 | 354.6 | 68.6484 | 68.6485 | 19.3594 | 19.3594
930 | feeder2_line5 | 1 | 80.1 | 5.7168e-07 | 9.9754e-07 | 7.1371e-07 | 1.2454e-06
930 | feeder2_line5 | 2 | 80.1 | 0.090031 | 0.090032 | 0.1124 | 0.1124
930 | feeder2_line5 | 3 | 80.1 | 5.7247e-07 | 9.9891e-07 | 7.147e-07 | 1.2471e-06
930 | feeder2_line6 | 1 | 80.1 | 5.7171e-07 | 1.1736e-06 | 7.1375e-07 | 1.4651e-06
930 | feeder2_line6 | 2 | 80.1 | 5.723e-07 | 1.1747e-06 | 7.1448e-07 | 1.4666e-06
930 | feeder2_line6 | 3 | 80.1 | 1.2681 | 1.2681 | 1.5832 | 1.5832
930 | feeder2_line7 | 1 | 354.6 | 54.2296 | 54.2263 | 15.2932 | 15.2923
930 | feeder2_line7 | 2 | 354.6 | 65.0459 | 65.0498 | 18.3435 | 18.3445
930 | feeder2_line7 | 3 | 354.6 | 69.9165 | 69.9165 | 19.717 | 19.717
930 | feeder2_line8 | 1 | 80.1 | 0.072714 | 0.072713 | 0.090779 | 0.090778
930 | feeder2_line8 | 2 | 80.1 | 5.7248e-07 | 1.1331e-06 | 7.1471e-07 | 1.4146e-06
930 | feeder2_line8 | 3 | 80.1 | 5.7276e-07 | 1.1336e-06 | 7.1506e-07 | 1.4153e-06
930 | feeder2_line9 | 1 | 354.6 | 54.3023 | 54.2989 | 15.3137 | 15.3127
930 | feeder2_line9 | 2 | 354.6 | 65.046 | 65.0498 | 18.3435 | 18.3445
930 | feeder2_line9 | 3 | 354.6 | 69.9166 | 69.9165 | 19.717 | 19.717
930 | feeder2_line10 | 1 | 80.1 | 8.4529e-07 | 1.4944e-06 | 1.0553e-06 | 1.8657e-06
930 | feeder2_line10 | 2 | 80.1 | 0.072568 | 0.072569 | 0.090597 | 0.090598
930 | feeder2_line10 | 3 | 80.1 | 8.4675e-07 | 1.4969e-06 | 1.0571e-06 | 1.8688e-06
930 | feeder2_line11 | 1 | 354.6 | 54.3022 | 54.2989 | 15.3137 | 15.3127
930 | feeder2_line11 | 2 | 354.6 | 65.1185 | 65.1223 | 18.3639 | 18.365
930 | feeder2_line11 | 3 | 354.6 | 69.9165 | 69.9165 | 19.717 | 19.717
930 | feeder2_line12 | 1 | 80.1 | 5.4693e-07 | 9.9137e-07 | 6.8281e-07 | 1.2377e-06
930 | feeder2_line12 | 2 | 80.1 | 5.4774e-07 | 9.9257e-07 | 6.8382e-07 | 1.2392e-06
930 | feeder2_line12 | 3 | 80.1 | 0.061737 | 0.061737 | 0.077075 | 0.077075
930 | feeder2_line13 | 1 | 354.6 | 54.3022 | 54.2989 | 15.3137 | 15.3127
930 | feeder2_line13 | 2 | 354.6 | 65.1185 | 65.1223 | 18.3639 | 18.365
930 | feeder2_line13 | 3 | 354.6 | 69.9782 | 69.9782 | 19.7344 | 19.7344
930 | feeder2_line14 | 1 | 80.1 | 0.086041 | 0.08604 | 0.10742 | 0.10742
930 | feeder2_line14 | 2 | 80.1 | 2.9875e-07 | 6.4731e-07 | 3.7297e-07 | 8.0812e-07
930 | feeder2_line14 | 3 | 80.1 | 2.9891e-07 | 6.4765e-07 | 3.7317e-07 | 8.0855e-07
930 | feeder2_line15 | 1 | 354.6 | 54.3881 | 54.3848 | 15.3379 | 15.3369
930 | feeder2_line15 | 2 | 354.6 | 65.1185 | 65.1223 | 18.3639 | 18.365
930 | feeder2_line15 | 3 | 354.6 | 69.9782 | 69.9782 | 19.7344 | 19.7344
930 | feeder2_line16 | 1 | 80.1 | 5.7198e-07 | 1.0305e-06 | 7.1408e-07 | 1.2865e-06
930 | feeder2_line16 | 2 | 80.1 | 1.4022 | 1.4022 | 1.7506 | 1.7506
930 | feeder2_line16 | 3 | 80.1 | 5.7307e-07 | 1.0324e-06 | 7.1544e-07 | 1.2889e-06
930 | feeder2_line17 | 1 | 354.6 | 54.3881 | 54.3848 | 15.3379 | 15.3369
930 | feeder2_line17 | 2 | 354.6 | 66.5124 | 66.5162 | 18.757 | 18.7581
930 | feeder2_line17 | 3 | 354.6 | 69.9782 | 69.9782 | 19.7344 | 19.7344
930 | feeder2_line18 | 1 | 80.1 | 5.4725e-07 | 7.3796e-07 | 6.832e-07 | 9.213e-07
930 | feeder2_line18 | 2 | 80.1 | 5.4837e-07 | 7.3921e-07 | 6.846e-07 | 9.2286e-07
930 | feeder2_line18 | 3 | 80.1 | 1.0976 | 1.0976 | 1.3703 | 1.3703
930 | feeder2_line19 | 1 | 354.6 | 54.3881 | 54.3848 | 15.3379 | 15.3369
930 | feeder2_line19 | 2 | 354.6 | 66.5124 | 66.5162 | 18.757 | 18.7581
930 | feeder2_line19 | 3 | 354.6 | 70.5302 | 70.5301 | 19.8901 | 19.89
930 | feeder2_line20 | 1 | 99 | 5.4733e-07 | 8.8493e-07 | 5.5286e-07 | 8.9387e-07
930 | feeder2_line20 | 2 | 99 | 5.4854e-07 | 8.8654e-07 | 5.5408e-07 | 8.9549e-07
930 | feeder2_line20 | 3 | 99 | 1.7066 | 1.7067 | 1.7239 | 1.7239
930 | feeder2_line21 | 1 | 354.6 | 54.3883 | 54.3848 | 15.3379 | 15.3369
930 | feeder2_line21 | 2 | 354.6 | 66.5126 | 66.5162 | 18.7571 | 18.7581
930 | feeder2_line21 | 3 | 354.6 | 71.7423 | 71.742 | 20.2319 | 20.2318
930 | feeder2_line22 | 1 | 99 | 5.7241e-07 | 1.0146e-06 | 5.7819e-07 | 1.0248e-06
930 | feeder2_line22 | 2 | 99 | 1.7605 | 1.7605 | 1.7783 | 1.7783
930 | feeder2_line22 | 3 | 99 | 5.7393e-07 | 1.0173e-06 | 5.7973e-07 | 1.0275e-06
930 | feeder2_line23 | 1 | 99 | 5.7241e-07 | 9.4973e-07 | 5.7819e-07 | 9.5933e-07
930 | feeder2_line23 | 2 | 99 | 5.735e-07 | 9.5152e-07 | 5.793e-07 | 9.6113e-07
930 | feeder2_line23 | 3 | 99 | 0.82934 | 0.82933 | 0.83772 | 0.83771
930 | feeder2_line24 | 1 | 354.6 | 54.3883 | 54.3848 | 15.3379 | 15.3369
930 | feeder2_line24 | 2 | 354.6 | 68.2621 | 68.2657 | 19.2505 | 19.2515
930 | feeder2_line24 | 3 | 354.6 | 72.2195 | 72.2192 | 20.3665 | 20.3664
930 | feeder2_line25 | 1 | 99 | 1.761 | 1.761 | 1.7788 | 1.7788
930 | feeder2_line25 | 2 | 99 | 4.9737e-08 | 6.9201e-07 | 5.024e-08 | 6.99e-07
930 | feeder2_line25 | 3 | 99 | 4.9786e-08 | 6.9257e-07 | 5.0289e-08 | 6.9957e-07
930 | feeder2_line26 | 1 | 99 | 0.085352 | 0.085351 | 0.086214 | 0.086213
930 | feeder2_line26 | 2 | 99 | 5.4883e-07 | 8.5736e-07 | 5.5437e-07 | 8.6602e-07
930 | feeder2_line26 | 3 | 99 | 5.4927e-07 | 8.5806e-07 | 5.5482e-07 | 8.6672e-07
930 | feeder2_line27 | 1 | 354.6 | 56.218 | 56.2145 | 15.8539 | 15.8529
930 | feeder2_line27 | 2 | 354.6 | 68.2621 | 68.2657 | 19.2505 | 19.2515
930 | feeder2_line27 | 3 | 354.6 | 72.2196 | 72.2192 | 20.3665 | 20.3664
930 | feeder2_line28 | 1 | 99 | 2.5378e-06 | 7.1048e-07 | 2.5634e-06 | 7.1766e-07
930 | feeder2_line28 | 2 | 99 | 0.076969 | 0.07697 | 0.077746 | 0.077747
930 | feeder2_line28 | 3 | 99 | 2.549e-06 | 7.1273e-07 | 2.5747e-06 | 7.1993e-07
930 | feeder2_line29 | 1 | 354.6 | 56.218 | 56.2145 | 15.8539 | 15.8529
930 | feeder2_line29 | 2 | 354.6 | 68.3391 | 68.3426 | 19.2722 | 19.2732
930 | feeder2_line29 | 3 | 354.6 | 72.2196 | 72.2192 | 20.3665 | 20.3664
930 | feeder2_line30 | 1 | 266.4 | 21.736 | 21.7358 | 8.1591 | 8.1591
930 | feeder2_line30 | 2 | 266.4 | 4.2694 | 4.2692 | 1.6026 | 1.6025
930 | feeder2_line30 | 3 | 266.4 | 4.4803 | 4.4801 | 1.6818 | 1.6817
930 | feeder2_line31 | 1 | 354.6 | 77.7106 | 77.7069 | 21.915 | 21.914
930 | feeder2_line31 | 2 | 354.6 | 72.4649 | 72.4682 | 20.4357 | 20.4366
930 | feeder2_line31 | 3 | 354.6 | 76.6047 | 76.604 | 21.6031 | 21.6029
930 | feeder2_line32 | 1 | 354.6 | 77.7106 | 77.7069 | 21.915 | 21.914
930 | feeder2_line32 | 2 | 354.6 | 72.542 | 72.5452 | 20.4574 | 20.4583
930 | feeder2_line32 | 3 | 354.6 | 76.6047 | 76.604 | 21.6031 | 21.6029
930 | feeder2_line33 | 1 | 99 | 5.0203e-08 | 6.8607e-07 | 5.0711e-08 | 6.93e-07
930 | feeder2_line33 | 2 | 99 | 0.077005 | 0.077007 | 0.077782 | 0.077785
930 | feeder2_line33 | 3 | 99 | 4.984e-08 | 6.8854e-07 | 5.0343e-08 | 6.955e-07
930 | feeder2_line34 | 1 | 354.6 | 77.7106 | 77.7069 | 21.915 | 21.914
930 | feeder2_line34 | 2 | 354.6 | 72.542 | 72.5452 | 20.4574 | 20.4583
930 | feeder2_line34 | 3 | 354.6 | 76.6901 | 76.6894 | 21.6272 | 21.627
930 | feeder2_line35 | 1 | 99 | 2.9924e-07 | 7.5991e-07 | 3.0226e-07 | 7.6759e-07
930 | feeder2_line35 | 2 | 99 | 2.9984e-07 | 7.6174e-07 | 3.0287e-07 | 7.6943e-07
930 | feeder2_line35 | 3 | 99 | 0.085366 | 0.085366 | 0.086228 | 0.086228
930 | feeder2_line36 | 1 | 354.6 | 78.3549 | 78.3511 | 22.0967 | 22.0956
930 | feeder2_line36 | 2 | 354.6 | 72.5419 | 72.5452 | 20.4574 | 20.4583
930 | feeder2_line36 | 3 | 354.6 | 76.69 | 76.6894 | 21.6272 | 21.627
930 | feeder2_line37 | 1 | 99 | 1.2333 | 1.2333 | 1.2457 | 1.2457
930 | feeder2_line37 | 2 | 99 | 2.999e-07 | 8.4301e-07 | 3.0293e-07 | 8.5153e-07
930 | feeder2_line37 | 3 | 99 | 3.0026e-07 | 8.4403e-07 | 3.0329e-07 | 8.5256e-07
930 | feeder2_line38 | 1 | 99 | 3.2409e-07 | 7.7529e-07 | 3.2737e-07 | 7.8312e-07
930 | feeder2_line38 | 2 | 99 | 0.077069 | 0.077072 | 0.077848 | 0.07785
930 | feeder2_line38 | 3 | 99 | 3.249e-07 | 7.782e-07 | 3.2818e-07 | 7.8606e-07
930 | feeder2_line39 | 1 | 266.4 | 21.736 | 21.7358 | 8.1591 | 8.1591
930 | feeder2_line39 | 2 | 266.4 | 4.1948 | 4.1945 | 1.5746 | 1.5745
930 | feeder2_line39 | 3 | 266.4 | 4.4803 | 4.4801 | 1.6818 | 1.6817
930 | feeder2_line40 | 1 | 354.6 | 80.1114 | 80.1076 | 22.5921 | 22.591
930 | feeder2_line40 | 2 | 354.6 | 72.542 | 72.5452 | 20.4574 | 20.4583
930 | feeder2_line40 | 3 | 354.6 | 76.6901 | 76.6894 | 21.6272 | 21.627
930 | feeder2_line41 | 1 | 99 | 1.7607 | 1.7607 | 1.7785 | 1.7785
930 | feeder2_line41 | 2 | 99 | 4.9842e-08 | 7.3671e-07 | 5.0345e-08 | 7.4415e-07
930 | feeder2_line41 | 3 | 99 | 4.9862e-08 | 7.3763e-07 | 5.0366e-08 | 7.4508e-07
930 | feeder2_line42 | 1 | 99 | 2.9893e-07 | 7.4816e-07 | 3.0195e-07 | 7.5572e-07
930 | feeder2_line42 | 2 | 99 | 2.9966e-07 | 7.5033e-07 | 3.0269e-07 | 7.5791e-07
930 | feeder2_line42 | 3 | 99 | 0.076949 | 0.076949 | 0.077726 | 0.077726
930 | feeder2_line43 | 1 | 266.4 | 21.7359 | 21.7358 | 8.1591 | 8.1591
930 | feeder2_line43 | 2 | 266.4 | 4.1947 | 4.1945 | 1.5746 | 1.5745
930 | feeder2_line43 | 3 | 266.4 | 4.4053 | 4.4051 | 1.6536 | 1.6536
930 | feeder2_line44 | 1 | 354.6 | 80.1115 | 80.1076 | 22.5921 | 22.591
930 | feeder2_line44 | 2 | 354.6 | 72.542 | 72.5452 | 20.4574 | 20.4583
930 | feeder2_line44 | 3 | 354.6 | 77.9484 | 77.9476 | 21.9821 | 21.9818
930 | feeder2_line45 | 1 | 99 | 5.0226e-08 | 5.7974e-07 | 5.0734e-08 | 5.856e-07
930 | feeder2_line45 | 2 | 99 | 4.9858e-08 | 5.8107e-07 | 5.0362e-08 | 5.8694e-07
930 | feeder2_line45 | 3 | 99 | 1.7079 | 1.7079 | 1.7251 | 1.7251
930 | feeder2_line46 | 1 | 99 | 5.7276e-07 | 1.3563e-06 | 5.7854e-07 | 1.37e-06
930 | feeder2_line46 | 2 | 99 | 5.7445e-07 | 1.3602e-06 | 5.8025e-07 | 1.374e-06
930 | feeder2_line46 | 3 | 99 | 2.902 | 2.902 | 2.9313 | 2.9313
930 | feeder2_line47 | 1 | 266.4 | 21.7359 | 21.7358 | 8.1591 | 8.1591
930 | feeder2_line47 | 2 | 266.4 | 4.1947 | 4.1945 | 1.5746 | 1.5745
930 | feeder2_line47 | 3 | 266.4 | 1.5364 | 1.5362 | 0.57674 | 0.57664
930 | feeder2_line48 | 1 | 99 | 1.1152 | 1.1151 | 1.1264 | 1.1264
930 | feeder2_line48 | 2 | 99 | 4.9745e-08 | 7.3236e-07 | 5.0247e-08 | 7.3976e-07
930 | feeder2_line48 | 3 | 99 | 4.9801e-08 | 7.3316e-07 | 5.0304e-08 | 7.4057e-07
930 | feeder2_line49 | 1 | 266.4 | 21.0205 | 21.0204 | 7.8906 | 7.8905
930 | feeder2_line49 | 2 | 266.4 | 4.1947 | 4.1945 | 1.5746 | 1.5745
930 | feeder2_line49 | 3 | 266.4 | 1.5364 | 1.5362 | 0.57673 | 0.57664
930 | feeder2_line50 | 1 | 99 | 5.7265e-07 | 1.2341e-06 | 5.7843e-07 | 1.2465e-06
930 | feeder2_line50 | 2 | 99 | 1.2671 | 1.2671 | 1.2799 | 1.2799
930 | feeder2_line50 | 3 | 99 | 5.7508e-07 | 1.2393e-06 | 5.8089e-07 | 1.2518e-06
930 | feeder2_line51 | 1 | 99 | 1.4453 | 1.4452 | 1.4599 | 1.4598
930 | feeder2_line51 | 2 | 99 | 5.7444e-07 | 1.3439e-06 | 5.8025e-07 | 1.3574e-06
930 | feeder2_line51 | 3 | 99 | 5.7508e-07 | 1.3454e-06 | 5.8089e-07 | 1.3589e-06
930 | feeder2_line52 | 1 | 266.4 | 19.5753 | 19.5754 | 7.3481 | 7.3481
930 | feeder2_line52 | 2 | 266.4 | 2.9917 | 2.9916 | 1.123 | 1.123
930 | feeder2_line52 | 3 | 266.4 | 1.5363 | 1.5362 | 0.57668 | 0.57664
930 | feeder2_line53 | 1 | 99 | 5.4753e-07 | 7.5316e-07 | 5.5306e-07 | 7.6076e-07
930 | feeder2_line53 | 2 | 99 | 2.9916 | 2.9916 | 3.0219 | 3.0219
930 | feeder2_line53 | 3 | 99 | 5.5019e-07 | 7.5634e-07 | 5.5574e-07 | 7.6398e-07
930 | feeder2_line54 | 1 | 266.4 | 19.5751 | 19.5754 | 7.348 | 7.3481
930 | feeder2_line54 | 2 | 266.4 | 8.5684e-05 | 4.6345e-06 | 3.2164e-05 | 1.7397e-06
930 | feeder2_line54 | 3 | 266.4 | 1.5361 | 1.5362 | 0.57661 | 0.57664
930 | feeder2_line55 | 1 | 99 | 1.1395 | 1.1395 | 1.151 | 1.151
930 | feeder2_line55 | 2 | 99 | 4.9902e-08 | 7.3241e-07 | 5.0406e-08 | 7.3981e-07
930 | feeder2_line55 | 3 | 99 | 4.9896e-08 | 7.3342e-07 | 5.04e-08 | 7.4083e-07
930 | feeder2_line56 | 1 | 354.6 | 81.2503 | 81.2465 | 22.9132 | 22.9121
930 | feeder2_line56 | 2 | 354.6 | 72.5421 | 72.5452 | 20.4574 | 20.4583
930 | feeder2_line56 | 3 | 354.6 | 77.9484 | 77.9476 | 21.9821 | 21.9818
930 | feeder2_line57 | 1 | 99 | 7.5331e-07 | 1.5426e-06 | 7.6092e-07 | 1.5582e-06
930 | feeder2_line57 | 2 | 99 | 7.4601e-07 | 1.5476e-06 | 7.5355e-07 | 1.5632e-06
930 | feeder2_line57 | 3 | 99 | 1.5362 | 1.5362 | 1.5517 | 1.5517
930 | feeder2_line58 | 1 | 266.4 | 19.5752 | 19.5754 | 7.348 | 7.3481
930 | feeder2_line58 | 2 | 266.4 | 1.8985e-05 | 2.6907e-06 | 7.1263e-06 | 1.01e-06
930 | feeder2_line58 | 3 | 266.4 | 1.9022e-05 | 2.6937e-06 | 7.1403e-06 | 1.0112e-06
930 | feeder2_line59 | 1 | 99 | 5.0219e-08 | 5.3621e-07 | 5.0727e-08 | 5.4162e-07
930 | feeder2_line59 | 2 | 99 | 4.9729e-08 | 5.3793e-07 | 5.0231e-08 | 5.4336e-07
930 | feeder2_line59 | 3 | 99 | 1.4747 | 1.4747 | 1.4896 | 1.4896
930 | feeder2_line60 | 1 | 99 | 2.9885e-07 | 8.1037e-07 | 3.0187e-07 | 8.1855e-07
930 | feeder2_line60 | 2 | 99 | 2.9966e-07 | 8.1299e-07 | 3.0269e-07 | 8.212e-07
930 | feeder2_line60 | 3 | 99 | 0.061549 | 0.061549 | 0.062171 | 0.062171
930 | feeder2_line61 | 1 | 266.4 | 1.4754 | 1.4756 | 0.55382 | 0.55389
930 | feeder2_line61 | 2 | 266.4 | 1.6006 | 1.6008 | 0.60082 | 0.60089
930 | feeder2_line61 | 3 | 266.4 | 3.1575 | 3.1577 | 1.1852 | 1.1853
930 | feeder2_line62 | 1 | 354.6 | 82.0818 | 82.0782 | 23.1477 | 23.1467
930 | feeder2_line62 | 2 | 354.6 | 74.0176 | 74.021 | 20.8735 | 20.8745
930 | feeder2_line62 | 3 | 354.6 | 81.0417 | 81.0412 | 22.8544 | 22.8543
930 | feeder2_line63 | 1 | 99 | 0.089335 | 0.089331 | 0.090237 | 0.090233
930 | feeder2_line63 | 2 | 99 | 5.7448e-07 | 1.2224e-06 | 5.8029e-07 | 1.2347e-06
930 | feeder2_line63 | 3 | 99 | 5.7512e-07 | 1.2237e-06 | 5.8093e-07 | 1.2361e-06
930 | feeder2_line64 | 1 | 99 | 19.4861 | 19.4863 | 19.6829 | 19.6831
930 | feeder2_line64 | 2 | 99 | 4.1212e-12 | 3.22e-07 | 4.1628e-12 | 3.2525e-07
930 | feeder2_line64 | 3 | 99 | 1.9092e-11 | 3.2235e-07 | 1.9284e-11 | 3.2561e-07
930 | feeder2_line65 | 1 | 99 | 5.0289e-08 | 6.4262e-07 | 5.0797e-08 | 6.4911e-07
930 | feeder2_line65 | 2 | 99 | 0.089577 | 0.089581 | 0.090481 | 0.090486
930 | feeder2_line65 | 3 | 99 | 4.994e-08 | 6.448e-07 | 5.0444e-08 | 6.5131e-07
930 | feeder2_line66 | 1 | 354.6 | 82.0818 | 82.0782 | 23.1477 | 23.1467
930 | feeder2_line66 | 2 | 354.6 | 74.1071 | 74.1106 | 20.8988 | 20.8998
930 | feeder2_line66 | 3 | 354.6 | 81.0417 | 81.0412 | 22.8544 | 22.8543
930 | feeder2_line67 | 1 | 99 | 2.513e-08 | 3.631e-07 | 2.5384e-08 | 3.6677e-07
930 | feeder2_line67 | 2 | 99 | 2.4967e-08 | 3.638e-07 | 2.5219e-08 | 3.6748e-07
930 | feeder2_line67 | 3 | 99 | 1.7597 | 1.7598 | 1.7775 | 1.7775
930 | feeder2_line68 | 1 | 266.4 | 1.4754 | 1.4756 | 0.55384 | 0.55389
930 | feeder2_line68 | 2 | 266.4 | 1.6006 | 1.6008 | 0.60084 | 0.60089
930 | feeder2_line68 | 3 | 266.4 | 1.4475 | 1.4477 | 0.54337 | 0.54342
930 | feeder2_line69 | 1 | 99 | 1.7808 | 1.7808 | 1.7988 | 1.7987
930 | feeder2_line69 | 2 | 99 | 2.5546e-06 | 6.6842e-07 | 2.5804e-06 | 6.7517e-07
930 | feeder2_line69 | 3 | 99 | 2.5596e-06 | 6.6953e-07 | 2.5855e-06 | 6.7629e-07
930 | feeder2_line70 | 1 | 354.6 | 83.8607 | 83.8572 | 23.6494 | 23.6484
930 | feeder2_line70 | 2 | 354.6 | 74.107 | 74.1106 | 20.8988 | 20.8998
930 | feeder2_line70 | 3 | 354.6 | 81.0416 | 81.0412 | 22.8544 | 22.8543
930 | feeder2_line71 | 1 | 99 | 5.0299e-08 | 7.1723e-07 | 5.0807e-08 | 7.2447e-07
930 | feeder2_line71 | 2 | 99 | 1.2484 | 1.2484 | 1.261 | 1.261
930 | feeder2_line71 | 3 | 99 | 4.9958e-08 | 7.1963e-07 | 5.0463e-08 | 7.269e-07
930 | feeder2_line72 | 1 | 354.6 | 83.8608 | 83.8572 | 23.6494 | 23.6484
930 | feeder2_line72 | 2 | 354.6 | 74.7747 | 74.7782 | 21.0871 | 21.088
930 | feeder2_line72 | 3 | 354.6 | 81.0417 | 81.0412 | 22.8544 | 22.8543
930 | feeder2_line73 | 1 | 99 | 5.9954e-07 | 1.5372e-06 | 6.056e-07 | 1.5527e-06
930 | feeder2_line73 | 2 | 99 | 0.076911 | 0.076915 | 0.077688 | 0.077691
930 | feeder2_line73 | 3 | 99 | 6.0135e-07 | 1.5424e-06 | 6.0742e-07 | 1.558e-06
930 | feeder2_line74 | 1 | 99 | 5.0267e-08 | 4.5848e-07 | 5.0775e-08 | 4.6311e-07
930 | feeder2_line74 | 2 | 99 | 1.4482 | 1.4482 | 1.4629 | 1.4629
930 | feeder2_line74 | 3 | 99 | 4.9917e-08 | 4.6004e-07 | 5.0422e-08 | 4.6468e-07
930 | feeder2_line75 | 1 | 266.4 | 1.4755 | 1.4756 | 0.55387 | 0.55389
930 | feeder2_line75 | 2 | 266.4 | 0.089536 | 0.08957 | 0.033609 | 0.033623
930 | feeder2_line75 | 3 | 266.4 | 1.4476 | 1.4477 | 0.54341 | 0.54342
930 | feeder2_line76 | 1 | 99 | 1.4756 | 1.4756 | 1.4905 | 1.4905
930 | feeder2_line76 | 2 | 99 | 8.5083e-07 | 1.5888e-06 | 8.5942e-07 | 1.6048e-06
930 | feeder2_line76 | 3 | 99 | 8.5209e-07 | 1.5911e-06 | 8.607e-07 | 1.6071e-06
930 | feeder2_line77 | 1 | 99 | 2.5127e-08 | 5.7615e-07 | 2.5381e-08 | 5.8197e-07
930 | feeder2_line77 | 2 | 99 | 2.4969e-08 | 5.7727e-07 | 2.5222e-08 | 5.831e-07
930 | feeder2_line77 | 3 | 99 | 1.4477 | 1.4477 | 1.4623 | 1.4623
930 | feeder2_line78 | 1 | 266.4 | 1.0428e-11 | 9.5571e-07 | 3.9142e-12 | 3.5875e-07
930 | feeder2_line78 | 2 | 266.4 | 0.089568 | 0.08957 | 0.033622 | 0.033622
930 | feeder2_line78 | 3 | 266.4 | 1.3768e-11 | 9.5865e-07 | 5.1683e-12 | 3.5985e-07
930 | feeder2_line79 | 1 | 354.6 | 3.0091 | 3.0086 | 0.84858 | 0.84846
930 | feeder2_line79 | 2 | 354.6 | 5.8358 | 5.8354 | 1.6457 | 1.6456
930 | feeder2_line79 | 3 | 354.6 | 5.099 | 5.0987 | 1.438 | 1.4379
930 | feeder2_line80 | 1 | 354.6 | 86.8698 | 86.8656 | 24.498 | 24.4968
930 | feeder2_line80 | 2 | 354.6 | 80.5725 | 80.5754 | 22.7221 | 22.7229
930 | feeder2_line80 | 3 | 354.6 | 85.1266 | 85.1256 | 24.0064 | 24.0061
930 | feeder2_line81 | 1 | 354.6 | 86.8698 | 86.8656 | 24.498 | 24.4968
930 | feeder2_line81 | 2 | 354.6 | 80.5724 | 80.5754 | 22.7221 | 22.7229
930 | feeder2_line81 | 3 | 354.6 | 86.8785 | 86.8774 | 24.5004 | 24.5001
930 | feeder2_line82 | 1 | 354.6 | 8.0385e-12 | 7.3622e-07 | 2.2669e-12 | 2.0762e-07
930 | feeder2_line82 | 2 | 354.6 | 2.1722e-11 | 7.3712e-07 | 6.1259e-12 | 2.0787e-07
930 | feeder2_line82 | 3 | 354.6 | 1.9222 | 1.9222 | 0.54208 | 0.54207
930 | feeder2_line83 | 1 | 354.6 | 86.8699 | 86.8656 | 24.498 | 24.4968
930 | feeder2_line83 | 2 | 354.6 | 81.338 | 81.3408 | 22.938 | 22.9388
930 | feeder2_line83 | 3 | 354.6 | 86.8787 | 86.8774 | 24.5005 | 24.5001
930 | feeder2_line84 | 1 | 354.6 | 1.4972e-11 | 1.3014e-06 | 4.2224e-12 | 3.67e-07
930 | feeder2_line84 | 2 | 354.6 | 1.3356 | 1.3356 | 0.37665 | 0.37665
930 | feeder2_line84 | 3 | 354.6 | 6.2958e-12 | 1.3053e-06 | 1.7755e-12 | 3.6811e-07
930 | feeder2_line85 | 1 | 99 | 0.077009 | 0.077005 | 0.077787 | 0.077783
930 | feeder2_line85 | 2 | 99 | 5.0084e-08 | 4.6509e-07 | 5.059e-08 | 4.6978e-07
930 | feeder2_line85 | 3 | 99 | 5.0003e-08 | 4.6598e-07 | 5.0508e-08 | 4.7069e-07
930 | feeder2_line86 | 1 | 354.6 | 86.947 | 86.9426 | 24.5197 | 24.5185
930 | feeder2_line86 | 2 | 354.6 | 81.3381 | 81.3408 | 22.938 | 22.9388
930 | feeder2_line86 | 3 | 354.6 | 86.8788 | 86.8774 | 24.5005 | 24.5001
930 | feeder2_line87 | 1 | 354.6 | 86.9472 | 86.9426 | 24.5198 | 24.5185
930 | feeder2_line87 | 2 | 354.6 | 87.9128 | 87.9153 | 24.7921 | 24.7928
930 | feeder2_line87 | 3 | 354.6 | 96.6296 | 96.628 | 27.2503 | 27.2499
930 | feeder2_line88 | 1 | 354.6 | 0.00011355 | 3.3735e-06 | 3.2021e-05 | 9.5134e-07
930 | feeder2_line88 | 2 | 354.6 | 6.9507 | 6.9507 | 1.9602 | 1.9602
930 | feeder2_line88 | 3 | 354.6 | 9.752 | 9.7519 | 2.7501 | 2.7501
930 | feeder2_line89 | 1 | 354.6 | 86.9449 | 86.9426 | 24.5191 | 24.5185
930 | feeder2_line89 | 2 | 354.6 | 90.5755 | 90.5804 | 25.543 | 25.5444
930 | feeder2_line89 | 3 | 354.6 | 96.6273 | 96.628 | 27.2497 | 27.2499
930 | feeder2_line90 | 1 | 354.6 | 0.00072527 | 2.0369e-06 | 0.00020453 | 5.7442e-07
930 | feeder2_line90 | 2 | 354.6 | 2.8595 | 2.8598 | 0.8064 | 0.80649
930 | feeder2_line90 | 3 | 354.6 | 0.00072923 | 2.0444e-06 | 0.00020565 | 5.7654e-07
930 | feeder2_line91 | 1 | 354.6 | 86.9448 | 86.9426 | 24.5191 | 24.5185
930 | feeder2_line91 | 2 | 354.6 | 90.5754 | 90.5804 | 25.543 | 25.5444
930 | feeder2_line91 | 3 | 354.6 | 96.6883 | 96.6891 | 27.2669 | 27.2671
930 | feeder2_line92 | 1 | 354.6 | 9.0598e-12 | 1.0276e-06 | 2.5549e-12 | 2.898e-07
930 | feeder2_line92 | 2 | 354.6 | 2.7327e-11 | 1.0288e-06 | 7.7064e-12 | 2.9012e-07
930 | feeder2_line92 | 3 | 354.6 | 0.06131 | 0.06131 | 0.01729 | 0.01729
930 | feeder2_line93 | 1 | 99 | 2.5182e-08 | 3.4297e-07 | 2.5436e-08 | 3.4644e-07
930 | feeder2_line93 | 2 | 99 | 1.3359 | 1.3359 | 1.3494 | 1.3494
930 | feeder2_line93 | 3 | 99 | 2.5014e-08 | 3.4414e-07 | 2.5267e-08 | 3.4761e-07
930 | feeder2_line94 | 1 | 354.6 | 2.5189e-06 | 1.67e-06 | 7.1034e-07 | 4.7096e-07
930 | feeder2_line94 | 2 | 354.6 | 1.8572 | 1.8572 | 0.52375 | 0.52376
930 | feeder2_line94 | 3 | 354.6 | 2.5012e-06 | 1.6753e-06 | 7.0536e-07 | 4.7243e-07
930 | feeder2_line95 | 1 | 99 | 3.5758e-06 | 2.616e-06 | 3.6119e-06 | 2.6425e-06
930 | feeder2_line95 | 2 | 99 | 6.9506 | 6.9507 | 7.0209 | 7.0209
930 | feeder2_line95 | 3 | 99 | 3.5906e-06 | 2.6246e-06 | 3.6269e-06 | 2.6511e-06
930 | feeder2_line96 | 1 | 354.6 | 0.00012138 | 6.2374e-07 | 3.423e-05 | 1.759e-07
930 | feeder2_line96 | 2 | 354.6 | 0.00012158 | 6.2458e-07 | 3.4287e-05 | 1.7614e-07
930 | feeder2_line96 | 3 | 354.6 | 9.752 | 9.7519 | 2.7501 | 2.7501
930 | feeder2_line97 | 1 | 354.6 | 89.2094 | 89.207 | 25.1578 | 25.1571
930 | feeder2_line97 | 2 | 354.6 | 90.5756 | 90.5804 | 25.543 | 25.5444
930 | feeder2_line97 | 3 | 354.6 | 96.6884 | 96.6891 | 27.2669 | 27.2671
930 | feeder2_line98 | 1 | 354.6 | 2.4874 | 2.4859 | 0.70146 | 0.70105
930 | feeder2_line98 | 2 | 354.6 | 0.0017126 | 6.2182e-07 | 0.00048297 | 1.7536e-07
930 | feeder2_line98 | 3 | 354.6 | 0.0017136 | 6.2592e-07 | 0.00048326 | 1.7651e-07
930 | feeder2_line99 | 1 | 99 | 2.5174e-08 | 4.4832e-07 | 2.5428e-08 | 4.5285e-07
930 | feeder2_line99 | 2 | 99 | 2.5051e-08 | 4.4889e-07 | 2.5304e-08 | 4.5342e-07
930 | feeder2_line99 | 3 | 99 | 9.7519 | 9.7519 | 9.8504 | 9.8504
930 | feeder2_line100 | 1 | 99 | 2.4859 | 2.4859 | 2.5111 | 2.511
930 | feeder2_line100 | 2 | 99 | 2.5076e-08 | 6.1657e-07 | 2.533e-08 | 6.2279e-07
930 | feeder2_line100 | 3 | 99 | 2.5016e-08 | 6.1792e-07 | 2.5269e-08 | 6.2416e-07
930 | feeder2_line101 | 1 | 354.6 | 1.8545 | 1.8541 | 0.52298 | 0.52286
930 | feeder2_line101 | 2 | 354.6 | 5.8358 | 5.8354 | 1.6457 | 1.6456
930 | feeder2_line101 | 3 | 354.6 | 5.099 | 5.0987 | 1.438 | 1.4379
930 | feeder2_line102 | 1 | 99 | 1.1549 | 1.1549 | 1.1666 | 1.1666
930 | feeder2_line102 | 2 | 99 | 2.3459e-06 | 8.8123e-07 | 2.3696e-06 | 8.9013e-07
930 | feeder2_line102 | 3 | 99 | 2.3487e-06 | 8.8282e-07 | 2.3724e-06 | 8.9174e-07
930 | feeder2_line103 | 1 | 99 | 5.5022e-07 | 8.0542e-07 | 5.5578e-07 | 8.1355e-07
930 | feeder2_line103 | 2 | 99 | 1.0743 | 1.0743 | 1.0851 | 1.0851
930 | feeder2_line103 | 3 | 99 | 5.5228e-07 | 8.0803e-07 | 5.5785e-07 | 8.162e-07
930 | feeder2_line104 | 1 | 354.6 | 1.8544 | 1.8541 | 0.52295 | 0.52286
930 | feeder2_line104 | 2 | 354.6 | 4.7687 | 4.7684 | 1.3448 | 1.3447
930 | feeder2_line104 | 3 | 354.6 | 5.0989 | 5.0987 | 1.4379 | 1.4379
930 | feeder2_line105 | 1 | 99 | 2.5498e-06 | 7.4109e-07 | 2.5756e-06 | 7.4857e-07
930 | feeder2_line105 | 2 | 99 | 2.5558e-06 | 7.4216e-07 | 2.5817e-06 | 7.4966e-07
930 | feeder2_line105 | 3 | 99 | 1.1003 | 1.1003 | 1.1114 | 1.1114
930 | feeder2_line106 | 1 | 354.6 | 1.8543 | 1.8541 | 0.52293 | 0.52286
930 | feeder2_line106 | 2 | 354.6 | 4.7687 | 4.7684 | 1.3448 | 1.3447
930 | feeder2_line106 | 3 | 354.6 | 4.0673 | 4.0671 | 1.147 | 1.147
930 | feeder2_line107 | 1 | 99 | 3.2542e-07 | 9.0312e-07 | 3.2871e-07 | 9.1224e-07
930 | feeder2_line107 | 2 | 99 | 2.6108 | 2.6108 | 2.6371 | 2.6371
930 | feeder2_line107 | 3 | 99 | 3.261e-07 | 9.0602e-07 | 3.2939e-07 | 9.1517e-07
930 | feeder2_line108 | 1 | 354.6 | 1.8543 | 1.8541 | 0.52293 | 0.52286
930 | feeder2_line108 | 2 | 354.6 | 2.1817 | 2.1814 | 0.61525 | 0.61519
930 | feeder2_line108 | 3 | 354.6 | 4.0673 | 4.0671 | 1.147 | 1.147
930 | feeder2_line109 | 1 | 354.6 | 91.905 | 91.9013 | 25.9179 | 25.9169
930 | feeder2_line109 | 2 | 354.6 | 90.5768 | 90.5804 | 25.5434 | 25.5444
930 | feeder2_line109 | 3 | 354.6 | 96.6897 | 96.6891 | 27.2672 | 27.2671
930 | feeder2_line110 | 1 | 99 | 2.9743 | 2.9736 | 3.0043 | 3.0036
930 | feeder2_line110 | 2 | 99 | 0.0008078 | 9.1286e-07 | 0.00081596 | 9.2208e-07
930 | feeder2_line110 | 3 | 99 | 0.00081032 | 9.148e-07 | 0.0008185 | 9.2404e-07
930 | feeder2_line111 | 1 | 99 | 2.5167e-08 | 3.8289e-07 | 2.5422e-08 | 3.8676e-07
930 | feeder2_line111 | 2 | 99 | 6.1237 | 6.1237 | 6.1855 | 6.1856
930 | feeder2_line111 | 3 | 99 | 2.5004e-08 | 3.8415e-07 | 2.5257e-08 | 3.8803e-07
930 | feeder2_line112 | 1 | 99 | 3.257e-07 | 9.201e-07 | 3.2899e-07 | 9.294e-07
930 | feeder2_line112 | 2 | 99 | 0.87711 | 0.87713 | 0.88597 | 0.88599
930 | feeder2_line112 | 3 | 99 | 3.2641e-07 | 9.2312e-07 | 3.2971e-07 | 9.3245e-07
930 | feeder2_line113 | 1 | 99 | 1.345 | 1.345 | 1.3586 | 1.3586
930 | feeder2_line113 | 2 | 99 | 3.2628e-07 | 9.0937e-07 | 3.2958e-07 | 9.1856e-07
930 | feeder2_line113 | 3 | 99 | 3.2685e-07 | 9.1146e-07 | 3.3015e-07 | 9.2066e-07
930 | feeder2_line114 | 1 | 99 | 1.0732 | 1.0732 | 1.0841 | 1.0841
930 | feeder2_line114 | 2 | 99 | 2.5024e-08 | 4.3822e-07 | 2.5277e-08 | 4.4264e-07
930 | feeder2_line114 | 3 | 99 | 2.4989e-08 | 4.3899e-07 | 2.5241e-08 | 4.4342e-07
930 | feeder2_line115 | 1 | 99 | 2.5155e-08 | 5.6359e-07 | 2.5409e-08 | 5.6928e-07
930 | feeder2_line115 | 2 | 99 | 0.2826 | 0.2826 | 0.28545 | 0.28545
930 | feeder2_line115 | 3 | 99 | 2.4989e-08 | 5.6538e-07 | 2.5242e-08 | 5.7109e-07
930 | feeder2_line116 | 1 | 354.6 | 1.8543 | 1.8541 | 0.52293 | 0.52286
930 | feeder2_line116 | 2 | 354.6 | 2.0032 | 2.0029 | 0.56491 | 0.56484
930 | feeder2_line116 | 3 | 354.6 | 4.0674 | 4.0671 | 1.147 | 1.147
930 | feeder2_line117 | 1 | 99 | 5.0451e-08 | 6.4499e-07 | 5.096e-08 | 6.515e-07
930 | feeder2_line117 | 2 | 99 | 2.8995 | 2.8995 | 2.9288 | 2.9288
930 | feeder2_line117 | 3 | 99 | 5.0066e-08 | 6.4736e-07 | 5.0572e-08 | 6.539e-07
930 | feeder2_line118 | 1 | 354.6 | 91.905 | 91.9013 | 25.9179 | 25.9169
930 | feeder2_line118 | 2 | 354.6 | 93.3973 | 93.4008 | 26.3388 | 26.3398
930 | feeder2_line118 | 3 | 354.6 | 96.6897 | 96.6891 | 27.2673 | 27.2671
930 | feeder2_line119 | 1 | 99 | 2.5153e-08 | 6.0643e-07 | 2.5407e-08 | 6.1256e-07
930 | feeder2_line119 | 2 | 99 | 2.5012e-08 | 6.0731e-07 | 2.5265e-08 | 6.1344e-07
930 | feeder2_line119 | 3 | 99 | 0.093211 | 0.093211 | 0.094153 | 0.094153
930 | feeder2_line120 | 1 | 354.6 | 1.8543 | 1.8541 | 0.52293 | 0.52286
930 | feeder2_line120 | 2 | 354.6 | 2.0032 | 2.0029 | 0.56491 | 0.56484
930 | feeder2_line120 | 3 | 354.6 | 3.9905 | 3.9903 | 1.1254 | 1.1253
930 | feeder2_line121 | 1 | 99 | 3.2541e-07 | 9.3906e-07 | 3.2869e-07 | 9.4855e-07
930 | feeder2_line121 | 2 | 99 | 1.235 | 1.235 | 1.2475 | 1.2475
930 | feeder2_line121 | 3 | 99 | 3.2606e-07 | 9.42e-07 | 3.2936e-07 | 9.5151e-07
930 | feeder2_line122 | 1 | 354.6 | 1.8543 | 1.8541 | 0.52293 | 0.52286
930 | feeder2_line122 | 2 | 354.6 | 1.1926 | 1.1925 | 0.33633 | 0.3363
930 | feeder2_line122 | 3 | 354.6 | 3.9905 | 3.9903 | 1.1253 | 1.1253
930 | feeder2_line123 | 1 | 99 | 5.7534e-07 | 9.7308e-07 | 5.8116e-07 | 9.8291e-07
930 | feeder2_line123 | 2 | 99 | 5.7621e-07 | 9.7453e-07 | 5.8203e-07 | 9.8437e-07
930 | feeder2_line123 | 3 | 99 | 0.076588 | 0.076588 | 0.077362 | 0.077361
930 | feeder2_line124 | 1 | 354.6 | 1.8542 | 1.8541 | 0.5229 | 0.52286
930 | feeder2_line124 | 2 | 354.6 | 1.1927 | 1.1925 | 0.33634 | 0.3363
930 | feeder2_line124 | 3 | 354.6 | 3.9284 | 3.9282 | 1.1078 | 1.1078
930 | feeder2_line125 | 1 | 99 | 5.7534e-07 | 9.0457e-07 | 5.8115e-07 | 9.1371e-07
930 | feeder2_line125 | 2 | 99 | 5.762e-07 | 9.0592e-07 | 5.8202e-07 | 9.1507e-07
930 | feeder2_line125 | 3 | 99 | 2.4861 | 2.4861 | 2.5113 | 2.5113
930 | feeder2_line126 | 1 | 354.6 | 1.8544 | 1.8541 | 0.52295 | 0.52286
930 | feeder2_line126 | 2 | 354.6 | 1.1928 | 1.1925 | 0.33637 | 0.3363
930 | feeder2_line126 | 3 | 354.6 | 1.5471 | 1.5469 | 0.43631 | 0.43622
930 | feeder2_line127 | 1 | 99 | 5.7533e-07 | 1.0829e-06 | 5.8115e-07 | 1.0938e-06
930 | feeder2_line127 | 2 | 99 | 5.762e-07 | 1.0845e-06 | 5.8202e-07 | 1.0955e-06
930 | feeder2_line127 | 3 | 99 | 1.4734 | 1.4734 | 1.4883 | 1.4883
930 | feeder2_line128 | 1 | 354.6 | 1.8543 | 1.8541 | 0.52292 | 0.52286
930 | feeder2_line128 | 2 | 354.6 | 1.1928 | 1.1925 | 0.33637 | 0.3363
930 | feeder2_line128 | 3 | 354.6 | 0.12612 | 0.1259 | 0.035566 | 0.035504
930 | feeder2_line129 | 1 | 99 | 5.5017e-07 | 8.7807e-07 | 5.5573e-07 | 8.8694e-07
930 | feeder2_line129 | 2 | 99 | 1.1925 | 1.1925 | 1.2046 | 1.2046
930 | feeder2_line129 | 3 | 99 | 5.5214e-07 | 8.808e-07 | 5.5772e-07 | 8.897e-07
930 | feeder2_line130 | 1 | 354.6 | 1.8543 | 1.8541 | 0.52293 | 0.52286
930 | feeder2_line130 | 2 | 354.6 | 0.00030918 | 4.6537e-06 | 8.7191e-05 | 1.3124e-06
930 | feeder2_line130 | 3 | 354.6 | 0.12613 | 0.1259 | 0.03557 | 0.035504
930 | feeder2_line131 | 1 | 99 | 5.7532e-07 | 9.732e-07 | 5.8113e-07 | 9.8303e-07
930 | feeder2_line131 | 2 | 99 | 5.7621e-07 | 9.7468e-07 | 5.8203e-07 | 9.8453e-07
930 | feeder2_line131 | 3 | 99 | 0.049249 | 0.049249 | 0.049747 | 0.049747
930 | feeder2_line132 | 1 | 354.6 | 1.8541 | 1.8541 | 0.52288 | 0.52286
930 | feeder2_line132 | 2 | 354.6 | 0.00012612 | 2.9258e-06 | 3.5567e-05 | 8.2509e-07
930 | feeder2_line132 | 3 | 354.6 | 0.076812 | 0.076743 | 0.021662 | 0.021642
930 | feeder2_line133 | 1 | 99 | 1.8541 | 1.8541 | 1.8728 | 1.8728
930 | feeder2_line133 | 2 | 99 | 3.0061e-07 | 9.8246e-07 | 3.0364e-07 | 9.9238e-07
930 | feeder2_line133 | 3 | 99 | 3.0106e-07 | 9.8403e-07 | 3.041e-07 | 9.9397e-07
930 | feeder2_line134 | 1 | 354.6 | 5.8279e-12 | 1.7892e-06 | 1.6435e-12 | 5.0456e-07
930 | feeder2_line134 | 2 | 354.6 | 7.8195e-12 | 1.7916e-06 | 2.2052e-12 | 5.0524e-07
930 | feeder2_line134 | 3 | 354.6 | 0.076743 | 0.076743 | 0.021642 | 0.021642
930 | feeder2_line135 | 1 | 99 | 1.2489 | 1.2489 | 1.2615 | 1.2615
930 | feeder2_line135 | 2 | 99 | 5.025e-08 | 5.8875e-07 | 5.0757e-08 | 5.947e-07
930 | feeder2_line135 | 3 | 99 | 5.0091e-08 | 5.9021e-07 | 5.0597e-08 | 5.9617e-07
930 | feeder2_line136 | 1 | 354.6 | 92.6343 | 92.6306 | 26.1236 | 26.1226
930 | feeder2_line136 | 2 | 354.6 | 93.3972 | 93.4008 | 26.3388 | 26.3398
930 | feeder2_line136 | 3 | 354.6 | 96.6896 | 96.6891 | 27.2672 | 27.2671
930 | feeder2_line137 | 1 | 99 | 1.3913 | 1.3912 | 1.4053 | 1.4053
930 | feeder2_line137 | 2 | 99 | 8.545e-07 | 1.5859e-06 | 8.6313e-07 | 1.6019e-06
930 | feeder2_line137 | 3 | 99 | 8.5672e-07 | 1.5899e-06 | 8.6537e-07 | 1.6059e-06
930 | feeder2_line138 | 1 | 354.6 | 94.0244 | 94.0207 | 26.5156 | 26.5146
930 | feeder2_line138 | 2 | 354.6 | 93.3973 | 93.4008 | 26.3388 | 26.3398
930 | feeder2_line138 | 3 | 354.6 | 96.6897 | 96.6891 | 27.2673 | 27.2671
930 | feeder2_line139 | 1 | 99 | 5.051e-08 | 4.9357e-07 | 5.102e-08 | 4.9856e-07
930 | feeder2_line139 | 2 | 99 | 5.0272e-08 | 4.9421e-07 | 5.078e-08 | 4.992e-07
930 | feeder2_line139 | 3 | 99 | 0.26148 | 0.26151 | 0.26413 | 0.26415
930 | feeder2_line140 | 1 | 354.6 | 94.0245 | 94.0207 | 26.5157 | 26.5146
930 | feeder2_line140 | 2 | 354.6 | 93.3974 | 93.4008 | 26.3388 | 26.3398
930 | feeder2_line140 | 3 | 354.6 | 96.9509 | 96.9502 | 27.3409 | 27.3407
930 | feeder2_line141 | 1 | 99 | 2.5339e-06 | 4.8831e-07 | 2.5595e-06 | 4.9324e-07
930 | feeder2_line141 | 2 | 99 | 0.076607 | 0.076611 | 0.077381 | 0.077385
930 | feeder2_line141 | 3 | 99 | 2.5479e-06 | 4.9018e-07 | 2.5737e-06 | 4.9513e-07
930 | feeder2_line142 | 1 | 354.6 | 94.0243 | 94.0207 | 26.5156 | 26.5146
930 | feeder2_line142 | 2 | 354.6 | 93.4735 | 93.4771 | 26.3603 | 26.3613
930 | feeder2_line142 | 3 | 354.6 | 96.9507 | 96.9502 | 27.3409 | 27.3407
930 | feeder2_line143 | 1 | 99 | 8.5371e-07 | 1.7353e-06 | 8.6234e-07 | 1.7528e-06
930 | feeder2_line143 | 2 | 99 | 2.6122 | 2.6122 | 2.6386 | 2.6386
930 | feeder2_line143 | 3 | 99 | 8.5716e-07 | 1.7419e-06 | 8.6582e-07 | 1.7595e-06
930 | feeder2_line144 | 1 | 354.6 | 94.0241 | 94.0207 | 26.5155 | 26.5146
930 | feeder2_line144 | 2 | 354.6 | 96.0851 | 96.0889 | 27.0967 | 27.0978
930 | feeder2_line144 | 3 | 354.6 | 96.9505 | 96.9502 | 27.3408 | 27.3407
930 | feeder2_line145 | 1 | 99 | 2.5261e-08 | 4.866e-07 | 2.5516e-08 | 4.9151e-07
930 | feeder2_line145 | 2 | 99 | 1.9217 | 1.9217 | 1.9412 | 1.9412
930 | feeder2_line145 | 3 | 99 | 2.5061e-08 | 4.8847e-07 | 2.5314e-08 | 4.934e-07
930 | feeder2_line146 | 1 | 354.6 | 94.024 | 94.0207 | 26.5155 | 26.5146
930 | feeder2_line146 | 2 | 354.6 | 97.8372 | 97.8411 | 27.5909 | 27.592
930 | feeder2_line146 | 3 | 354.6 | 96.9504 | 96.9502 | 27.3408 | 27.3407
930 | feeder2_line147 | 1 | 99 | 1.9021 | 1.9021 | 1.9213 | 1.9213
930 | feeder2_line147 | 2 | 99 | 1.1568e-06 | 2.2474e-06 | 1.1685e-06 | 2.2701e-06
930 | feeder2_line147 | 3 | 99 | 1.1598e-06 | 2.2532e-06 | 1.1715e-06 | 2.2759e-06
930 | feeder2_line148 | 1 | 99 | 0.084665 | 0.08466 | 0.08552 | 0.085515
930 | feeder2_line148 | 2 | 99 | 6.0358e-07 | 1.506e-06 | 6.0967e-07 | 1.5212e-06
930 | feeder2_line148 | 3 | 99 | 6.0498e-07 | 1.5098e-06 | 6.1109e-07 | 1.5251e-06
930 | feeder2_line149 | 1 | 354.6 | 96.0057 | 96.0021 | 27.0744 | 27.0734
930 | feeder2_line149 | 2 | 354.6 | 97.8373 | 97.8411 | 27.5909 | 27.592
930 | feeder2_line149 | 3 | 354.6 | 96.9505 | 96.9502 | 27.3408 | 27.3407
930 | feeder2_line150 | 1 | 354.6 | 96.0058 | 96.0021 | 27.0744 | 27.0734
930 | feeder2_line150 | 2 | 354.6 | 99.0001 | 99.0038 | 27.9188 | 27.9198
930 | feeder2_line150 | 3 | 354.6 | 96.9506 | 96.9502 | 27.3408 | 27.3407
930 | feeder2_line151 | 1 | 99 | 9.7915e-06 | 1.7869e-06 | 9.8904e-06 | 1.8049e-06
930 | feeder2_line151 | 2 | 99 | 1.1652 | 1.1652 | 1.177 | 1.177
930 | feeder2_line151 | 3 | 99 | 9.8511e-06 | 1.7938e-06 | 9.9506e-06 | 1.8119e-06
930 | feeder2_line152 | 1 | 354.6 | 4.5383e-12 | 1.1913e-06 | 1.2798e-12 | 3.3595e-07
930 | feeder2_line152 | 2 | 354.6 | 1.8352e-11 | 1.1927e-06 | 5.1755e-12 | 3.3635e-07
930 | feeder2_line152 | 3 | 354.6 | 1.673 | 1.673 | 0.47181 | 0.47181
930 | feeder2_line153 | 1 | 99 | 1.2358 | 1.2358 | 1.2483 | 1.2483
930 | feeder2_line153 | 2 | 99 | 5.0349e-08 | 5.9672e-07 | 5.0858e-08 | 6.0274e-07
930 | feeder2_line153 | 3 | 99 | 5.0176e-08 | 5.9824e-07 | 5.0683e-08 | 6.0428e-07
930 | feeder2_line154 | 1 | 99 | 5.7823e-07 | 8.8676e-07 | 5.8408e-07 | 8.9571e-07
930 | feeder2_line154 | 2 | 99 | 5.7903e-07 | 8.8795e-07 | 5.8488e-07 | 8.9692e-07
930 | feeder2_line154 | 3 | 99 | 0.040411 | 0.040427 | 0.040819 | 0.040835
930 | feeder2_line155 | 1 | 99 | 97.1896 | 97.1861 | 98.1713 | 98.1677
930 | feeder2_line155 | 2 | 99 | 99 | 99.0038 | 100 | 100.0038
930 | feeder2_line155 | 3 | 99 | 98.663 | 98.6626 | 99.6596 | 99.6592
930 | feeder2_line156 | 1 | 99 | 6.0326e-07 | 1.1668e-06 | 6.0935e-07 | 1.1786e-06
930 | feeder2_line156 | 2 | 99 | 1.076 | 1.076 | 1.0869 | 1.0869
930 | feeder2_line156 | 3 | 99 | 6.0531e-07 | 1.1713e-06 | 6.1142e-07 | 1.1831e-06
930 | feeder2_line157 | 1 | 99 | 2.5294e-08 | 2.5331e-07 | 2.5549e-08 | 2.5587e-07
930 | feeder2_line157 | 2 | 99 | 0.089192 | 0.089195 | 0.090093 | 0.090096
930 | feeder2_line157 | 3 | 99 | 2.5077e-08 | 2.5429e-07 | 2.5331e-08 | 2.5685e-07
960 | feeder2_line1 | 1 | 354.6 | 32.868 | 32.8769 | 9.269 | 9.2715
960 | feeder2_line1 | 2 | 354.6 | 38.5501 | 38.5604 | 10.8714 | 10.8743
960 | feeder2_line1 | 3 | 354.6 | 65.7806 | 65.7642 | 18.5506 | 18.546
960 | feeder2_line2 | 1 | 354.6 | 33.4912 | 33.5003 | 9.4448 | 9.4474
960 | feeder2_line2 | 2 | 354.6 | 38.5502 | 38.5604 | 10.8715 | 10.8743
960 | feeder2_line2 | 3 | 354.6 | 65.7808 | 65.7642 | 18.5507 | 18.546
960 | feeder2_line3 | 1 | 80.1 | 1.2568 | 1.2568 | 1.5691 | 1.5691
960 | feeder2_line3 | 2 | 80.1 | 5.6947e-07 | 1.0524e-06 | 7.1095e-07 | 1.3138e-06
960 | feeder2_line3 | 3 | 80.1 | 5.7177e-07 | 1.0566e-06 | 7.1381e-07 | 1.3191e-06
960 | feeder2_line4 | 1 | 354.6 | 33.4912 | 33.5003 | 9.4448 | 9.4474
960 | feeder2_line4 | 2 | 354.6 | 37.6746 | 37.6848 | 10.6245 | 10.6274
960 | feeder2_line4 | 3 | 354.6 | 65.7809 | 65.7642 | 18.5507 | 18.546
960 | feeder2_line5 | 1 | 80.1 | 5.7032e-07 | 9.9518e-07 | 7.1201e-07 | 1.2424e-06
960 | feeder2_line5 | 2 | 80.1 | 1.4023 | 1.4023 | 1.7507 | 1.7507
960 | feeder2_line5 | 3 | 80.1 | 5.7181e-07 | 9.9773e-07 | 7.1387e-07 | 1.2456e-06
960 | feeder2_line6 | 1 | 80.1 | 5.7031e-07 | 1.1707e-06 | 7.12e-07 | 1.4615e-06
960 | feeder2_line6 | 2 | 80.1 | 5.6941e-07 | 1.1688e-06 | 7.1087e-07 | 1.4592e-06
960 | feeder2_line6 | 3 | 80.1 | 0.085307 | 0.085277 | 0.1065 | 0.10646
960 | feeder2_line7 | 1 | 354.6 | 33.4913 | 33.5003 | 9.4448 | 9.4474
960 | feeder2_line7 | 2 | 354.6 | 37.6746 | 37.6848 | 10.6245 | 10.6274
960 | feeder2_line7 | 3 | 354.6 | 65.8591 | 65.8423 | 18.5728 | 18.568
960 | feeder2_line8 | 1 | 80.1 | 0.72087 | 0.72087 | 0.89996 | 0.89996
960 | feeder2_line8 | 2 | 80.1 | 5.6929e-07 | 1.1268e-06 | 7.1072e-07 | 1.4067e-06
960 | feeder2_line8 | 3 | 80.1 | 5.7208e-07 | 1.1322e-06 | 7.1421e-07 | 1.4135e-06
960 | feeder2_line9 | 1 | 354.6 | 33.887 | 33.8963 | 9.5564 | 9.559
960 | feeder2_line9 | 2 | 354.6 | 37.6745 | 37.6848 | 10.6245 | 10.6274
960 | feeder2_line9 | 3 | 354.6 | 65.8591 | 65.8423 | 18.5728 | 18.568
960 | feeder2_line10 | 1 | 80.1 | 8.4294e-07 | 1.4903e-06 | 1.0524e-06 | 1.8606e-06
960 | feeder2_line10 | 2 | 80.1 | 0.72074 | 0.72074 | 0.8998 | 0.8998
960 | feeder2_line10 | 3 | 80.1 | 8.4582e-07 | 1.4951e-06 | 1.056e-06 | 1.8665e-06
960 | feeder2_line11 | 1 | 354.6 | 33.8871 | 33.8963 | 9.5564 | 9.559
960 | feeder2_line11 | 2 | 354.6 | 37.8872 | 37.8975 | 10.6845 | 10.6874
960 | feeder2_line11 | 3 | 354.6 | 65.8592 | 65.8423 | 18.5728 | 18.568
960 | feeder2_line12 | 1 | 80.1 | 5.4533e-07 | 9.8855e-07 | 6.8081e-07 | 1.2342e-06
960 | feeder2_line12 | 2 | 80.1 | 5.4438e-07 | 9.8676e-07 | 6.7963e-07 | 1.2319e-06
960 | feeder2_line12 | 3 | 80.1 | 0.81864 | 0.81867 | 1.022 | 1.0221
960 | feeder2_line13 | 1 | 354.6 | 33.8871 | 33.8963 | 9.5564 | 9.559
960 | feeder2_line13 | 2 | 354.6 | 37.8873 | 37.8975 | 10.6845 | 10.6874
960 | feeder2_line13 | 3 | 354.6 | 66.0138 | 65.9969 | 18.6164 | 18.6116
960 | feeder2_line14 | 1 | 80.1 | 0.086262 | 0.086268 | 0.10769 | 0.1077
960 | feeder2_line14 | 2 | 80.1 | 2.9701e-07 | 6.4341e-07 | 3.708e-07 | 8.0325e-07
960 | feeder2_line14 | 3 | 80.1 | 2.9846e-07 | 6.4685e-07 | 3.726e-07 | 8.0756e-07
960 | feeder2_line15 | 1 | 354.6 | 33.9372 | 33.9464 | 9.5705 | 9.5731
960 | feeder2_line15 | 2 | 354.6 | 37.8873 | 37.8975 | 10.6845 | 10.6874
960 | feeder2_line15 | 3 | 354.6 | 66.0138 | 65.9969 | 18.6164 | 18.6116
960 | feeder2_line16 | 1 | 80.1 | 5.7022e-07 | 1.0273e-06 | 7.1189e-07 | 1.2825e-06
960 | feeder2_line16 | 2 | 80.1 | 0.029002 | 0.029001 | 0.036207 | 0.036206
960 | feeder2_line16 | 3 | 80.1 | 5.7237e-07 | 1.0311e-06 | 7.1457e-07 | 1.2873e-06
960 | feeder2_line17 | 1 | 354.6 | 33.9372 | 33.9464 | 9.5706 | 9.5731
960 | feeder2_line17 | 2 | 354.6 | 37.897 | 37.9071 | 10.6872 | 10.6901
960 | feeder2_line17 | 3 | 354.6 | 66.0138 | 65.9969 | 18.6164 | 18.6116
960 | feeder2_line18 | 1 | 80.1 | 5.4518e-07 | 7.3524e-07 | 6.8062e-07 | 9.179e-07
960 | feeder2_line18 | 2 | 80.1 | 5.4395e-07 | 7.3354e-07 | 6.7909e-07 | 9.1578e-07
960 | feeder2_line18 | 3 | 80.1 | 0.040104 | 0.040056 | 0.050068 | 0.050008
960 | feeder2_line19 | 1 | 354.6 | 33.9372 | 33.9464 | 9.5706 | 9.5731
960 | feeder2_line19 | 2 | 354.6 | 37.897 | 37.9071 | 10.6872 | 10.6901
960 | feeder2_line19 | 3 | 354.6 | 66.0501 | 66.0331 | 18.6267 | 18.6218
960 | feeder2_line20 | 1 | 99 | 5.4513e-07 | 8.8146e-07 | 5.5063e-07 | 8.9036e-07
960 | feeder2_line20 | 2 | 99 | 5.4383e-07 | 8.7931e-07 | 5.4932e-07 | 8.8819e-07
960 | feeder2_line20 | 3 | 99 | 1.6995 | 1.6995 | 1.7167 | 1.7167
960 | feeder2_line21 | 1 | 354.6 | 33.9373 | 33.9464 | 9.5706 | 9.5731
960 | feeder2_line21 | 2 | 354.6 | 37.897 | 37.9071 | 10.6873 | 10.6901
960 | feeder2_line21 | 3 | 354.6 | 67.5786 | 67.5614 | 19.0577 | 19.0528
960 | feeder2_line22 | 1 | 99 | 5.7006e-07 | 1.0104e-06 | 5.7582e-07 | 1.0207e-06
960 | feeder2_line22 | 2 | 99 | 12.221 | 12.221 | 12.3444 | 12.3444
960 | feeder2_line22 | 3 | 99 | 5.7317e-07 | 1.0159e-06 | 5.7896e-07 | 1.0261e-06
960 | feeder2_line23 | 1 | 99 | 5.7007e-07 | 9.4587e-07 | 5.7583e-07 | 9.5543e-07
960 | feeder2_line23 | 2 | 99 | 5.6864e-07 | 9.4348e-07 | 5.7438e-07 | 9.5301e-07
960 | feeder2_line23 | 3 | 99 | 0.081717 | 0.081711 | 0.082542 | 0.082537
960 | feeder2_line24 | 1 | 354.6 | 33.9373 | 33.9464 | 9.5706 | 9.5731
960 | feeder2_line24 | 2 | 354.6 | 42.6669 | 42.6769 | 12.0324 | 12.0352
960 | feeder2_line24 | 3 | 354.6 | 67.6543 | 67.6371 | 19.0791 | 19.0742
960 | feeder2_line25 | 1 | 99 | 12.2463 | 12.246 | 12.37 | 12.3697
960 | feeder2_line25 | 2 | 99 | 4.9775e-08 | 6.8585e-07 | 5.0278e-08 | 6.9278e-07
960 | feeder2_line25 | 3 | 99 | 4.9111e-08 | 6.9161e-07 | 4.9607e-08 | 6.9859e-07
960 | feeder2_line26 | 1 | 99 | 0.085718 | 0.085726 | 0.086584 | 0.086592
960 | feeder2_line26 | 2 | 99 | 5.437e-07 | 8.4975e-07 | 5.4919e-07 | 8.5833e-07
960 | feeder2_line26 | 3 | 99 | 5.4883e-07 | 8.5687e-07 | 5.5438e-07 | 8.6552e-07
960 | feeder2_line27 | 1 | 354.6 | 41.6737 | 41.6852 | 11.7523 | 11.7556
960 | feeder2_line27 | 2 | 354.6 | 42.6669 | 42.6769 | 12.0324 | 12.0352
960 | feeder2_line27 | 3 | 354.6 | 67.6544 | 67.6371 | 19.0791 | 19.0742
960 | feeder2_line28 | 1 | 99 | 2.5252e-06 | 7.0718e-07 | 2.5508e-06 | 7.1432e-07
960 | feeder2_line28 | 2 | 99 | 0.75428 | 0.7543 | 0.7619 | 0.76192
960 | feeder2_line28 | 3 | 99 | 2.5495e-06 | 7.1165e-07 | 2.5752e-06 | 7.1884e-07
960 | feeder2_line29 | 1 | 354.6 | 41.6737 | 41.6852 | 11.7523 | 11.7556
960 | feeder2_line29 | 2 | 354.6 | 42.4322 | 42.4422 | 11.9662 | 11.969
960 | feeder2_line29 | 3 | 354.6 | 67.6544 | 67.6371 | 19.0791 | 19.0742
960 | feeder2_line30 | 1 | 266.4 | 14.6064 | 14.6064 | 5.4829 | 5.4829
960 | feeder2_line30 | 2 | 266.4 | 3.0014 | 3.0013 | 1.1266 | 1.1266
960 | feeder2_line30 | 3 | 266.4 | 4.914 | 4.9138 | 1.8446 | 1.8445
960 | feeder2_line31 | 1 | 354.6 | 51.9317 | 51.9446 | 14.6451 | 14.6488
960 | feeder2_line31 | 2 | 354.6 | 43.388 | 43.3973 | 12.2358 | 12.2384
960 | feeder2_line31 | 3 | 354.6 | 71.3006 | 71.2826 | 20.1073 | 20.1023
960 | feeder2_line32 | 1 | 354.6 | 51.9317 | 51.9446 | 14.6451 | 14.6488
960 | feeder2_line32 | 2 | 354.6 | 43.439 | 43.4483 | 12.2502 | 12.2528
960 | feeder2_line32 | 3 | 354.6 | 71.3006 | 71.2826 | 20.1073 | 20.1023
960 | feeder2_line33 | 1 | 99 | 5.0052e-08 | 6.824e-07 | 5.0557e-08 | 6.893e-07
960 | feeder2_line33 | 2 | 99 | 0.077925 | 0.077928 | 0.078712 | 0.078715
960 | feeder2_line33 | 3 | 99 | 4.9007e-08 | 6.8733e-07 | 4.9502e-08 | 6.9427e-07
960 | feeder2_line34 | 1 | 354.6 | 51.9317 | 51.9446 | 14.6451 | 14.6488
960 | feeder2_line34 | 2 | 354.6 | 43.439 | 43.4483 | 12.2501 | 12.2528
960 | feeder2_line34 | 3 | 354.6 | 71.38 | 71.362 | 20.1297 | 20.1246
960 | feeder2_line35 | 1 | 99 | 2.9763e-07 | 7.5575e-07 | 3.0063e-07 | 7.6338e-07
960 | feeder2_line35 | 2 | 99 | 2.9657e-07 | 7.5306e-07 | 2.9957e-07 | 7.6066e-07
960 | feeder2_line35 | 3 | 99 | 0.085329 | 0.085314 | 0.086191 | 0.086175
960 | feeder2_line36 | 1 | 354.6 | 51.9567 | 51.9698 | 14.6522 | 14.6559
960 | feeder2_line36 | 2 | 354.6 | 43.439 | 43.4483 | 12.2501 | 12.2528
960 | feeder2_line36 | 3 | 354.6 | 71.38 | 71.362 | 20.1297 | 20.1246
960 | feeder2_line37 | 1 | 99 | 0.028318 | 0.028676 | 0.028604 | 0.028966
960 | feeder2_line37 | 2 | 99 | 2.9655e-07 | 8.3317e-07 | 2.9955e-07 | 8.4159e-07
960 | feeder2_line37 | 3 | 99 | 2.9953e-07 | 8.425e-07 | 3.0256e-07 | 8.5101e-07
960 | feeder2_line38 | 1 | 99 | 3.2254e-07 | 7.7139e-07 | 3.258e-07 | 7.7918e-07
960 | feeder2_line38 | 2 | 99 | 0.077952 | 0.077955 | 0.07874 | 0.078742
960 | feeder2_line38 | 3 | 99 | 3.2383e-07 | 7.7687e-07 | 3.271e-07 | 7.8472e-07
960 | feeder2_line39 | 1 | 266.4 | 14.6065 | 14.6064 | 5.4829 | 5.4829
960 | feeder2_line39 | 2 | 266.4 | 2.9286 | 2.9285 | 1.0993 | 1.0993
960 | feeder2_line39 | 3 | 266.4 | 4.914 | 4.9138 | 1.8446 | 1.8445
960 | feeder2_line40 | 1 | 354.6 | 62.7587 | 62.7722 | 17.6984 | 17.7023
960 | feeder2_line40 | 2 | 354.6 | 43.439 | 43.4483 | 12.2501 | 12.2528
960 | feeder2_line40 | 3 | 354.6 | 71.38 | 71.362 | 20.1297 | 20.1246
960 | feeder2_line41 | 1 | 99 | 12.2493 | 12.249 | 12.3731 | 12.3727
960 | feeder2_line41 | 2 | 99 | 4.9921e-08 | 7.2799e-07 | 5.0425e-08 | 7.3535e-07
960 | feeder2_line41 | 3 | 99 | 4.8971e-08 | 7.3626e-07 | 4.9466e-08 | 7.437e-07
960 | feeder2_line42 | 1 | 99 | 2.9747e-07 | 7.4446e-07 | 3.0048e-07 | 7.5198e-07
960 | feeder2_line42 | 2 | 99 | 2.9661e-07 | 7.4234e-07 | 2.9961e-07 | 7.4984e-07
960 | feeder2_line42 | 3 | 99 | 1.1853 | 1.1854 | 1.1973 | 1.1973
960 | feeder2_line43 | 1 | 266.4 | 14.6064 | 14.6064 | 5.4829 | 5.4829
960 | feeder2_line43 | 2 | 266.4 | 2.9286 | 2.9285 | 1.0993 | 1.0993
960 | feeder2_line43 | 3 | 266.4 | 4.0031 | 4.0028 | 1.5027 | 1.5026
960 | feeder2_line44 | 1 | 354.6 | 62.7587 | 62.7722 | 17.6985 | 17.7023
960 | feeder2_line44 | 2 | 354.6 | 43.439 | 43.4483 | 12.2502 | 12.2528
960 | feeder2_line44 | 3 | 354.6 | 72.9538 | 72.9357 | 20.5736 | 20.5685
960 | feeder2_line45 | 1 | 99 | 5.0065e-08 | 5.7638e-07 | 5.0571e-08 | 5.822e-07
960 | feeder2_line45 | 2 | 99 | 4.9942e-08 | 5.7408e-07 | 5.0446e-08 | 5.7988e-07
960 | feeder2_line45 | 3 | 99 | 1.7028 | 1.7027 | 1.72 | 1.7199
960 | feeder2_line46 | 1 | 99 | 5.6991e-07 | 1.3496e-06 | 5.7567e-07 | 1.3632e-06
960 | feeder2_line46 | 2 | 99 | 5.6831e-07 | 1.3457e-06 | 5.7405e-07 | 1.3593e-06
960 | feeder2_line46 | 3 | 99 | 2.2057 | 2.2056 | 2.228 | 2.2279
960 | feeder2_line47 | 1 | 266.4 | 14.6064 | 14.6064 | 5.4829 | 5.4829
960 | feeder2_line47 | 2 | 266.4 | 2.9286 | 2.9285 | 1.0993 | 1.0993
960 | feeder2_line47 | 3 | 266.4 | 1.8833 | 1.8831 | 0.70694 | 0.70688
960 | feeder2_line48 | 1 | 99 | 2.8081 | 2.808 | 2.8364 | 2.8364
960 | feeder2_line48 | 2 | 99 | 4.983e-08 | 7.2457e-07 | 5.0334e-08 | 7.3188e-07
960 | feeder2_line48 | 3 | 99 | 4.9011e-08 | 7.3189e-07 | 4.9506e-08 | 7.3929e-07
960 | feeder2_line49 | 1 | 266.4 | 12.2985 | 12.2985 | 4.6166 | 4.6165
960 | feeder2_line49 | 2 | 266.4 | 2.9286 | 2.9285 | 1.0993 | 1.0993
960 | feeder2_line49 | 3 | 266.4 | 1.8833 | 1.8831 | 0.70693 | 0.70688
960 | feeder2_line50 | 1 | 99 | 5.6985e-07 | 1.228e-06 | 5.7561e-07 | 1.2404e-06
960 | feeder2_line50 | 2 | 99 | 0.085975 | 0.08604 | 0.086844 | 0.086909
960 | feeder2_line50 | 3 | 99 | 5.7411e-07 | 1.2371e-06 | 5.7991e-07 | 1.2496e-06
960 | feeder2_line51 | 1 | 99 | 1.0701 | 1.0704 | 1.0809 | 1.0812
960 | feeder2_line51 | 2 | 99 | 5.6831e-07 | 1.3296e-06 | 5.7405e-07 | 1.343e-06
960 | feeder2_line51 | 3 | 99 | 5.7411e-07 | 1.343e-06 | 5.7991e-07 | 1.3566e-06
960 | feeder2_line52 | 1 | 266.4 | 11.2301 | 11.2299 | 4.2155 | 4.2154
960 | feeder2_line52 | 2 | 266.4 | 2.8481 | 2.8481 | 1.0691 | 1.0691
960 | feeder2_line52 | 3 | 266.4 | 1.8831 | 1.8831 | 0.70688 | 0.70688
960 | feeder2_line53 | 1 | 99 | 5.4481e-07 | 7.4949e-07 | 5.5031e-07 | 7.5706e-07
960 | feeder2_line53 | 2 | 99 | 2.8481 | 2.8481 | 2.8768 | 2.8768
960 | feeder2_line53 | 3 | 99 | 5.4961e-07 | 7.5503e-07 | 5.5516e-07 | 7.6266e-07
960 | feeder2_line54 | 1 | 266.4 | 11.23 | 11.2299 | 4.2155 | 4.2154
960 | feeder2_line54 | 2 | 266.4 | 8.4851e-05 | 4.5858e-06 | 3.1851e-05 | 1.7214e-06
960 | feeder2_line54 | 3 | 266.4 | 1.883 | 1.8831 | 0.70684 | 0.70688
960 | feeder2_line55 | 1 | 99 | 10.516 | 10.5156 | 10.6222 | 10.6218
960 | feeder2_line55 | 2 | 99 | 4.9991e-08 | 7.2306e-07 | 5.0496e-08 | 7.3037e-07
960 | feeder2_line55 | 3 | 99 | 4.8941e-08 | 7.3195e-07 | 4.9436e-08 | 7.3935e-07
960 | feeder2_line56 | 1 | 354.6 | 72.4085 | 72.4219 | 20.4198 | 20.4236
960 | feeder2_line56 | 2 | 354.6 | 43.4391 | 43.4483 | 12.2502 | 12.2528
960 | feeder2_line56 | 3 | 354.6 | 72.9539 | 72.9357 | 20.5736 | 20.5685
960 | feeder2_line57 | 1 | 99 | 7.5092e-07 | 1.5351e-06 | 7.585e-07 | 1.5506e-06
960 | feeder2_line57 | 2 | 99 | 7.4735e-07 | 1.5311e-06 | 7.549e-07 | 1.5465e-06
960 | feeder2_line57 | 3 | 99 | 1.8831 | 1.8831 | 1.9021 | 1.9021
960 | feeder2_line58 | 1 | 266.4 | 11.23 | 11.2299 | 4.2155 | 4.2154
960 | feeder2_line58 | 2 | 266.4 | 1.8758e-05 | 2.6625e-06 | 7.0413e-06 | 9.9944e-07
960 | feeder2_line58 | 3 | 266.4 | 1.8998e-05 | 2.6885e-06 | 7.1314e-06 | 1.0092e-06
960 | feeder2_line59 | 1 | 99 | 5.0059e-08 | 5.3361e-07 | 5.0565e-08 | 5.39e-07
960 | feeder2_line59 | 2 | 99 | 4.9825e-08 | 5.3221e-07 | 5.0328e-08 | 5.3759e-07
960 | feeder2_line59 | 3 | 99 | 1.2612 | 1.2612 | 1.2739 | 1.2739
960 | feeder2_line60 | 1 | 99 | 2.9742e-07 | 8.0646e-07 | 3.0042e-07 | 8.146e-07
960 | feeder2_line60 | 2 | 99 | 2.9661e-07 | 8.0433e-07 | 2.9961e-07 | 8.1246e-07
960 | feeder2_line60 | 3 | 99 | 0.81983 | 0.81986 | 0.82811 | 0.82814
960 | feeder2_line61 | 1 | 266.4 | 0.086103 | 0.086283 | 0.032321 | 0.032388
960 | feeder2_line61 | 2 | 266.4 | 0.70552 | 0.70575 | 0.26484 | 0.26492
960 | feeder2_line61 | 3 | 266.4 | 12.9316 | 12.9322 | 4.8542 | 4.8544
960 | feeder2_line62 | 1 | 354.6 | 72.4909 | 72.5046 | 20.443 | 20.4469
960 | feeder2_line62 | 2 | 354.6 | 43.8836 | 43.893 | 12.3755 | 12.3782
960 | feeder2_line62 | 3 | 354.6 | 84.9827 | 84.9652 | 23.9658 | 23.9608
960 | feeder2_line63 | 1 | 99 | 0.089733 | 0.089748 | 0.09064 | 0.090655
960 | feeder2_line63 | 2 | 99 | 5.6833e-07 | 1.2093e-06 | 5.7407e-07 | 1.2215e-06
960 | feeder2_line63 | 3 | 99 | 5.7413e-07 | 1.2216e-06 | 5.7993e-07 | 1.2339e-06
960 | feeder2_line64 | 1 | 99 | 11.1407 | 11.1405 | 11.2532 | 11.253
960 | feeder2_line64 | 2 | 99 | 5.8229e-12 | 3.1856e-07 | 5.8817e-12 | 3.2178e-07
960 | feeder2_line64 | 3 | 99 | 1.2212e-11 | 3.2178e-07 | 1.2335e-11 | 3.2503e-07
960 | feeder2_line65 | 1 | 99 | 5.0055e-08 | 6.386e-07 | 5.0561e-08 | 6.4505e-07
960 | feeder2_line65 | 2 | 99 | 1.4002 | 1.4002 | 1.4144 | 1.4144
960 | feeder2_line65 | 3 | 99 | 4.8905e-08 | 6.4344e-07 | 4.9399e-08 | 6.4994e-07
960 | feeder2_line66 | 1 | 354.6 | 72.4909 | 72.5046 | 20.443 | 20.4469
960 | feeder2_line66 | 2 | 354.6 | 43.548 | 43.5574 | 12.2809 | 12.2835
960 | feeder2_line66 | 3 | 354.6 | 84.9826 | 84.9652 | 23.9658 | 23.9608
960 | feeder2_line67 | 1 | 99 | 2.5022e-08 | 3.6087e-07 | 2.5275e-08 | 3.6451e-07
960 | feeder2_line67 | 2 | 99 | 2.5034e-08 | 3.5895e-07 | 2.5287e-08 | 3.6257e-07
960 | feeder2_line67 | 3 | 99 | 12.3926 | 12.3931 | 12.5177 | 12.5182
960 | feeder2_line68 | 1 | 266.4 | 0.086141 | 0.086283 | 0.032335 | 0.032388
960 | feeder2_line68 | 2 | 266.4 | 0.70556 | 0.70575 | 0.26485 | 0.26492
960 | feeder2_line68 | 3 | 266.4 | 0.53944 | 0.53951 | 0.20249 | 0.20252
960 | feeder2_line69 | 1 | 99 | 1.7146 | 1.7147 | 1.7319 | 1.732
960 | feeder2_line69 | 2 | 99 | 2.5121e-06 | 6.5885e-07 | 2.5375e-06 | 6.655e-07
960 | feeder2_line69 | 3 | 99 | 2.5606e-06 | 6.6811e-07 | 2.5864e-06 | 6.7486e-07
960 | feeder2_line70 | 1 | 354.6 | 74.1098 | 74.1236 | 20.8995 | 20.9034
960 | feeder2_line70 | 2 | 354.6 | 43.548 | 43.5574 | 12.2809 | 12.2835
960 | feeder2_line70 | 3 | 354.6 | 84.9825 | 84.9652 | 23.9657 | 23.9608
960 | feeder2_line71 | 1 | 99 | 5.0058e-08 | 7.1265e-07 | 5.0564e-08 | 7.1985e-07
960 | feeder2_line71 | 2 | 99 | 2.9016 | 2.9017 | 2.9309 | 2.931
960 | feeder2_line71 | 3 | 99 | 4.8881e-08 | 7.1811e-07 | 4.9374e-08 | 7.2536e-07
960 | feeder2_line72 | 1 | 354.6 | 74.1099 | 74.1236 | 20.8996 | 20.9034
960 | feeder2_line72 | 2 | 354.6 | 44.5507 | 44.5599 | 12.5637 | 12.5663
960 | feeder2_line72 | 3 | 354.6 | 84.9826 | 84.9652 | 23.9658 | 23.9608
960 | feeder2_line73 | 1 | 99 | 5.9592e-07 | 1.5278e-06 | 6.0194e-07 | 1.5432e-06
960 | feeder2_line73 | 2 | 99 | 0.078022 | 0.078026 | 0.07881 | 0.078814
960 | feeder2_line73 | 3 | 99 | 5.9964e-07 | 1.5391e-06 | 6.057e-07 | 1.5546e-06
960 | feeder2_line74 | 1 | 99 | 5.0043e-08 | 4.5567e-07 | 5.0548e-08 | 4.6028e-07
960 | feeder2_line74 | 2 | 99 | 0.53709 | 0.53713 | 0.54251 | 0.54256
960 | feeder2_line74 | 3 | 99 | 4.8939e-08 | 4.5904e-07 | 4.9433e-08 | 4.6367e-07
960 | feeder2_line75 | 1 | 266.4 | 0.086238 | 0.086283 | 0.032371 | 0.032388
960 | feeder2_line75 | 2 | 266.4 | 0.090696 | 0.09073 | 0.034045 | 0.034058
960 | feeder2_line75 | 3 | 266.4 | 0.53954 | 0.53951 | 0.20253 | 0.20252
960 | feeder2_line76 | 1 | 99 | 0.08627 | 0.086282 | 0.087141 | 0.087154
960 | feeder2_line76 | 2 | 99 | 8.3923e-07 | 1.5676e-06 | 8.4771e-07 | 1.5834e-06
960 | feeder2_line76 | 3 | 99 | 8.5052e-07 | 1.5876e-06 | 8.5911e-07 | 1.6037e-06
960 | feeder2_line77 | 1 | 99 | 2.5027e-08 | 5.7263e-07 | 2.528e-08 | 5.7842e-07
960 | feeder2_line77 | 2 | 99 | 2.5027e-08 | 5.6956e-07 | 2.528e-08 | 5.7532e-07
960 | feeder2_line77 | 3 | 99 | 0.53957 | 0.53951 | 0.54502 | 0.54496
960 | feeder2_line78 | 1 | 266.4 | 9.9337e-12 | 9.4996e-07 | 3.7288e-12 | 3.5659e-07
960 | feeder2_line78 | 2 | 266.4 | 0.090728 | 0.09073 | 0.034057 | 0.034058
960 | feeder2_line78 | 3 | 266.4 | 2.7434e-12 | 9.5602e-07 | 1.0298e-12 | 3.5887e-07
960 | feeder2_line79 | 1 | 354.6 | 3.3243 | 3.3239 | 0.93748 | 0.93736
960 | feeder2_line79 | 2 | 354.6 | 32.5765 | 32.5758 | 9.1868 | 9.1866
960 | feeder2_line79 | 3 | 354.6 | 5.5036 | 5.5029 | 1.5521 | 1.5519
960 | feeder2_line80 | 1 | 354.6 | 77.2576 | 77.2708 | 21.7873 | 21.791
960 | feeder2_line80 | 2 | 354.6 | 68.1647 | 68.1706 | 19.223 | 19.2247
960 | feeder2_line80 | 3 | 354.6 | 89.4827 | 89.4644 | 25.2348 | 25.2297
960 | feeder2_line81 | 1 | 354.6 | 77.2575 | 77.2708 | 21.7872 | 21.791
960 | feeder2_line81 | 2 | 354.6 | 68.1646 | 68.1706 | 19.223 | 19.2247
960 | feeder2_line81 | 3 | 354.6 | 90.0036 | 89.9853 | 25.3817 | 25.3766
960 | feeder2_line82 | 1 | 354.6 | 6.6409e-12 | 7.3138e-07 | 1.8728e-12 | 2.0626e-07
960 | feeder2_line82 | 2 | 354.6 | 2.7902e-11 | 7.2615e-07 | 7.8685e-12 | 2.0478e-07
960 | feeder2_line82 | 3 | 354.6 | 0.539 | 0.53899 | 0.152 | 0.152
960 | feeder2_line83 | 1 | 354.6 | 77.2577 | 77.2708 | 21.7873 | 21.791
960 | feeder2_line83 | 2 | 354.6 | 68.4326 | 68.4385 | 19.2985 | 19.3002
960 | feeder2_line83 | 3 | 354.6 | 90.0037 | 89.9853 | 25.3818 | 25.3766
960 | feeder2_line84 | 1 | 354.6 | 3.1511e-12 | 1.2927e-06 | 8.8865e-13 | 3.6455e-07
960 | feeder2_line84 | 2 | 354.6 | 0.97226 | 0.97226 | 0.27418 | 0.27418
960 | feeder2_line84 | 3 | 354.6 | 2.887e-12 | 1.3019e-06 | 8.1416e-13 | 3.6713e-07
960 | feeder2_line85 | 1 | 99 | 0.0775 | 0.077515 | 0.078283 | 0.078298
960 | feeder2_line85 | 2 | 99 | 5.0286e-08 | 4.5787e-07 | 5.0794e-08 | 4.625e-07
960 | feeder2_line85 | 3 | 99 | 4.8846e-08 | 4.6498e-07 | 4.934e-08 | 4.6967e-07
960 | feeder2_line86 | 1 | 354.6 | 77.3328 | 77.3458 | 21.8085 | 21.8121
960 | feeder2_line86 | 2 | 354.6 | 68.4327 | 68.4385 | 19.2986 | 19.3002
960 | feeder2_line86 | 3 | 354.6 | 90.0039 | 89.9853 | 25.3818 | 25.3766
960 | feeder2_line87 | 1 | 354.6 | 77.3329 | 77.3458 | 21.8085 | 21.8121
960 | feeder2_line87 | 2 | 354.6 | 81.2487 | 81.2538 | 22.9128 | 22.9142
960 | feeder2_line87 | 3 | 354.6 | 94.7195 | 94.7009 | 26.7117 | 26.7064
960 | feeder2_line88 | 1 | 354.6 | 0.00011092 | 3.3504e-06 | 3.128e-05 | 9.4483e-07
960 | feeder2_line88 | 2 | 354.6 | 14.2361 | 14.2361 | 4.0147 | 4.0147
960 | feeder2_line88 | 3 | 354.6 | 5.3564 | 5.3564 | 1.5105 | 1.5105
960 | feeder2_line89 | 1 | 354.6 | 77.3307 | 77.3458 | 21.8079 | 21.8121
960 | feeder2_line89 | 2 | 354.6 | 83.4772 | 83.4844 | 23.5412 | 23.5433
960 | feeder2_line89 | 3 | 354.6 | 94.7172 | 94.7009 | 26.711 | 26.7064
960 | feeder2_line90 | 1 | 354.6 | 0.00071906 | 2.0212e-06 | 0.00020278 | 5.6999e-07
960 | feeder2_line90 | 2 | 354.6 | 2.6554 | 2.6558 | 0.74884 | 0.74896
960 | feeder2_line90 | 3 | 354.6 | 0.000731 | 2.0384e-06 | 0.00020615 | 5.7483e-07
960 | feeder2_line91 | 1 | 354.6 | 77.3307 | 77.3458 | 21.8079 | 21.8121
960 | feeder2_line91 | 2 | 354.6 | 83.4771 | 83.4844 | 23.5412 | 23.5433
960 | feeder2_line91 | 3 | 354.6 | 95.0313 | 95.015 | 26.7996 | 26.795
960 | feeder2_line92 | 1 | 354.6 | 2.3454e-11 | 1.0204e-06 | 6.6143e-12 | 2.8776e-07
960 | feeder2_line92 | 2 | 354.6 | 2.3454e-11 | 1.013e-06 | 6.6143e-12 | 2.8568e-07
960 | feeder2_line92 | 3 | 354.6 | 0.8214 | 0.82144 | 0.23164 | 0.23165
960 | feeder2_line93 | 1 | 99 | 2.5061e-08 | 3.4055e-07 | 2.5314e-08 | 3.4398e-07
960 | feeder2_line93 | 2 | 99 | 0.97234 | 0.97234 | 0.98216 | 0.98216
960 | feeder2_line93 | 3 | 99 | 2.4423e-08 | 3.4335e-07 | 2.4669e-08 | 3.4681e-07
960 | feeder2_line94 | 1 | 354.6 | 2.5066e-06 | 1.6583e-06 | 7.0689e-07 | 4.6765e-07
960 | feeder2_line94 | 2 | 354.6 | 1.9473 | 1.9474 | 0.54916 | 0.54918
960 | feeder2_line94 | 3 | 354.6 | 2.4421e-06 | 1.6705e-06 | 6.887e-07 | 4.711e-07
960 | feeder2_line95 | 1 | 99 | 3.5565e-06 | 2.598e-06 | 3.5924e-06 | 2.6242e-06
960 | feeder2_line95 | 2 | 99 | 14.236 | 14.2361 | 14.3798 | 14.3799
960 | feeder2_line95 | 3 | 99 | 3.5866e-06 | 2.6188e-06 | 3.6228e-06 | 2.6452e-06
960 | feeder2_line96 | 1 | 354.6 | 0.00012049 | 6.1943e-07 | 3.3979e-05 | 1.7468e-07
960 | feeder2_line96 | 2 | 354.6 | 0.0001196 | 6.149e-07 | 3.3728e-05 | 1.7341e-07
960 | feeder2_line96 | 3 | 354.6 | 5.3564 | 5.3564 | 1.5105 | 1.5105
960 | feeder2_line97 | 1 | 354.6 | 79.5626 | 79.5777 | 22.4373 | 22.4415
960 | feeder2_line97 | 2 | 354.6 | 83.4773 | 83.4844 | 23.5413 | 23.5433
960 | feeder2_line97 | 3 | 354.6 | 95.0316 | 95.015 | 26.7997 | 26.795
960 | feeder2_line98 | 1 | 354.6 | 2.3517 | 2.3501 | 0.66321 | 0.66276
960 | feeder2_line98 | 2 | 354.6 | 0.0016825 | 6.1508e-07 | 0.00047449 | 1.7346e-07
960 | feeder2_line98 | 3 | 354.6 | 0.0017266 | 6.2494e-07 | 0.00048691 | 1.7624e-07
960 | feeder2_line99 | 1 | 99 | 2.5051e-08 | 4.4523e-07 | 2.5304e-08 | 4.4973e-07
960 | feeder2_line99 | 2 | 99 | 2.5148e-08 | 4.4186e-07 | 2.5402e-08 | 4.4632e-07
960 | feeder2_line99 | 3 | 99 | 5.3563 | 5.3564 | 5.4104 | 5.4105
960 | feeder2_line100 | 1 | 99 | 2.3501 | 2.3501 | 2.3738 | 2.3739
960 | feeder2_line100 | 2 | 99 | 2.517e-08 | 6.0676e-07 | 2.5424e-08 | 6.1289e-07
960 | feeder2_line100 | 3 | 99 | 2.4422e-08 | 6.1647e-07 | 2.4669e-08 | 6.2269e-07
960 | feeder2_line101 | 1 | 354.6 | 1.9555 | 1.9551 | 0.55148 | 0.55136
960 | feeder2_line101 | 2 | 354.6 | 32.5764 | 32.5758 | 9.1868 | 9.1866
960 | feeder2_line101 | 3 | 354.6 | 5.5036 | 5.5029 | 1.5521 | 1.5519
960 | feeder2_line102 | 1 | 99 | 1.3691 | 1.3691 | 1.3829 | 1.3829
960 | feeder2_line102 | 2 | 99 | 2.3024e-06 | 8.6744e-07 | 2.3257e-06 | 8.762e-07
960 | feeder2_line102 | 3 | 99 | 2.3585e-06 | 8.81e-07 | 2.3823e-06 | 8.899e-07
960 | feeder2_line103 | 1 | 99 | 5.4671e-07 | 8.0031e-07 | 5.5224e-07 | 8.0839e-07
960 | feeder2_line103 | 2 | 99 | 1.2832 | 1.2832 | 1.2962 | 1.2962
960 | feeder2_line103 | 3 | 99 | 5.5172e-07 | 8.0638e-07 | 5.5729e-07 | 8.1452e-07
960 | feeder2_line104 | 1 | 354.6 | 1.9554 | 1.9551 | 0.55145 | 0.55136
960 | feeder2_line104 | 2 | 354.6 | 31.3097 | 31.3091 | 8.8296 | 8.8294
960 | feeder2_line104 | 3 | 354.6 | 5.5035 | 5.5029 | 1.552 | 1.5519
960 | feeder2_line105 | 1 | 99 | 2.5337e-06 | 7.3641e-07 | 2.5593e-06 | 7.4385e-07
960 | feeder2_line105 | 2 | 99 | 2.5081e-06 | 7.3034e-07 | 2.5335e-06 | 7.3772e-07
960 | feeder2_line105 | 3 | 99 | 0.039798 | 0.039687 | 0.0402 | 0.040088
960 | feeder2_line106 | 1 | 354.6 | 1.9554 | 1.9551 | 0.55143 | 0.55136
960 | feeder2_line106 | 2 | 354.6 | 31.3096 | 31.3091 | 8.8296 | 8.8294
960 | feeder2_line106 | 3 | 354.6 | 5.4657 | 5.4653 | 1.5414 | 1.5413
960 | feeder2_line107 | 1 | 99 | 3.2337e-07 | 8.9748e-07 | 3.2664e-07 | 9.0655e-07
960 | feeder2_line107 | 2 | 99 | 11.5187 | 11.5186 | 11.635 | 11.6349
960 | feeder2_line107 | 3 | 99 | 3.2464e-07 | 9.0418e-07 | 3.2792e-07 | 9.1331e-07
960 | feeder2_line108 | 1 | 354.6 | 1.9554 | 1.9551 | 0.55143 | 0.55136
960 | feeder2_line108 | 2 | 354.6 | 19.9743 | 19.9739 | 5.6329 | 5.6328
960 | feeder2_line108 | 3 | 354.6 | 5.4657 | 5.4653 | 1.5414 | 1.5413
960 | feeder2_line109 | 1 | 354.6 | 81.851 | 81.8651 | 23.0826 | 23.0866
960 | feeder2_line109 | 2 | 354.6 | 83.4784 | 83.4844 | 23.5416 | 23.5433
960 | feeder2_line109 | 3 | 354.6 | 95.0327 | 95.015 | 26.8 | 26.795
960 | feeder2_line110 | 1 | 99 | 2.6643 | 2.6635 | 2.6912 | 2.6904
960 | feeder2_line110 | 2 | 99 | 0.00079226 | 8.9966e-07 | 0.00080027 | 9.0875e-07
960 | feeder2_line110 | 3 | 99 | 0.00081129 | 9.1242e-07 | 0.00081949 | 9.2163e-07
960 | feeder2_line111 | 1 | 99 | 2.5043e-08 | 3.8024e-07 | 2.5296e-08 | 3.8409e-07
960 | feeder2_line111 | 2 | 99 | 2.2599 | 2.2599 | 2.2827 | 2.2827
960 | feeder2_line111 | 3 | 99 | 2.4411e-08 | 3.8329e-07 | 2.4658e-08 | 3.8717e-07
960 | feeder2_line112 | 1 | 99 | 3.2349e-07 | 9.1375e-07 | 3.2676e-07 | 9.2298e-07
960 | feeder2_line112 | 2 | 99 | 12.2368 | 12.2368 | 12.3604 | 12.3604
960 | feeder2_line112 | 3 | 99 | 3.2488e-07 | 9.2106e-07 | 3.2816e-07 | 9.3036e-07
960 | feeder2_line113 | 1 | 99 | 0.09791 | 0.097923 | 0.098899 | 0.098912
960 | feeder2_line113 | 2 | 99 | 3.2176e-07 | 8.9482e-07 | 3.2501e-07 | 9.0386e-07
960 | feeder2_line113 | 3 | 99 | 3.2527e-07 | 9.0924e-07 | 3.2855e-07 | 9.1842e-07
960 | feeder2_line114 | 1 | 99 | 1.2872 | 1.2871 | 1.3002 | 1.3001
960 | feeder2_line114 | 2 | 99 | 2.5143e-08 | 4.3135e-07 | 2.5397e-08 | 4.3571e-07
960 | feeder2_line114 | 3 | 99 | 2.4414e-08 | 4.3808e-07 | 2.466e-08 | 4.4251e-07
960 | feeder2_line115 | 1 | 99 | 2.4994e-08 | 5.601e-07 | 2.5246e-08 | 5.6576e-07
960 | feeder2_line115 | 2 | 99 | 17.8938 | 17.8936 | 18.0746 | 18.0744
960 | feeder2_line115 | 3 | 99 | 2.4391e-08 | 5.6424e-07 | 2.4637e-08 | 5.6994e-07
960 | feeder2_line116 | 1 | 354.6 | 1.9554 | 1.9551 | 0.55143 | 0.55136
960 | feeder2_line116 | 2 | 354.6 | 2.1261 | 2.1259 | 0.59958 | 0.59952
960 | feeder2_line116 | 3 | 354.6 | 5.4657 | 5.4653 | 1.5414 | 1.5413
960 | feeder2_line117 | 1 | 99 | 5.0214e-08 | 6.401e-07 | 5.0721e-08 | 6.4657e-07
960 | feeder2_line117 | 2 | 99 | 2.2169 | 2.217 | 2.2393 | 2.2394
960 | feeder2_line117 | 3 | 99 | 4.8851e-08 | 6.4572e-07 | 4.9344e-08 | 6.5224e-07
960 | feeder2_line118 | 1 | 354.6 | 81.851 | 81.8651 | 23.0826 | 23.0866
960 | feeder2_line118 | 2 | 354.6 | 85.6302 | 85.6362 | 24.1484 | 24.1501
960 | feeder2_line118 | 3 | 354.6 | 95.0327 | 95.015 | 26.8 | 26.795
960 | feeder2_line119 | 1 | 99 | 2.4998e-08 | 6.027e-07 | 2.5251e-08 | 6.0879e-07
960 | feeder2_line119 | 2 | 99 | 2.5164e-08 | 5.9736e-07 | 2.5419e-08 | 6.034e-07
960 | feeder2_line119 | 3 | 99 | 1.4139 | 1.4139 | 1.4282 | 1.4282
960 | feeder2_line120 | 1 | 354.6 | 1.9554 | 1.9551 | 0.55143 | 0.55136
960 | feeder2_line120 | 2 | 354.6 | 2.1261 | 2.1259 | 0.59958 | 0.59952
960 | feeder2_line120 | 3 | 354.6 | 4.3962 | 4.3959 | 1.2398 | 1.2397
960 | feeder2_line121 | 1 | 99 | 3.2338e-07 | 9.3329e-07 | 3.2665e-07 | 9.4272e-07
960 | feeder2_line121 | 2 | 99 | 1.0455 | 1.0455 | 1.0561 | 1.0561
960 | feeder2_line121 | 3 | 99 | 3.2461e-07 | 9.4007e-07 | 3.2789e-07 | 9.4957e-07
960 | feeder2_line122 | 1 | 354.6 | 1.9554 | 1.9551 | 0.55143 | 0.55136
960 | feeder2_line122 | 2 | 354.6 | 1.4707 | 1.4706 | 0.41474 | 0.41471
960 | feeder2_line122 | 3 | 354.6 | 4.3962 | 4.3959 | 1.2398 | 1.2397
960 | feeder2_line123 | 1 | 99 | 5.7181e-07 | 9.6711e-07 | 5.7759e-07 | 9.7688e-07
960 | feeder2_line123 | 2 | 99 | 5.6672e-07 | 9.5854e-07 | 5.7244e-07 | 9.6823e-07
960 | feeder2_line123 | 3 | 99 | 0.75751 | 0.75754 | 0.76516 | 0.76519
960 | feeder2_line124 | 1 | 354.6 | 1.9553 | 1.9551 | 0.5514 | 0.55136
960 | feeder2_line124 | 2 | 354.6 | 1.4707 | 1.4706 | 0.41476 | 0.41471
960 | feeder2_line124 | 3 | 354.6 | 3.8943 | 3.894 | 1.0982 | 1.0981
960 | feeder2_line125 | 1 | 99 | 5.7181e-07 | 8.9902e-07 | 5.7758e-07 | 9.081e-07
960 | feeder2_line125 | 2 | 99 | 5.6672e-07 | 8.9107e-07 | 5.7244e-07 | 9.0007e-07
960 | feeder2_line125 | 3 | 99 | 2.3456 | 2.3455 | 2.3693 | 2.3692
960 | feeder2_line126 | 1 | 354.6 | 1.9554 | 1.9551 | 0.55145 | 0.55136
960 | feeder2_line126 | 2 | 354.6 | 1.4708 | 1.4706 | 0.41479 | 0.41471
960 | feeder2_line126 | 3 | 354.6 | 1.5494 | 1.5491 | 0.43694 | 0.43685
960 | feeder2_line127 | 1 | 99 | 5.7181e-07 | 1.0763e-06 | 5.7758e-07 | 1.0871e-06
960 | feeder2_line127 | 2 | 99 | 5.6672e-07 | 1.0668e-06 | 5.7244e-07 | 1.0775e-06
960 | feeder2_line127 | 3 | 99 | 0.076654 | 0.076636 | 0.077428 | 0.07741
960 | feeder2_line128 | 1 | 354.6 | 1.9554 | 1.9551 | 0.55143 | 0.55136
960 | feeder2_line128 | 2 | 354.6 | 1.4708 | 1.4706 | 0.41479 | 0.41471
960 | feeder2_line128 | 3 | 354.6 | 1.4727 | 1.4725 | 0.41531 | 0.41525
960 | feeder2_line129 | 1 | 99 | 5.4682e-07 | 8.7269e-07 | 5.5234e-07 | 8.8151e-07
960 | feeder2_line129 | 2 | 99 | 1.4706 | 1.4706 | 1.4854 | 1.4854
960 | feeder2_line129 | 3 | 99 | 5.516e-07 | 8.79e-07 | 5.5717e-07 | 8.8788e-07
960 | feeder2_line130 | 1 | 354.6 | 1.9554 | 1.9551 | 0.55143 | 0.55136
960 | feeder2_line130 | 2 | 354.6 | 0.00030409 | 4.5789e-06 | 8.5756e-05 | 1.2913e-06
960 | feeder2_line130 | 3 | 354.6 | 1.4727 | 1.4725 | 0.41532 | 0.41525
960 | feeder2_line131 | 1 | 99 | 5.718e-07 | 9.6724e-07 | 5.7757e-07 | 9.7701e-07
960 | feeder2_line131 | 2 | 99 | 5.6672e-07 | 9.587e-07 | 5.7244e-07 | 9.6838e-07
960 | feeder2_line131 | 3 | 99 | 1.3959 | 1.3959 | 1.41 | 1.41
960 | feeder2_line132 | 1 | 354.6 | 1.9552 | 1.9551 | 0.55138 | 0.55136
960 | feeder2_line132 | 2 | 354.6 | 0.00012373 | 2.8789e-06 | 3.4893e-05 | 8.1186e-07
960 | feeder2_line132 | 3 | 354.6 | 0.076725 | 0.076637 | 0.021637 | 0.021612
960 | feeder2_line133 | 1 | 99 | 1.9551 | 1.9551 | 1.9749 | 1.9749
960 | feeder2_line133 | 2 | 99 | 2.9594e-07 | 9.6635e-07 | 2.9893e-07 | 9.7611e-07
960 | feeder2_line133 | 3 | 99 | 3.002e-07 | 9.82e-07 | 3.0323e-07 | 9.9192e-07
960 | feeder2_line134 | 1 | 354.6 | 1.2765e-11 | 1.7782e-06 | 3.5998e-12 | 5.0146e-07
960 | feeder2_line134 | 2 | 354.6 | 1.031e-11 | 1.7632e-06 | 2.9076e-12 | 4.9723e-07
960 | feeder2_line134 | 3 | 354.6 | 0.076655 | 0.076637 | 0.021617 | 0.021612
960 | feeder2_line135 | 1 | 99 | 2.8943 | 2.8944 | 2.9235 | 2.9236
960 | feeder2_line135 | 2 | 99 | 5.0394e-08 | 5.7912e-07 | 5.0903e-08 | 5.8496e-07
960 | feeder2_line135 | 3 | 99 | 4.8857e-08 | 5.8864e-07 | 4.9351e-08 | 5.9459e-07
960 | feeder2_line136 | 1 | 354.6 | 84.1323 | 84.1466 | 23.726 | 23.73
960 | feeder2_line136 | 2 | 354.6 | 85.6302 | 85.6362 | 24.1484 | 24.1501
960 | feeder2_line136 | 3 | 354.6 | 95.0327 | 95.015 | 26.8 | 26.795
960 | feeder2_line137 | 1 | 99 | 1.2508 | 1.2508 | 1.2634 | 1.2634
960 | feeder2_line137 | 2 | 99 | 8.4017e-07 | 1.5599e-06 | 8.4865e-07 | 1.5756e-06
960 | feeder2_line137 | 3 | 99 | 8.5476e-07 | 1.5856e-06 | 8.6339e-07 | 1.6016e-06
960 | feeder2_line138 | 1 | 354.6 | 85.3393 | 85.3535 | 24.0663 | 24.0704
960 | feeder2_line138 | 2 | 354.6 | 85.6302 | 85.6362 | 24.1484 | 24.1501
960 | feeder2_line138 | 3 | 354.6 | 95.0328 | 95.015 | 26.8 | 26.795
960 | feeder2_line139 | 1 | 99 | 5.0263e-08 | 4.8964e-07 | 5.0771e-08 | 4.9458e-07
960 | feeder2_line139 | 2 | 99 | 5.0411e-08 | 4.8606e-07 | 5.0921e-08 | 4.9097e-07
960 | feeder2_line139 | 3 | 99 | 2.1323 | 2.1316 | 2.1538 | 2.1531
960 | feeder2_line140 | 1 | 354.6 | 85.3393 | 85.3535 | 24.0664 | 24.0704
960 | feeder2_line140 | 2 | 354.6 | 85.6303 | 85.6362 | 24.1484 | 24.1501
960 | feeder2_line140 | 3 | 354.6 | 96.593 | 96.574 | 27.24 | 27.2346
960 | feeder2_line141 | 1 | 99 | 2.5125e-06 | 4.8439e-07 | 2.5379e-06 | 4.8928e-07
960 | feeder2_line141 | 2 | 99 | 1.1799 | 1.1799 | 1.1919 | 1.1918
960 | feeder2_line141 | 3 | 99 | 2.5489e-06 | 4.8882e-07 | 2.5746e-06 | 4.9376e-07
960 | feeder2_line142 | 1 | 354.6 | 85.3392 | 85.3535 | 24.0663 | 24.0704
960 | feeder2_line142 | 2 | 354.6 | 86.0635 | 86.0695 | 24.2706 | 24.2723
960 | feeder2_line142 | 3 | 354.6 | 96.5929 | 96.574 | 27.24 | 27.2346
960 | feeder2_line143 | 1 | 99 | 8.4675e-07 | 1.7212e-06 | 8.553e-07 | 1.7386e-06
960 | feeder2_line143 | 2 | 99 | 11.5463 | 11.5462 | 11.663 | 11.6629
960 | feeder2_line143 | 3 | 99 | 8.5509e-07 | 1.737e-06 | 8.6373e-07 | 1.7546e-06
960 | feeder2_line144 | 1 | 354.6 | 85.339 | 85.3535 | 24.0663 | 24.0704
960 | feeder2_line144 | 2 | 354.6 | 97.14 | 97.1457 | 27.3942 | 27.3958
960 | feeder2_line144 | 3 | 354.6 | 96.5927 | 96.574 | 27.2399 | 27.2346
960 | feeder2_line145 | 1 | 99 | 2.5142e-08 | 4.8266e-07 | 2.5396e-08 | 4.8754e-07
960 | feeder2_line145 | 2 | 99 | 0.53557 | 0.53558 | 0.54098 | 0.54099
960 | feeder2_line145 | 3 | 99 | 2.4436e-08 | 4.871e-07 | 2.4683e-08 | 4.9202e-07
960 | feeder2_line146 | 1 | 354.6 | 85.3389 | 85.3535 | 24.0662 | 24.0704
960 | feeder2_line146 | 2 | 354.6 | 97.6641 | 97.6699 | 27.542 | 27.5437
960 | feeder2_line146 | 3 | 354.6 | 96.5926 | 96.574 | 27.2399 | 27.2346
960 | feeder2_line147 | 1 | 99 | 2.5683 | 2.5683 | 2.5943 | 2.5943
960 | feeder2_line147 | 2 | 99 | 1.1376e-06 | 2.2101e-06 | 1.149e-06 | 2.2324e-06
960 | feeder2_line147 | 3 | 99 | 1.1566e-06 | 2.2468e-06 | 1.1683e-06 | 2.2695e-06
960 | feeder2_line148 | 1 | 99 | 0.085329 | 0.08535 | 0.086191 | 0.086212
960 | feeder2_line148 | 2 | 99 | 5.9399e-07 | 1.4809e-06 | 5.9999e-07 | 1.4959e-06
960 | feeder2_line148 | 3 | 99 | 6.0277e-07 | 1.5056e-06 | 6.0886e-07 | 1.5208e-06
960 | feeder2_line149 | 1 | 354.6 | 87.6715 | 87.6861 | 24.7241 | 24.7282
960 | feeder2_line149 | 2 | 354.6 | 97.6642 | 97.6699 | 27.5421 | 27.5437
960 | feeder2_line149 | 3 | 354.6 | 96.5927 | 96.574 | 27.2399 | 27.2346
960 | feeder2_line150 | 1 | 354.6 | 87.6716 | 87.6861 | 24.7241 | 24.7282
960 | feeder2_line150 | 2 | 354.6 | 99.0001 | 99.0056 | 27.9188 | 27.9204
960 | feeder2_line150 | 3 | 354.6 | 96.5928 | 96.574 | 27.2399 | 27.2346
960 | feeder2_line151 | 1 | 99 | 9.6977e-06 | 1.772e-06 | 9.7957e-06 | 1.7899e-06
960 | feeder2_line151 | 2 | 99 | 1.375 | 1.375 | 1.3889 | 1.3889
960 | feeder2_line151 | 3 | 99 | 9.8646e-06 | 1.7885e-06 | 9.9642e-06 | 1.8066e-06
960 | feeder2_line152 | 1 | 354.6 | 4.4914e-12 | 1.1812e-06 | 1.2666e-12 | 3.3312e-07
960 | feeder2_line152 | 2 | 354.6 | 2.0386e-11 | 1.1732e-06 | 5.7491e-12 | 3.3086e-07
960 | feeder2_line152 | 3 | 354.6 | 0.076198 | 0.076186 | 0.021489 | 0.021485
960 | feeder2_line153 | 1 | 99 | 1.0468 | 1.0468 | 1.0573 | 1.0573
960 | feeder2_line153 | 2 | 99 | 5.0449e-08 | 5.8672e-07 | 5.0959e-08 | 5.9264e-07
960 | feeder2_line153 | 3 | 99 | 4.891e-08 | 5.9645e-07 | 4.9404e-08 | 6.0247e-07
960 | feeder2_line154 | 1 | 99 | 5.7331e-07 | 8.7922e-07 | 5.791e-07 | 8.881e-07
960 | feeder2_line154 | 2 | 99 | 5.6928e-07 | 8.7306e-07 | 5.7503e-07 | 8.8188e-07
960 | feeder2_line154 | 3 | 99 | 0.040398 | 0.040276 | 0.040806 | 0.040683
960 | feeder2_line155 | 1 | 99 | 88.7178 | 88.7324 | 89.6139 | 89.6286
960 | feeder2_line155 | 2 | 99 | 99 | 99.0056 | 100 | 100.0056
960 | feeder2_line155 | 3 | 99 | 96.7073 | 96.6884 | 97.6842 | 97.6651
960 | feeder2_line156 | 1 | 99 | 5.983e-07 | 1.1571e-06 | 6.0434e-07 | 1.1687e-06
960 | feeder2_line156 | 2 | 99 | 1.2846 | 1.2846 | 1.2975 | 1.2975
960 | feeder2_line156 | 3 | 99 | 6.0304e-07 | 1.1679e-06 | 6.0913e-07 | 1.1797e-06
960 | feeder2_line157 | 1 | 99 | 2.5156e-08 | 2.5121e-07 | 2.541e-08 | 2.5375e-07
960 | feeder2_line157 | 2 | 99 | 0.090631 | 0.090634 | 0.091547 | 0.091549
960 | feeder2_line157 | 3 | 99 | 2.4446e-08 | 2.5354e-07 | 2.4693e-08 | 2.5611e-07
990 | feeder2_line1 | 1 | 354.6 | 26.4391 | 26.4398 | 7.456 | 7.4562
990 | feeder2_line1 | 2 | 354.6 | 56.827 | 56.8328 | 16.0257 | 16.0273
990 | feeder2_line1 | 3 | 354.6 | 57.1802 | 57.1753 | 16.1253 | 16.1239
990 | feeder2_line2 | 1 | 354.6 | 26.4059 | 26.4066 | 7.4467 | 7.4469
990 | feeder2_line2 | 2 | 354.6 | 56.8271 | 56.8328 | 16.0257 | 16.0273
990 | feeder2_line2 | 3 | 354.6 | 57.1804 | 57.1753 | 16.1253 | 16.1239
990 | feeder2_line3 | 1 | 80.1 | 2.0861 | 2.0861 | 2.6044 | 2.6044
990 | feeder2_line3 | 2 | 80.1 | 5.715e-07 | 1.0561e-06 | 7.1348e-07 | 1.3185e-06
990 | feeder2_line3 | 3 | 80.1 | 5.7136e-07 | 1.0559e-06 | 7.1331e-07 | 1.3182e-06
990 | feeder2_line4 | 1 | 354.6 | 26.4059 | 26.4066 | 7.4467 | 7.4469
990 | feeder2_line4 | 2 | 354.6 | 56.91 | 56.9155 | 16.0491 | 16.0506
990 | feeder2_line4 | 3 | 354.6 | 57.1805 | 57.1753 | 16.1254 | 16.1239
990 | feeder2_line5 | 1 | 80.1 | 5.6984e-07 | 9.9434e-07 | 7.1141e-07 | 1.2414e-06
990 | feeder2_line5 | 2 | 80.1 | 0.09007 | 0.090072 | 0.11245 | 0.11245
990 | feeder2_line5 | 3 | 80.1 | 5.7139e-07 | 9.9703e-07 | 7.1335e-07 | 1.2447e-06
990 | feeder2_line6 | 1 | 80.1 | 5.698e-07 | 1.1696e-06 | 7.1136e-07 | 1.4602e-06
990 | feeder2_line6 | 2 | 80.1 | 5.7157e-07 | 1.1732e-06 | 7.1357e-07 | 1.4647e-06
990 | feeder2_line6 | 3 | 80.1 | 2.5709 | 2.5708 | 3.2096 | 3.2095
990 | feeder2_line7 | 1 | 354.6 | 26.406 | 26.4066 | 7.4467 | 7.4469
990 | feeder2_line7 | 2 | 354.6 | 56.9101 | 56.9155 | 16.0491 | 16.0506
990 | feeder2_line7 | 3 | 354.6 | 58.0303 | 58.0249 | 16.365 | 16.3635
990 | feeder2_line8 | 1 | 80.1 | 1.3009 | 1.3009 | 1.6241 | 1.6241
990 | feeder2_line8 | 2 | 80.1 | 5.7173e-07 | 1.1316e-06 | 7.1377e-07 | 1.4127e-06
990 | feeder2_line8 | 3 | 80.1 | 5.7156e-07 | 1.1312e-06 | 7.1355e-07 | 1.4123e-06
990 | feeder2_line9 | 1 | 354.6 | 27.11 | 27.1107 | 7.6452 | 7.6454
990 | feeder2_line9 | 2 | 354.6 | 56.9101 | 56.9155 | 16.0491 | 16.0506
990 | feeder2_line9 | 3 | 354.6 | 58.0303 | 58.0249 | 16.365 | 16.3635
990 | feeder2_line10 | 1 | 80.1 | 8.4203e-07 | 1.4888e-06 | 1.0512e-06 | 1.8587e-06
990 | feeder2_line10 | 2 | 80.1 | 1.2985 | 1.2985 | 1.6211 | 1.6211
990 | feeder2_line10 | 3 | 80.1 | 8.4494e-07 | 1.4937e-06 | 1.0549e-06 | 1.8648e-06
990 | feeder2_line11 | 1 | 354.6 | 27.11 | 27.1107 | 7.6452 | 7.6454
990 | feeder2_line11 | 2 | 354.6 | 58.0791 | 58.0845 | 16.3788 | 16.3803
990 | feeder2_line11 | 3 | 354.6 | 58.0303 | 58.0249 | 16.365 | 16.3635
990 | feeder2_line12 | 1 | 80.1 | 5.4466e-07 | 9.8749e-07 | 6.7998e-07 | 1.2328e-06
990 | feeder2_line12 | 2 | 80.1 | 5.4715e-07 | 9.9122e-07 | 6.8308e-07 | 1.2375e-06
990 | feeder2_line12 | 3 | 80.1 | 1.9105 | 1.9105 | 2.3852 | 2.3852
990 | feeder2_line13 | 1 | 354.6 | 27.1101 | 27.1107 | 7.6453 | 7.6454
990 | feeder2_line13 | 2 | 354.6 | 58.0791 | 58.0845 | 16.3788 | 16.3803
990 | feeder2_line13 | 3 | 354.6 | 58.5519 | 58.5463 | 16.5121 | 16.5105
990 | feeder2_line14 | 1 | 80.1 | 1.4723 | 1.4722 | 1.838 | 1.838
990 | feeder2_line14 | 2 | 80.1 | 2.9827e-07 | 6.4642e-07 | 3.7237e-07 | 8.0701e-07
990 | feeder2_line14 | 3 | 80.1 | 2.9825e-07 | 6.4621e-07 | 3.7235e-07 | 8.0675e-07
990 | feeder2_line15 | 1 | 354.6 | 26.6435 | 26.6443 | 7.5137 | 7.5139
990 | feeder2_line15 | 2 | 354.6 | 58.0791 | 58.0845 | 16.3788 | 16.3803
990 | feeder2_line15 | 3 | 354.6 | 58.5519 | 58.5463 | 16.5121 | 16.5105
990 | feeder2_line16 | 1 | 80.1 | 5.6954e-07 | 1.0261e-06 | 7.1104e-07 | 1.281e-06
990 | feeder2_line16 | 2 | 80.1 | 1.2409 | 1.2409 | 1.5492 | 1.5492
990 | feeder2_line16 | 3 | 80.1 | 5.7174e-07 | 1.03e-06 | 7.1379e-07 | 1.2859e-06
990 | feeder2_line17 | 1 | 354.6 | 26.6435 | 26.6443 | 7.5137 | 7.5139
990 | feeder2_line17 | 2 | 354.6 | 59.1818 | 59.1872 | 16.6897 | 16.6912
990 | feeder2_line17 | 3 | 354.6 | 58.5519 | 58.5463 | 16.5121 | 16.5105
990 | feeder2_line18 | 1 | 80.1 | 5.4426e-07 | 7.3418e-07 | 6.7948e-07 | 9.1658e-07
990 | feeder2_line18 | 2 | 80.1 | 5.4773e-07 | 7.3806e-07 | 6.8381e-07 | 9.2143e-07
990 | feeder2_line18 | 3 | 80.1 | 0.15298 | 0.15297 | 0.19099 | 0.19098
990 | feeder2_line19 | 1 | 354.6 | 26.6436 | 26.6443 | 7.5137 | 7.5139
990 | feeder2_line19 | 2 | 354.6 | 59.1818 | 59.1872 | 16.6897 | 16.6912
990 | feeder2_line19 | 3 | 354.6 | 58.6871 | 58.6815 | 16.5502 | 16.5487
990 | feeder2_line20 | 1 | 99 | 5.4415e-07 | 8.801e-07 | 5.4965e-07 | 8.8899e-07
990 | feeder2_line20 | 2 | 99 | 5.4789e-07 | 8.8513e-07 | 5.5342e-07 | 8.9407e-07
990 | feeder2_line20 | 3 | 99 | 1.5218 | 1.5218 | 1.5371 | 1.5371
990 | feeder2_line21 | 1 | 354.6 | 26.6436 | 26.6443 | 7.5137 | 7.5139
990 | feeder2_line21 | 2 | 354.6 | 59.1819 | 59.1872 | 16.6898 | 16.6912
990 | feeder2_line21 | 3 | 354.6 | 60.0421 | 60.0363 | 16.9323 | 16.9307
990 | feeder2_line22 | 1 | 99 | 5.6915e-07 | 1.0088e-06 | 5.749e-07 | 1.019e-06
990 | feeder2_line22 | 2 | 99 | 2.4402 | 2.4402 | 2.4648 | 2.4648
990 | feeder2_line22 | 3 | 99 | 5.7226e-07 | 1.0143e-06 | 5.7804e-07 | 1.0245e-06
990 | feeder2_line23 | 1 | 99 | 5.6915e-07 | 9.4435e-07 | 5.749e-07 | 9.5389e-07
990 | feeder2_line23 | 2 | 99 | 5.7259e-07 | 9.4998e-07 | 5.7838e-07 | 9.5958e-07
990 | feeder2_line23 | 3 | 99 | 0.081943 | 0.081941 | 0.082771 | 0.082769
990 | feeder2_line24 | 1 | 354.6 | 26.6437 | 26.6443 | 7.5137 | 7.5139
990 | feeder2_line24 | 2 | 354.6 | 61.4016 | 61.4068 | 17.3157 | 17.3172
990 | feeder2_line24 | 3 | 354.6 | 60.1176 | 60.1118 | 16.9536 | 16.952
990 | feeder2_line25 | 1 | 99 | 2.4408 | 2.4408 | 2.4655 | 2.4655
990 | feeder2_line25 | 2 | 99 | 4.918e-08 | 6.9086e-07 | 4.9677e-08 | 6.9784e-07
990 | feeder2_line25 | 3 | 99 | 4.9699e-08 | 6.9045e-07 | 5.0201e-08 | 6.9742e-07
990 | feeder2_line26 | 1 | 99 | 0.085921 | 0.085923 | 0.086789 | 0.086791
990 | feeder2_line26 | 2 | 99 | 5.4817e-07 | 8.5593e-07 | 5.537e-07 | 8.6457e-07
990 | feeder2_line26 | 3 | 99 | 5.4755e-07 | 8.5542e-07 | 5.5308e-07 | 8.6406e-07
990 | feeder2_line27 | 1 | 354.6 | 28.2345 | 28.2353 | 7.9623 | 7.9626
990 | feeder2_line27 | 2 | 354.6 | 61.4016 | 61.4068 | 17.3157 | 17.3172
990 | feeder2_line27 | 3 | 354.6 | 60.1176 | 60.1118 | 16.9536 | 16.952
990 | feeder2_line28 | 1 | 99 | 2.5179e-06 | 7.0578e-07 | 2.5434e-06 | 7.1291e-07
990 | feeder2_line28 | 2 | 99 | 1.9751 | 1.975 | 1.995 | 1.995
990 | feeder2_line28 | 3 | 99 | 2.5401e-06 | 7.1035e-07 | 2.5657e-06 | 7.1752e-07
990 | feeder2_line29 | 1 | 354.6 | 28.2345 | 28.2353 | 7.9623 | 7.9626
990 | feeder2_line29 | 2 | 354.6 | 61.8005 | 61.8056 | 17.4282 | 17.4297
990 | feeder2_line29 | 3 | 354.6 | 60.1176 | 60.1118 | 16.9536 | 16.952
990 | feeder2_line30 | 1 | 266.4 | 13.5971 | 13.5968 | 5.104 | 5.1039
990 | feeder2_line30 | 2 | 266.4 | 9.1145 | 9.1145 | 3.4214 | 3.4214
990 | feeder2_line30 | 3 | 266.4 | 5.4772 | 5.477 | 2.056 | 2.0559
990 | feeder2_line31 | 1 | 354.6 | 38.2789 | 38.2798 | 10.7949 | 10.7952
990 | feeder2_line31 | 2 | 354.6 | 67.4508 | 67.4554 | 19.0217 | 19.023
990 | feeder2_line31 | 3 | 354.6 | 64.3995 | 64.3931 | 18.1612 | 18.1594
990 | feeder2_line32 | 1 | 354.6 | 38.2789 | 38.2798 | 10.795 | 10.7952
990 | feeder2_line32 | 2 | 354.6 | 67.5259 | 67.5305 | 19.0428 | 19.0441
990 | feeder2_line32 | 3 | 354.6 | 64.3996 | 64.3931 | 18.1612 | 18.1594
990 | feeder2_line33 | 1 | 99 | 5.0394e-08 | 6.8059e-07 | 5.0904e-08 | 6.8746e-07
990 | feeder2_line33 | 2 | 99 | 0.076985 | 0.076988 | 0.077762 | 0.077766
990 | feeder2_line33 | 3 | 99 | 4.9722e-08 | 6.8589e-07 | 5.0224e-08 | 6.9282e-07
990 | feeder2_line34 | 1 | 354.6 | 38.2789 | 38.2798 | 10.795 | 10.7952
990 | feeder2_line34 | 2 | 354.6 | 67.5259 | 67.5305 | 19.0428 | 19.0441
990 | feeder2_line34 | 3 | 354.6 | 64.4791 | 64.4726 | 18.1836 | 18.1818
990 | feeder2_line35 | 1 | 99 | 2.9691e-07 | 7.5363e-07 | 2.9991e-07 | 7.6124e-07
990 | feeder2_line35 | 2 | 99 | 2.9916e-07 | 7.6042e-07 | 3.0218e-07 | 7.681e-07
990 | feeder2_line35 | 3 | 99 | 0.085642 | 0.085637 | 0.086507 | 0.086502
990 | feeder2_line36 | 1 | 354.6 | 38.3311 | 38.3322 | 10.8097 | 10.81
990 | feeder2_line36 | 2 | 354.6 | 67.5259 | 67.5305 | 19.0428 | 19.0441
990 | feeder2_line36 | 3 | 354.6 | 64.479 | 64.4726 | 18.1836 | 18.1818
990 | feeder2_line37 | 1 | 99 | 1.2284 | 1.2285 | 1.2408 | 1.2409
990 | feeder2_line37 | 2 | 99 | 2.9923e-07 | 8.4157e-07 | 3.0225e-07 | 8.5007e-07
990 | feeder2_line37 | 3 | 99 | 2.9907e-07 | 8.4066e-07 | 3.0209e-07 | 8.4915e-07
990 | feeder2_line38 | 1 | 99 | 3.2208e-07 | 7.6956e-07 | 3.2533e-07 | 7.7733e-07
990 | feeder2_line38 | 2 | 99 | 0.077067 | 0.07707 | 0.077846 | 0.077849
990 | feeder2_line38 | 3 | 99 | 3.2374e-07 | 7.7529e-07 | 3.2701e-07 | 7.8312e-07
990 | feeder2_line39 | 1 | 266.4 | 13.5971 | 13.5968 | 5.104 | 5.1039
990 | feeder2_line39 | 2 | 266.4 | 9.0524 | 9.0524 | 3.398 | 3.398
990 | feeder2_line39 | 3 | 266.4 | 5.4772 | 5.477 | 2.056 | 2.0559
990 | feeder2_line40 | 1 | 354.6 | 40.4402 | 40.4413 | 11.4044 | 11.4048
990 | feeder2_line40 | 2 | 354.6 | 67.5259 | 67.5305 | 19.0428 | 19.0441
990 | feeder2_line40 | 3 | 354.6 | 64.4791 | 64.4726 | 18.1836 | 18.1818
990 | feeder2_line41 | 1 | 99 | 2.4409 | 2.4409 | 2.4656 | 2.4656
990 | feeder2_line41 | 2 | 99 | 4.903e-08 | 7.3547e-07 | 4.9525e-08 | 7.4289e-07
990 | feeder2_line41 | 3 | 99 | 4.973e-08 | 7.3465e-07 | 5.0232e-08 | 7.4207e-07
990 | feeder2_line42 | 1 | 99 | 2.9687e-07 | 7.4271e-07 | 2.9987e-07 | 7.5021e-07
990 | feeder2_line42 | 2 | 99 | 2.9896e-07 | 7.4892e-07 | 3.0198e-07 | 7.5648e-07
990 | feeder2_line42 | 3 | 99 | 0.077229 | 0.077225 | 0.078009 | 0.078005
990 | feeder2_line43 | 1 | 266.4 | 13.597 | 13.5968 | 5.104 | 5.1039
990 | feeder2_line43 | 2 | 266.4 | 9.0524 | 9.0524 | 3.398 | 3.398
990 | feeder2_line43 | 3 | 266.4 | 5.4037 | 5.4035 | 2.0284 | 2.0283
990 | feeder2_line44 | 1 | 354.6 | 40.4402 | 40.4413 | 11.4045 | 11.4048
990 | feeder2_line44 | 2 | 354.6 | 67.5259 | 67.5305 | 19.0428 | 19.0441
990 | feeder2_line44 | 3 | 354.6 | 65.8819 | 65.8753 | 18.5792 | 18.5774
990 | feeder2_line45 | 1 | 99 | 5.0474e-08 | 5.7457e-07 | 5.0984e-08 | 5.8037e-07
990 | feeder2_line45 | 2 | 99 | 4.9026e-08 | 5.8008e-07 | 4.9521e-08 | 5.8594e-07
990 | feeder2_line45 | 3 | 99 | 1.5236 | 1.5235 | 1.539 | 1.5389
990 | feeder2_line46 | 1 | 99 | 5.6857e-07 | 1.3464e-06 | 5.7431e-07 | 1.36e-06
990 | feeder2_line46 | 2 | 99 | 5.7338e-07 | 1.3576e-06 | 5.7918e-07 | 1.3714e-06
990 | feeder2_line46 | 3 | 99 | 1.8976 | 1.8975 | 1.9167 | 1.9167
990 | feeder2_line47 | 1 | 266.4 | 13.597 | 13.5968 | 5.104 | 5.1039
990 | feeder2_line47 | 2 | 266.4 | 9.0525 | 9.0524 | 3.3981 | 3.398
990 | feeder2_line47 | 3 | 266.4 | 3.5852 | 3.585 | 1.3458 | 1.3457
990 | feeder2_line48 | 1 | 99 | 1.5113 | 1.5113 | 1.5266 | 1.5266
990 | feeder2_line48 | 2 | 99 | 4.9068e-08 | 7.3096e-07 | 4.9563e-08 | 7.3834e-07
990 | feeder2_line48 | 3 | 99 | 4.9708e-08 | 7.3038e-07 | 5.021e-08 | 7.3776e-07
990 | feeder2_line49 | 1 | 266.4 | 12.0893 | 12.0891 | 4.538 | 4.538
990 | feeder2_line49 | 2 | 266.4 | 9.0525 | 9.0524 | 3.3981 | 3.398
990 | feeder2_line49 | 3 | 266.4 | 3.5852 | 3.585 | 1.3458 | 1.3457
990 | feeder2_line50 | 1 | 99 | 5.6851e-07 | 1.2252e-06 | 5.7425e-07 | 1.2376e-06
990 | feeder2_line50 | 2 | 99 | 2.5708 | 2.5708 | 2.5967 | 2.5967
990 | feeder2_line50 | 3 | 99 | 5.7289e-07 | 1.2345e-06 | 5.7868e-07 | 1.247e-06
990 | feeder2_line51 | 1 | 99 | 1.7487 | 1.7487 | 1.7663 | 1.7664
990 | feeder2_line51 | 2 | 99 | 5.7335e-07 | 1.3413e-06 | 5.7914e-07 | 1.3548e-06
990 | feeder2_line51 | 3 | 99 | 5.7288e-07 | 1.3402e-06 | 5.7867e-07 | 1.3538e-06
990 | feeder2_line52 | 1 | 266.4 | 10.3439 | 10.3438 | 3.8828 | 3.8828
990 | feeder2_line52 | 2 | 266.4 | 6.5191 | 6.5191 | 2.4471 | 2.4471
990 | feeder2_line52 | 3 | 266.4 | 3.5851 | 3.585 | 1.3457 | 1.3457
990 | feeder2_line53 | 1 | 99 | 5.4333e-07 | 7.4774e-07 | 5.4882e-07 | 7.553e-07
990 | feeder2_line53 | 2 | 99 | 6.5191 | 6.5191 | 6.585 | 6.585
990 | feeder2_line53 | 3 | 99 | 5.4804e-07 | 7.5346e-07 | 5.5357e-07 | 7.6107e-07
990 | feeder2_line54 | 1 | 266.4 | 10.3437 | 10.3438 | 3.8828 | 3.8828
990 | feeder2_line54 | 2 | 266.4 | 8.5468e-05 | 4.6249e-06 | 3.2083e-05 | 1.7361e-06
990 | feeder2_line54 | 3 | 266.4 | 3.5849 | 3.585 | 1.3457 | 1.3457
990 | feeder2_line55 | 1 | 99 | 1.1195 | 1.1195 | 1.1308 | 1.1308
990 | feeder2_line55 | 2 | 99 | 4.8998e-08 | 7.3121e-07 | 4.9493e-08 | 7.386e-07
990 | feeder2_line55 | 3 | 99 | 4.9744e-08 | 7.3028e-07 | 5.0246e-08 | 7.3765e-07
990 | feeder2_line56 | 1 | 354.6 | 41.2898 | 41.2909 | 11.644 | 11.6444
990 | feeder2_line56 | 2 | 354.6 | 67.526 | 67.5305 | 19.0429 | 19.0441
990 | feeder2_line56 | 3 | 354.6 | 65.8819 | 65.8753 | 18.5792 | 18.5774
990 | feeder2_line57 | 1 | 99 | 7.5521e-07 | 1.5316e-06 | 7.6284e-07 | 1.547e-06
990 | feeder2_line57 | 2 | 99 | 7.3588e-07 | 1.5446e-06 | 7.4331e-07 | 1.5602e-06
990 | feeder2_line57 | 3 | 99 | 3.585 | 3.585 | 3.6212 | 3.6213
990 | feeder2_line58 | 1 | 266.4 | 10.3438 | 10.3438 | 3.8828 | 3.8828
990 | feeder2_line58 | 2 | 266.4 | 1.8957e-05 | 2.685e-06 | 7.1159e-06 | 1.0079e-06
990 | feeder2_line58 | 3 | 266.4 | 1.8958e-05 | 2.6834e-06 | 7.1164e-06 | 1.0073e-06
990 | feeder2_line59 | 1 | 99 | 5.0347e-08 | 5.3239e-07 | 5.0856e-08 | 5.3777e-07
990 | feeder2_line59 | 2 | 99 | 4.9053e-08 | 5.3688e-07 | 4.9549e-08 | 5.423e-07
990 | feeder2_line59 | 3 | 99 | 2.0139 | 2.014 | 2.0343 | 2.0343
990 | feeder2_line60 | 1 | 99 | 2.9683e-07 | 8.046e-07 | 2.9983e-07 | 8.1273e-07
990 | feeder2_line60 | 2 | 99 | 2.9894e-07 | 8.114e-07 | 3.0196e-07 | 8.196e-07
990 | feeder2_line60 | 3 | 99 | 1.9116 | 1.9116 | 1.9309 | 1.9309
990 | feeder2_line61 | 1 | 266.4 | 0.086558 | 0.086727 | 0.032492 | 0.032555
990 | feeder2_line61 | 2 | 266.4 | 2.5515 | 2.5517 | 0.95776 | 0.95783
990 | feeder2_line61 | 3 | 266.4 | 3.7428 | 3.743 | 1.405 | 1.405
990 | feeder2_line62 | 1 | 354.6 | 41.3681 | 41.3693 | 11.6661 | 11.6665
990 | feeder2_line62 | 2 | 354.6 | 69.3802 | 69.3848 | 19.5658 | 19.5671
990 | feeder2_line62 | 3 | 354.6 | 69.3724 | 69.366 | 19.5636 | 19.5618
990 | feeder2_line63 | 1 | 99 | 0.090023 | 0.090025 | 0.090932 | 0.090934
990 | feeder2_line63 | 2 | 99 | 5.7337e-07 | 1.22e-06 | 5.7916e-07 | 1.2323e-06
990 | feeder2_line63 | 3 | 99 | 5.729e-07 | 1.219e-06 | 5.7868e-07 | 1.2313e-06
990 | feeder2_line64 | 1 | 99 | 10.2539 | 10.2539 | 10.3575 | 10.3575
990 | feeder2_line64 | 2 | 99 | 5.5869e-12 | 3.2135e-07 | 5.6434e-12 | 3.246e-07
990 | feeder2_line64 | 3 | 99 | 2.0415e-12 | 3.2111e-07 | 2.0621e-12 | 3.2435e-07
990 | feeder2_line65 | 1 | 99 | 5.0648e-08 | 6.3562e-07 | 5.116e-08 | 6.4204e-07
990 | feeder2_line65 | 2 | 99 | 0.089476 | 0.089482 | 0.09038 | 0.090385
990 | feeder2_line65 | 3 | 99 | 4.9761e-08 | 6.4184e-07 | 5.0264e-08 | 6.4832e-07
990 | feeder2_line66 | 1 | 354.6 | 41.368 | 41.3693 | 11.6661 | 11.6665
990 | feeder2_line66 | 2 | 354.6 | 69.4678 | 69.4725 | 19.5905 | 19.5918
990 | feeder2_line66 | 3 | 354.6 | 69.3724 | 69.366 | 19.5636 | 19.5618
990 | feeder2_line67 | 1 | 99 | 2.5286e-08 | 3.5938e-07 | 2.5541e-08 | 3.6301e-07
990 | feeder2_line67 | 2 | 99 | 2.4492e-08 | 3.6322e-07 | 2.474e-08 | 3.6689e-07
990 | feeder2_line67 | 3 | 99 | 2.4401 | 2.4401 | 2.4648 | 2.4648
990 | feeder2_line68 | 1 | 266.4 | 0.086596 | 0.086727 | 0.032506 | 0.032555
990 | feeder2_line68 | 2 | 266.4 | 2.5515 | 2.5517 | 0.95778 | 0.95783
990 | feeder2_line68 | 3 | 266.4 | 1.3027 | 1.3029 | 0.48902 | 0.48906
990 | feeder2_line69 | 1 | 99 | 1.0914 | 1.0914 | 1.1025 | 1.1025
990 | feeder2_line69 | 2 | 99 | 2.5573e-06 | 6.6743e-07 | 2.5831e-06 | 6.7417e-07
990 | feeder2_line69 | 3 | 99 | 2.5475e-06 | 6.6641e-07 | 2.5732e-06 | 6.7314e-07
990 | feeder2_line70 | 1 | 354.6 | 42.3443 | 42.3457 | 11.9414 | 11.9418
990 | feeder2_line70 | 2 | 354.6 | 69.4677 | 69.4725 | 19.5904 | 19.5918
990 | feeder2_line70 | 3 | 354.6 | 69.3723 | 69.366 | 19.5635 | 19.5618
990 | feeder2_line71 | 1 | 99 | 5.0689e-08 | 7.0905e-07 | 5.1201e-08 | 7.1621e-07
990 | feeder2_line71 | 2 | 99 | 1.7708 | 1.7708 | 1.7887 | 1.7887
990 | feeder2_line71 | 3 | 99 | 4.9765e-08 | 7.1624e-07 | 5.0267e-08 | 7.2347e-07
990 | feeder2_line72 | 1 | 354.6 | 42.3444 | 42.3457 | 11.9415 | 11.9418
990 | feeder2_line72 | 2 | 354.6 | 71.1722 | 71.1769 | 20.0711 | 20.0725
990 | feeder2_line72 | 3 | 354.6 | 69.3724 | 69.366 | 19.5636 | 19.5618
990 | feeder2_line73 | 1 | 99 | 5.9379e-07 | 1.5215e-06 | 5.9979e-07 | 1.5368e-06
990 | feeder2_line73 | 2 | 99 | 0.076834 | 0.076838 | 0.07761 | 0.077615
990 | feeder2_line73 | 3 | 99 | 5.9869e-07 | 1.5356e-06 | 6.0474e-07 | 1.5511e-06
990 | feeder2_line74 | 1 | 99 | 5.0584e-08 | 4.5378e-07 | 5.1095e-08 | 4.5837e-07
990 | feeder2_line74 | 2 | 99 | 1.3047 | 1.3047 | 1.3179 | 1.3179
990 | feeder2_line74 | 3 | 99 | 4.9755e-08 | 4.5799e-07 | 5.0258e-08 | 4.6261e-07
990 | feeder2_line75 | 1 | 266.4 | 0.086692 | 0.086726 | 0.032542 | 0.032555
990 | feeder2_line75 | 2 | 266.4 | 1.4802 | 1.4802 | 0.55564 | 0.55565
990 | feeder2_line75 | 3 | 266.4 | 1.3028 | 1.3029 | 0.48905 | 0.48906
990 | feeder2_line76 | 1 | 99 | 0.086724 | 0.086726 | 0.0876 | 0.087602
990 | feeder2_line76 | 2 | 99 | 8.4973e-07 | 1.5862e-06 | 8.5831e-07 | 1.6022e-06
990 | feeder2_line76 | 3 | 99 | 8.4829e-07 | 1.584e-06 | 8.5686e-07 | 1.6e-06
990 | feeder2_line77 | 1 | 99 | 2.5293e-08 | 5.7025e-07 | 2.5549e-08 | 5.7601e-07
990 | feeder2_line77 | 2 | 99 | 2.4486e-08 | 5.7633e-07 | 2.4733e-08 | 5.8215e-07
990 | feeder2_line77 | 3 | 99 | 1.3029 | 1.3029 | 1.316 | 1.316
990 | feeder2_line78 | 1 | 266.4 | 5.9978e-12 | 9.4649e-07 | 2.2514e-12 | 3.5529e-07
990 | feeder2_line78 | 2 | 266.4 | 1.4803 | 1.4803 | 0.55566 | 0.55565
990 | feeder2_line78 | 3 | 266.4 | 4.4862e-12 | 9.5441e-07 | 1.684e-12 | 3.5826e-07
990 | feeder2_line79 | 1 | 354.6 | 2.1595 | 2.1591 | 0.60899 | 0.60887
990 | feeder2_line79 | 2 | 354.6 | 16.8044 | 16.8039 | 4.739 | 4.7388
990 | feeder2_line79 | 3 | 354.6 | 27.4421 | 27.442 | 7.7389 | 7.7389
990 | feeder2_line80 | 1 | 354.6 | 44.2593 | 44.2601 | 12.4815 | 12.4817
990 | feeder2_line80 | 2 | 354.6 | 87.1414 | 87.1454 | 24.5746 | 24.5757
990 | feeder2_line80 | 3 | 354.6 | 94.5755 | 94.5687 | 26.671 | 26.6691
990 | feeder2_line81 | 1 | 354.6 | 44.2592 | 44.2601 | 12.4815 | 12.4817
990 | feeder2_line81 | 2 | 354.6 | 87.1413 | 87.1454 | 24.5745 | 24.5757
990 | feeder2_line81 | 3 | 354.6 | 95.4213 | 95.4146 | 26.9096 | 26.9077
990 | feeder2_line82 | 1 | 354.6 | 3.6291e-11 | 7.275e-07 | 1.0234e-11 | 2.0516e-07
990 | feeder2_line82 | 2 | 354.6 | 3.2826e-11 | 7.3573e-07 | 9.2573e-12 | 2.0748e-07
990 | feeder2_line82 | 3 | 354.6 | 0.87265 | 0.87264 | 0.2461 | 0.24609
990 | feeder2_line83 | 1 | 354.6 | 44.2594 | 44.2601 | 12.4815 | 12.4817
990 | feeder2_line83 | 2 | 354.6 | 87.2294 | 87.2333 | 24.5994 | 24.6005
990 | feeder2_line83 | 3 | 354.6 | 95.4215 | 95.4146 | 26.9096 | 26.9077
990 | feeder2_line84 | 1 | 354.6 | 7.77e-12 | 1.2856e-06 | 2.1912e-12 | 3.6255e-07
990 | feeder2_line84 | 2 | 354.6 | 0.088638 | 0.088666 | 0.024997 | 0.025005
990 | feeder2_line84 | 3 | 354.6 | 7.6597e-12 | 1.2991e-06 | 2.1601e-12 | 3.6635e-07
990 | feeder2_line85 | 1 | 99 | 0.07817 | 0.078173 | 0.07896 | 0.078962
990 | feeder2_line85 | 2 | 99 | 4.889e-08 | 4.645e-07 | 4.9384e-08 | 4.6919e-07
990 | feeder2_line85 | 3 | 99 | 4.9771e-08 | 4.6376e-07 | 5.0273e-08 | 4.6844e-07
990 | feeder2_line86 | 1 | 354.6 | 44.3317 | 44.3323 | 12.5019 | 12.5021
990 | feeder2_line86 | 2 | 354.6 | 87.2295 | 87.2333 | 24.5994 | 24.6005
990 | feeder2_line86 | 3 | 354.6 | 95.4216 | 95.4146 | 26.9096 | 26.9077
990 | feeder2_line87 | 1 | 354.6 | 44.3318 | 44.3323 | 12.5019 | 12.5021
990 | feeder2_line87 | 2 | 354.6 | 90.7646 | 90.7683 | 25.5963 | 25.5974
990 | feeder2_line87 | 3 | 354.6 | 95.8584 | 95.8512 | 27.0328 | 27.0308
990 | feeder2_line88 | 1 | 354.6 | 0.00011035 | 3.329e-06 | 3.112e-05 | 9.3881e-07
990 | feeder2_line88 | 2 | 354.6 | 3.5691 | 3.5691 | 1.0065 | 1.0065
990 | feeder2_line88 | 3 | 354.6 | 1.0449 | 1.0448 | 0.29467 | 0.29464
990 | feeder2_line89 | 1 | 354.6 | 44.3297 | 44.3323 | 12.5013 | 12.5021
990 | feeder2_line89 | 2 | 354.6 | 90.9309 | 90.937 | 25.6432 | 25.6449
990 | feeder2_line89 | 3 | 354.6 | 95.8561 | 95.8512 | 27.0322 | 27.0308
990 | feeder2_line90 | 1 | 354.6 | 0.00071207 | 2.0106e-06 | 0.00020081 | 5.67e-07
990 | feeder2_line90 | 2 | 354.6 | 0.16931 | 0.16992 | 0.047747 | 0.047918
990 | feeder2_line90 | 3 | 354.6 | 0.00072496 | 2.0338e-06 | 0.00020444 | 5.7356e-07
990 | feeder2_line91 | 1 | 354.6 | 44.3297 | 44.3323 | 12.5013 | 12.5021
990 | feeder2_line91 | 2 | 354.6 | 90.9309 | 90.937 | 25.6432 | 25.6449
990 | feeder2_line91 | 3 | 354.6 | 96.865 | 96.8601 | 27.3167 | 27.3153
990 | feeder2_line92 | 1 | 354.6 | 1.2966e-11 | 1.0141e-06 | 3.6564e-12 | 2.8597e-07
990 | feeder2_line92 | 2 | 354.6 | 6.5734e-12 | 1.027e-06 | 1.8537e-12 | 2.8962e-07
990 | feeder2_line92 | 3 | 354.6 | 1.9138 | 1.9138 | 0.53971 | 0.53971
990 | feeder2_line93 | 1 | 99 | 2.5477e-08 | 3.3826e-07 | 2.5735e-08 | 3.4168e-07
990 | feeder2_line93 | 2 | 99 | 0.088541 | 0.088571 | 0.089436 | 0.089466
990 | feeder2_line93 | 3 | 99 | 2.4883e-08 | 3.4251e-07 | 2.5135e-08 | 3.4597e-07
990 | feeder2_line94 | 1 | 354.6 | 2.5479e-06 | 1.6481e-06 | 7.1852e-07 | 4.6477e-07
990 | feeder2_line94 | 2 | 354.6 | 0.081318 | 0.081348 | 0.022932 | 0.022941
990 | feeder2_line94 | 3 | 354.6 | 2.4883e-06 | 1.6673e-06 | 7.0172e-07 | 4.7019e-07
990 | feeder2_line95 | 1 | 99 | 3.518e-06 | 2.5815e-06 | 3.5535e-06 | 2.6076e-06
990 | feeder2_line95 | 2 | 99 | 3.569 | 3.5691 | 3.605 | 3.6051
990 | feeder2_line95 | 3 | 99 | 3.5807e-06 | 2.6122e-06 | 3.6168e-06 | 2.6386e-06
990 | feeder2_line96 | 1 | 354.6 | 0.00011967 | 6.1541e-07 | 3.3748e-05 | 1.7355e-07
990 | feeder2_line96 | 2 | 354.6 | 0.00012159 | 6.2369e-07 | 3.4289e-05 | 1.7589e-07
990 | feeder2_line96 | 3 | 354.6 | 1.0449 | 1.0448 | 0.29466 | 0.29464
990 | feeder2_line97 | 1 | 354.6 | 47.2804 | 47.2829 | 13.3334 | 13.3342
990 | feeder2_line97 | 2 | 354.6 | 90.9311 | 90.937 | 25.6433 | 25.6449
990 | feeder2_line97 | 3 | 354.6 | 96.8652 | 96.8601 | 27.3167 | 27.3153
990 | feeder2_line98 | 1 | 354.6 | 3.3473 | 3.3457 | 0.94397 | 0.94351
990 | feeder2_line98 | 2 | 354.6 | 0.0017329 | 6.2267e-07 | 0.00048868 | 1.756e-07
990 | feeder2_line98 | 3 | 354.6 | 0.0016904 | 6.2403e-07 | 0.0004767 | 1.7598e-07
990 | feeder2_line99 | 1 | 99 | 2.5446e-08 | 4.4239e-07 | 2.5703e-08 | 4.4685e-07
990 | feeder2_line99 | 2 | 99 | 2.4435e-08 | 4.4834e-07 | 2.4682e-08 | 4.5287e-07
990 | feeder2_line99 | 3 | 99 | 1.0449 | 1.0448 | 1.0554 | 1.0554
990 | feeder2_line100 | 1 | 99 | 3.3457 | 3.3457 | 3.3795 | 3.3795
990 | feeder2_line100 | 2 | 99 | 2.4424e-08 | 6.159e-07 | 2.467e-08 | 6.2212e-07
990 | feeder2_line100 | 3 | 99 | 2.4881e-08 | 6.15e-07 | 2.5132e-08 | 6.2121e-07
990 | feeder2_line101 | 1 | 354.6 | 0.083045 | 0.082625 | 0.023419 | 0.023301
990 | feeder2_line101 | 2 | 354.6 | 16.8044 | 16.8039 | 4.739 | 4.7388
990 | feeder2_line101 | 3 | 354.6 | 27.4421 | 27.442 | 7.7389 | 7.7389
990 | feeder2_line102 | 1 | 99 | 2.0766 | 2.0766 | 2.0976 | 2.0976
990 | feeder2_line102 | 2 | 99 | 2.357e-06 | 8.7992e-07 | 2.3808e-06 | 8.888e-07
990 | feeder2_line102 | 3 | 99 | 2.3287e-06 | 8.7826e-07 | 2.3523e-06 | 8.8713e-07
990 | feeder2_line103 | 1 | 99 | 5.4313e-07 | 7.9581e-07 | 5.4861e-07 | 8.0385e-07
990 | feeder2_line103 | 2 | 99 | 1.9621 | 1.9621 | 1.9819 | 1.9819
990 | feeder2_line103 | 3 | 99 | 5.4932e-07 | 8.0376e-07 | 5.5487e-07 | 8.1188e-07
990 | feeder2_line104 | 1 | 354.6 | 0.08294 | 0.082625 | 0.02339 | 0.023301
990 | feeder2_line104 | 2 | 354.6 | 14.8494 | 14.849 | 4.1876 | 4.1875
990 | feeder2_line104 | 3 | 354.6 | 27.442 | 27.442 | 7.7389 | 7.7389
990 | feeder2_line105 | 1 | 99 | 2.513e-06 | 7.3228e-07 | 2.5384e-06 | 7.3968e-07
990 | feeder2_line105 | 2 | 99 | 2.5589e-06 | 7.41e-07 | 2.5848e-06 | 7.4849e-07
990 | feeder2_line105 | 3 | 99 | 0.15307 | 0.15304 | 0.15462 | 0.15459
990 | feeder2_line106 | 1 | 354.6 | 0.082886 | 0.082625 | 0.023375 | 0.023301
990 | feeder2_line106 | 2 | 354.6 | 14.8493 | 14.849 | 4.1876 | 4.1875
990 | feeder2_line106 | 3 | 354.6 | 27.2897 | 27.2897 | 7.6959 | 7.6959
990 | feeder2_line107 | 1 | 99 | 3.2227e-07 | 8.9246e-07 | 3.2553e-07 | 9.0147e-07
990 | feeder2_line107 | 2 | 99 | 2.3587 | 2.3587 | 2.3825 | 2.3825
990 | feeder2_line107 | 3 | 99 | 3.2435e-07 | 9.0096e-07 | 3.2763e-07 | 9.1006e-07
990 | feeder2_line108 | 1 | 354.6 | 0.082875 | 0.082625 | 0.023371 | 0.023301
990 | feeder2_line108 | 2 | 354.6 | 12.493 | 12.4927 | 3.5231 | 3.523
990 | feeder2_line108 | 3 | 354.6 | 27.2897 | 27.2897 | 7.6959 | 7.6959
990 | feeder2_line109 | 1 | 354.6 | 57.3128 | 57.3145 | 16.1627 | 16.1632
990 | feeder2_line109 | 2 | 354.6 | 90.9323 | 90.937 | 25.6436 | 25.6449
990 | feeder2_line109 | 3 | 354.6 | 96.8663 | 96.8601 | 27.3171 | 27.3153
990 | feeder2_line110 | 1 | 99 | 11.391 | 11.3901 | 11.5061 | 11.5052
990 | feeder2_line110 | 2 | 99 | 0.00081052 | 9.1165e-07 | 0.00081871 | 9.2086e-07
990 | feeder2_line110 | 3 | 99 | 0.00080671 | 9.1056e-07 | 0.00081486 | 9.1976e-07
990 | feeder2_line111 | 1 | 99 | 2.544e-08 | 3.7783e-07 | 2.5697e-08 | 3.8165e-07
990 | feeder2_line111 | 2 | 99 | 1.1682 | 1.1682 | 1.18 | 1.18
990 | feeder2_line111 | 3 | 99 | 2.488e-08 | 3.8234e-07 | 2.5131e-08 | 3.862e-07
990 | feeder2_line112 | 1 | 99 | 3.2228e-07 | 9.0795e-07 | 3.2554e-07 | 9.1712e-07
990 | feeder2_line112 | 2 | 99 | 2.4084 | 2.4085 | 2.4327 | 2.4328
990 | feeder2_line112 | 3 | 99 | 3.2484e-07 | 9.1877e-07 | 3.2813e-07 | 9.2805e-07
990 | feeder2_line113 | 1 | 99 | 1.4089 | 1.4089 | 1.4232 | 1.4231
990 | feeder2_line113 | 2 | 99 | 3.2499e-07 | 9.0842e-07 | 3.2827e-07 | 9.176e-07
990 | feeder2_line113 | 3 | 99 | 3.2525e-07 | 9.0715e-07 | 3.2853e-07 | 9.1632e-07
990 | feeder2_line114 | 1 | 99 | 1.9421 | 1.9421 | 1.9617 | 1.9617
990 | feeder2_line114 | 2 | 99 | 2.4457e-08 | 4.3754e-07 | 2.4704e-08 | 4.4196e-07
990 | feeder2_line114 | 3 | 99 | 2.4895e-08 | 4.3672e-07 | 2.5146e-08 | 4.4113e-07
990 | feeder2_line115 | 1 | 99 | 2.5321e-08 | 5.5699e-07 | 2.5577e-08 | 5.6262e-07
990 | feeder2_line115 | 2 | 99 | 1.9484 | 1.9484 | 1.9681 | 1.9681
990 | feeder2_line115 | 3 | 99 | 2.4916e-08 | 5.6208e-07 | 2.5168e-08 | 5.6776e-07
990 | feeder2_line116 | 1 | 354.6 | 0.082881 | 0.082625 | 0.023373 | 0.023301
990 | feeder2_line116 | 2 | 354.6 | 10.942 | 10.9417 | 3.0857 | 3.0856
990 | feeder2_line116 | 3 | 354.6 | 27.2897 | 27.2897 | 7.6959 | 7.6959
990 | feeder2_line117 | 1 | 99 | 5.1129e-08 | 6.3528e-07 | 5.1645e-08 | 6.417e-07
990 | feeder2_line117 | 2 | 99 | 1.8901 | 1.8902 | 1.9092 | 1.9093
990 | feeder2_line117 | 3 | 99 | 4.9764e-08 | 6.443e-07 | 5.0267e-08 | 6.5081e-07
990 | feeder2_line118 | 1 | 354.6 | 57.3128 | 57.3145 | 16.1627 | 16.1632
990 | feeder2_line118 | 2 | 354.6 | 92.7864 | 92.7911 | 26.1665 | 26.1678
990 | feeder2_line118 | 3 | 354.6 | 96.8664 | 96.8601 | 27.3171 | 27.3153
990 | feeder2_line119 | 1 | 99 | 2.5305e-08 | 5.994e-07 | 2.556e-08 | 6.0545e-07
990 | feeder2_line119 | 2 | 99 | 2.4455e-08 | 6.0628e-07 | 2.4702e-08 | 6.124e-07
990 | feeder2_line119 | 3 | 99 | 0.093708 | 0.093694 | 0.094654 | 0.09464
990 | feeder2_line120 | 1 | 354.6 | 0.082883 | 0.082624 | 0.023374 | 0.023301
990 | feeder2_line120 | 2 | 354.6 | 10.942 | 10.9417 | 3.0857 | 3.0856
990 | feeder2_line120 | 3 | 354.6 | 27.197 | 27.1971 | 7.6698 | 7.6698
990 | feeder2_line121 | 1 | 99 | 3.2228e-07 | 9.2829e-07 | 3.2553e-07 | 9.3766e-07
990 | feeder2_line121 | 2 | 99 | 10.8532 | 10.8531 | 10.9629 | 10.9628
990 | feeder2_line121 | 3 | 99 | 3.241e-07 | 9.3594e-07 | 3.2737e-07 | 9.4539e-07
990 | feeder2_line122 | 1 | 354.6 | 0.082871 | 0.082624 | 0.02337 | 0.023301
990 | feeder2_line122 | 2 | 354.6 | 0.088913 | 0.088676 | 0.025074 | 0.025007
990 | feeder2_line122 | 3 | 354.6 | 27.197 | 27.1971 | 7.6698 | 7.6698
990 | feeder2_line123 | 1 | 99 | 5.6874e-07 | 9.6197e-07 | 5.7449e-07 | 9.7169e-07
990 | feeder2_line123 | 2 | 99 | 5.7526e-07 | 9.7285e-07 | 5.8107e-07 | 9.8268e-07
990 | feeder2_line123 | 3 | 99 | 1.974 | 1.9739 | 1.9939 | 1.9939
990 | feeder2_line124 | 1 | 354.6 | 0.082775 | 0.082624 | 0.023343 | 0.023301
990 | feeder2_line124 | 2 | 354.6 | 0.088817 | 0.088676 | 0.025047 | 0.025007
990 | feeder2_line124 | 3 | 354.6 | 25.9161 | 25.9164 | 7.3086 | 7.3086
990 | feeder2_line125 | 1 | 99 | 5.6874e-07 | 8.9426e-07 | 5.7449e-07 | 9.0329e-07
990 | feeder2_line125 | 2 | 99 | 5.7527e-07 | 9.0439e-07 | 5.8108e-07 | 9.1353e-07
990 | feeder2_line125 | 3 | 99 | 3.3359 | 3.3358 | 3.3696 | 3.3695
990 | feeder2_line126 | 1 | 354.6 | 0.082929 | 0.082624 | 0.023387 | 0.023301
990 | feeder2_line126 | 2 | 354.6 | 0.088974 | 0.088676 | 0.025091 | 0.025007
990 | feeder2_line126 | 3 | 354.6 | 22.581 | 22.5811 | 6.368 | 6.368
990 | feeder2_line127 | 1 | 99 | 5.6876e-07 | 1.0706e-06 | 5.7451e-07 | 1.0814e-06
990 | feeder2_line127 | 2 | 99 | 5.753e-07 | 1.0828e-06 | 5.8111e-07 | 1.0937e-06
990 | feeder2_line127 | 3 | 99 | 0.75243 | 0.75243 | 0.76003 | 0.76003
990 | feeder2_line128 | 1 | 354.6 | 0.082845 | 0.082624 | 0.023363 | 0.023301
990 | feeder2_line128 | 2 | 354.6 | 0.088888 | 0.088675 | 0.025067 | 0.025007
990 | feeder2_line128 | 3 | 354.6 | 21.8456 | 21.8458 | 6.1606 | 6.1607
990 | feeder2_line129 | 1 | 99 | 5.4351e-07 | 8.6812e-07 | 5.49e-07 | 8.7689e-07
990 | feeder2_line129 | 2 | 99 | 0.088671 | 0.088675 | 0.089567 | 0.089571
990 | feeder2_line129 | 3 | 99 | 5.482e-07 | 8.7474e-07 | 5.5374e-07 | 8.8357e-07
990 | feeder2_line130 | 1 | 354.6 | 0.082858 | 0.082624 | 0.023367 | 0.0233
990 | feeder2_line130 | 2 | 354.6 | 0.00030795 | 4.6448e-06 | 8.6846e-05 | 1.3099e-06
990 | feeder2_line130 | 3 | 354.6 | 21.8456 | 21.8458 | 6.1606 | 6.1607
990 | feeder2_line131 | 1 | 99 | 5.6876e-07 | 9.6218e-07 | 5.745e-07 | 9.719e-07
990 | feeder2_line131 | 2 | 99 | 5.7531e-07 | 9.7311e-07 | 5.8112e-07 | 9.8293e-07
990 | feeder2_line131 | 3 | 99 | 21.7688 | 21.7692 | 21.9887 | 21.9891
990 | feeder2_line132 | 1 | 354.6 | 0.0827 | 0.082623 | 0.023322 | 0.0233
990 | feeder2_line132 | 2 | 354.6 | 0.00012621 | 2.9202e-06 | 3.5591e-05 | 8.2352e-07
990 | feeder2_line132 | 3 | 354.6 | 0.077363 | 0.077288 | 0.021817 | 0.021796
990 | feeder2_line133 | 1 | 99 | 0.082631 | 0.082623 | 0.083466 | 0.083458
990 | feeder2_line133 | 2 | 99 | 2.9989e-07 | 9.809e-07 | 3.0292e-07 | 9.908e-07
990 | feeder2_line133 | 3 | 99 | 2.9901e-07 | 9.771e-07 | 3.0203e-07 | 9.8697e-07
990 | feeder2_line134 | 1 | 354.6 | 1.1588e-11 | 1.7697e-06 | 3.268e-12 | 4.9906e-07
990 | feeder2_line134 | 2 | 354.6 | 1.0741e-11 | 1.7878e-06 | 3.0292e-12 | 5.0416e-07
990 | feeder2_line134 | 3 | 354.6 | 0.077294 | 0.077287 | 0.021798 | 0.021796
990 | feeder2_line135 | 1 | 99 | 1.7713 | 1.7713 | 1.7892 | 1.7892
990 | feeder2_line135 | 2 | 99 | 4.8812e-08 | 5.8816e-07 | 4.9305e-08 | 5.941e-07
990 | feeder2_line135 | 3 | 99 | 4.9771e-08 | 5.8741e-07 | 5.0274e-08 | 5.9334e-07
990 | feeder2_line136 | 1 | 354.6 | 58.9827 | 58.9845 | 16.6336 | 16.6341
990 | feeder2_line136 | 2 | 354.6 | 92.7864 | 92.7911 | 26.1665 | 26.1678
990 | feeder2_line136 | 3 | 354.6 | 96.8663 | 96.8601 | 27.3171 | 27.3153
990 | feeder2_line137 | 1 | 99 | 2.4287 | 2.4287 | 2.4532 | 2.4532
990 | feeder2_line137 | 2 | 99 | 8.5408e-07 | 1.5843e-06 | 8.6271e-07 | 1.6003e-06
990 | feeder2_line137 | 3 | 99 | 8.5268e-07 | 1.5823e-06 | 8.6129e-07 | 1.5983e-06
990 | feeder2_line138 | 1 | 354.6 | 60.2857 | 60.2874 | 17.001 | 17.0015
990 | feeder2_line138 | 2 | 354.6 | 92.7865 | 92.7911 | 26.1665 | 26.1678
990 | feeder2_line138 | 3 | 354.6 | 96.8664 | 96.8601 | 27.3171 | 27.3153
990 | feeder2_line139 | 1 | 99 | 5.1249e-08 | 4.8572e-07 | 5.1767e-08 | 4.9063e-07
990 | feeder2_line139 | 2 | 99 | 4.8803e-08 | 4.9372e-07 | 4.9296e-08 | 4.987e-07
990 | feeder2_line139 | 3 | 99 | 1.3176 | 1.3173 | 1.3309 | 1.3307
990 | feeder2_line140 | 1 | 354.6 | 60.2857 | 60.2874 | 17.0011 | 17.0015
990 | feeder2_line140 | 2 | 354.6 | 92.7866 | 92.7911 | 26.1665 | 26.1678
990 | feeder2_line140 | 3 | 354.6 | 97.404 | 97.3972 | 27.4687 | 27.4668
990 | feeder2_line141 | 1 | 99 | 2.4819e-06 | 4.8045e-07 | 2.507e-06 | 4.853e-07
990 | feeder2_line141 | 2 | 99 | 0.076372 | 0.076377 | 0.077143 | 0.077148
990 | feeder2_line141 | 3 | 99 | 2.5368e-06 | 4.8784e-07 | 2.5624e-06 | 4.9277e-07
990 | feeder2_line142 | 1 | 354.6 | 60.2856 | 60.2874 | 17.001 | 17.0015
990 | feeder2_line142 | 2 | 354.6 | 92.8623 | 92.867 | 26.1879 | 26.1892
990 | feeder2_line142 | 3 | 354.6 | 97.4038 | 97.3972 | 27.4686 | 27.4668
990 | feeder2_line143 | 1 | 99 | 8.3941e-07 | 1.7072e-06 | 8.4789e-07 | 1.7244e-06
990 | feeder2_line143 | 2 | 99 | 2.3565 | 2.3566 | 2.3803 | 2.3804
990 | feeder2_line143 | 3 | 99 | 8.5312e-07 | 1.7336e-06 | 8.6174e-07 | 1.7511e-06
990 | feeder2_line144 | 1 | 354.6 | 60.2854 | 60.2874 | 17.001 | 17.0015
990 | feeder2_line144 | 2 | 354.6 | 95.0971 | 95.1021 | 26.8181 | 26.8195
990 | feeder2_line144 | 3 | 354.6 | 97.4036 | 97.3972 | 27.4686 | 27.4668
990 | feeder2_line145 | 1 | 99 | 2.5643e-08 | 4.7869e-07 | 2.5902e-08 | 4.8352e-07
990 | feeder2_line145 | 2 | 99 | 0.86963 | 0.86964 | 0.87841 | 0.87843
990 | feeder2_line145 | 3 | 99 | 2.4891e-08 | 4.8614e-07 | 2.5142e-08 | 4.9105e-07
990 | feeder2_line146 | 1 | 354.6 | 60.2853 | 60.2874 | 17.0009 | 17.0015
990 | feeder2_line146 | 2 | 354.6 | 95.9513 | 95.9564 | 27.059 | 27.0605
990 | feeder2_line146 | 3 | 354.6 | 97.4035 | 97.3972 | 27.4686 | 27.4668
990 | feeder2_line147 | 1 | 99 | 10.442 | 10.4419 | 10.5474 | 10.5473
990 | feeder2_line147 | 2 | 99 | 1.1557e-06 | 2.2451e-06 | 1.1674e-06 | 2.2678e-06
990 | feeder2_line147 | 3 | 99 | 1.1543e-06 | 2.2424e-06 | 1.1659e-06 | 2.265e-06
990 | feeder2_line148 | 1 | 99 | 0.086327 | 0.08633 | 0.087199 | 0.087202
990 | feeder2_line148 | 2 | 99 | 6.023e-07 | 1.5045e-06 | 6.0839e-07 | 1.5197e-06
990 | feeder2_line148 | 3 | 99 | 6.0203e-07 | 1.5026e-06 | 6.0811e-07 | 1.5178e-06
990 | feeder2_line149 | 1 | 354.6 | 70.4095 | 70.4115 | 19.856 | 19.8566
990 | feeder2_line149 | 2 | 354.6 | 95.9515 | 95.9564 | 27.0591 | 27.0605
990 | feeder2_line149 | 3 | 354.6 | 97.4037 | 97.3972 | 27.4686 | 27.4668
990 | feeder2_line150 | 1 | 354.6 | 70.4096 | 70.4115 | 19.8561 | 19.8566
990 | feeder2_line150 | 2 | 354.6 | 98.5629 | 98.5677 | 27.7955 | 27.7969
990 | feeder2_line150 | 3 | 354.6 | 97.4038 | 97.3972 | 27.4686 | 27.4668
990 | feeder2_line151 | 1 | 99 | 9.5743e-06 | 1.757e-06 | 9.671e-06 | 1.7748e-06
990 | feeder2_line151 | 2 | 99 | 3.098 | 3.098 | 3.1293 | 3.1293
990 | feeder2_line151 | 3 | 99 | 9.8001e-06 | 1.7852e-06 | 9.8991e-06 | 1.8032e-06
990 | feeder2_line152 | 1 | 354.6 | 4.5081e-12 | 1.172e-06 | 1.2713e-12 | 3.3051e-07
990 | feeder2_line152 | 2 | 354.6 | 2.0941e-11 | 1.1906e-06 | 5.9056e-12 | 3.3575e-07
990 | feeder2_line152 | 3 | 354.6 | 1.188 | 1.188 | 0.33503 | 0.33503
990 | feeder2_line153 | 1 | 99 | 10.6494 | 10.6493 | 10.7569 | 10.7569
990 | feeder2_line153 | 2 | 99 | 4.8783e-08 | 5.9611e-07 | 4.9275e-08 | 6.0213e-07
990 | feeder2_line153 | 3 | 99 | 4.9802e-08 | 5.9535e-07 | 5.0305e-08 | 6.0137e-07
990 | feeder2_line154 | 1 | 99 | 5.6835e-07 | 8.717e-07 | 5.7409e-07 | 8.805e-07
990 | feeder2_line154 | 2 | 99 | 5.7848e-07 | 8.8704e-07 | 5.8433e-07 | 8.96e-07
990 | feeder2_line154 | 3 | 99 | 2.2195 | 2.2195 | 2.2419 | 2.2419
990 | feeder2_line155 | 1 | 99 | 80.7967 | 80.7987 | 81.6128 | 81.6149
990 | feeder2_line155 | 2 | 99 | 98.5628 | 98.5677 | 99.5584 | 99.5633
990 | feeder2_line155 | 3 | 99 | 99 | 98.9934 | 100 | 99.9934
990 | feeder2_line156 | 1 | 99 | 5.9393e-07 | 1.1473e-06 | 5.9993e-07 | 1.1589e-06
990 | feeder2_line156 | 2 | 99 | 1.9683 | 1.9683 | 1.9882 | 1.9881
990 | feeder2_line156 | 3 | 99 | 6.0233e-07 | 1.1657e-06 | 6.0842e-07 | 1.1775e-06
990 | feeder2_line157 | 1 | 99 | 2.5676e-08 | 2.4907e-07 | 2.5935e-08 | 2.5159e-07
990 | feeder2_line157 | 2 | 99 | 1.4841 | 1.4841 | 1.4991 | 1.4991
990 | feeder2_line157 | 3 | 99 | 2.4898e-08 | 2.5307e-07 | 2.515e-08 | 2.5562e-07
1020 | feeder2_line1 | 1 | 354.6 | 7.5642 | 7.5663 | 2.1332 | 2.1338
1020 | feeder2_line1 | 2 | 354.6 | 30.9538 | 30.9497 | 8.7292 | 8.7281
1020 | feeder2_line1 | 3 | 354.6 | 12.3625 | 12.3631 | 3.4863 | 3.4865
1020 | feeder2_line2 | 1 | 354.6 | 7.4092 | 7.4119 | 2.0895 | 2.0902
1020 | feeder2_line2 | 2 | 354.6 | 30.954 | 30.9497 | 8.7293 | 8.7281
1020 | feeder2_line2 | 3 | 354.6 | 12.3626 | 12.3631 | 3.4864 | 3.4865
1020 | feeder2_line3 | 1 | 80.1 | 1.3301 | 1.3301 | 1.6606 | 1.6606
1020 | feeder2_line3 | 2 | 80.1 | 5.7152e-07 | 1.0561e-06 | 7.1351e-07 | 1.3185e-06
1020 | feeder2_line3 | 3 | 80.1 | 5.7045e-07 | 1.0542e-06 | 7.1218e-07 | 1.3161e-06
1020 | feeder2_line4 | 1 | 354.6 | 7.4091 | 7.4119 | 2.0894 | 2.0902
1020 | feeder2_line4 | 2 | 354.6 | 31.0356 | 31.0312 | 8.7523 | 8.751
1020 | feeder2_line4 | 3 | 354.6 | 12.3626 | 12.3631 | 3.4864 | 3.4865
1020 | feeder2_line5 | 1 | 80.1 | 5.7044e-07 | 9.9537e-07 | 7.1216e-07 | 1.2427e-06
1020 | feeder2_line5 | 2 | 80.1 | 0.090084 | 0.090082 | 0.11246 | 0.11246
1020 | feeder2_line5 | 3 | 80.1 | 5.7044e-07 | 9.9539e-07 | 7.1216e-07 | 1.2427e-06
1020 | feeder2_line6 | 1 | 80.1 | 5.7042e-07 | 1.1709e-06 | 7.1214e-07 | 1.4618e-06
1020 | feeder2_line6 | 2 | 80.1 | 5.7158e-07 | 1.1733e-06 | 7.1359e-07 | 1.4647e-06
1020 | feeder2_line6 | 3 | 80.1 | 2.2212 | 2.2212 | 2.7731 | 2.7731
1020 | feeder2_line7 | 1 | 354.6 | 7.4092 | 7.4119 | 2.0894 | 2.0902
1020 | feeder2_line7 | 2 | 354.6 | 31.0357 | 31.0312 | 8.7523 | 8.751
1020 | feeder2_line7 | 3 | 354.6 | 12.2616 | 12.2626 | 3.4579 | 3.4582
1020 | feeder2_line8 | 1 | 80.1 | 0.6666 | 0.6666 | 0.8322 | 0.8322
1020 | feeder2_line8 | 2 | 80.1 | 5.7171e-07 | 1.1315e-06 | 7.1374e-07 | 1.4126e-06
1020 | feeder2_line8 | 3 | 80.1 | 5.7036e-07 | 1.1289e-06 | 7.1207e-07 | 1.4094e-06
1020 | feeder2_line9 | 1 | 354.6 | 7.466 | 7.4691 | 2.1055 | 2.1064
1020 | feeder2_line9 | 2 | 354.6 | 31.0357 | 31.0312 | 8.7523 | 8.751
1020 | feeder2_line9 | 3 | 354.6 | 12.2616 | 12.2626 | 3.4579 | 3.4582
1020 | feeder2_line10 | 1 | 80.1 | 8.4315e-07 | 1.4906e-06 | 1.0526e-06 | 1.8609e-06
1020 | feeder2_line10 | 2 | 80.1 | 0.66672 | 0.66672 | 0.83236 | 0.83236
1020 | feeder2_line10 | 3 | 80.1 | 8.4307e-07 | 1.4906e-06 | 1.0525e-06 | 1.8609e-06
1020 | feeder2_line11 | 1 | 354.6 | 7.4661 | 7.4691 | 2.1055 | 2.1064
1020 | feeder2_line11 | 2 | 354.6 | 31.6369 | 31.6322 | 8.9218 | 8.9205
1020 | feeder2_line11 | 3 | 354.6 | 12.2616 | 12.2626 | 3.4579 | 3.4582
1020 | feeder2_line12 | 1 | 80.1 | 5.4553e-07 | 9.887e-07 | 6.8106e-07 | 1.2343e-06
1020 | feeder2_line12 | 2 | 80.1 | 5.4707e-07 | 9.9115e-07 | 6.8298e-07 | 1.2374e-06
1020 | feeder2_line12 | 3 | 80.1 | 3.3323 | 3.3323 | 4.1602 | 4.1601
1020 | feeder2_line13 | 1 | 354.6 | 7.4662 | 7.4692 | 2.1055 | 2.1064
1020 | feeder2_line13 | 2 | 354.6 | 31.6369 | 31.6322 | 8.9218 | 8.9205
1020 | feeder2_line13 | 3 | 354.6 | 13.6753 | 13.6769 | 3.8566 | 3.857
1020 | feeder2_line14 | 1 | 80.1 | 0.22112 | 0.22112 | 0.27606 | 0.27606
1020 | feeder2_line14 | 2 | 80.1 | 2.9825e-07 | 6.4636e-07 | 3.7235e-07 | 8.0694e-07
1020 | feeder2_line14 | 3 | 80.1 | 2.9763e-07 | 6.447e-07 | 3.7157e-07 | 8.0486e-07
1020 | feeder2_line15 | 1 | 354.6 | 7.4885 | 7.4916 | 2.1118 | 2.1127
1020 | feeder2_line15 | 2 | 354.6 | 31.6369 | 31.6322 | 8.9219 | 8.9205
1020 | feeder2_line15 | 3 | 354.6 | 13.6753 | 13.6769 | 3.8566 | 3.857
1020 | feeder2_line16 | 1 | 80.1 | 5.703e-07 | 1.0274e-06 | 7.1199e-07 | 1.2827e-06
1020 | feeder2_line16 | 2 | 80.1 | 2.261 | 2.261 | 2.8228 | 2.8228
1020 | feeder2_line16 | 3 | 80.1 | 5.703e-07 | 1.0274e-06 | 7.1198e-07 | 1.2827e-06
1020 | feeder2_line17 | 1 | 354.6 | 7.4885 | 7.4916 | 2.1118 | 2.1127
1020 | feeder2_line17 | 2 | 354.6 | 33.6349 | 33.6301 | 9.4853 | 9.484
1020 | feeder2_line17 | 3 | 354.6 | 13.6754 | 13.6769 | 3.8566 | 3.857
1020 | feeder2_line18 | 1 | 80.1 | 5.4535e-07 | 7.3529e-07 | 6.8083e-07 | 9.1796e-07
1020 | feeder2_line18 | 2 | 80.1 | 5.4755e-07 | 7.3788e-07 | 6.8358e-07 | 9.2119e-07
1020 | feeder2_line18 | 3 | 80.1 | 1.6309 | 1.6309 | 2.0361 | 2.0361
1020 | feeder2_line19 | 1 | 354.6 | 7.4886 | 7.4916 | 2.1118 | 2.1127
1020 | feeder2_line19 | 2 | 354.6 | 33.6349 | 33.6301 | 9.4853 | 9.484
1020 | feeder2_line19 | 3 | 354.6 | 13.745 | 13.7467 | 3.8762 | 3.8767
1020 | feeder2_line20 | 1 | 99 | 5.4529e-07 | 8.8149e-07 | 5.508e-07 | 8.904e-07
1020 | feeder2_line20 | 2 | 99 | 5.4767e-07 | 8.8485e-07 | 5.5321e-07 | 8.9379e-07
1020 | feeder2_line20 | 3 | 99 | 2.9039 | 2.9039 | 2.9332 | 2.9332
1020 | feeder2_line21 | 1 | 354.6 | 7.4886 | 7.4916 | 2.1118 | 2.1127
1020 | feeder2_line21 | 2 | 354.6 | 33.6351 | 33.6301 | 9.4854 | 9.484
1020 | feeder2_line21 | 3 | 354.6 | 14.806 | 14.8081 | 4.1754 | 4.176
1020 | feeder2_line22 | 1 | 99 | 5.701e-07 | 1.0105e-06 | 5.7585e-07 | 1.0207e-06
1020 | feeder2_line22 | 2 | 99 | 3.2524 | 3.2524 | 3.2852 | 3.2852
1020 | feeder2_line22 | 3 | 99 | 5.7016e-07 | 1.0106e-06 | 5.7592e-07 | 1.0208e-06
1020 | feeder2_line23 | 1 | 99 | 5.7006e-07 | 9.4586e-07 | 5.7582e-07 | 9.5541e-07
1020 | feeder2_line23 | 2 | 99 | 5.7236e-07 | 9.4963e-07 | 5.7814e-07 | 9.5922e-07
1020 | feeder2_line23 | 3 | 99 | 20.8662 | 20.8661 | 21.077 | 21.0769
1020 | feeder2_line24 | 1 | 354.6 | 7.4886 | 7.4916 | 2.1119 | 2.1127
1020 | feeder2_line24 | 2 | 354.6 | 36.5196 | 36.5145 | 10.2988 | 10.2974
1020 | feeder2_line24 | 3 | 354.6 | 33.0968 | 33.0994 | 9.3336 | 9.3343
1020 | feeder2_line25 | 1 | 99 | 3.2541 | 3.2541 | 3.2869 | 3.2869
1020 | feeder2_line25 | 2 | 99 | 4.9254e-08 | 6.9054e-07 | 4.9752e-08 | 6.9752e-07
1020 | feeder2_line25 | 3 | 99 | 4.9979e-08 | 6.8789e-07 | 5.0483e-08 | 6.9484e-07
1020 | feeder2_line26 | 1 | 99 | 0.085654 | 0.085656 | 0.086519 | 0.086521
1020 | feeder2_line26 | 2 | 99 | 5.4787e-07 | 8.5554e-07 | 5.534e-07 | 8.6419e-07
1020 | feeder2_line26 | 3 | 99 | 5.4527e-07 | 8.5225e-07 | 5.5078e-07 | 8.6086e-07
1020 | feeder2_line27 | 1 | 354.6 | 8.4031 | 8.4069 | 2.3697 | 2.3708
1020 | feeder2_line27 | 2 | 354.6 | 36.5196 | 36.5145 | 10.2988 | 10.2974
1020 | feeder2_line27 | 3 | 354.6 | 33.0968 | 33.0994 | 9.3336 | 9.3343
1020 | feeder2_line28 | 1 | 99 | 2.5263e-06 | 7.0701e-07 | 2.5518e-06 | 7.1415e-07
1020 | feeder2_line28 | 2 | 99 | 0.077045 | 0.077042 | 0.077823 | 0.077821
1020 | feeder2_line28 | 3 | 99 | 2.5272e-06 | 7.0764e-07 | 2.5527e-06 | 7.1478e-07
1020 | feeder2_line29 | 1 | 354.6 | 8.4031 | 8.4069 | 2.3697 | 2.3708
1020 | feeder2_line29 | 2 | 354.6 | 36.5915 | 36.5864 | 10.3191 | 10.3177
1020 | feeder2_line29 | 3 | 354.6 | 33.0969 | 33.0994 | 9.3336 | 9.3343
1020 | feeder2_line30 | 1 | 266.4 | 14.6381 | 14.6378 | 5.4948 | 5.4947
1020 | feeder2_line30 | 2 | 266.4 | 5.1262 | 5.1261 | 1.9243 | 1.9242
1020 | feeder2_line30 | 3 | 266.4 | 10.3266 | 10.3264 | 3.8763 | 3.8763
1020 | feeder2_line31 | 1 | 354.6 | 19.6833 | 19.6867 | 5.5508 | 5.5518
1020 | feeder2_line31 | 2 | 354.6 | 40.3661 | 40.3603 | 11.3836 | 11.3819
1020 | feeder2_line31 | 3 | 354.6 | 42.4301 | 42.4324 | 11.9656 | 11.9663
1020 | feeder2_line32 | 1 | 354.6 | 19.6833 | 19.6867 | 5.5509 | 5.5518
1020 | feeder2_line32 | 2 | 354.6 | 40.4407 | 40.4348 | 11.4046 | 11.4029
1020 | feeder2_line32 | 3 | 354.6 | 42.4302 | 42.4324 | 11.9656 | 11.9663
1020 | feeder2_line33 | 1 | 99 | 4.9813e-08 | 6.8192e-07 | 5.0317e-08 | 6.8881e-07
1020 | feeder2_line33 | 2 | 99 | 0.077103 | 0.077098 | 0.077882 | 0.077877
1020 | feeder2_line33 | 3 | 99 | 5.0008e-08 | 6.8313e-07 | 5.0513e-08 | 6.9003e-07
1020 | feeder2_line34 | 1 | 354.6 | 19.6833 | 19.6867 | 5.5509 | 5.5518
1020 | feeder2_line34 | 2 | 354.6 | 40.4407 | 40.4348 | 11.4046 | 11.4029
1020 | feeder2_line34 | 3 | 354.6 | 42.5157 | 42.518 | 11.9898 | 11.9904
1020 | feeder2_line35 | 1 | 99 | 2.9735e-07 | 7.5515e-07 | 3.0035e-07 | 7.6278e-07
1020 | feeder2_line35 | 2 | 99 | 2.9884e-07 | 7.5948e-07 | 3.0186e-07 | 7.6716e-07
1020 | feeder2_line35 | 3 | 99 | 0.086019 | 0.086022 | 0.086888 | 0.086891
1020 | feeder2_line36 | 1 | 354.6 | 24.1819 | 24.1853 | 6.8195 | 6.8204
1020 | feeder2_line36 | 2 | 354.6 | 40.4406 | 40.4348 | 11.4046 | 11.4029
1020 | feeder2_line36 | 3 | 354.6 | 42.5157 | 42.518 | 11.9898 | 11.9904
1020 | feeder2_line37 | 1 | 99 | 4.7045 | 4.7046 | 4.752 | 4.7521
1020 | feeder2_line37 | 2 | 99 | 2.9887e-07 | 8.4043e-07 | 3.0189e-07 | 8.4892e-07
1020 | feeder2_line37 | 3 | 99 | 2.9797e-07 | 8.3725e-07 | 3.0098e-07 | 8.457e-07
1020 | feeder2_line38 | 1 | 99 | 3.222e-07 | 7.7098e-07 | 3.2546e-07 | 7.7877e-07
1020 | feeder2_line38 | 2 | 99 | 1.327 | 1.327 | 1.3404 | 1.3404
1020 | feeder2_line38 | 3 | 99 | 3.228e-07 | 7.7218e-07 | 3.2606e-07 | 7.7998e-07
1020 | feeder2_line39 | 1 | 266.4 | 14.6381 | 14.6378 | 5.4948 | 5.4947
1020 | feeder2_line39 | 2 | 266.4 | 4.062 | 4.0618 | 1.5248 | 1.5247
1020 | feeder2_line39 | 3 | 266.4 | 10.3266 | 10.3264 | 3.8764 | 3.8763
1020 | feeder2_line40 | 1 | 354.6 | 27.3142 | 27.3175 | 7.7028 | 7.7038
1020 | feeder2_line40 | 2 | 354.6 | 40.4407 | 40.4348 | 11.4046 | 11.4029
1020 | feeder2_line40 | 3 | 354.6 | 42.5157 | 42.518 | 11.9898 | 11.9904
1020 | feeder2_line41 | 1 | 99 | 3.2543 | 3.2543 | 3.2872 | 3.2872
1020 | feeder2_line41 | 2 | 99 | 4.9182e-08 | 7.3443e-07 | 4.9679e-08 | 7.4184e-07
1020 | feeder2_line41 | 3 | 99 | 5.0014e-08 | 7.3166e-07 | 5.0519e-08 | 7.3905e-07
1020 | feeder2_line42 | 1 | 99 | 2.9727e-07 | 7.4407e-07 | 3.0027e-07 | 7.5158e-07
1020 | feeder2_line42 | 2 | 99 | 2.9874e-07 | 7.483e-07 | 3.0176e-07 | 7.5586e-07
1020 | feeder2_line42 | 3 | 99 | 1.658 | 1.658 | 1.6747 | 1.6747
1020 | feeder2_line43 | 1 | 266.4 | 14.638 | 14.6378 | 5.4948 | 5.4947
1020 | feeder2_line43 | 2 | 266.4 | 4.062 | 4.0618 | 1.5248 | 1.5247
1020 | feeder2_line43 | 3 | 266.4 | 8.7465 | 8.7464 | 3.2832 | 3.2832
1020 | feeder2_line44 | 1 | 354.6 | 27.3142 | 27.3175 | 7.7028 | 7.7038
1020 | feeder2_line44 | 2 | 354.6 | 40.4407 | 40.4348 | 11.4046 | 11.4029
1020 | feeder2_line44 | 3 | 354.6 | 45.0526 | 45.0549 | 12.7052 | 12.7058
1020 | feeder2_line45 | 1 | 99 | 4.9853e-08 | 5.7581e-07 | 5.0357e-08 | 5.8163e-07
1020 | feeder2_line45 | 2 | 99 | 4.9181e-08 | 5.7923e-07 | 4.9678e-08 | 5.8508e-07
1020 | feeder2_line45 | 3 | 99 | 2.9051 | 2.9051 | 2.9345 | 2.9345
1020 | feeder2_line46 | 1 | 99 | 5.6964e-07 | 1.3489e-06 | 5.7539e-07 | 1.3625e-06
1020 | feeder2_line46 | 2 | 99 | 5.729e-07 | 1.3565e-06 | 5.7869e-07 | 1.3702e-06
1020 | feeder2_line46 | 3 | 99 | 3.9255 | 3.9255 | 3.9651 | 3.9651
1020 | feeder2_line47 | 1 | 266.4 | 14.6381 | 14.6378 | 5.4948 | 5.4947
1020 | feeder2_line47 | 2 | 266.4 | 4.062 | 4.0618 | 1.5248 | 1.5247
1020 | feeder2_line47 | 3 | 266.4 | 5.0982 | 5.0979 | 1.9137 | 1.9136
1020 | feeder2_line48 | 1 | 99 | 2.0551 | 2.0551 | 2.0758 | 2.0758
1020 | feeder2_line48 | 2 | 99 | 4.9163e-08 | 7.3037e-07 | 4.9659e-08 | 7.3775e-07
1020 | feeder2_line48 | 3 | 99 | 4.9997e-08 | 7.2741e-07 | 5.0502e-08 | 7.3476e-07
1020 | feeder2_line49 | 1 | 266.4 | 12.6042 | 12.604 | 4.7313 | 4.7312
1020 | feeder2_line49 | 2 | 266.4 | 4.062 | 4.0618 | 1.5248 | 1.5247
1020 | feeder2_line49 | 3 | 266.4 | 5.0981 | 5.0979 | 1.9137 | 1.9136
1020 | feeder2_line50 | 1 | 99 | 5.6957e-07 | 1.2274e-06 | 5.7532e-07 | 1.2398e-06
1020 | feeder2_line50 | 2 | 99 | 2.2143 | 2.2143 | 2.2367 | 2.2366
1020 | feeder2_line50 | 3 | 99 | 5.7054e-07 | 1.2295e-06 | 5.763e-07 | 1.2419e-06
1020 | feeder2_line51 | 1 | 99 | 1.5333 | 1.5334 | 1.5488 | 1.5489
1020 | feeder2_line51 | 2 | 99 | 5.729e-07 | 1.3402e-06 | 5.7869e-07 | 1.3537e-06
1020 | feeder2_line51 | 3 | 99 | 5.7054e-07 | 1.3348e-06 | 5.763e-07 | 1.3483e-06
1020 | feeder2_line52 | 1 | 266.4 | 11.0782 | 11.0781 | 4.1585 | 4.1584
1020 | feeder2_line52 | 2 | 266.4 | 1.8641 | 1.864 | 0.69972 | 0.69969
1020 | feeder2_line52 | 3 | 266.4 | 5.098 | 5.0979 | 1.9137 | 1.9136
1020 | feeder2_line53 | 1 | 99 | 5.4466e-07 | 7.491e-07 | 5.5017e-07 | 7.5667e-07
1020 | feeder2_line53 | 2 | 99 | 1.864 | 1.864 | 1.8828 | 1.8828
1020 | feeder2_line53 | 3 | 99 | 5.4554e-07 | 7.504e-07 | 5.5105e-07 | 7.5798e-07
1020 | feeder2_line54 | 1 | 266.4 | 11.0781 | 11.0781 | 4.1584 | 4.1584
1020 | feeder2_line54 | 2 | 266.4 | 8.5388e-05 | 4.6214e-06 | 3.2052e-05 | 1.7348e-06
1020 | feeder2_line54 | 3 | 266.4 | 5.0979 | 5.0979 | 1.9136 | 1.9136
1020 | feeder2_line55 | 1 | 99 | 2.1655 | 2.1655 | 2.1874 | 2.1874
1020 | feeder2_line55 | 2 | 99 | 4.9189e-08 | 7.2989e-07 | 4.9686e-08 | 7.3726e-07
1020 | feeder2_line55 | 3 | 99 | 5.0025e-08 | 7.2726e-07 | 5.0531e-08 | 7.3461e-07
1020 | feeder2_line56 | 1 | 354.6 | 29.2184 | 29.2216 | 8.2398 | 8.2407
1020 | feeder2_line56 | 2 | 354.6 | 40.4407 | 40.4348 | 11.4046 | 11.4029
1020 | feeder2_line56 | 3 | 354.6 | 45.0526 | 45.0549 | 12.7052 | 12.7058
1020 | feeder2_line57 | 1 | 99 | 7.4704e-07 | 1.5343e-06 | 7.5458e-07 | 1.5498e-06
1020 | feeder2_line57 | 2 | 99 | 7.3735e-07 | 1.5433e-06 | 7.4479e-07 | 1.5589e-06
1020 | feeder2_line57 | 3 | 99 | 5.0979 | 5.0979 | 5.1494 | 5.1494
1020 | feeder2_line58 | 1 | 266.4 | 11.0782 | 11.0781 | 4.1585 | 4.1584
1020 | feeder2_line58 | 2 | 266.4 | 1.8952e-05 | 2.683e-06 | 7.1141e-06 | 1.0071e-06
1020 | feeder2_line58 | 3 | 266.4 | 1.886e-05 | 2.6729e-06 | 7.0796e-06 | 1.0033e-06
1020 | feeder2_line59 | 1 | 99 | 4.9802e-08 | 5.3334e-07 | 5.0305e-08 | 5.3873e-07
1020 | feeder2_line59 | 2 | 99 | 4.9154e-08 | 5.3648e-07 | 4.9651e-08 | 5.419e-07
1020 | feeder2_line59 | 3 | 99 | 1.8049 | 1.8049 | 1.8231 | 1.8231
1020 | feeder2_line60 | 1 | 99 | 2.9721e-07 | 8.0604e-07 | 3.0021e-07 | 8.1418e-07
1020 | feeder2_line60 | 2 | 99 | 2.9874e-07 | 8.1077e-07 | 3.0176e-07 | 8.1896e-07
1020 | feeder2_line60 | 3 | 99 | 3.3324 | 3.3324 | 3.3661 | 3.3661
1020 | feeder2_line61 | 1 | 266.4 | 1.6994 | 1.6996 | 0.63792 | 0.63799
1020 | feeder2_line61 | 2 | 266.4 | 2.8488 | 2.8489 | 1.0694 | 1.0694
1020 | feeder2_line61 | 3 | 266.4 | 5.9179 | 5.9181 | 2.2214 | 2.2215
1020 | feeder2_line62 | 1 | 354.6 | 30.2538 | 30.2571 | 8.5318 | 8.5327
1020 | feeder2_line62 | 2 | 354.6 | 42.9102 | 42.9044 | 12.101 | 12.0994
1020 | feeder2_line62 | 3 | 354.6 | 50.847 | 50.8495 | 14.3392 | 14.3399
1020 | feeder2_line63 | 1 | 99 | 1.4044 | 1.4044 | 1.4186 | 1.4186
1020 | feeder2_line63 | 2 | 99 | 5.7292e-07 | 1.219e-06 | 5.7871e-07 | 1.2313e-06
1020 | feeder2_line63 | 3 | 99 | 5.7054e-07 | 1.214e-06 | 5.7631e-07 | 1.2263e-06
1020 | feeder2_line64 | 1 | 99 | 10.1526 | 10.1525 | 10.2551 | 10.255
1020 | feeder2_line64 | 2 | 99 | 1.9064e-12 | 3.2111e-07 | 1.9256e-12 | 3.2436e-07
1020 | feeder2_line64 | 3 | 99 | 1.9064e-12 | 3.198e-07 | 1.9256e-12 | 3.2303e-07
1020 | feeder2_line65 | 1 | 99 | 4.9915e-08 | 6.3736e-07 | 5.0419e-08 | 6.438e-07
1020 | feeder2_line65 | 2 | 99 | 0.089728 | 0.089721 | 0.090634 | 0.090628
1020 | feeder2_line65 | 3 | 99 | 5.0043e-08 | 6.3915e-07 | 5.0549e-08 | 6.456e-07
1020 | feeder2_line66 | 1 | 354.6 | 30.2537 | 30.2571 | 8.5318 | 8.5327
1020 | feeder2_line66 | 2 | 354.6 | 42.9975 | 42.9918 | 12.1256 | 12.124
1020 | feeder2_line66 | 3 | 354.6 | 50.8469 | 50.8495 | 14.3392 | 14.3399
1020 | feeder2_line67 | 1 | 99 | 2.4939e-08 | 3.6027e-07 | 2.5191e-08 | 3.6391e-07
1020 | feeder2_line67 | 2 | 99 | 2.4598e-08 | 3.6247e-07 | 2.4847e-08 | 3.6613e-07
1020 | feeder2_line67 | 3 | 99 | 3.2535 | 3.2535 | 3.2864 | 3.2864
1020 | feeder2_line68 | 1 | 266.4 | 1.6995 | 1.6996 | 0.63794 | 0.63799
1020 | feeder2_line68 | 2 | 266.4 | 2.8488 | 2.8489 | 1.0694 | 1.0694
1020 | feeder2_line68 | 3 | 266.4 | 2.6905 | 2.6907 | 1.01 | 1.01
1020 | feeder2_line69 | 1 | 99 | 13.7225 | 13.7225 | 13.8611 | 13.8611
1020 | feeder2_line69 | 2 | 99 | 2.5484e-06 | 6.6578e-07 | 2.5742e-06 | 6.7251e-07
1020 | feeder2_line69 | 3 | 99 | 2.5334e-06 | 6.636e-07 | 2.559e-06 | 6.7031e-07
1020 | feeder2_line70 | 1 | 354.6 | 43.5005 | 43.5038 | 12.2675 | 12.2684
1020 | feeder2_line70 | 2 | 354.6 | 42.9974 | 42.9918 | 12.1256 | 12.124
1020 | feeder2_line70 | 3 | 354.6 | 50.8468 | 50.8495 | 14.3392 | 14.3399
1020 | feeder2_line71 | 1 | 99 | 4.9925e-08 | 7.1115e-07 | 5.0429e-08 | 7.1833e-07
1020 | feeder2_line71 | 2 | 99 | 1.6126 | 1.6125 | 1.6289 | 1.6288
1020 | feeder2_line71 | 3 | 99 | 5.005e-08 | 7.1321e-07 | 5.0556e-08 | 7.2042e-07
1020 | feeder2_line72 | 1 | 354.6 | 43.5006 | 43.5038 | 12.2675 | 12.2684
1020 | feeder2_line72 | 2 | 354.6 | 44.539 | 44.5331 | 12.5603 | 12.5587
1020 | feeder2_line72 | 3 | 354.6 | 50.8469 | 50.8495 | 14.3392 | 14.3399
1020 | feeder2_line73 | 1 | 99 | 5.9491e-07 | 1.5253e-06 | 6.0091e-07 | 1.5407e-06
1020 | feeder2_line73 | 2 | 99 | 0.077046 | 0.07704 | 0.077824 | 0.077818
1020 | feeder2_line73 | 3 | 99 | 5.9642e-07 | 1.5291e-06 | 6.0244e-07 | 1.5446e-06
1020 | feeder2_line74 | 1 | 99 | 4.9889e-08 | 4.5492e-07 | 5.0393e-08 | 4.5952e-07
1020 | feeder2_line74 | 2 | 99 | 2.6889 | 2.6889 | 2.7161 | 2.716
1020 | feeder2_line74 | 3 | 99 | 5.0035e-08 | 4.5607e-07 | 5.054e-08 | 4.6068e-07
1020 | feeder2_line75 | 1 | 266.4 | 1.6996 | 1.6996 | 0.63797 | 0.63799
1020 | feeder2_line75 | 2 | 266.4 | 0.089677 | 0.089707 | 0.033662 | 0.033674
1020 | feeder2_line75 | 3 | 266.4 | 2.6906 | 2.6907 | 1.01 | 1.01
1020 | feeder2_line76 | 1 | 99 | 1.6996 | 1.6996 | 1.7168 | 1.7168
1020 | feeder2_line76 | 2 | 99 | 8.4789e-07 | 1.5829e-06 | 8.5645e-07 | 1.5989e-06
1020 | feeder2_line76 | 3 | 99 | 8.4457e-07 | 1.5774e-06 | 8.531e-07 | 1.5933e-06
1020 | feeder2_line77 | 1 | 99 | 2.4945e-08 | 5.7168e-07 | 2.5197e-08 | 5.7746e-07
1020 | feeder2_line77 | 2 | 99 | 2.4602e-08 | 5.7515e-07 | 2.485e-08 | 5.8096e-07
1020 | feeder2_line77 | 3 | 99 | 2.6907 | 2.6907 | 2.7178 | 2.7178
1020 | feeder2_line78 | 1 | 266.4 | 4.8232e-12 | 9.4832e-07 | 1.8105e-12 | 3.5598e-07
1020 | feeder2_line78 | 2 | 266.4 | 0.089709 | 0.089706 | 0.033675 | 0.033674
1020 | feeder2_line78 | 3 | 266.4 | 2.7583e-12 | 9.5072e-07 | 1.0354e-12 | 3.5688e-07
1020 | feeder2_line79 | 1 | 354.6 | 12.6027 | 12.6022 | 3.5541 | 3.5539
1020 | feeder2_line79 | 2 | 354.6 | 19.2993 | 19.2991 | 5.4426 | 5.4425
1020 | feeder2_line79 | 3 | 354.6 | 13.8992 | 13.899 | 3.9197 | 3.9196
1020 | feeder2_line80 | 1 | 354.6 | 55.9316 | 55.9341 | 15.7732 | 15.7739
1020 | feeder2_line80 | 2 | 354.6 | 61.8215 | 61.815 | 17.4341 | 17.4323
1020 | feeder2_line80 | 3 | 354.6 | 63.895 | 63.8972 | 18.0189 | 18.0195
1020 | feeder2_line81 | 1 | 354.6 | 55.9316 | 55.9341 | 15.7732 | 15.7739
1020 | feeder2_line81 | 2 | 354.6 | 61.8214 | 61.815 | 17.4341 | 17.4323
1020 | feeder2_line81 | 3 | 354.6 | 74.5711 | 74.5732 | 21.0297 | 21.0302
1020 | feeder2_line82 | 1 | 354.6 | 1.0873e-11 | 7.297e-07 | 3.0663e-12 | 2.0578e-07
1020 | feeder2_line82 | 2 | 354.6 | 1.9314e-11 | 7.3371e-07 | 5.4468e-12 | 2.0691e-07
1020 | feeder2_line82 | 3 | 354.6 | 10.6762 | 10.6761 | 3.0108 | 3.0107
1020 | feeder2_line83 | 1 | 354.6 | 55.9318 | 55.9341 | 15.7732 | 15.7739
1020 | feeder2_line83 | 2 | 354.6 | 62.6725 | 62.6658 | 17.6741 | 17.6723
1020 | feeder2_line83 | 3 | 354.6 | 74.5713 | 74.5732 | 21.0297 | 21.0302
1020 | feeder2_line84 | 1 | 354.6 | 1.4342e-11 | 1.2898e-06 | 4.0447e-12 | 3.6372e-07
1020 | feeder2_line84 | 2 | 354.6 | 1.4136 | 1.4136 | 0.39865 | 0.39864
1020 | feeder2_line84 | 3 | 354.6 | 1.4091e-11 | 1.2936e-06 | 3.9737e-12 | 3.6481e-07
1020 | feeder2_line85 | 1 | 99 | 1.324 | 1.324 | 1.3374 | 1.3374
1020 | feeder2_line85 | 2 | 99 | 4.9251e-08 | 4.6306e-07 | 4.9748e-08 | 4.6774e-07
1020 | feeder2_line85 | 3 | 99 | 5.0086e-08 | 4.6168e-07 | 5.0592e-08 | 4.6634e-07
1020 | feeder2_line86 | 1 | 354.6 | 56.7461 | 56.7483 | 16.0029 | 16.0035
1020 | feeder2_line86 | 2 | 354.6 | 62.6726 | 62.6658 | 17.6742 | 17.6723
1020 | feeder2_line86 | 3 | 354.6 | 74.5714 | 74.5732 | 21.0297 | 21.0302
1020 | feeder2_line87 | 1 | 354.6 | 56.7463 | 56.7483 | 16.0029 | 16.0035
1020 | feeder2_line87 | 2 | 354.6 | 66.6072 | 66.6002 | 18.7838 | 18.7818
1020 | feeder2_line87 | 3 | 354.6 | 74.6533 | 74.655 | 21.0528 | 21.0533
1020 | feeder2_line88 | 1 | 354.6 | 0.00011329 | 3.3428e-06 | 3.195e-05 | 9.427e-07
1020 | feeder2_line88 | 2 | 354.6 | 4.9707 | 4.9705 | 1.4018 | 1.4017
1020 | feeder2_line88 | 3 | 354.6 | 0.082102 | 0.081991 | 0.023153 | 0.023122
1020 | feeder2_line89 | 1 | 354.6 | 56.744 | 56.7483 | 16.0023 | 16.0035
1020 | feeder2_line89 | 2 | 354.6 | 67.608 | 67.6032 | 19.066 | 19.0646
1020 | feeder2_line89 | 3 | 354.6 | 74.6511 | 74.655 | 21.0522 | 21.0533
1020 | feeder2_line90 | 1 | 354.6 | 0.00071872 | 2.018e-06 | 0.00020269 | 5.6909e-07
1020 | feeder2_line90 | 2 | 354.6 | 1.4667 | 1.4666 | 0.41361 | 0.4136
1020 | feeder2_line90 | 3 | 354.6 | 0.00072051 | 2.0257e-06 | 0.00020319 | 5.7125e-07
1020 | feeder2_line91 | 1 | 354.6 | 56.7439 | 56.7483 | 16.0022 | 16.0035
1020 | feeder2_line91 | 2 | 354.6 | 67.6079 | 67.6032 | 19.066 | 19.0646
1020 | feeder2_line91 | 3 | 354.6 | 77.9913 | 77.9952 | 21.9941 | 21.9953
1020 | feeder2_line92 | 1 | 354.6 | 4.6849e-12 | 1.0181e-06 | 1.3212e-12 | 2.871e-07
1020 | feeder2_line92 | 2 | 354.6 | 1.4243e-11 | 1.0238e-06 | 4.0166e-12 | 2.8872e-07
1020 | feeder2_line92 | 3 | 354.6 | 3.3406 | 3.3405 | 0.94207 | 0.94206
1020 | feeder2_line93 | 1 | 99 | 2.5004e-08 | 3.3978e-07 | 2.5256e-08 | 3.4321e-07
1020 | feeder2_line93 | 2 | 99 | 1.4137 | 1.4137 | 1.428 | 1.428
1020 | feeder2_line93 | 3 | 99 | 2.5053e-08 | 3.4091e-07 | 2.5306e-08 | 3.4435e-07
1020 | feeder2_line94 | 1 | 354.6 | 2.5e-06 | 1.6545e-06 | 7.0503e-07 | 4.6659e-07
1020 | feeder2_line94 | 2 | 354.6 | 0.081654 | 0.081634 | 0.023027 | 0.023021
1020 | feeder2_line94 | 3 | 354.6 | 2.5053e-06 | 1.66e-06 | 7.0651e-07 | 4.6813e-07
1020 | feeder2_line95 | 1 | 99 | 3.5393e-06 | 2.5921e-06 | 3.575e-06 | 2.6183e-06
1020 | feeder2_line95 | 2 | 99 | 4.9706 | 4.9705 | 5.0208 | 5.0207
1020 | feeder2_line95 | 3 | 99 | 3.5562e-06 | 2.6004e-06 | 3.5921e-06 | 2.6266e-06
1020 | feeder2_line96 | 1 | 354.6 | 0.00012029 | 6.1781e-07 | 3.3922e-05 | 1.7423e-07
1020 | feeder2_line96 | 2 | 354.6 | 0.0001211 | 6.2147e-07 | 3.4151e-05 | 1.7526e-07
1020 | feeder2_line96 | 3 | 354.6 | 0.082087 | 0.081991 | 0.023149 | 0.023122
1020 | feeder2_line97 | 1 | 354.6 | 59.2439 | 59.2481 | 16.7073 | 16.7084
1020 | feeder2_line97 | 2 | 354.6 | 67.6081 | 67.6032 | 19.066 | 19.0646
1020 | feeder2_line97 | 3 | 354.6 | 77.9914 | 77.9952 | 21.9942 | 21.9953
1020 | feeder2_line98 | 1 | 354.6 | 2.5017 | 2.5 | 0.70549 | 0.70503
1020 | feeder2_line98 | 2 | 354.6 | 0.001709 | 6.2229e-07 | 0.00048194 | 1.7549e-07
1020 | feeder2_line98 | 3 | 354.6 | 0.0016869 | 6.1841e-07 | 0.00047573 | 1.744e-07
1020 | feeder2_line99 | 1 | 99 | 2.4989e-08 | 4.4422e-07 | 2.5242e-08 | 4.4871e-07
1020 | feeder2_line99 | 2 | 99 | 2.4632e-08 | 4.4689e-07 | 2.4881e-08 | 4.5141e-07
1020 | feeder2_line99 | 3 | 99 | 0.081996 | 0.081991 | 0.082825 | 0.082819
1020 | feeder2_line100 | 1 | 99 | 2.5 | 2.5 | 2.5252 | 2.5253
1020 | feeder2_line100 | 2 | 99 | 2.4636e-08 | 6.1374e-07 | 2.4885e-08 | 6.1994e-07
1020 | feeder2_line100 | 3 | 99 | 2.5056e-08 | 6.1208e-07 | 2.5309e-08 | 6.1827e-07
1020 | feeder2_line101 | 1 | 354.6 | 0.082696 | 0.082304 | 0.023321 | 0.02321
1020 | feeder2_line101 | 2 | 354.6 | 19.2993 | 19.2991 | 5.4426 | 5.4425
1020 | feeder2_line101 | 3 | 354.6 | 13.8992 | 13.899 | 3.9197 | 3.9196
1020 | feeder2_line102 | 1 | 99 | 12.5221 | 12.522 | 12.6485 | 12.6484
1020 | feeder2_line102 | 2 | 99 | 2.3402e-06 | 8.7733e-07 | 2.3638e-06 | 8.8619e-07
1020 | feeder2_line102 | 3 | 99 | 2.3189e-06 | 8.7465e-07 | 2.3424e-06 | 8.8349e-07
1020 | feeder2_line103 | 1 | 99 | 5.4536e-07 | 7.9833e-07 | 5.5087e-07 | 8.064e-07
1020 | feeder2_line103 | 2 | 99 | 9.9528 | 9.953 | 10.0534 | 10.0535
1020 | feeder2_line103 | 3 | 99 | 5.4684e-07 | 8.0052e-07 | 5.5237e-07 | 8.0861e-07
1020 | feeder2_line104 | 1 | 354.6 | 0.082591 | 0.082304 | 0.023291 | 0.02321
1020 | feeder2_line104 | 2 | 354.6 | 9.9647 | 9.9645 | 2.8101 | 2.8101
1020 | feeder2_line104 | 3 | 354.6 | 13.8991 | 13.899 | 3.9197 | 3.9196
1020 | feeder2_line105 | 1 | 99 | 2.5273e-06 | 7.3459e-07 | 2.5528e-06 | 7.4201e-07
1020 | feeder2_line105 | 2 | 99 | 2.5483e-06 | 7.3882e-07 | 2.574e-06 | 7.4629e-07
1020 | feeder2_line105 | 3 | 99 | 1.632 | 1.632 | 1.6485 | 1.6485
1020 | feeder2_line106 | 1 | 354.6 | 0.082536 | 0.082304 | 0.023276 | 0.02321
1020 | feeder2_line106 | 2 | 354.6 | 9.9647 | 9.9645 | 2.8101 | 2.8101
1020 | feeder2_line106 | 3 | 354.6 | 12.3228 | 12.3227 | 3.4751 | 3.4751
1020 | feeder2_line107 | 1 | 99 | 3.2258e-07 | 8.9524e-07 | 3.2584e-07 | 9.0428e-07
1020 | feeder2_line107 | 2 | 99 | 6.0971 | 6.0972 | 6.1587 | 6.1588
1020 | feeder2_line107 | 3 | 99 | 3.2344e-07 | 8.9748e-07 | 3.2671e-07 | 9.0655e-07
1020 | feeder2_line108 | 1 | 354.6 | 0.082525 | 0.082304 | 0.023273 | 0.02321
1020 | feeder2_line108 | 2 | 354.6 | 3.8997 | 3.8995 | 1.0997 | 1.0997
1020 | feeder2_line108 | 3 | 354.6 | 12.3228 | 12.3227 | 3.4751 | 3.4751
1020 | feeder2_line109 | 1 | 354.6 | 70.7346 | 70.7375 | 19.9477 | 19.9485
1020 | feeder2_line109 | 2 | 354.6 | 67.6093 | 67.6032 | 19.0664 | 19.0646
1020 | feeder2_line109 | 3 | 354.6 | 77.9926 | 77.9952 | 21.9945 | 21.9953
1020 | feeder2_line110 | 1 | 99 | 11.5271 | 11.5262 | 11.6435 | 11.6426
1020 | feeder2_line110 | 2 | 99 | 0.00080581 | 9.093e-07 | 0.00081395 | 9.1848e-07
1020 | feeder2_line110 | 3 | 99 | 0.00080111 | 9.0621e-07 | 0.0008092 | 9.1536e-07
1020 | feeder2_line111 | 1 | 99 | 2.498e-08 | 3.7939e-07 | 2.5232e-08 | 3.8322e-07
1020 | feeder2_line111 | 2 | 99 | 1.6969 | 1.6968 | 1.714 | 1.714
1020 | feeder2_line111 | 3 | 99 | 2.5046e-08 | 3.806e-07 | 2.5299e-08 | 3.8444e-07
1020 | feeder2_line112 | 1 | 99 | 3.2278e-07 | 9.1169e-07 | 3.2604e-07 | 9.2089e-07
1020 | feeder2_line112 | 2 | 99 | 3.2886 | 3.2885 | 3.3218 | 3.3218
1020 | feeder2_line112 | 3 | 99 | 3.2379e-07 | 9.146e-07 | 3.2706e-07 | 9.2384e-07
1020 | feeder2_line113 | 1 | 99 | 1.4126 | 1.4125 | 1.4268 | 1.4268
1020 | feeder2_line113 | 2 | 99 | 3.2429e-07 | 9.0514e-07 | 3.2756e-07 | 9.1428e-07
1020 | feeder2_line113 | 3 | 99 | 3.2413e-07 | 9.0278e-07 | 3.2741e-07 | 9.119e-07
1020 | feeder2_line114 | 1 | 99 | 9.8684 | 9.8683 | 9.9681 | 9.968
1020 | feeder2_line114 | 2 | 99 | 2.4614e-08 | 4.3626e-07 | 2.4862e-08 | 4.4066e-07
1020 | feeder2_line114 | 3 | 99 | 2.5026e-08 | 4.3493e-07 | 2.5279e-08 | 4.3932e-07
1020 | feeder2_line115 | 1 | 99 | 2.4938e-08 | 5.587e-07 | 2.519e-08 | 5.6434e-07
1020 | feeder2_line115 | 2 | 99 | 2.6424 | 2.6424 | 2.6691 | 2.6691
1020 | feeder2_line115 | 3 | 99 | 2.5043e-08 | 5.5999e-07 | 2.5295e-08 | 5.6565e-07
1020 | feeder2_line116 | 1 | 354.6 | 0.082531 | 0.082303 | 0.023274 | 0.02321
1020 | feeder2_line116 | 2 | 354.6 | 1.5625 | 1.5622 | 0.44063 | 0.44056
1020 | feeder2_line116 | 3 | 354.6 | 12.3228 | 12.3227 | 3.4751 | 3.4751
1020 | feeder2_line117 | 1 | 99 | 5.0064e-08 | 6.3875e-07 | 5.0569e-08 | 6.4521e-07
1020 | feeder2_line117 | 2 | 99 | 3.9278 | 3.9278 | 3.9675 | 3.9675
1020 | feeder2_line117 | 3 | 99 | 5.0137e-08 | 6.4112e-07 | 5.0644e-08 | 6.4759e-07
1020 | feeder2_line118 | 1 | 354.6 | 70.7346 | 70.7375 | 19.9477 | 19.9485
1020 | feeder2_line118 | 2 | 354.6 | 70.8032 | 70.7971 | 19.9671 | 19.9653
1020 | feeder2_line118 | 3 | 354.6 | 77.9926 | 77.9952 | 21.9945 | 21.9953
1020 | feeder2_line119 | 1 | 99 | 2.4939e-08 | 6.0119e-07 | 2.5191e-08 | 6.0726e-07
1020 | feeder2_line119 | 2 | 99 | 2.4611e-08 | 6.0458e-07 | 2.486e-08 | 6.1069e-07
1020 | feeder2_line119 | 3 | 99 | 0.094083 | 0.094089 | 0.095034 | 0.09504
1020 | feeder2_line120 | 1 | 354.6 | 0.082533 | 0.082303 | 0.023275 | 0.02321
1020 | feeder2_line120 | 2 | 354.6 | 1.5625 | 1.5622 | 0.44063 | 0.44056
1020 | feeder2_line120 | 3 | 354.6 | 12.2341 | 12.2339 | 3.4501 | 3.4501
1020 | feeder2_line121 | 1 | 99 | 3.2259e-07 | 9.3099e-07 | 3.2585e-07 | 9.4039e-07
1020 | feeder2_line121 | 2 | 99 | 1.4732 | 1.4732 | 1.4881 | 1.4881
1020 | feeder2_line121 | 3 | 99 | 3.2333e-07 | 9.3279e-07 | 3.2659e-07 | 9.4221e-07
1020 | feeder2_line122 | 1 | 354.6 | 0.082521 | 0.082303 | 0.023271 | 0.02321
1020 | feeder2_line122 | 2 | 354.6 | 0.089248 | 0.089002 | 0.025169 | 0.025099
1020 | feeder2_line122 | 3 | 354.6 | 12.234 | 12.2339 | 3.4501 | 3.4501
1020 | feeder2_line123 | 1 | 99 | 5.704e-07 | 9.6473e-07 | 5.7617e-07 | 9.7448e-07
1020 | feeder2_line123 | 2 | 99 | 5.7368e-07 | 9.7021e-07 | 5.7947e-07 | 9.8001e-07
1020 | feeder2_line123 | 3 | 99 | 0.077397 | 0.077399 | 0.078179 | 0.078181
1020 | feeder2_line124 | 1 | 354.6 | 0.082424 | 0.082303 | 0.023244 | 0.02321
1020 | feeder2_line124 | 2 | 354.6 | 0.089152 | 0.089002 | 0.025142 | 0.025099
1020 | feeder2_line124 | 3 | 354.6 | 12.1613 | 12.1613 | 3.4296 | 3.4296
1020 | feeder2_line125 | 1 | 99 | 5.704e-07 | 8.9681e-07 | 5.7616e-07 | 9.0587e-07
1020 | feeder2_line125 | 2 | 99 | 5.7368e-07 | 9.0191e-07 | 5.7948e-07 | 9.1102e-07
1020 | feeder2_line125 | 3 | 99 | 2.4993 | 2.4993 | 2.5246 | 2.5246
1020 | feeder2_line126 | 1 | 354.6 | 0.082579 | 0.082303 | 0.023288 | 0.02321
1020 | feeder2_line126 | 2 | 354.6 | 0.089309 | 0.089002 | 0.025186 | 0.025099
1020 | feeder2_line126 | 3 | 354.6 | 9.7714 | 9.7712 | 2.7556 | 2.7556
1020 | feeder2_line127 | 1 | 99 | 5.704e-07 | 1.0736e-06 | 5.7616e-07 | 1.0845e-06
1020 | feeder2_line127 | 2 | 99 | 5.737e-07 | 1.0798e-06 | 5.795e-07 | 1.0907e-06
1020 | feeder2_line127 | 3 | 99 | 0.86804 | 0.86804 | 0.8768 | 0.87681
1020 | feeder2_line128 | 1 | 354.6 | 0.082494 | 0.082303 | 0.023264 | 0.02321
1020 | feeder2_line128 | 2 | 354.6 | 0.089223 | 0.089002 | 0.025162 | 0.025099
1020 | feeder2_line128 | 3 | 354.6 | 8.9702 | 8.97 | 2.5297 | 2.5296
1020 | feeder2_line129 | 1 | 99 | 5.4548e-07 | 8.7057e-07 | 5.5099e-07 | 8.7936e-07
1020 | feeder2_line129 | 2 | 99 | 0.089007 | 0.089002 | 0.089906 | 0.089901
1020 | feeder2_line129 | 3 | 99 | 5.463e-07 | 8.7203e-07 | 5.5181e-07 | 8.8084e-07
1020 | feeder2_line130 | 1 | 354.6 | 0.082507 | 0.082303 | 0.023268 | 0.02321
1020 | feeder2_line130 | 2 | 354.6 | 0.0003079 | 4.6325e-06 | 8.683e-05 | 1.3064e-06
1020 | feeder2_line130 | 3 | 354.6 | 8.9702 | 8.97 | 2.5297 | 2.5296
1020 | feeder2_line131 | 1 | 99 | 5.704e-07 | 9.6489e-07 | 5.7616e-07 | 9.7463e-07
1020 | feeder2_line131 | 2 | 99 | 5.7371e-07 | 9.7041e-07 | 5.795e-07 | 9.8022e-07
1020 | feeder2_line131 | 3 | 99 | 7.8482 | 7.8483 | 7.9275 | 7.9276
1020 | feeder2_line132 | 1 | 354.6 | 0.082349 | 0.082302 | 0.023223 | 0.02321
1020 | feeder2_line132 | 2 | 354.6 | 0.00012575 | 2.9124e-06 | 3.5462e-05 | 8.2131e-07
1020 | feeder2_line132 | 3 | 354.6 | 1.3246 | 1.3244 | 0.37354 | 0.3735
1020 | feeder2_line133 | 1 | 99 | 0.08228 | 0.082302 | 0.083111 | 0.083134
1020 | feeder2_line133 | 2 | 99 | 2.9916e-07 | 9.7818e-07 | 3.0218e-07 | 9.8806e-07
1020 | feeder2_line133 | 3 | 99 | 2.9819e-07 | 9.7416e-07 | 3.012e-07 | 9.84e-07
1020 | feeder2_line134 | 1 | 354.6 | 9.8524e-12 | 1.7739e-06 | 2.7785e-12 | 5.0024e-07
1020 | feeder2_line134 | 2 | 354.6 | 6.3819e-12 | 1.7832e-06 | 1.7997e-12 | 5.0288e-07
1020 | feeder2_line134 | 3 | 354.6 | 1.3244 | 1.3244 | 0.3735 | 0.3735
1020 | feeder2_line135 | 1 | 99 | 1.6133 | 1.6134 | 1.6296 | 1.6297
1020 | feeder2_line135 | 2 | 99 | 4.9343e-08 | 5.8583e-07 | 4.9841e-08 | 5.9174e-07
1020 | feeder2_line135 | 3 | 99 | 5.0157e-08 | 5.8444e-07 | 5.0664e-08 | 5.9034e-07
1020 | feeder2_line136 | 1 | 354.6 | 72.3473 | 72.3502 | 20.4025 | 20.4033
1020 | feeder2_line136 | 2 | 354.6 | 70.8032 | 70.7971 | 19.9671 | 19.9653
1020 | feeder2_line136 | 3 | 354.6 | 77.9926 | 77.9952 | 21.9945 | 21.9953
1020 | feeder2_line137 | 1 | 99 | 5.4392 | 5.4392 | 5.4941 | 5.4942
1020 | feeder2_line137 | 2 | 99 | 8.5042e-07 | 1.578e-06 | 8.5901e-07 | 1.5939e-06
1020 | feeder2_line137 | 3 | 99 | 8.4812e-07 | 1.5742e-06 | 8.5669e-07 | 1.5901e-06
1020 | feeder2_line138 | 1 | 354.6 | 77.769 | 77.7718 | 21.9315 | 21.9323
1020 | feeder2_line138 | 2 | 354.6 | 70.8033 | 70.7971 | 19.9671 | 19.9653
1020 | feeder2_line138 | 3 | 354.6 | 77.9926 | 77.9952 | 21.9945 | 21.9953
1020 | feeder2_line139 | 1 | 99 | 5.0109e-08 | 4.8872e-07 | 5.0615e-08 | 4.9366e-07
1020 | feeder2_line139 | 2 | 99 | 4.9357e-08 | 4.9172e-07 | 4.9856e-08 | 4.9669e-07
1020 | feeder2_line139 | 3 | 99 | 0.95536 | 0.95562 | 0.96501 | 0.96528
1020 | feeder2_line140 | 1 | 354.6 | 77.7691 | 77.7718 | 21.9315 | 21.9323
1020 | feeder2_line140 | 2 | 354.6 | 70.8034 | 70.7971 | 19.9671 | 19.9653
1020 | feeder2_line140 | 3 | 354.6 | 78.5744 | 78.577 | 22.1586 | 22.1593
1020 | feeder2_line141 | 1 | 99 | 2.5083e-06 | 4.835e-07 | 2.5337e-06 | 4.8838e-07
1020 | feeder2_line141 | 2 | 99 | 1.6552 | 1.6552 | 1.6719 | 1.6719
1020 | feeder2_line141 | 3 | 99 | 2.5187e-06 | 4.8532e-07 | 2.5441e-06 | 4.9022e-07
1020 | feeder2_line142 | 1 | 354.6 | 77.7689 | 77.7718 | 21.9314 | 21.9323
1020 | feeder2_line142 | 2 | 354.6 | 72.4581 | 72.4519 | 20.4337 | 20.432
1020 | feeder2_line142 | 3 | 354.6 | 78.5742 | 78.577 | 22.1585 | 22.1593
1020 | feeder2_line143 | 1 | 99 | 8.4524e-07 | 1.7181e-06 | 8.5378e-07 | 1.7355e-06
1020 | feeder2_line143 | 2 | 99 | 6.0973 | 6.0974 | 6.1589 | 6.159
1020 | feeder2_line143 | 3 | 99 | 8.4849e-07 | 1.7246e-06 | 8.5706e-07 | 1.742e-06
1020 | feeder2_line144 | 1 | 354.6 | 77.7687 | 77.7718 | 21.9314 | 21.9323
1020 | feeder2_line144 | 2 | 354.6 | 77.6117 | 77.6058 | 21.8871 | 21.8854
1020 | feeder2_line144 | 3 | 354.6 | 78.574 | 78.577 | 22.1585 | 22.1593
1020 | feeder2_line145 | 1 | 99 | 2.5059e-08 | 4.818e-07 | 2.5312e-08 | 4.8666e-07
1020 | feeder2_line145 | 2 | 99 | 10.7597 | 10.7599 | 10.8684 | 10.8685
1020 | feeder2_line145 | 3 | 99 | 2.5089e-08 | 4.836e-07 | 2.5342e-08 | 4.8849e-07
1020 | feeder2_line146 | 1 | 354.6 | 77.7686 | 77.7718 | 21.9314 | 21.9323
1020 | feeder2_line146 | 2 | 354.6 | 88.3688 | 88.3631 | 24.9207 | 24.9191
1020 | feeder2_line146 | 3 | 354.6 | 78.5739 | 78.577 | 22.1585 | 22.1593
1020 | feeder2_line147 | 1 | 99 | 10.6003 | 10.6001 | 10.7073 | 10.7072
1020 | feeder2_line147 | 2 | 99 | 1.1509e-06 | 2.2358e-06 | 1.1625e-06 | 2.2584e-06
1020 | feeder2_line147 | 3 | 99 | 1.1482e-06 | 2.2307e-06 | 1.1598e-06 | 2.2532e-06
1020 | feeder2_line148 | 1 | 99 | 0.085452 | 0.085457 | 0.086315 | 0.08632
1020 | feeder2_line148 | 2 | 99 | 6.0018e-07 | 1.4982e-06 | 6.0624e-07 | 1.5134e-06
1020 | feeder2_line148 | 3 | 99 | 5.9921e-07 | 1.4948e-06 | 6.0526e-07 | 1.5099e-06
1020 | feeder2_line149 | 1 | 354.6 | 88.45 | 88.453 | 24.9436 | 24.9444
1020 | feeder2_line149 | 2 | 354.6 | 88.369 | 88.3631 | 24.9208 | 24.9191
1020 | feeder2_line149 | 3 | 354.6 | 78.5741 | 78.577 | 22.1585 | 22.1593
1020 | feeder2_line150 | 1 | 354.6 | 88.4501 | 88.453 | 24.9436 | 24.9444
1020 | feeder2_line150 | 2 | 354.6 | 98.4414 | 98.4357 | 27.7613 | 27.7596
1020 | feeder2_line150 | 3 | 354.6 | 78.5741 | 78.577 | 22.1585 | 22.1593
1020 | feeder2_line151 | 1 | 99 | 9.6956e-06 | 1.7692e-06 | 9.7935e-06 | 1.787e-06
1020 | feeder2_line151 | 2 | 99 | 10.0744 | 10.0746 | 10.1762 | 10.1764
1020 | feeder2_line151 | 3 | 99 | 9.7285e-06 | 1.7756e-06 | 9.8268e-06 | 1.7935e-06
1020 | feeder2_line152 | 1 | 354.6 | 1.2252e-11 | 1.1795e-06 | 3.4552e-12 | 3.3264e-07
1020 | feeder2_line152 | 2 | 354.6 | 1.3882e-11 | 1.1862e-06 | 3.9148e-12 | 3.3452e-07
1020 | feeder2_line152 | 3 | 354.6 | 0.077059 | 0.077061 | 0.021731 | 0.021732
1020 | feeder2_line153 | 1 | 99 | 1.4724 | 1.4724 | 1.4873 | 1.4873
1020 | feeder2_line153 | 2 | 99 | 4.9409e-08 | 5.9369e-07 | 4.9908e-08 | 5.9969e-07
1020 | feeder2_line153 | 3 | 99 | 5.0263e-08 | 5.921e-07 | 5.0771e-08 | 5.9808e-07
1020 | feeder2_line154 | 1 | 99 | 5.7248e-07 | 8.7795e-07 | 5.7826e-07 | 8.8682e-07
1020 | feeder2_line154 | 2 | 99 | 5.7609e-07 | 8.8342e-07 | 5.819e-07 | 8.9235e-07
1020 | feeder2_line154 | 3 | 99 | 20.362 | 20.3619 | 20.5677 | 20.5676
1020 | feeder2_line155 | 1 | 99 | 89.9102 | 89.9131 | 90.8183 | 90.8213
1020 | feeder2_line155 | 2 | 99 | 98.4414 | 98.4357 | 99.4357 | 99.43
1020 | feeder2_line155 | 3 | 99 | 99 | 99.0028 | 100 | 100.0029
1020 | feeder2_line156 | 1 | 99 | 5.9731e-07 | 1.1552e-06 | 6.0334e-07 | 1.1669e-06
1020 | feeder2_line156 | 2 | 99 | 9.9853 | 9.9854 | 10.0861 | 10.0863
1020 | feeder2_line156 | 3 | 99 | 5.9941e-07 | 1.1594e-06 | 6.0547e-07 | 1.1711e-06
1020 | feeder2_line157 | 1 | 99 | 2.5071e-08 | 2.5081e-07 | 2.5325e-08 | 2.5334e-07
1020 | feeder2_line157 | 2 | 99 | 0.089428 | 0.089424 | 0.090331 | 0.090327
1020 | feeder2_line157 | 3 | 99 | 2.5111e-08 | 2.5171e-07 | 2.5364e-08 | 2.5425e-07
1050 | feeder2_line1 | 1 | 354.6 | 55.92 | 55.9217 | 15.7699 | 15.7704
1050 | feeder2_line1 | 2 | 354.6 | 59.8946 | 59.8928 | 16.8908 | 16.8902
1050 | feeder2_line1 | 3 | 354.6 | 62.2076 | 62.2132 | 17.543 | 17.5446
1050 | feeder2_line2 | 1 | 354.6 | 51.4778 | 51.4786 | 14.5171 | 14.5174
1050 | feeder2_line2 | 2 | 354.6 | 59.8947 | 59.8928 | 16.8908 | 16.8902
1050 | feeder2_line2 | 3 | 354.6 | 62.2078 | 62.2132 | 17.5431 | 17.5446
1050 | feeder2_line3 | 1 | 80.1 | 12.4052 | 12.4052 | 15.4871 | 15.4871
1050 | feeder2_line3 | 2 | 80.1 | 5.6841e-07 | 1.0504e-06 | 7.0962e-07 | 1.3114e-06
1050 | feeder2_line3 | 3 | 80.1 | 5.7016e-07 | 1.0537e-06 | 7.1182e-07 | 1.3154e-06
1050 | feeder2_line4 | 1 | 354.6 | 51.4777 | 51.4786 | 14.5171 | 14.5174
1050 | feeder2_line4 | 2 | 354.6 | 59.8774 | 59.8756 | 16.8859 | 16.8854
1050 | feeder2_line4 | 3 | 354.6 | 62.2078 | 62.2132 | 17.5431 | 17.5446
1050 | feeder2_line5 | 1 | 80.1 | 5.6854e-07 | 9.9207e-07 | 7.0979e-07 | 1.2385e-06
1050 | feeder2_line5 | 2 | 80.1 | 0.090546 | 0.090546 | 0.11304 | 0.11304
1050 | feeder2_line5 | 3 | 80.1 | 5.702e-07 | 9.9493e-07 | 7.1186e-07 | 1.2421e-06
1050 | feeder2_line6 | 1 | 80.1 | 5.6848e-07 | 1.1669e-06 | 7.0971e-07 | 1.4568e-06
1050 | feeder2_line6 | 2 | 80.1 | 5.683e-07 | 1.1665e-06 | 7.0949e-07 | 1.4564e-06
1050 | feeder2_line6 | 3 | 80.1 | 2.1828 | 2.1828 | 2.7251 | 2.7251
1050 | feeder2_line7 | 1 | 354.6 | 51.4777 | 51.4786 | 14.5171 | 14.5174
1050 | feeder2_line7 | 2 | 354.6 | 59.8774 | 59.8756 | 16.8859 | 16.8854
1050 | feeder2_line7 | 3 | 354.6 | 62.5878 | 62.5933 | 17.6503 | 17.6518
1050 | feeder2_line8 | 1 | 80.1 | 1.7924 | 1.7924 | 2.2378 | 2.2378
1050 | feeder2_line8 | 2 | 80.1 | 5.6809e-07 | 1.1244e-06 | 7.0922e-07 | 1.4037e-06
1050 | feeder2_line8 | 3 | 80.1 | 5.7024e-07 | 1.1286e-06 | 7.1191e-07 | 1.409e-06
1050 | feeder2_line9 | 1 | 354.6 | 51.2412 | 51.2421 | 14.4504 | 14.4507
1050 | feeder2_line9 | 2 | 354.6 | 59.8773 | 59.8756 | 16.8859 | 16.8854
1050 | feeder2_line9 | 3 | 354.6 | 62.5878 | 62.5933 | 17.6502 | 17.6518
1050 | feeder2_line10 | 1 | 80.1 | 8.4001e-07 | 1.4852e-06 | 1.0487e-06 | 1.8542e-06
1050 | feeder2_line10 | 2 | 80.1 | 1.7924 | 1.7924 | 2.2377 | 2.2377
1050 | feeder2_line10 | 3 | 80.1 | 8.4306e-07 | 1.4902e-06 | 1.0525e-06 | 1.8605e-06
1050 | feeder2_line11 | 1 | 354.6 | 51.2413 | 51.2421 | 14.4505 | 14.4507
1050 | feeder2_line11 | 2 | 354.6 | 59.4416 | 59.4398 | 16.763 | 16.7625
1050 | feeder2_line11 | 3 | 354.6 | 62.5879 | 62.5933 | 17.6503 | 17.6518
1050 | feeder2_line12 | 1 | 80.1 | 5.4337e-07 | 9.8506e-07 | 6.7836e-07 | 1.2298e-06
1050 | feeder2_line12 | 2 | 80.1 | 5.4326e-07 | 9.8459e-07 | 6.7822e-07 | 1.2292e-06
1050 | feeder2_line12 | 3 | 80.1 | 1.7149 | 1.7149 | 2.141 | 2.141
1050 | feeder2_line13 | 1 | 354.6 | 51.2414 | 51.2421 | 14.4505 | 14.4507
1050 | feeder2_line13 | 2 | 354.6 | 59.4417 | 59.4398 | 16.763 | 16.7625
1050 | feeder2_line13 | 3 | 354.6 | 63.3775 | 63.383 | 17.873 | 17.8745
1050 | feeder2_line14 | 1 | 80.1 | 9.6918 | 9.6918 | 12.0996 | 12.0996
1050 | feeder2_line14 | 2 | 80.1 | 2.963e-07 | 6.4194e-07 | 3.6991e-07 | 8.0142e-07
1050 | feeder2_line14 | 3 | 80.1 | 2.9743e-07 | 6.4461e-07 | 3.7133e-07 | 8.0476e-07
1050 | feeder2_line15 | 1 | 354.6 | 50.9377 | 50.9377 | 14.3648 | 14.3648
1050 | feeder2_line15 | 2 | 354.6 | 59.4417 | 59.4398 | 16.763 | 16.7625
1050 | feeder2_line15 | 3 | 354.6 | 63.3775 | 63.383 | 17.873 | 17.8745
1050 | feeder2_line16 | 1 | 80.1 | 5.6812e-07 | 1.0235e-06 | 7.0926e-07 | 1.2778e-06
1050 | feeder2_line16 | 2 | 80.1 | 2.7682 | 2.7682 | 3.4559 | 3.4559
1050 | feeder2_line16 | 3 | 80.1 | 5.703e-07 | 1.0274e-06 | 7.1198e-07 | 1.2826e-06
1050 | feeder2_line17 | 1 | 354.6 | 50.9377 | 50.9377 | 14.3648 | 14.3648
1050 | feeder2_line17 | 2 | 354.6 | 58.2032 | 58.2013 | 16.4138 | 16.4132
1050 | feeder2_line17 | 3 | 354.6 | 63.3776 | 63.383 | 17.873 | 17.8745
1050 | feeder2_line18 | 1 | 80.1 | 5.4297e-07 | 7.323e-07 | 6.7787e-07 | 9.1423e-07
1050 | feeder2_line18 | 2 | 80.1 | 5.4251e-07 | 7.315e-07 | 6.7729e-07 | 9.1323e-07
1050 | feeder2_line18 | 3 | 80.1 | 1.4229 | 1.4229 | 1.7764 | 1.7764
1050 | feeder2_line19 | 1 | 354.6 | 50.9377 | 50.9377 | 14.3648 | 14.3648
1050 | feeder2_line19 | 2 | 354.6 | 58.2032 | 58.2013 | 16.4138 | 16.4132
1050 | feeder2_line19 | 3 | 354.6 | 64.0875 | 64.093 | 18.0732 | 18.0747
1050 | feeder2_line20 | 1 | 99 | 5.4287e-07 | 8.7783e-07 | 5.4835e-07 | 8.8669e-07
1050 | feeder2_line20 | 2 | 99 | 5.4231e-07 | 8.7672e-07 | 5.4779e-07 | 8.8557e-07
1050 | feeder2_line20 | 3 | 99 | 1.5649 | 1.565 | 1.5808 | 1.5808
1050 | feeder2_line21 | 1 | 354.6 | 50.9377 | 50.9377 | 14.3648 | 14.3648
1050 | feeder2_line21 | 2 | 354.6 | 58.2032 | 58.2013 | 16.4138 | 16.4132
1050 | feeder2_line21 | 3 | 354.6 | 64.8629 | 64.8684 | 18.2918 | 18.2934
1050 | feeder2_line22 | 1 | 99 | 5.6768e-07 | 1.0062e-06 | 5.7341e-07 | 1.0164e-06
1050 | feeder2_line22 | 2 | 99 | 2.545 | 2.545 | 2.5707 | 2.5707
1050 | feeder2_line22 | 3 | 99 | 5.7043e-07 | 1.011e-06 | 5.7619e-07 | 1.0212e-06
1050 | feeder2_line23 | 1 | 99 | 5.6768e-07 | 9.419e-07 | 5.7341e-07 | 9.5141e-07
1050 | feeder2_line23 | 2 | 99 | 5.6691e-07 | 9.4061e-07 | 5.7264e-07 | 9.5011e-07
1050 | feeder2_line23 | 3 | 99 | 1.094 | 1.094 | 1.1051 | 1.1051
1050 | feeder2_line24 | 1 | 354.6 | 50.9378 | 50.9377 | 14.3649 | 14.3648
1050 | feeder2_line24 | 2 | 354.6 | 57.6243 | 57.6222 | 16.2505 | 16.2499
1050 | feeder2_line24 | 3 | 354.6 | 65.4155 | 65.421 | 18.4477 | 18.4492
1050 | feeder2_line25 | 1 | 99 | 2.5447 | 2.5447 | 2.5704 | 2.5704
1050 | feeder2_line25 | 2 | 99 | 4.9463e-08 | 6.836e-07 | 4.9963e-08 | 6.9051e-07
1050 | feeder2_line25 | 3 | 99 | 4.9004e-08 | 6.8811e-07 | 4.9499e-08 | 6.9506e-07
1050 | feeder2_line26 | 1 | 99 | 0.086058 | 0.086056 | 0.086928 | 0.086925
1050 | feeder2_line26 | 2 | 99 | 5.4198e-07 | 8.4694e-07 | 5.4746e-07 | 8.5549e-07
1050 | feeder2_line26 | 3 | 99 | 5.4598e-07 | 8.5253e-07 | 5.515e-07 | 8.6114e-07
1050 | feeder2_line27 | 1 | 354.6 | 51.0585 | 51.0581 | 14.3989 | 14.3988
1050 | feeder2_line27 | 2 | 354.6 | 57.6243 | 57.6222 | 16.2505 | 16.2499
1050 | feeder2_line27 | 3 | 354.6 | 65.4155 | 65.421 | 18.4477 | 18.4492
1050 | feeder2_line28 | 1 | 99 | 2.5134e-06 | 7.0389e-07 | 2.5388e-06 | 7.11e-07
1050 | feeder2_line28 | 2 | 99 | 0.077975 | 0.077975 | 0.078763 | 0.078762
1050 | feeder2_line28 | 3 | 99 | 2.5346e-06 | 7.0777e-07 | 2.5603e-06 | 7.1492e-07
1050 | feeder2_line29 | 1 | 354.6 | 51.0585 | 51.0581 | 14.3989 | 14.3988
1050 | feeder2_line29 | 2 | 354.6 | 57.6175 | 57.6154 | 16.2486 | 16.248
1050 | feeder2_line29 | 3 | 354.6 | 65.4155 | 65.421 | 18.4477 | 18.4492
1050 | feeder2_line30 | 1 | 266.4 | 32.268 | 32.2678 | 12.1126 | 12.1125
1050 | feeder2_line30 | 2 | 266.4 | 3.8517 | 3.8515 | 1.4458 | 1.4457
1050 | feeder2_line30 | 3 | 266.4 | 11.3711 | 11.371 | 4.2684 | 4.2684
1050 | feeder2_line31 | 1 | 354.6 | 63.5825 | 63.5795 | 17.9308 | 17.9299
1050 | feeder2_line31 | 2 | 354.6 | 56.7376 | 56.7348 | 16.0004 | 15.9997
1050 | feeder2_line31 | 3 | 354.6 | 69.5788 | 69.5841 | 19.6218 | 19.6233
1050 | feeder2_line32 | 1 | 354.6 | 63.5825 | 63.5795 | 17.9308 | 17.9299
1050 | feeder2_line32 | 2 | 354.6 | 56.7782 | 56.7753 | 16.0119 | 16.0111
1050 | feeder2_line32 | 3 | 354.6 | 69.5788 | 69.5841 | 19.6218 | 19.6233
1050 | feeder2_line33 | 1 | 99 | 4.9769e-08 | 6.7886e-07 | 5.0272e-08 | 6.8572e-07
1050 | feeder2_line33 | 2 | 99 | 10.6873 | 10.6873 | 10.7952 | 10.7953
1050 | feeder2_line33 | 3 | 99 | 4.8817e-08 | 6.8302e-07 | 4.9311e-08 | 6.8992e-07
1050 | feeder2_line34 | 1 | 354.6 | 63.5825 | 63.5796 | 17.9308 | 17.9299
1050 | feeder2_line34 | 2 | 354.6 | 56.7782 | 56.7753 | 16.0119 | 16.0111
1050 | feeder2_line34 | 3 | 354.6 | 69.6354 | 69.6406 | 19.6377 | 19.6392
1050 | feeder2_line35 | 1 | 99 | 2.9607e-07 | 7.518e-07 | 2.9906e-07 | 7.5939e-07
1050 | feeder2_line35 | 2 | 99 | 2.9514e-07 | 7.4949e-07 | 2.9812e-07 | 7.5706e-07
1050 | feeder2_line35 | 3 | 99 | 0.085787 | 0.085792 | 0.086654 | 0.086659
1050 | feeder2_line36 | 1 | 354.6 | 64.4905 | 64.4875 | 18.1868 | 18.186
1050 | feeder2_line36 | 2 | 354.6 | 56.7782 | 56.7753 | 16.0119 | 16.0111
1050 | feeder2_line36 | 3 | 354.6 | 69.6354 | 69.6406 | 19.6377 | 19.6392
1050 | feeder2_line37 | 1 | 99 | 1.346 | 1.3459 | 1.3596 | 1.3595
1050 | feeder2_line37 | 2 | 99 | 2.9508e-07 | 8.291e-07 | 2.9806e-07 | 8.3747e-07
1050 | feeder2_line37 | 3 | 99 | 2.976e-07 | 8.3699e-07 | 3.0061e-07 | 8.4544e-07
1050 | feeder2_line38 | 1 | 99 | 3.2087e-07 | 7.6735e-07 | 3.2411e-07 | 7.751e-07
1050 | feeder2_line38 | 2 | 99 | 0.078221 | 0.07822 | 0.079011 | 0.07901
1050 | feeder2_line38 | 3 | 99 | 3.2197e-07 | 7.7218e-07 | 3.2522e-07 | 7.7998e-07
1050 | feeder2_line39 | 1 | 266.4 | 32.268 | 32.2678 | 12.1126 | 12.1125
1050 | feeder2_line39 | 2 | 266.4 | 3.7751 | 3.7749 | 1.4171 | 1.417
1050 | feeder2_line39 | 3 | 266.4 | 11.3711 | 11.371 | 4.2684 | 4.2684
1050 | feeder2_line40 | 1 | 354.6 | 65.9917 | 65.9886 | 18.6102 | 18.6093
1050 | feeder2_line40 | 2 | 354.6 | 56.7782 | 56.7753 | 16.0119 | 16.0111
1050 | feeder2_line40 | 3 | 354.6 | 69.6354 | 69.6406 | 19.6377 | 19.6392
1050 | feeder2_line41 | 1 | 99 | 2.545 | 2.545 | 2.5707 | 2.5707
1050 | feeder2_line41 | 2 | 99 | 4.9573e-08 | 7.2439e-07 | 5.0074e-08 | 7.3171e-07
1050 | feeder2_line41 | 3 | 99 | 4.8789e-08 | 7.3139e-07 | 4.9282e-08 | 7.3878e-07
1050 | feeder2_line42 | 1 | 99 | 2.9587e-07 | 7.4042e-07 | 2.9886e-07 | 7.479e-07
1050 | feeder2_line42 | 2 | 99 | 2.9533e-07 | 7.3922e-07 | 2.9831e-07 | 7.4669e-07
1050 | feeder2_line42 | 3 | 99 | 0.077372 | 0.077375 | 0.078154 | 0.078157
1050 | feeder2_line43 | 1 | 266.4 | 32.2679 | 32.2678 | 12.1126 | 12.1125
1050 | feeder2_line43 | 2 | 266.4 | 3.7751 | 3.7749 | 1.4171 | 1.417
1050 | feeder2_line43 | 3 | 266.4 | 11.2975 | 11.2974 | 4.2408 | 4.2408
1050 | feeder2_line44 | 1 | 354.6 | 65.9918 | 65.9886 | 18.6102 | 18.6093
1050 | feeder2_line44 | 2 | 354.6 | 56.7782 | 56.7753 | 16.0119 | 16.0111
1050 | feeder2_line44 | 3 | 354.6 | 70.659 | 70.6642 | 19.9264 | 19.9279
1050 | feeder2_line45 | 1 | 99 | 4.9758e-08 | 5.733e-07 | 5.0261e-08 | 5.7909e-07
1050 | feeder2_line45 | 2 | 99 | 4.9586e-08 | 5.7119e-07 | 5.0087e-08 | 5.7696e-07
1050 | feeder2_line45 | 3 | 99 | 1.5663 | 1.5663 | 1.5821 | 1.5821
1050 | feeder2_line46 | 1 | 99 | 5.6682e-07 | 1.3422e-06 | 5.7255e-07 | 1.3558e-06
1050 | feeder2_line46 | 2 | 99 | 5.6592e-07 | 1.3401e-06 | 5.7164e-07 | 1.3536e-06
1050 | feeder2_line46 | 3 | 99 | 2.665 | 2.665 | 2.6919 | 2.6919
1050 | feeder2_line47 | 1 | 266.4 | 32.2679 | 32.2678 | 12.1126 | 12.1125
1050 | feeder2_line47 | 2 | 266.4 | 3.7751 | 3.7749 | 1.4171 | 1.417
1050 | feeder2_line47 | 3 | 266.4 | 8.6577 | 8.6575 | 3.2499 | 3.2498
1050 | feeder2_line48 | 1 | 99 | 1.9468 | 1.9468 | 1.9665 | 1.9664
1050 | feeder2_line48 | 2 | 99 | 4.9432e-08 | 7.2153e-07 | 4.9931e-08 | 7.2881e-07
1050 | feeder2_line48 | 3 | 99 | 4.8849e-08 | 7.2742e-07 | 4.9343e-08 | 7.3477e-07
1050 | feeder2_line49 | 1 | 266.4 | 30.3233 | 30.3232 | 11.3826 | 11.3826
1050 | feeder2_line49 | 2 | 266.4 | 3.7751 | 3.7749 | 1.4171 | 1.417
1050 | feeder2_line49 | 3 | 266.4 | 8.6577 | 8.6575 | 3.2499 | 3.2498
1050 | feeder2_line50 | 1 | 99 | 5.6666e-07 | 1.2212e-06 | 5.7239e-07 | 1.2335e-06
1050 | feeder2_line50 | 2 | 99 | 2.1874 | 2.1874 | 2.2095 | 2.2095
1050 | feeder2_line50 | 3 | 99 | 5.7058e-07 | 1.2295e-06 | 5.7635e-07 | 1.2419e-06
1050 | feeder2_line51 | 1 | 99 | 20.0598 | 20.0598 | 20.2624 | 20.2624
1050 | feeder2_line51 | 2 | 99 | 5.6589e-07 | 1.324e-06 | 5.7161e-07 | 1.3373e-06
1050 | feeder2_line51 | 3 | 99 | 5.7055e-07 | 1.3347e-06 | 5.7631e-07 | 1.3482e-06
1050 | feeder2_line52 | 1 | 266.4 | 10.2635 | 10.2635 | 3.8527 | 3.8527
1050 | feeder2_line52 | 2 | 266.4 | 1.6342 | 1.6341 | 0.61344 | 0.6134
1050 | feeder2_line52 | 3 | 266.4 | 8.6576 | 8.6575 | 3.2498 | 3.2498
1050 | feeder2_line53 | 1 | 99 | 5.4174e-07 | 7.453e-07 | 5.4721e-07 | 7.5283e-07
1050 | feeder2_line53 | 2 | 99 | 1.6341 | 1.6341 | 1.6506 | 1.6506
1050 | feeder2_line53 | 3 | 99 | 5.4615e-07 | 7.5039e-07 | 5.5167e-07 | 7.5797e-07
1050 | feeder2_line54 | 1 | 266.4 | 10.2633 | 10.2635 | 3.8526 | 3.8527
1050 | feeder2_line54 | 2 | 266.4 | 8.4476e-05 | 4.5665e-06 | 3.171e-05 | 1.7141e-06
1050 | feeder2_line54 | 3 | 266.4 | 8.6574 | 8.6575 | 3.2498 | 3.2498
1050 | feeder2_line55 | 1 | 99 | 1.8385 | 1.8385 | 1.8571 | 1.8571
1050 | feeder2_line55 | 2 | 99 | 4.9636e-08 | 7.1922e-07 | 5.0138e-08 | 7.2649e-07
1050 | feeder2_line55 | 3 | 99 | 4.8743e-08 | 7.268e-07 | 4.9235e-08 | 7.3414e-07
1050 | feeder2_line56 | 1 | 354.6 | 67.1204 | 67.1171 | 18.9285 | 18.9276
1050 | feeder2_line56 | 2 | 354.6 | 56.7782 | 56.7753 | 16.0119 | 16.0111
1050 | feeder2_line56 | 3 | 354.6 | 70.659 | 70.6642 | 19.9264 | 19.9279
1050 | feeder2_line57 | 1 | 99 | 7.4752e-07 | 1.5265e-06 | 7.5507e-07 | 1.542e-06
1050 | feeder2_line57 | 2 | 99 | 7.4121e-07 | 1.5247e-06 | 7.4869e-07 | 1.5401e-06
1050 | feeder2_line57 | 3 | 99 | 8.6575 | 8.6575 | 8.7449 | 8.745
1050 | feeder2_line58 | 1 | 266.4 | 10.2634 | 10.2635 | 3.8526 | 3.8527
1050 | feeder2_line58 | 2 | 266.4 | 1.8686e-05 | 2.6513e-06 | 7.0141e-06 | 9.9522e-07
1050 | feeder2_line58 | 3 | 266.4 | 1.888e-05 | 2.6719e-06 | 7.0871e-06 | 1.003e-06
1050 | feeder2_line59 | 1 | 99 | 4.983e-08 | 5.3064e-07 | 5.0333e-08 | 5.36e-07
1050 | feeder2_line59 | 2 | 99 | 4.9413e-08 | 5.2999e-07 | 4.9912e-08 | 5.3534e-07
1050 | feeder2_line59 | 3 | 99 | 6.9934 | 6.9935 | 7.064 | 7.0641
1050 | feeder2_line60 | 1 | 99 | 2.9577e-07 | 8.0196e-07 | 2.9876e-07 | 8.1006e-07
1050 | feeder2_line60 | 2 | 99 | 2.9533e-07 | 8.0098e-07 | 2.9831e-07 | 8.0907e-07
1050 | feeder2_line60 | 3 | 99 | 1.7152 | 1.7152 | 1.7325 | 1.7325
1050 | feeder2_line61 | 1 | 266.4 | 0.46046 | 0.46062 | 0.17285 | 0.17291
1050 | feeder2_line61 | 2 | 266.4 | 21.0414 | 21.0416 | 7.8984 | 7.8985
1050 | feeder2_line61 | 3 | 266.4 | 12.9519 | 12.952 | 4.8618 | 4.8619
1050 | feeder2_line62 | 1 | 354.6 | 67.4459 | 67.4427 | 19.0203 | 19.0194
1050 | feeder2_line62 | 2 | 354.6 | 61.9724 | 61.9694 | 17.4767 | 17.4758
1050 | feeder2_line62 | 3 | 354.6 | 79.122 | 79.1274 | 22.313 | 22.3145
1050 | feeder2_line63 | 1 | 99 | 0.090201 | 0.090196 | 0.091112 | 0.091107
1050 | feeder2_line63 | 2 | 99 | 5.6597e-07 | 1.2043e-06 | 5.7169e-07 | 1.2165e-06
1050 | feeder2_line63 | 3 | 99 | 5.7057e-07 | 1.214e-06 | 5.7634e-07 | 1.2263e-06
1050 | feeder2_line64 | 1 | 99 | 10.1734 | 10.1735 | 10.2761 | 10.2762
1050 | feeder2_line64 | 2 | 99 | 3.6722e-12 | 3.1724e-07 | 3.7093e-12 | 3.2044e-07
1050 | feeder2_line64 | 3 | 99 | 3.912e-12 | 3.1979e-07 | 3.9515e-12 | 3.2302e-07
1050 | feeder2_line65 | 1 | 99 | 4.9727e-08 | 6.346e-07 | 5.023e-08 | 6.4101e-07
1050 | feeder2_line65 | 2 | 99 | 0.091185 | 0.091184 | 0.092106 | 0.092105
1050 | feeder2_line65 | 3 | 99 | 4.869e-08 | 6.3854e-07 | 4.9182e-08 | 6.4499e-07
1050 | feeder2_line66 | 1 | 354.6 | 67.4459 | 67.4427 | 19.0203 | 19.0194
1050 | feeder2_line66 | 2 | 354.6 | 62.0185 | 62.0155 | 17.4897 | 17.4889
1050 | feeder2_line66 | 3 | 354.6 | 79.122 | 79.1274 | 22.313 | 22.3146
1050 | feeder2_line67 | 1 | 99 | 2.4856e-08 | 3.5876e-07 | 2.5107e-08 | 3.6238e-07
1050 | feeder2_line67 | 2 | 99 | 2.4842e-08 | 3.5691e-07 | 2.5093e-08 | 3.6052e-07
1050 | feeder2_line67 | 3 | 99 | 2.5386 | 2.5386 | 2.5642 | 2.5642
1050 | feeder2_line68 | 1 | 266.4 | 0.4605 | 0.46062 | 0.17286 | 0.17291
1050 | feeder2_line68 | 2 | 266.4 | 21.0415 | 21.0416 | 7.8984 | 7.8985
1050 | feeder2_line68 | 3 | 266.4 | 10.4134 | 10.4134 | 3.9089 | 3.9089
1050 | feeder2_line69 | 1 | 99 | 3.5474 | 3.5474 | 3.5832 | 3.5832
1050 | feeder2_line69 | 2 | 99 | 2.4994e-06 | 6.5523e-07 | 2.5247e-06 | 6.6184e-07
1050 | feeder2_line69 | 3 | 99 | 2.5396e-06 | 6.6294e-07 | 2.5653e-06 | 6.6964e-07
1050 | feeder2_line70 | 1 | 354.6 | 69.9023 | 69.8991 | 19.713 | 19.7121
1050 | feeder2_line70 | 2 | 354.6 | 62.0186 | 62.0155 | 17.4897 | 17.4889
1050 | feeder2_line70 | 3 | 354.6 | 79.1219 | 79.1274 | 22.313 | 22.3146
1050 | feeder2_line71 | 1 | 99 | 4.9727e-08 | 7.08e-07 | 5.0229e-08 | 7.1515e-07
1050 | feeder2_line71 | 2 | 99 | 3.0125 | 3.0125 | 3.043 | 3.0429
1050 | feeder2_line71 | 3 | 99 | 4.8671e-08 | 7.1247e-07 | 4.9162e-08 | 7.1966e-07
1050 | feeder2_line72 | 1 | 354.6 | 69.9024 | 69.8991 | 19.713 | 19.7121
1050 | feeder2_line72 | 2 | 354.6 | 62.4402 | 62.4371 | 17.6086 | 17.6077
1050 | feeder2_line72 | 3 | 354.6 | 79.122 | 79.1274 | 22.313 | 22.3146
1050 | feeder2_line73 | 1 | 99 | 5.9239e-07 | 1.5189e-06 | 5.9838e-07 | 1.5342e-06
1050 | feeder2_line73 | 2 | 99 | 10.6601 | 10.6601 | 10.7677 | 10.7678
1050 | feeder2_line73 | 3 | 99 | 5.9524e-07 | 1.5277e-06 | 6.0126e-07 | 1.5431e-06
1050 | feeder2_line74 | 1 | 99 | 4.9697e-08 | 4.5302e-07 | 5.0199e-08 | 4.5759e-07
1050 | feeder2_line74 | 2 | 99 | 10.2989 | 10.2989 | 10.4029 | 10.4029
1050 | feeder2_line74 | 3 | 99 | 4.8698e-08 | 4.5566e-07 | 4.919e-08 | 4.6026e-07
1050 | feeder2_line75 | 1 | 266.4 | 0.4606 | 0.46062 | 0.1729 | 0.17291
1050 | feeder2_line75 | 2 | 266.4 | 0.091113 | 0.091145 | 0.034202 | 0.034214
1050 | feeder2_line75 | 3 | 266.4 | 10.4135 | 10.4134 | 3.909 | 3.9089
1050 | feeder2_line76 | 1 | 99 | 0.46063 | 0.46062 | 0.46528 | 0.46528
1050 | feeder2_line76 | 2 | 99 | 8.3434e-07 | 1.5584e-06 | 8.4277e-07 | 1.5741e-06
1050 | feeder2_line76 | 3 | 99 | 8.4417e-07 | 1.5759e-06 | 8.527e-07 | 1.5918e-06
1050 | feeder2_line77 | 1 | 99 | 2.4848e-08 | 5.6929e-07 | 2.5099e-08 | 5.7504e-07
1050 | feeder2_line77 | 2 | 99 | 2.484e-08 | 5.6623e-07 | 2.5091e-08 | 5.7195e-07
1050 | feeder2_line77 | 3 | 99 | 10.4135 | 10.4134 | 10.5187 | 10.5186
1050 | feeder2_line78 | 1 | 266.4 | 5.9187e-12 | 9.4436e-07 | 2.2217e-12 | 3.5449e-07
1050 | feeder2_line78 | 2 | 266.4 | 0.091145 | 0.091145 | 0.034214 | 0.034214
1050 | feeder2_line78 | 3 | 266.4 | 5.8382e-12 | 9.49e-07 | 2.1915e-12 | 3.5623e-07
1050 | feeder2_line79 | 1 | 354.6 | 13.0092 | 13.0088 | 3.6687 | 3.6686
1050 | feeder2_line79 | 2 | 354.6 | 24.4248 | 24.4244 | 6.888 | 6.8879
1050 | feeder2_line79 | 3 | 354.6 | 18.559 | 18.5585 | 5.2338 | 5.2336
1050 | feeder2_line80 | 1 | 354.6 | 78.3458 | 78.3417 | 22.0941 | 22.093
1050 | feeder2_line80 | 2 | 354.6 | 75.3637 | 75.3605 | 21.2532 | 21.2523
1050 | feeder2_line80 | 3 | 354.6 | 92.0719 | 92.0767 | 25.965 | 25.9664
1050 | feeder2_line81 | 1 | 354.6 | 78.3457 | 78.3417 | 22.0941 | 22.093
1050 | feeder2_line81 | 2 | 354.6 | 75.3636 | 75.3605 | 21.2531 | 21.2523
1050 | feeder2_line81 | 3 | 354.6 | 92.2903 | 92.2953 | 26.0266 | 26.028
1050 | feeder2_line82 | 1 | 354.6 | 1.7348e-11 | 7.2631e-07 | 4.8924e-12 | 2.0483e-07
1050 | feeder2_line82 | 2 | 354.6 | 3.8042e-11 | 7.2209e-07 | 1.0728e-11 | 2.0363e-07
1050 | feeder2_line82 | 3 | 354.6 | 1.1233 | 1.1233 | 0.31678 | 0.31677
1050 | feeder2_line83 | 1 | 354.6 | 78.3459 | 78.3417 | 22.0942 | 22.093
1050 | feeder2_line83 | 2 | 354.6 | 76.2688 | 76.2656 | 21.5084 | 21.5075
1050 | feeder2_line83 | 3 | 354.6 | 92.2905 | 92.2953 | 26.0266 | 26.028
1050 | feeder2_line84 | 1 | 354.6 | 1.2642e-11 | 1.2836e-06 | 3.5652e-12 | 3.6198e-07
1050 | feeder2_line84 | 2 | 354.6 | 1.2278 | 1.2278 | 0.34626 | 0.34626
1050 | feeder2_line84 | 3 | 354.6 | 1.0485e-11 | 1.2912e-06 | 2.9568e-12 | 3.6412e-07
1050 | feeder2_line85 | 1 | 99 | 0.078007 | 0.078003 | 0.078795 | 0.07879
1050 | feeder2_line85 | 2 | 99 | 4.9775e-08 | 4.5529e-07 | 5.0278e-08 | 4.5989e-07
1050 | feeder2_line85 | 3 | 99 | 4.8637e-08 | 4.6109e-07 | 4.9129e-08 | 4.6575e-07
1050 | feeder2_line86 | 1 | 354.6 | 78.4114 | 78.4071 | 22.1126 | 22.1114
1050 | feeder2_line86 | 2 | 354.6 | 76.2689 | 76.2656 | 21.5084 | 21.5075
1050 | feeder2_line86 | 3 | 354.6 | 92.2906 | 92.2953 | 26.0267 | 26.028
1050 | feeder2_line87 | 1 | 354.6 | 78.4115 | 78.4071 | 22.1127 | 22.1114
1050 | feeder2_line87 | 2 | 354.6 | 78.122 | 78.1186 | 22.031 | 22.0301
1050 | feeder2_line87 | 3 | 354.6 | 92.4915 | 92.4961 | 26.0833 | 26.0846
1050 | feeder2_line88 | 1 | 354.6 | 0.00011041 | 3.3262e-06 | 3.1135e-05 | 9.3802e-07
1050 | feeder2_line88 | 2 | 354.6 | 4.2307 | 4.2305 | 1.1931 | 1.193
1050 | feeder2_line88 | 3 | 354.6 | 2.6213 | 2.6213 | 0.73923 | 0.73922
1050 | feeder2_line89 | 1 | 354.6 | 78.4095 | 78.4071 | 22.1121 | 22.1114
1050 | feeder2_line89 | 2 | 354.6 | 79.0798 | 79.0782 | 22.3011 | 22.3007
1050 | feeder2_line89 | 3 | 354.6 | 92.4894 | 92.4961 | 26.0827 | 26.0846
1050 | feeder2_line90 | 1 | 354.6 | 0.00071392 | 2.0092e-06 | 0.00020133 | 5.6661e-07
1050 | feeder2_line90 | 2 | 354.6 | 1.9206 | 1.9209 | 0.54162 | 0.5417
1050 | feeder2_line90 | 3 | 354.6 | 0.00072404 | 2.0207e-06 | 0.00020419 | 5.6985e-07
1050 | feeder2_line91 | 1 | 354.6 | 78.4096 | 78.4071 | 22.1121 | 22.1114
1050 | feeder2_line91 | 2 | 354.6 | 79.0798 | 79.0782 | 22.3011 | 22.3007
1050 | feeder2_line91 | 3 | 354.6 | 93.9859 | 93.9926 | 26.5048 | 26.5067
1050 | feeder2_line92 | 1 | 354.6 | 1.4003e-11 | 1.0129e-06 | 3.949e-12 | 2.8565e-07
1050 | feeder2_line92 | 2 | 354.6 | 1.425e-11 | 1.0069e-06 | 4.0186e-12 | 2.8394e-07
1050 | feeder2_line92 | 3 | 354.6 | 1.7158 | 1.7158 | 0.48386 | 0.48386
1050 | feeder2_line93 | 1 | 99 | 2.4893e-08 | 3.3805e-07 | 2.5144e-08 | 3.4147e-07
1050 | feeder2_line93 | 2 | 99 | 1.2278 | 1.2278 | 1.2402 | 1.2402
1050 | feeder2_line93 | 3 | 99 | 2.4312e-08 | 3.404e-07 | 2.4558e-08 | 3.4383e-07
1050 | feeder2_line94 | 1 | 354.6 | 2.4889e-06 | 1.6461e-06 | 7.019e-07 | 4.6422e-07
1050 | feeder2_line94 | 2 | 354.6 | 0.89583 | 0.89583 | 0.25263 | 0.25263
1050 | feeder2_line94 | 3 | 354.6 | 2.4312e-06 | 1.6563e-06 | 6.8562e-07 | 4.671e-07
1050 | feeder2_line95 | 1 | 99 | 3.5294e-06 | 2.5793e-06 | 3.565e-06 | 2.6054e-06
1050 | feeder2_line95 | 2 | 99 | 4.2306 | 4.2305 | 4.2733 | 4.2733
1050 | feeder2_line95 | 3 | 99 | 3.556e-06 | 2.5968e-06 | 3.5919e-06 | 2.623e-06
1050 | feeder2_line96 | 1 | 354.6 | 0.00011963 | 6.1482e-07 | 3.3736e-05 | 1.7338e-07
1050 | feeder2_line96 | 2 | 354.6 | 0.00011894 | 6.1129e-07 | 3.3541e-05 | 1.7239e-07
1050 | feeder2_line96 | 3 | 354.6 | 2.6213 | 2.6213 | 0.73922 | 0.73922
1050 | feeder2_line97 | 1 | 354.6 | 80.2334 | 80.2306 | 22.6265 | 22.6257
1050 | feeder2_line97 | 2 | 354.6 | 79.08 | 79.0782 | 22.3012 | 22.3007
1050 | feeder2_line97 | 3 | 354.6 | 93.9862 | 93.9926 | 26.5049 | 26.5067
1050 | feeder2_line98 | 1 | 354.6 | 3.1767 | 3.1752 | 0.89585 | 0.89542
1050 | feeder2_line98 | 2 | 354.6 | 0.0016734 | 6.0935e-07 | 0.00047191 | 1.7184e-07
1050 | feeder2_line98 | 3 | 354.6 | 0.0017081 | 6.1937e-07 | 0.00048168 | 1.7467e-07
1050 | feeder2_line99 | 1 | 99 | 2.4881e-08 | 4.4202e-07 | 2.5132e-08 | 4.4648e-07
1050 | feeder2_line99 | 2 | 99 | 2.4891e-08 | 4.3933e-07 | 2.5143e-08 | 4.4377e-07
1050 | feeder2_line99 | 3 | 99 | 2.6213 | 2.6213 | 2.6478 | 2.6477
1050 | feeder2_line100 | 1 | 99 | 3.1752 | 3.1752 | 3.2073 | 3.2072
1050 | feeder2_line100 | 2 | 99 | 2.4906e-08 | 6.0309e-07 | 2.5157e-08 | 6.0918e-07
1050 | feeder2_line100 | 3 | 99 | 2.4308e-08 | 6.1112e-07 | 2.4553e-08 | 6.1729e-07
1050 | feeder2_line101 | 1 | 354.6 | 0.89756 | 0.8974 | 0.25312 | 0.25307
1050 | feeder2_line101 | 2 | 354.6 | 24.4247 | 24.4244 | 6.888 | 6.8879
1050 | feeder2_line101 | 3 | 354.6 | 18.559 | 18.5585 | 5.2338 | 5.2336
1050 | feeder2_line102 | 1 | 99 | 12.3658 | 12.3659 | 12.4907 | 12.4908
1050 | feeder2_line102 | 2 | 99 | 2.2923e-06 | 8.6283e-07 | 2.3155e-06 | 8.7155e-07
1050 | feeder2_line102 | 3 | 99 | 2.3354e-06 | 8.7362e-07 | 2.359e-06 | 8.8245e-07
1050 | feeder2_line103 | 1 | 99 | 5.4284e-07 | 7.9465e-07 | 5.4832e-07 | 8.0268e-07
1050 | feeder2_line103 | 2 | 99 | 10.6688 | 10.6688 | 10.7766 | 10.7766
1050 | feeder2_line103 | 3 | 99 | 5.4693e-07 | 7.9957e-07 | 5.5245e-07 | 8.0765e-07
1050 | feeder2_line104 | 1 | 354.6 | 0.89756 | 0.8974 | 0.25312 | 0.25307
1050 | feeder2_line104 | 2 | 354.6 | 13.7559 | 13.7556 | 3.8793 | 3.8792
1050 | feeder2_line104 | 3 | 354.6 | 18.5589 | 18.5585 | 5.2337 | 5.2336
1050 | feeder2_line105 | 1 | 99 | 2.5156e-06 | 7.3122e-07 | 2.541e-06 | 7.386e-07
1050 | feeder2_line105 | 2 | 99 | 2.4971e-06 | 7.2659e-07 | 2.5223e-06 | 7.3393e-07
1050 | feeder2_line105 | 3 | 99 | 1.4248 | 1.4248 | 1.4392 | 1.4392
1050 | feeder2_line106 | 1 | 354.6 | 0.89754 | 0.8974 | 0.25311 | 0.25307
1050 | feeder2_line106 | 2 | 354.6 | 13.7558 | 13.7556 | 3.8792 | 3.8792
1050 | feeder2_line106 | 3 | 354.6 | 17.1608 | 17.1604 | 4.8395 | 4.8394
1050 | feeder2_line107 | 1 | 99 | 3.2111e-07 | 8.9112e-07 | 3.2435e-07 | 9.0012e-07
1050 | feeder2_line107 | 2 | 99 | 11.6867 | 11.6867 | 11.8047 | 11.8048
1050 | feeder2_line107 | 3 | 99 | 3.2203e-07 | 8.9638e-07 | 3.2529e-07 | 9.0543e-07
1050 | feeder2_line108 | 1 | 354.6 | 0.89754 | 0.8974 | 0.25311 | 0.25307
1050 | feeder2_line108 | 2 | 354.6 | 2.0816 | 2.0814 | 0.58703 | 0.58697
1050 | feeder2_line108 | 3 | 354.6 | 17.1608 | 17.1604 | 4.8395 | 4.8394
1050 | feeder2_line109 | 1 | 354.6 | 86.6198 | 86.616 | 24.4275 | 24.4264
1050 | feeder2_line109 | 2 | 354.6 | 79.0809 | 79.0782 | 22.3014 | 22.3007
1050 | feeder2_line109 | 3 | 354.6 | 93.9872 | 93.9926 | 26.5051 | 26.5067
1050 | feeder2_line110 | 1 | 99 | 7.7777 | 7.7769 | 7.8562 | 7.8555
1050 | feeder2_line110 | 2 | 99 | 0.00078786 | 8.9273e-07 | 0.00079582 | 9.0175e-07
1050 | feeder2_line110 | 3 | 99 | 0.00080362 | 9.0449e-07 | 0.00081174 | 9.1362e-07
1050 | feeder2_line111 | 1 | 99 | 2.4879e-08 | 3.7751e-07 | 2.513e-08 | 3.8132e-07
1050 | feeder2_line111 | 2 | 99 | 1.9548 | 1.9547 | 1.9745 | 1.9745
1050 | feeder2_line111 | 3 | 99 | 2.4314e-08 | 3.8007e-07 | 2.4559e-08 | 3.8391e-07
1050 | feeder2_line112 | 1 | 99 | 3.2121e-07 | 9.0719e-07 | 3.2446e-07 | 9.1636e-07
1050 | feeder2_line112 | 2 | 99 | 2.2874 | 2.2873 | 2.3105 | 2.3104
1050 | feeder2_line112 | 3 | 99 | 3.2233e-07 | 9.1333e-07 | 3.2558e-07 | 9.2256e-07
1050 | feeder2_line113 | 1 | 99 | 0.098512 | 0.098508 | 0.099507 | 0.099503
1050 | feeder2_line113 | 2 | 99 | 3.196e-07 | 8.8922e-07 | 3.2283e-07 | 8.982e-07
1050 | feeder2_line113 | 3 | 99 | 3.2255e-07 | 9.0124e-07 | 3.2581e-07 | 9.1035e-07
1050 | feeder2_line114 | 1 | 99 | 10.7326 | 10.7326 | 10.841 | 10.8411
1050 | feeder2_line114 | 2 | 99 | 2.487e-08 | 4.2906e-07 | 2.5121e-08 | 4.3339e-07
1050 | feeder2_line114 | 3 | 99 | 2.4314e-08 | 4.3441e-07 | 2.456e-08 | 4.388e-07
1050 | feeder2_line115 | 1 | 99 | 2.4833e-08 | 5.5613e-07 | 2.5084e-08 | 5.6175e-07
1050 | feeder2_line115 | 2 | 99 | 0.062085 | 0.062084 | 0.062712 | 0.062711
1050 | feeder2_line115 | 3 | 99 | 2.433e-08 | 5.5928e-07 | 2.4575e-08 | 5.6493e-07
1050 | feeder2_line116 | 1 | 354.6 | 0.89756 | 0.8974 | 0.25312 | 0.25307
1050 | feeder2_line116 | 2 | 354.6 | 2.0222 | 2.022 | 0.57028 | 0.57022
1050 | feeder2_line116 | 3 | 354.6 | 17.1608 | 17.1604 | 4.8395 | 4.8394
1050 | feeder2_line117 | 1 | 99 | 4.982e-08 | 6.3527e-07 | 5.0324e-08 | 6.4168e-07
1050 | feeder2_line117 | 2 | 99 | 2.6696 | 2.6696 | 2.6966 | 2.6966
1050 | feeder2_line117 | 3 | 99 | 4.8607e-08 | 6.3993e-07 | 4.9098e-08 | 6.464e-07
1050 | feeder2_line118 | 1 | 354.6 | 86.6198 | 86.616 | 24.4275 | 24.4264
1050 | feeder2_line118 | 2 | 354.6 | 80.4797 | 80.477 | 22.6959 | 22.6951
1050 | feeder2_line118 | 3 | 354.6 | 93.9872 | 93.9926 | 26.5051 | 26.5067
1050 | feeder2_line119 | 1 | 99 | 2.4825e-08 | 5.9843e-07 | 2.5076e-08 | 6.0448e-07
1050 | feeder2_line119 | 2 | 99 | 2.4874e-08 | 5.9457e-07 | 2.5125e-08 | 6.0058e-07
1050 | feeder2_line119 | 3 | 99 | 1.4095 | 1.4095 | 1.4237 | 1.4237
1050 | feeder2_line120 | 1 | 354.6 | 0.89755 | 0.8974 | 0.25312 | 0.25307
1050 | feeder2_line120 | 2 | 354.6 | 2.0222 | 2.022 | 0.57028 | 0.57022
1050 | feeder2_line120 | 3 | 354.6 | 16.1588 | 16.1584 | 4.5569 | 4.5568
1050 | feeder2_line121 | 1 | 99 | 3.2111e-07 | 9.2673e-07 | 3.2436e-07 | 9.3609e-07
1050 | feeder2_line121 | 2 | 99 | 1.9353 | 1.9353 | 1.9548 | 1.9548
1050 | feeder2_line121 | 3 | 99 | 3.219e-07 | 9.3152e-07 | 3.2515e-07 | 9.4093e-07
1050 | feeder2_line122 | 1 | 354.6 | 0.89753 | 0.8974 | 0.25311 | 0.25308
1050 | feeder2_line122 | 2 | 354.6 | 0.090969 | 0.090731 | 0.025654 | 0.025587
1050 | feeder2_line122 | 3 | 354.6 | 16.1588 | 16.1584 | 4.5569 | 4.5568
1050 | feeder2_line123 | 1 | 99 | 5.678e-07 | 9.6032e-07 | 5.7353e-07 | 9.7002e-07
1050 | feeder2_line123 | 2 | 99 | 5.6413e-07 | 9.5415e-07 | 5.6983e-07 | 9.6379e-07
1050 | feeder2_line123 | 3 | 99 | 0.077206 | 0.077209 | 0.077986 | 0.077989
1050 | feeder2_line124 | 1 | 354.6 | 0.89757 | 0.89741 | 0.25312 | 0.25308
1050 | feeder2_line124 | 2 | 354.6 | 0.090874 | 0.09073 | 0.025627 | 0.025587
1050 | feeder2_line124 | 3 | 354.6 | 16.0825 | 16.0822 | 4.5354 | 4.5353
1050 | feeder2_line125 | 1 | 99 | 5.6781e-07 | 8.9273e-07 | 5.7354e-07 | 9.0174e-07
1050 | feeder2_line125 | 2 | 99 | 5.6413e-07 | 8.8698e-07 | 5.6983e-07 | 8.9594e-07
1050 | feeder2_line125 | 3 | 99 | 3.1718 | 3.1718 | 3.2038 | 3.2039
1050 | feeder2_line126 | 1 | 354.6 | 0.8977 | 0.89741 | 0.25316 | 0.25308
1050 | feeder2_line126 | 2 | 354.6 | 0.091027 | 0.09073 | 0.02567 | 0.025587
1050 | feeder2_line126 | 3 | 354.6 | 12.9998 | 12.9993 | 3.666 | 3.6659
1050 | feeder2_line127 | 1 | 99 | 5.6781e-07 | 1.0687e-06 | 5.7355e-07 | 1.0795e-06
1050 | feeder2_line127 | 2 | 99 | 5.6415e-07 | 1.0619e-06 | 5.6985e-07 | 1.0726e-06
1050 | feeder2_line127 | 3 | 99 | 2.5884 | 2.5884 | 2.6145 | 2.6145
1050 | feeder2_line128 | 1 | 354.6 | 0.89768 | 0.89741 | 0.25315 | 0.25308
1050 | feeder2_line128 | 2 | 354.6 | 0.090943 | 0.09073 | 0.025647 | 0.025587
1050 | feeder2_line128 | 3 | 354.6 | 10.4709 | 10.4705 | 2.9529 | 2.9528
1050 | feeder2_line129 | 1 | 99 | 5.4301e-07 | 8.666e-07 | 5.485e-07 | 8.7536e-07
1050 | feeder2_line129 | 2 | 99 | 0.090731 | 0.09073 | 0.091647 | 0.091646
1050 | feeder2_line129 | 3 | 99 | 5.4624e-07 | 8.7079e-07 | 5.5176e-07 | 8.7958e-07
1050 | feeder2_line130 | 1 | 354.6 | 0.89772 | 0.89741 | 0.25317 | 0.25308
1050 | feeder2_line130 | 2 | 354.6 | 0.00030275 | 4.5576e-06 | 8.5378e-05 | 1.2853e-06
1050 | feeder2_line130 | 3 | 354.6 | 10.4709 | 10.4705 | 2.9529 | 2.9528
1050 | feeder2_line131 | 1 | 99 | 5.678e-07 | 9.6049e-07 | 5.7354e-07 | 9.7019e-07
1050 | feeder2_line131 | 2 | 99 | 5.6415e-07 | 9.5434e-07 | 5.6985e-07 | 9.6398e-07
1050 | feeder2_line131 | 3 | 99 | 10.3936 | 10.3934 | 10.4985 | 10.4984
1050 | feeder2_line132 | 1 | 354.6 | 0.89755 | 0.89741 | 0.25312 | 0.25308
1050 | feeder2_line132 | 2 | 354.6 | 0.00012327 | 2.8656e-06 | 3.4764e-05 | 8.0812e-07
1050 | feeder2_line132 | 3 | 354.6 | 0.077463 | 0.0774 | 0.021845 | 0.021828
1050 | feeder2_line133 | 1 | 99 | 0.89742 | 0.89741 | 0.90649 | 0.90648
1050 | feeder2_line133 | 2 | 99 | 2.9451e-07 | 9.6197e-07 | 2.9749e-07 | 9.7169e-07
1050 | feeder2_line133 | 3 | 99 | 2.9746e-07 | 9.7277e-07 | 3.0046e-07 | 9.826e-07
1050 | feeder2_line134 | 1 | 354.6 | 9.9589e-12 | 1.7658e-06 | 2.8085e-12 | 4.9797e-07
1050 | feeder2_line134 | 2 | 354.6 | 1.2906e-11 | 1.7549e-06 | 3.6395e-12 | 4.9488e-07
1050 | feeder2_line134 | 3 | 354.6 | 0.077395 | 0.0774 | 0.021826 | 0.021828
1050 | feeder2_line135 | 1 | 99 | 3.0125 | 3.0125 | 3.043 | 3.0429
1050 | feeder2_line135 | 2 | 99 | 4.9878e-08 | 5.7515e-07 | 5.0381e-08 | 5.8096e-07
1050 | feeder2_line135 | 3 | 99 | 4.8601e-08 | 5.8326e-07 | 4.9092e-08 | 5.8915e-07
1050 | feeder2_line136 | 1 | 354.6 | 88.4917 | 88.4878 | 24.9554 | 24.9543
1050 | feeder2_line136 | 2 | 354.6 | 80.4796 | 80.477 | 22.6959 | 22.6951
1050 | feeder2_line136 | 3 | 354.6 | 93.9872 | 93.9926 | 26.5051 | 26.5067
1050 | feeder2_line137 | 1 | 99 | 0.086544 | 0.086537 | 0.087419 | 0.087412
1050 | feeder2_line137 | 2 | 99 | 8.3442e-07 | 1.5491e-06 | 8.4285e-07 | 1.5647e-06
1050 | feeder2_line137 | 3 | 99 | 8.4684e-07 | 1.571e-06 | 8.5539e-07 | 1.5869e-06
1050 | feeder2_line138 | 1 | 354.6 | 88.5688 | 88.5648 | 24.9771 | 24.976
1050 | feeder2_line138 | 2 | 354.6 | 80.4797 | 80.477 | 22.6959 | 22.6951
1050 | feeder2_line138 | 3 | 354.6 | 93.9873 | 93.9926 | 26.5052 | 26.5067
1050 | feeder2_line139 | 1 | 99 | 4.9847e-08 | 4.8589e-07 | 5.0351e-08 | 4.9079e-07
1050 | feeder2_line139 | 2 | 99 | 4.9888e-08 | 4.8266e-07 | 5.0392e-08 | 4.8754e-07
1050 | feeder2_line139 | 3 | 99 | 2.2487 | 2.2488 | 2.2715 | 2.2715
1050 | feeder2_line140 | 1 | 354.6 | 88.5688 | 88.5648 | 24.9771 | 24.976
1050 | feeder2_line140 | 2 | 354.6 | 80.4798 | 80.477 | 22.6959 | 22.6951
1050 | feeder2_line140 | 3 | 354.6 | 94.2171 | 94.2228 | 26.57 | 26.5716
1050 | feeder2_line141 | 1 | 99 | 2.4934e-06 | 4.8064e-07 | 2.5186e-06 | 4.855e-07
1050 | feeder2_line141 | 2 | 99 | 0.078448 | 0.078447 | 0.079241 | 0.07924
1050 | feeder2_line141 | 3 | 99 | 2.5238e-06 | 4.8427e-07 | 2.5493e-06 | 4.8916e-07
1050 | feeder2_line142 | 1 | 354.6 | 88.5687 | 88.5648 | 24.9771 | 24.976
1050 | feeder2_line142 | 2 | 354.6 | 80.5458 | 80.5431 | 22.7146 | 22.7138
1050 | feeder2_line142 | 3 | 354.6 | 94.217 | 94.2228 | 26.5699 | 26.5716
1050 | feeder2_line143 | 1 | 99 | 8.4021e-07 | 1.7079e-06 | 8.487e-07 | 1.7252e-06
1050 | feeder2_line143 | 2 | 99 | 11.6894 | 11.6894 | 11.8074 | 11.8075
1050 | feeder2_line143 | 3 | 99 | 8.4705e-07 | 1.7208e-06 | 8.5561e-07 | 1.7382e-06
1050 | feeder2_line144 | 1 | 354.6 | 88.5685 | 88.5648 | 24.977 | 24.976
1050 | feeder2_line144 | 2 | 354.6 | 89.5378 | 89.5356 | 25.2504 | 25.2497
1050 | feeder2_line144 | 3 | 354.6 | 94.2168 | 94.2228 | 26.5699 | 26.5716
1050 | feeder2_line145 | 1 | 99 | 2.4928e-08 | 4.7892e-07 | 2.518e-08 | 4.8376e-07
1050 | feeder2_line145 | 2 | 99 | 1.119 | 1.119 | 1.1303 | 1.1303
1050 | feeder2_line145 | 3 | 99 | 2.4301e-08 | 4.8255e-07 | 2.4547e-08 | 4.8742e-07
1050 | feeder2_line146 | 1 | 354.6 | 88.5684 | 88.5648 | 24.977 | 24.976
1050 | feeder2_line146 | 2 | 354.6 | 89.7831 | 89.781 | 25.3195 | 25.319
1050 | feeder2_line146 | 3 | 354.6 | 94.2167 | 94.2228 | 26.5699 | 26.5716
1050 | feeder2_line147 | 1 | 99 | 7.679 | 7.6791 | 7.7566 | 7.7567
1050 | feeder2_line147 | 2 | 99 | 1.1293e-06 | 2.1941e-06 | 1.1407e-06 | 2.2163e-06
1050 | feeder2_line147 | 3 | 99 | 1.1457e-06 | 2.2257e-06 | 1.1573e-06 | 2.2482e-06
1050 | feeder2_line148 | 1 | 99 | 0.085924 | 0.085918 | 0.086792 | 0.086786
1050 | feeder2_line148 | 2 | 99 | 5.8964e-07 | 1.4703e-06 | 5.9559e-07 | 1.4851e-06
1050 | feeder2_line148 | 3 | 99 | 5.9719e-07 | 1.4914e-06 | 6.0323e-07 | 1.5065e-06
1050 | feeder2_line149 | 1 | 354.6 | 95.2714 | 95.2676 | 26.8673 | 26.8662
1050 | feeder2_line149 | 2 | 354.6 | 89.7833 | 89.781 | 25.3196 | 25.319
1050 | feeder2_line149 | 3 | 354.6 | 94.2169 | 94.2228 | 26.5699 | 26.5716
1050 | feeder2_line150 | 1 | 354.6 | 95.2715 | 95.2676 | 26.8673 | 26.8662
1050 | feeder2_line150 | 2 | 354.6 | 98.5618 | 98.5597 | 27.7952 | 27.7946
1050 | feeder2_line150 | 3 | 354.6 | 94.217 | 94.2228 | 26.5699 | 26.5716
1050 | feeder2_line151 | 1 | 99 | 9.6255e-06 | 1.7581e-06 | 9.7227e-06 | 1.7759e-06
1050 | feeder2_line151 | 2 | 99 | 10.7629 | 10.7629 | 10.8716 | 10.8716
1050 | feeder2_line151 | 3 | 99 | 9.7636e-06 | 1.7714e-06 | 9.8622e-06 | 1.7893e-06
1050 | feeder2_line152 | 1 | 354.6 | 2.2232e-11 | 1.1719e-06 | 6.2697e-12 | 3.305e-07
1050 | feeder2_line152 | 2 | 354.6 | 1.2091e-11 | 1.1642e-06 | 3.4099e-12 | 3.2833e-07
1050 | feeder2_line152 | 3 | 354.6 | 0.076905 | 0.076909 | 0.021688 | 0.021689
1050 | feeder2_line153 | 1 | 99 | 1.9299 | 1.9299 | 1.9494 | 1.9494
1050 | feeder2_line153 | 2 | 99 | 4.9945e-08 | 5.8226e-07 | 5.0449e-08 | 5.8814e-07
1050 | feeder2_line153 | 3 | 99 | 4.8625e-08 | 5.9066e-07 | 4.9116e-08 | 5.9663e-07
1050 | feeder2_line154 | 1 | 99 | 5.6882e-07 | 8.7233e-07 | 5.7457e-07 | 8.8114e-07
1050 | feeder2_line154 | 2 | 99 | 5.6495e-07 | 8.6643e-07 | 5.7066e-07 | 8.7518e-07
1050 | feeder2_line154 | 3 | 99 | 2.653 | 2.653 | 2.6798 | 2.6798
1050 | feeder2_line155 | 1 | 99 | 96.7156 | 96.7118 | 97.6926 | 97.6886
1050 | feeder2_line155 | 2 | 99 | 98.5618 | 98.5597 | 99.5573 | 99.5552
1050 | feeder2_line155 | 3 | 99 | 96.5716 | 96.5775 | 97.5471 | 97.5531
1050 | feeder2_line156 | 1 | 99 | 5.9358e-07 | 1.148e-06 | 5.9958e-07 | 1.1596e-06
1050 | feeder2_line156 | 2 | 99 | 10.6731 | 10.6731 | 10.7809 | 10.7809
1050 | feeder2_line156 | 3 | 99 | 5.9733e-07 | 1.1567e-06 | 6.0336e-07 | 1.1684e-06
1050 | feeder2_line157 | 1 | 99 | 2.4943e-08 | 2.4924e-07 | 2.5195e-08 | 2.5176e-07
1050 | feeder2_line157 | 2 | 99 | 0.09117 | 0.09117 | 0.092091 | 0.09209
1050 | feeder2_line157 | 3 | 99 | 2.4304e-08 | 2.5112e-07 | 2.4549e-08 | 2.5366e-07
1080 | feeder2_line1 | 1 | 354.6 | 45.6513 | 45.6503 | 12.874 | 12.8738
1080 | feeder2_line1 | 2 | 354.6 | 53.9622 | 53.967 | 15.2178 | 15.2191
1080 | feeder2_line1 | 3 | 354.6 | 61.862 | 61.8597 | 17.4456 | 17.4449
1080 | feeder2_line2 | 1 | 354.6 | 44.6576 | 44.6567 | 12.5938 | 12.5935
1080 | feeder2_line2 | 2 | 354.6 | 53.9624 | 53.967 | 15.2178 | 15.2191
1080 | feeder2_line2 | 3 | 354.6 | 61.8622 | 61.8597 | 17.4456 | 17.4449
1080 | feeder2_line3 | 1 | 80.1 | 1.4514 | 1.4514 | 1.812 | 1.812
1080 | feeder2_line3 | 2 | 80.1 | 5.7119e-07 | 1.0555e-06 | 7.1309e-07 | 1.3177e-06
1080 | feeder2_line3 | 3 | 80.1 | 5.7216e-07 | 1.0573e-06 | 7.1431e-07 | 1.32e-06
1080 | feeder2_line4 | 1 | 354.6 | 44.6574 | 44.6567 | 12.5938 | 12.5935
1080 | feeder2_line4 | 2 | 354.6 | 54.082 | 54.0864 | 15.2515 | 15.2528
1080 | feeder2_line4 | 3 | 354.6 | 61.8624 | 61.8597 | 17.4457 | 17.4449
1080 | feeder2_line5 | 1 | 80.1 | 5.6805e-07 | 9.9124e-07 | 7.0917e-07 | 1.2375e-06
1080 | feeder2_line5 | 2 | 80.1 | 1.4044 | 1.4044 | 1.7533 | 1.7533
1080 | feeder2_line5 | 3 | 80.1 | 5.7221e-07 | 9.9845e-07 | 7.1438e-07 | 1.2465e-06
1080 | feeder2_line6 | 1 | 80.1 | 5.6792e-07 | 1.1658e-06 | 7.0902e-07 | 1.4555e-06
1080 | feeder2_line6 | 2 | 80.1 | 5.7127e-07 | 1.1726e-06 | 7.1319e-07 | 1.4639e-06
1080 | feeder2_line6 | 3 | 80.1 | 0.99476 | 0.99476 | 1.2419 | 1.2419
1080 | feeder2_line7 | 1 | 354.6 | 44.6574 | 44.6567 | 12.5937 | 12.5935
1080 | feeder2_line7 | 2 | 354.6 | 54.0821 | 54.0864 | 15.2516 | 15.2528
1080 | feeder2_line7 | 3 | 354.6 | 62.7871 | 62.7844 | 17.7065 | 17.7057
1080 | feeder2_line8 | 1 | 80.1 | 7.1799 | 7.1799 | 8.9637 | 8.9637
1080 | feeder2_line8 | 2 | 80.1 | 5.714e-07 | 1.1309e-06 | 7.1336e-07 | 1.4119e-06
1080 | feeder2_line8 | 3 | 80.1 | 5.7251e-07 | 1.1331e-06 | 7.1474e-07 | 1.4146e-06
1080 | feeder2_line9 | 1 | 354.6 | 39.0128 | 39.0122 | 11.0019 | 11.0017
1080 | feeder2_line9 | 2 | 354.6 | 54.0821 | 54.0864 | 15.2516 | 15.2528
1080 | feeder2_line9 | 3 | 354.6 | 62.7871 | 62.7844 | 17.7065 | 17.7057
1080 | feeder2_line10 | 1 | 80.1 | 8.387e-07 | 1.4832e-06 | 1.0471e-06 | 1.8517e-06
1080 | feeder2_line10 | 2 | 80.1 | 7.1148 | 7.1149 | 8.8824 | 8.8825
1080 | feeder2_line10 | 3 | 80.1 | 8.4644e-07 | 1.4963e-06 | 1.0567e-06 | 1.868e-06
1080 | feeder2_line11 | 1 | 354.6 | 39.0129 | 39.0122 | 11.002 | 11.0017
1080 | feeder2_line11 | 2 | 354.6 | 59.4686 | 59.4728 | 16.7706 | 16.7718
1080 | feeder2_line11 | 3 | 354.6 | 62.7872 | 62.7844 | 17.7065 | 17.7057
1080 | feeder2_line12 | 1 | 80.1 | 5.4226e-07 | 9.8362e-07 | 6.7698e-07 | 1.228e-06
1080 | feeder2_line12 | 2 | 80.1 | 5.4695e-07 | 9.9066e-07 | 6.8283e-07 | 1.2368e-06
1080 | feeder2_line12 | 3 | 80.1 | 1.1682 | 1.1682 | 1.4584 | 1.4585
1080 | feeder2_line13 | 1 | 354.6 | 39.013 | 39.0122 | 11.002 | 11.0017
1080 | feeder2_line13 | 2 | 354.6 | 59.4686 | 59.4728 | 16.7706 | 16.7718
1080 | feeder2_line13 | 3 | 354.6 | 63.8501 | 63.8473 | 18.0062 | 18.0054
1080 | feeder2_line14 | 1 | 80.1 | 18.5896 | 18.5895 | 23.2079 | 23.2078
1080 | feeder2_line14 | 2 | 80.1 | 2.9804e-07 | 6.4605e-07 | 3.7208e-07 | 8.0655e-07
1080 | feeder2_line14 | 3 | 80.1 | 2.9872e-07 | 6.4738e-07 | 3.7293e-07 | 8.0821e-07
1080 | feeder2_line15 | 1 | 354.6 | 31.1605 | 31.1598 | 8.7875 | 8.7873
1080 | feeder2_line15 | 2 | 354.6 | 59.4686 | 59.4728 | 16.7706 | 16.7718
1080 | feeder2_line15 | 3 | 354.6 | 63.8501 | 63.8473 | 18.0062 | 18.0054
1080 | feeder2_line16 | 1 | 80.1 | 5.6713e-07 | 1.0218e-06 | 7.0803e-07 | 1.2756e-06
1080 | feeder2_line16 | 2 | 80.1 | 2.4449 | 2.445 | 3.0523 | 3.0524
1080 | feeder2_line16 | 3 | 80.1 | 5.7284e-07 | 1.032e-06 | 7.1515e-07 | 1.2884e-06
1080 | feeder2_line17 | 1 | 354.6 | 31.1606 | 31.1598 | 8.7875 | 8.7873
1080 | feeder2_line17 | 2 | 354.6 | 61.6542 | 61.6585 | 17.387 | 17.3882
1080 | feeder2_line17 | 3 | 354.6 | 63.8501 | 63.8473 | 18.0062 | 18.0054
1080 | feeder2_line18 | 1 | 80.1 | 5.4131e-07 | 7.3064e-07 | 6.7579e-07 | 9.1217e-07
1080 | feeder2_line18 | 2 | 80.1 | 5.4758e-07 | 7.3769e-07 | 6.8362e-07 | 9.2097e-07
1080 | feeder2_line18 | 3 | 80.1 | 1.3122 | 1.3122 | 1.6382 | 1.6382
1080 | feeder2_line19 | 1 | 354.6 | 31.1606 | 31.1598 | 8.7875 | 8.7873
1080 | feeder2_line19 | 2 | 354.6 | 61.6542 | 61.6585 | 17.387 | 17.3882
1080 | feeder2_line19 | 3 | 354.6 | 65.0354 | 65.0325 | 18.3405 | 18.3397
1080 | feeder2_line20 | 1 | 99 | 5.4106e-07 | 8.7567e-07 | 5.4652e-07 | 8.8451e-07
1080 | feeder2_line20 | 2 | 99 | 5.4775e-07 | 8.8469e-07 | 5.5329e-07 | 8.9363e-07
1080 | feeder2_line20 | 3 | 99 | 1.4838 | 1.4838 | 1.4988 | 1.4987
1080 | feeder2_line21 | 1 | 354.6 | 31.1606 | 31.1598 | 8.7875 | 8.7873
1080 | feeder2_line21 | 2 | 354.6 | 61.6544 | 61.6585 | 17.387 | 17.3882
1080 | feeder2_line21 | 3 | 354.6 | 66.3849 | 66.3819 | 18.7211 | 18.7202
1080 | feeder2_line22 | 1 | 99 | 5.6617e-07 | 1.0036e-06 | 5.7189e-07 | 1.0137e-06
1080 | feeder2_line22 | 2 | 99 | 2.1737 | 2.1737 | 2.1956 | 2.1956
1080 | feeder2_line22 | 3 | 99 | 5.7365e-07 | 1.0167e-06 | 5.7945e-07 | 1.027e-06
1080 | feeder2_line23 | 1 | 99 | 5.6617e-07 | 9.3945e-07 | 5.7189e-07 | 9.4894e-07
1080 | feeder2_line23 | 2 | 99 | 5.7233e-07 | 9.4952e-07 | 5.7811e-07 | 9.5911e-07
1080 | feeder2_line23 | 3 | 99 | 1.6389 | 1.6389 | 1.6555 | 1.6555
1080 | feeder2_line24 | 1 | 354.6 | 31.1606 | 31.1598 | 8.7875 | 8.7873
1080 | feeder2_line24 | 2 | 354.6 | 63.5405 | 63.5445 | 17.9189 | 17.9201
1080 | feeder2_line24 | 3 | 354.6 | 67.8766 | 67.8735 | 19.1417 | 19.1409
1080 | feeder2_line25 | 1 | 99 | 2.188 | 2.188 | 2.2101 | 2.2101
1080 | feeder2_line25 | 2 | 99 | 4.891e-08 | 6.9053e-07 | 4.9404e-08 | 6.9751e-07
1080 | feeder2_line25 | 3 | 99 | 4.939e-08 | 6.922e-07 | 4.9889e-08 | 6.9919e-07
1080 | feeder2_line26 | 1 | 99 | 0.93968 | 0.93968 | 0.94917 | 0.94918
1080 | feeder2_line26 | 2 | 99 | 5.4805e-07 | 8.5553e-07 | 5.5359e-07 | 8.6417e-07
1080 | feeder2_line26 | 3 | 99 | 5.4919e-07 | 8.576e-07 | 5.5473e-07 | 8.6626e-07
1080 | feeder2_line27 | 1 | 354.6 | 30.6585 | 30.6577 | 8.6459 | 8.6457
1080 | feeder2_line27 | 2 | 354.6 | 63.5405 | 63.5445 | 17.9189 | 17.9201
1080 | feeder2_line27 | 3 | 354.6 | 67.8766 | 67.8735 | 19.1417 | 19.1409
1080 | feeder2_line28 | 1 | 99 | 2.4981e-06 | 7.0167e-07 | 2.5233e-06 | 7.0875e-07
1080 | feeder2_line28 | 2 | 99 | 0.80012 | 0.80013 | 0.80821 | 0.80821
1080 | feeder2_line28 | 3 | 99 | 2.5504e-06 | 7.1232e-07 | 2.5762e-06 | 7.1952e-07
1080 | feeder2_line29 | 1 | 354.6 | 30.6585 | 30.6577 | 8.6459 | 8.6457
1080 | feeder2_line29 | 2 | 354.6 | 64.2623 | 64.2663 | 18.1225 | 18.1236
1080 | feeder2_line29 | 3 | 354.6 | 67.8766 | 67.8735 | 19.1417 | 19.1409
1080 | feeder2_line30 | 1 | 266.4 | 31.9595 | 31.9592 | 11.9968 | 11.9967
1080 | feeder2_line30 | 2 | 266.4 | 2.3855 | 2.3852 | 0.89546 | 0.89533
1080 | feeder2_line30 | 3 | 266.4 | 12.6579 | 12.6578 | 4.7515 | 4.7514
1080 | feeder2_line31 | 1 | 354.6 | 41.9956 | 41.9946 | 11.8431 | 11.8428
1080 | feeder2_line31 | 2 | 354.6 | 66.4825 | 66.486 | 18.7486 | 18.7496
1080 | feeder2_line31 | 3 | 354.6 | 77.0199 | 77.0161 | 21.7202 | 21.7192
1080 | feeder2_line32 | 1 | 354.6 | 41.9957 | 41.9946 | 11.8431 | 11.8428
1080 | feeder2_line32 | 2 | 354.6 | 68.8654 | 68.8689 | 19.4206 | 19.4216
1080 | feeder2_line32 | 3 | 354.6 | 77.0199 | 77.0161 | 21.7202 | 21.7192
1080 | feeder2_line33 | 1 | 99 | 5.0912e-08 | 6.762e-07 | 5.1426e-08 | 6.8303e-07
1080 | feeder2_line33 | 2 | 99 | 2.6666 | 2.6666 | 2.6935 | 2.6935
1080 | feeder2_line33 | 3 | 99 | 4.9313e-08 | 6.8815e-07 | 4.9812e-08 | 6.951e-07
1080 | feeder2_line34 | 1 | 354.6 | 41.9956 | 41.9946 | 11.8431 | 11.8428
1080 | feeder2_line34 | 2 | 354.6 | 68.8654 | 68.8689 | 19.4206 | 19.4216
1080 | feeder2_line34 | 3 | 354.6 | 77.1022 | 77.0984 | 21.7434 | 21.7424
1080 | feeder2_line35 | 1 | 99 | 2.9519e-07 | 7.4877e-07 | 2.9817e-07 | 7.5633e-07
1080 | feeder2_line35 | 2 | 99 | 2.9891e-07 | 7.5991e-07 | 3.0192e-07 | 7.6759e-07
1080 | feeder2_line35 | 3 | 99 | 0.085291 | 0.085288 | 0.086153 | 0.086149
1080 | feeder2_line36 | 1 | 354.6 | 51.656 | 51.6552 | 14.5674 | 14.5672
1080 | feeder2_line36 | 2 | 354.6 | 68.8654 | 68.8689 | 19.4206 | 19.4216
1080 | feeder2_line36 | 3 | 354.6 | 77.1021 | 77.0984 | 21.7434 | 21.7424
1080 | feeder2_line37 | 1 | 99 | 14.658 | 14.658 | 14.806 | 14.806
1080 | feeder2_line37 | 2 | 99 | 2.9894e-07 | 8.4094e-07 | 3.0196e-07 | 8.4944e-07
1080 | feeder2_line37 | 3 | 99 | 2.9996e-07 | 8.4358e-07 | 3.0299e-07 | 8.521e-07
1080 | feeder2_line38 | 1 | 99 | 3.206e-07 | 7.6452e-07 | 3.2384e-07 | 7.7224e-07
1080 | feeder2_line38 | 2 | 99 | 0.077026 | 0.077029 | 0.077804 | 0.077807
1080 | feeder2_line38 | 3 | 99 | 3.2433e-07 | 7.7769e-07 | 3.2761e-07 | 7.8554e-07
1080 | feeder2_line39 | 1 | 266.4 | 31.9595 | 31.9592 | 11.9968 | 11.9967
1080 | feeder2_line39 | 2 | 266.4 | 2.3085 | 2.3082 | 0.86656 | 0.86643
1080 | feeder2_line39 | 3 | 266.4 | 12.6579 | 12.6578 | 4.7515 | 4.7514
1080 | feeder2_line40 | 1 | 354.6 | 53.4684 | 53.4677 | 15.0785 | 15.0783
1080 | feeder2_line40 | 2 | 354.6 | 68.8654 | 68.8689 | 19.4206 | 19.4216
1080 | feeder2_line40 | 3 | 354.6 | 77.1022 | 77.0984 | 21.7434 | 21.7424
1080 | feeder2_line41 | 1 | 99 | 2.1906 | 2.1906 | 2.2128 | 2.2128
1080 | feeder2_line41 | 2 | 99 | 4.8779e-08 | 7.3489e-07 | 4.9271e-08 | 7.4232e-07
1080 | feeder2_line41 | 3 | 99 | 4.9301e-08 | 7.3724e-07 | 4.9799e-08 | 7.4469e-07
1080 | feeder2_line42 | 1 | 99 | 2.9507e-07 | 7.3768e-07 | 2.9805e-07 | 7.4513e-07
1080 | feeder2_line42 | 2 | 99 | 2.9881e-07 | 7.4872e-07 | 3.0182e-07 | 7.5629e-07
1080 | feeder2_line42 | 3 | 99 | 1.1855 | 1.1855 | 1.1974 | 1.1974
1080 | feeder2_line43 | 1 | 266.4 | 31.9594 | 31.9592 | 11.9968 | 11.9967
1080 | feeder2_line43 | 2 | 266.4 | 2.3084 | 2.3082 | 0.86652 | 0.86643
1080 | feeder2_line43 | 3 | 266.4 | 11.6385 | 11.6384 | 4.3688 | 4.3688
1080 | feeder2_line44 | 1 | 354.6 | 53.4684 | 53.4677 | 15.0785 | 15.0783
1080 | feeder2_line44 | 2 | 354.6 | 68.8655 | 68.8689 | 19.4206 | 19.4216
1080 | feeder2_line44 | 3 | 354.6 | 78.5297 | 78.5258 | 22.146 | 22.1449
1080 | feeder2_line45 | 1 | 99 | 5.0994e-08 | 5.7089e-07 | 5.1509e-08 | 5.7666e-07
1080 | feeder2_line45 | 2 | 99 | 4.8779e-08 | 5.796e-07 | 4.9271e-08 | 5.8545e-07
1080 | feeder2_line45 | 3 | 99 | 1.4869 | 1.4869 | 1.5019 | 1.5019
1080 | feeder2_line46 | 1 | 99 | 5.6467e-07 | 1.3373e-06 | 5.7038e-07 | 1.3508e-06
1080 | feeder2_line46 | 2 | 99 | 5.7326e-07 | 1.3573e-06 | 5.7905e-07 | 1.371e-06
1080 | feeder2_line46 | 3 | 99 | 1.1081 | 1.1081 | 1.1193 | 1.1193
1080 | feeder2_line47 | 1 | 266.4 | 31.9595 | 31.9592 | 11.9968 | 11.9967
1080 | feeder2_line47 | 2 | 266.4 | 2.3084 | 2.3082 | 0.86652 | 0.86643
1080 | feeder2_line47 | 3 | 266.4 | 10.627 | 10.6268 | 3.9891 | 3.989
1080 | feeder2_line48 | 1 | 99 | 2.8362 | 2.8362 | 2.8649 | 2.8649
1080 | feeder2_line48 | 2 | 99 | 4.8717e-08 | 7.3082e-07 | 4.9209e-08 | 7.3821e-07
1080 | feeder2_line48 | 3 | 99 | 4.9316e-08 | 7.3259e-07 | 4.9814e-08 | 7.3999e-07
1080 | feeder2_line49 | 1 | 266.4 | 29.2231 | 29.2229 | 10.9696 | 10.9695
1080 | feeder2_line49 | 2 | 266.4 | 2.3084 | 2.3082 | 0.86651 | 0.86643
1080 | feeder2_line49 | 3 | 266.4 | 10.6269 | 10.6268 | 3.9891 | 3.989
1080 | feeder2_line50 | 1 | 99 | 5.6451e-07 | 1.2167e-06 | 5.7021e-07 | 1.2289e-06
1080 | feeder2_line50 | 2 | 99 | 0.99465 | 0.99466 | 1.0047 | 1.0047
1080 | feeder2_line50 | 3 | 99 | 5.7464e-07 | 1.2383e-06 | 5.8044e-07 | 1.2508e-06
1080 | feeder2_line51 | 1 | 99 | 19.9582 | 19.9582 | 20.1598 | 20.1598
1080 | feeder2_line51 | 2 | 99 | 5.7324e-07 | 1.341e-06 | 5.7903e-07 | 1.3546e-06
1080 | feeder2_line51 | 3 | 99 | 5.746e-07 | 1.3442e-06 | 5.8041e-07 | 1.3578e-06
1080 | feeder2_line52 | 1 | 266.4 | 9.2648 | 9.2647 | 3.4778 | 3.4777
1080 | feeder2_line52 | 2 | 266.4 | 1.3146 | 1.3145 | 0.49347 | 0.49344
1080 | feeder2_line52 | 3 | 266.4 | 10.6268 | 10.6268 | 3.989 | 3.989
1080 | feeder2_line53 | 1 | 99 | 5.3905e-07 | 7.4253e-07 | 5.4449e-07 | 7.5003e-07
1080 | feeder2_line53 | 2 | 99 | 1.3145 | 1.3145 | 1.3278 | 1.3278
1080 | feeder2_line53 | 3 | 99 | 5.4999e-07 | 7.5572e-07 | 5.5554e-07 | 7.6335e-07
1080 | feeder2_line54 | 1 | 266.4 | 9.2646 | 9.2647 | 3.4777 | 3.4777
1080 | feeder2_line54 | 2 | 266.4 | 8.5457e-05 | 4.6239e-06 | 3.2078e-05 | 1.7357e-06
1080 | feeder2_line54 | 3 | 266.4 | 10.6267 | 10.6268 | 3.989 | 3.989
1080 | feeder2_line55 | 1 | 99 | 2.3801 | 2.3801 | 2.4041 | 2.4041
1080 | feeder2_line55 | 2 | 99 | 4.879e-08 | 7.3046e-07 | 4.9283e-08 | 7.3784e-07
1080 | feeder2_line55 | 3 | 99 | 4.9293e-08 | 7.3302e-07 | 4.9791e-08 | 7.4043e-07
1080 | feeder2_line56 | 1 | 354.6 | 54.9121 | 54.9113 | 15.4857 | 15.4854
1080 | feeder2_line56 | 2 | 354.6 | 68.8655 | 68.8689 | 19.4206 | 19.4216
1080 | feeder2_line56 | 3 | 354.6 | 78.5297 | 78.5258 | 22.146 | 22.1449
1080 | feeder2_line57 | 1 | 99 | 7.6371e-07 | 1.5209e-06 | 7.7142e-07 | 1.5363e-06
1080 | feeder2_line57 | 2 | 99 | 7.3042e-07 | 1.5443e-06 | 7.378e-07 | 1.5599e-06
1080 | feeder2_line57 | 3 | 99 | 10.6268 | 10.6268 | 10.7341 | 10.7341
1080 | feeder2_line58 | 1 | 266.4 | 9.2647 | 9.2647 | 3.4777 | 3.4777
1080 | feeder2_line58 | 2 | 266.4 | 1.8946e-05 | 2.6844e-06 | 7.112e-06 | 1.0077e-06
1080 | feeder2_line58 | 3 | 266.4 | 1.9042e-05 | 2.6909e-06 | 7.1481e-06 | 1.0101e-06
1080 | feeder2_line59 | 1 | 99 | 5.0911e-08 | 5.2866e-07 | 5.1425e-08 | 5.34e-07
1080 | feeder2_line59 | 2 | 99 | 4.8686e-08 | 5.3682e-07 | 4.9178e-08 | 5.4224e-07
1080 | feeder2_line59 | 3 | 99 | 9.5743 | 9.5743 | 9.671 | 9.671
1080 | feeder2_line60 | 1 | 99 | 2.9496e-07 | 7.9898e-07 | 2.9794e-07 | 8.0705e-07
1080 | feeder2_line60 | 2 | 99 | 2.9882e-07 | 8.113e-07 | 3.0184e-07 | 8.195e-07
1080 | feeder2_line60 | 3 | 99 | 1.1715 | 1.1715 | 1.1833 | 1.1833
1080 | feeder2_line61 | 1 | 266.4 | 1.4297 | 1.4298 | 0.53666 | 0.53673
1080 | feeder2_line61 | 2 | 266.4 | 4.8289 | 4.8291 | 1.8127 | 1.8127
1080 | feeder2_line61 | 3 | 266.4 | 4.239 | 4.2392 | 1.5912 | 1.5913
1080 | feeder2_line62 | 1 | 354.6 | 56.1859 | 56.1853 | 15.8449 | 15.8447
1080 | feeder2_line62 | 2 | 354.6 | 73.3288 | 73.3324 | 20.6793 | 20.6803
1080 | feeder2_line62 | 3 | 354.6 | 82.596 | 82.5923 | 23.2927 | 23.2917
1080 | feeder2_line63 | 1 | 99 | 0.090833 | 0.090833 | 0.09175 | 0.09175
1080 | feeder2_line63 | 2 | 99 | 5.7332e-07 | 1.2198e-06 | 5.7911e-07 | 1.2321e-06
1080 | feeder2_line63 | 3 | 99 | 5.7462e-07 | 1.2226e-06 | 5.8042e-07 | 1.235e-06
1080 | feeder2_line64 | 1 | 99 | 9.174 | 9.174 | 9.2667 | 9.2667
1080 | feeder2_line64 | 2 | 99 | 7.8532e-12 | 3.2133e-07 | 7.9325e-12 | 3.2458e-07
1080 | feeder2_line64 | 3 | 99 | 7.1853e-12 | 3.2206e-07 | 7.2579e-12 | 3.2531e-07
1080 | feeder2_line65 | 1 | 99 | 5.1128e-08 | 6.3185e-07 | 5.1644e-08 | 6.3823e-07
1080 | feeder2_line65 | 2 | 99 | 1.4076 | 1.4076 | 1.4218 | 1.4218
1080 | feeder2_line65 | 3 | 99 | 4.9294e-08 | 6.4444e-07 | 4.9792e-08 | 6.5095e-07
1080 | feeder2_line66 | 1 | 354.6 | 56.1859 | 56.1853 | 15.8449 | 15.8447
1080 | feeder2_line66 | 2 | 354.6 | 73.7189 | 73.7226 | 20.7893 | 20.7904
1080 | feeder2_line66 | 3 | 354.6 | 82.596 | 82.5923 | 23.2927 | 23.2917
1080 | feeder2_line67 | 1 | 99 | 2.554e-08 | 3.5719e-07 | 2.5798e-08 | 3.608e-07
1080 | feeder2_line67 | 2 | 99 | 2.4397e-08 | 3.628e-07 | 2.4644e-08 | 3.6646e-07
1080 | feeder2_line67 | 3 | 99 | 2.1685 | 2.1685 | 2.1904 | 2.1904
1080 | feeder2_line68 | 1 | 266.4 | 1.4297 | 1.4298 | 0.53668 | 0.53673
1080 | feeder2_line68 | 2 | 266.4 | 4.829 | 4.8291 | 1.8127 | 1.8127
1080 | feeder2_line68 | 3 | 266.4 | 2.0798 | 2.0799 | 0.78071 | 0.78076
1080 | feeder2_line69 | 1 | 99 | 6.0333 | 6.0332 | 6.0942 | 6.0941
1080 | feeder2_line69 | 2 | 99 | 2.5543e-06 | 6.665e-07 | 2.5801e-06 | 6.7323e-07
1080 | feeder2_line69 | 3 | 99 | 2.5626e-06 | 6.6914e-07 | 2.5885e-06 | 6.759e-07
1080 | feeder2_line70 | 1 | 354.6 | 60.4011 | 60.4007 | 17.0336 | 17.0335
1080 | feeder2_line70 | 2 | 354.6 | 73.7188 | 73.7226 | 20.7893 | 20.7904
1080 | feeder2_line70 | 3 | 354.6 | 82.5959 | 82.5923 | 23.2927 | 23.2917
1080 | feeder2_line71 | 1 | 99 | 5.1153e-08 | 7.0494e-07 | 5.167e-08 | 7.1206e-07
1080 | feeder2_line71 | 2 | 99 | 6.6404 | 6.6405 | 6.7075 | 6.7075
1080 | feeder2_line71 | 3 | 99 | 4.9288e-08 | 7.1921e-07 | 4.9786e-08 | 7.2647e-07
1080 | feeder2_line72 | 1 | 354.6 | 60.4012 | 60.4007 | 17.0336 | 17.0335
1080 | feeder2_line72 | 2 | 354.6 | 79.5419 | 79.5455 | 22.4314 | 22.4325
1080 | feeder2_line72 | 3 | 354.6 | 82.596 | 82.5923 | 23.2927 | 23.2917
1080 | feeder2_line73 | 1 | 99 | 5.9052e-07 | 1.5121e-06 | 5.9649e-07 | 1.5274e-06
1080 | feeder2_line73 | 2 | 99 | 2.665 | 2.665 | 2.6919 | 2.6919
1080 | feeder2_line73 | 3 | 99 | 6.0071e-07 | 1.5416e-06 | 6.0678e-07 | 1.5571e-06
1080 | feeder2_line74 | 1 | 99 | 5.1072e-08 | 4.5101e-07 | 5.1588e-08 | 4.5556e-07
1080 | feeder2_line74 | 2 | 99 | 2.0823 | 2.0823 | 2.1033 | 2.1034
1080 | feeder2_line74 | 3 | 99 | 4.929e-08 | 4.5978e-07 | 4.9788e-08 | 4.6442e-07
1080 | feeder2_line75 | 1 | 266.4 | 1.4298 | 1.4298 | 0.53672 | 0.53673
1080 | feeder2_line75 | 2 | 266.4 | 0.089512 | 0.089547 | 0.033601 | 0.033614
1080 | feeder2_line75 | 3 | 266.4 | 2.0799 | 2.0799 | 0.78074 | 0.78076
1080 | feeder2_line76 | 1 | 99 | 1.4298 | 1.4298 | 1.4443 | 1.4443
1080 | feeder2_line76 | 2 | 99 | 8.4874e-07 | 1.5843e-06 | 8.5731e-07 | 1.6003e-06
1080 | feeder2_line76 | 3 | 99 | 8.5181e-07 | 1.5902e-06 | 8.6042e-07 | 1.6063e-06
1080 | feeder2_line77 | 1 | 99 | 2.554e-08 | 5.6676e-07 | 2.5798e-08 | 5.7249e-07
1080 | feeder2_line77 | 2 | 99 | 2.4398e-08 | 5.7564e-07 | 2.4644e-08 | 5.8145e-07
1080 | feeder2_line77 | 3 | 99 | 2.0799 | 2.0799 | 2.1009 | 2.1009
1080 | feeder2_line78 | 1 | 266.4 | 6.0093e-12 | 9.4118e-07 | 2.2557e-12 | 3.533e-07
1080 | feeder2_line78 | 2 | 266.4 | 0.089545 | 0.089547 | 0.033613 | 0.033614
1080 | feeder2_line78 | 3 | 266.4 | 1.6121e-11 | 9.577e-07 | 6.0514e-12 | 3.595e-07
1080 | feeder2_line79 | 1 | 354.6 | 13.5672 | 13.5668 | 3.8261 | 3.8259
1080 | feeder2_line79 | 2 | 354.6 | 6.4547 | 6.4544 | 1.8203 | 1.8202
1080 | feeder2_line79 | 3 | 354.6 | 9.6824 | 9.6819 | 2.7305 | 2.7304
1080 | feeder2_line80 | 1 | 354.6 | 72.8795 | 72.8786 | 20.5526 | 20.5523
1080 | feeder2_line80 | 2 | 354.6 | 84.8127 | 84.8159 | 23.9179 | 23.9188
1080 | feeder2_line80 | 3 | 354.6 | 91.3263 | 91.322 | 25.7547 | 25.7535
1080 | feeder2_line81 | 1 | 354.6 | 72.8794 | 72.8786 | 20.5526 | 20.5523
1080 | feeder2_line81 | 2 | 354.6 | 84.8127 | 84.8159 | 23.9178 | 23.9188
1080 | feeder2_line81 | 3 | 354.6 | 92.1618 | 92.1576 | 25.9904 | 25.9892
1080 | feeder2_line82 | 1 | 354.6 | 6.8629e-12 | 7.238e-07 | 1.9354e-12 | 2.0412e-07
1080 | feeder2_line82 | 2 | 354.6 | 3.6327e-11 | 7.345e-07 | 1.0245e-11 | 2.0714e-07
1080 | feeder2_line82 | 3 | 354.6 | 0.85572 | 0.85572 | 0.24132 | 0.24132
1080 | feeder2_line83 | 1 | 354.6 | 72.8796 | 72.8786 | 20.5526 | 20.5523
1080 | feeder2_line83 | 2 | 354.6 | 86.4535 | 86.4566 | 24.3806 | 24.3814
1080 | feeder2_line83 | 3 | 354.6 | 92.162 | 92.1576 | 25.9904 | 25.9892
1080 | feeder2_line84 | 1 | 354.6 | 1.5986e-11 | 1.2793e-06 | 4.5081e-12 | 3.6078e-07
1080 | feeder2_line84 | 2 | 354.6 | 2.0566 | 2.0566 | 0.57997 | 0.57997
1080 | feeder2_line84 | 3 | 354.6 | 2.5546e-11 | 1.304e-06 | 7.2041e-12 | 3.6775e-07
1080 | feeder2_line85 | 1 | 99 | 0.07869 | 0.078691 | 0.079485 | 0.079485
1080 | feeder2_line85 | 2 | 99 | 4.8831e-08 | 4.6372e-07 | 4.9324e-08 | 4.684e-07
1080 | feeder2_line85 | 3 | 99 | 4.9312e-08 | 4.6568e-07 | 4.981e-08 | 4.7038e-07
1080 | feeder2_line86 | 1 | 354.6 | 72.9565 | 72.9554 | 20.5743 | 20.574
1080 | feeder2_line86 | 2 | 354.6 | 86.4536 | 86.4566 | 24.3806 | 24.3814
1080 | feeder2_line86 | 3 | 354.6 | 92.1621 | 92.1576 | 25.9904 | 25.9892
1080 | feeder2_line87 | 1 | 354.6 | 72.9566 | 72.9554 | 20.5743 | 20.574
1080 | feeder2_line87 | 2 | 354.6 | 88.9997 | 89.0026 | 25.0986 | 25.0994
1080 | feeder2_line87 | 3 | 354.6 | 92.2425 | 92.2378 | 26.0131 | 26.0118
1080 | feeder2_line88 | 1 | 354.6 | 0.00010782 | 3.3129e-06 | 3.0405e-05 | 9.3425e-07
1080 | feeder2_line88 | 2 | 354.6 | 2.6129 | 2.6129 | 0.73685 | 0.73685
1080 | feeder2_line88 | 3 | 354.6 | 0.081301 | 0.081183 | 0.022928 | 0.022894
1080 | feeder2_line89 | 1 | 354.6 | 72.9544 | 72.9554 | 20.5737 | 20.574
1080 | feeder2_line89 | 2 | 354.6 | 91.0482 | 91.0534 | 25.6763 | 25.6778
1080 | feeder2_line89 | 3 | 354.6 | 92.2402 | 92.2378 | 26.0125 | 26.0118
1080 | feeder2_line90 | 1 | 354.6 | 0.0007068 | 2.0009e-06 | 0.00019932 | 5.6426e-07
1080 | feeder2_line90 | 2 | 354.6 | 2.8754 | 2.8755 | 0.81087 | 0.81093
1080 | feeder2_line90 | 3 | 354.6 | 0.00072954 | 2.0422e-06 | 0.00020574 | 5.7593e-07
1080 | feeder2_line91 | 1 | 354.6 | 72.9544 | 72.9554 | 20.5737 | 20.574
1080 | feeder2_line91 | 2 | 354.6 | 91.0481 | 91.0534 | 25.6763 | 25.6778
1080 | feeder2_line91 | 3 | 354.6 | 93.3957 | 93.3933 | 26.3383 | 26.3377
1080 | feeder2_line92 | 1 | 354.6 | 5.6877e-12 | 1.0097e-06 | 1.604e-12 | 2.8475e-07
1080 | feeder2_line92 | 2 | 354.6 | 1.2584e-11 | 1.0251e-06 | 3.5487e-12 | 2.8909e-07
1080 | feeder2_line92 | 3 | 354.6 | 1.1762 | 1.1763 | 0.33171 | 0.33171
1080 | feeder2_line93 | 1 | 99 | 2.5652e-08 | 3.3668e-07 | 2.5912e-08 | 3.4008e-07
1080 | feeder2_line93 | 2 | 99 | 2.0564 | 2.0564 | 2.0771 | 2.0771
1080 | feeder2_line93 | 3 | 99 | 2.4662e-08 | 3.4387e-07 | 2.4912e-08 | 3.4734e-07
1080 | feeder2_line94 | 1 | 354.6 | 2.5653e-06 | 1.6409e-06 | 7.2343e-07 | 4.6276e-07
1080 | feeder2_line94 | 2 | 354.6 | 0.9015 | 0.90152 | 0.25423 | 0.25423
1080 | feeder2_line94 | 3 | 354.6 | 2.4663e-06 | 1.6734e-06 | 6.9553e-07 | 4.719e-07
1080 | feeder2_line95 | 1 | 99 | 3.4987e-06 | 2.5687e-06 | 3.534e-06 | 2.5947e-06
1080 | feeder2_line95 | 2 | 99 | 2.6128 | 2.6129 | 2.6392 | 2.6393
1080 | feeder2_line95 | 3 | 99 | 3.6009e-06 | 2.6229e-06 | 3.6373e-06 | 2.6494e-06
1080 | feeder2_line96 | 1 | 354.6 | 0.000119 | 6.1246e-07 | 3.3558e-05 | 1.7272e-07
1080 | feeder2_line96 | 2 | 354.6 | 0.0001214 | 6.2253e-07 | 3.4237e-05 | 1.7556e-07
1080 | feeder2_line96 | 3 | 354.6 | 0.081287 | 0.081183 | 0.022924 | 0.022894
1080 | feeder2_line97 | 1 | 354.6 | 75.8037 | 75.8046 | 21.3773 | 21.3775
1080 | feeder2_line97 | 2 | 354.6 | 91.0484 | 91.0534 | 25.6764 | 25.6778
1080 | feeder2_line97 | 3 | 354.6 | 93.3959 | 93.3933 | 26.3384 | 26.3377
1080 | feeder2_line98 | 1 | 354.6 | 2.962 | 2.9603 | 0.8353 | 0.83483
1080 | feeder2_line98 | 2 | 354.6 | 0.0017361 | 6.2061e-07 | 0.00048959 | 1.7502e-07
1080 | feeder2_line98 | 3 | 354.6 | 0.0017012 | 6.2502e-07 | 0.00047976 | 1.7626e-07
1080 | feeder2_line99 | 1 | 99 | 2.5638e-08 | 4.4021e-07 | 2.5897e-08 | 4.4465e-07
1080 | feeder2_line99 | 2 | 99 | 2.4419e-08 | 4.4758e-07 | 2.4666e-08 | 4.521e-07
1080 | feeder2_line99 | 3 | 99 | 0.081195 | 0.081183 | 0.082016 | 0.082003
1080 | feeder2_line100 | 1 | 99 | 2.9603 | 2.9603 | 2.9902 | 2.9902
1080 | feeder2_line100 | 2 | 99 | 2.4426e-08 | 6.1474e-07 | 2.4673e-08 | 6.2095e-07
1080 | feeder2_line100 | 3 | 99 | 2.4666e-08 | 6.174e-07 | 2.4915e-08 | 6.2364e-07
1080 | feeder2_line101 | 1 | 354.6 | 0.89545 | 0.8953 | 0.25252 | 0.25248
1080 | feeder2_line101 | 2 | 354.6 | 6.4547 | 6.4544 | 1.8203 | 1.8202
1080 | feeder2_line101 | 3 | 354.6 | 9.6824 | 9.6819 | 2.7305 | 2.7304
1080 | feeder2_line102 | 1 | 99 | 12.9729 | 12.9729 | 13.1039 | 13.1039
1080 | feeder2_line102 | 2 | 99 | 2.3598e-06 | 8.7867e-07 | 2.3836e-06 | 8.8755e-07
1080 | feeder2_line102 | 3 | 99 | 2.3441e-06 | 8.8223e-07 | 2.3678e-06 | 8.9114e-07
1080 | feeder2_line103 | 1 | 99 | 5.3952e-07 | 7.9117e-07 | 5.4497e-07 | 7.9916e-07
1080 | feeder2_line103 | 2 | 99 | 0.85317 | 0.85317 | 0.86179 | 0.86179
1080 | feeder2_line103 | 3 | 99 | 5.5226e-07 | 8.0748e-07 | 5.5784e-07 | 8.1563e-07
1080 | feeder2_line104 | 1 | 354.6 | 0.89545 | 0.8953 | 0.25252 | 0.25248
1080 | feeder2_line104 | 2 | 354.6 | 5.6541 | 5.6539 | 1.5945 | 1.5944
1080 | feeder2_line104 | 3 | 354.6 | 9.6823 | 9.6819 | 2.7305 | 2.7304
1080 | feeder2_line105 | 1 | 99 | 2.4929e-06 | 7.2798e-07 | 2.518e-06 | 7.3534e-07
1080 | feeder2_line105 | 2 | 99 | 2.556e-06 | 7.4001e-07 | 2.5818e-06 | 7.4749e-07
1080 | feeder2_line105 | 3 | 99 | 1.317 | 1.317 | 1.3303 | 1.3303
1080 | feeder2_line106 | 1 | 354.6 | 0.89542 | 0.8953 | 0.25252 | 0.25248
1080 | feeder2_line106 | 2 | 354.6 | 5.654 | 5.6539 | 1.5945 | 1.5944
1080 | feeder2_line106 | 3 | 354.6 | 8.3969 | 8.3966 | 2.368 | 2.3679
1080 | feeder2_line107 | 1 | 99 | 3.2096e-07 | 8.8717e-07 | 3.242e-07 | 8.9613e-07
1080 | feeder2_line107 | 2 | 99 | 3.0159 | 3.016 | 3.0464 | 3.0464
1080 | feeder2_line107 | 3 | 99 | 3.2537e-07 | 9.0533e-07 | 3.2866e-07 | 9.1447e-07
1080 | feeder2_line108 | 1 | 354.6 | 0.89543 | 0.8953 | 0.25252 | 0.25248
1080 | feeder2_line108 | 2 | 354.6 | 2.985 | 2.9848 | 0.84179 | 0.84175
1080 | feeder2_line108 | 3 | 354.6 | 8.3969 | 8.3966 | 2.368 | 2.3679
1080 | feeder2_line109 | 1 | 354.6 | 88.8454 | 88.8452 | 25.0551 | 25.0551
1080 | feeder2_line109 | 2 | 354.6 | 91.0496 | 91.0534 | 25.6767 | 25.6778
1080 | feeder2_line109 | 3 | 354.6 | 93.3971 | 93.3933 | 26.3387 | 26.3377
1080 | feeder2_line110 | 1 | 99 | 13.5825 | 13.5817 | 13.7197 | 13.7189
1080 | feeder2_line110 | 2 | 99 | 0.00080868 | 9.1013e-07 | 0.00081685 | 9.1932e-07
1080 | feeder2_line110 | 3 | 99 | 0.00081147 | 9.1384e-07 | 0.00081967 | 9.2307e-07
1080 | feeder2_line111 | 1 | 99 | 2.5634e-08 | 3.7597e-07 | 2.5893e-08 | 3.7977e-07
1080 | feeder2_line111 | 2 | 99 | 1.5004 | 1.5004 | 1.5156 | 1.5156
1080 | feeder2_line111 | 3 | 99 | 2.4655e-08 | 3.839e-07 | 2.4904e-08 | 3.8778e-07
1080 | feeder2_line112 | 1 | 99 | 3.2116e-07 | 9.0348e-07 | 3.2441e-07 | 9.126e-07
1080 | feeder2_line112 | 2 | 99 | 1.1124 | 1.1124 | 1.1236 | 1.1237
1080 | feeder2_line112 | 3 | 99 | 3.2569e-07 | 9.2253e-07 | 3.2898e-07 | 9.3185e-07
1080 | feeder2_line113 | 1 | 99 | 11.7536 | 11.7536 | 11.8723 | 11.8723
1080 | feeder2_line113 | 2 | 99 | 3.2441e-07 | 9.0664e-07 | 3.2768e-07 | 9.1579e-07
1080 | feeder2_line113 | 3 | 99 | 3.2602e-07 | 9.106e-07 | 3.2932e-07 | 9.198e-07
1080 | feeder2_line114 | 1 | 99 | 0.85428 | 0.85428 | 0.86291 | 0.86291
1080 | feeder2_line114 | 2 | 99 | 2.4396e-08 | 4.3693e-07 | 2.4642e-08 | 4.4134e-07
1080 | feeder2_line114 | 3 | 99 | 2.465e-08 | 4.3869e-07 | 2.4899e-08 | 4.4312e-07
1080 | feeder2_line115 | 1 | 99 | 2.5593e-08 | 5.5365e-07 | 2.5852e-08 | 5.5924e-07
1080 | feeder2_line115 | 2 | 99 | 0.060789 | 0.060794 | 0.061403 | 0.061408
1080 | feeder2_line115 | 3 | 99 | 2.466e-08 | 5.6492e-07 | 2.4909e-08 | 5.7062e-07
1080 | feeder2_line116 | 1 | 354.6 | 0.89545 | 0.89531 | 0.25252 | 0.25248
1080 | feeder2_line116 | 2 | 354.6 | 2.9425 | 2.9423 | 0.82981 | 0.82976
1080 | feeder2_line116 | 3 | 354.6 | 8.3969 | 8.3966 | 2.368 | 2.3679
1080 | feeder2_line117 | 1 | 99 | 5.1392e-08 | 6.3288e-07 | 5.1912e-08 | 6.3927e-07
1080 | feeder2_line117 | 2 | 99 | 1.1097 | 1.1097 | 1.1209 | 1.1209
1080 | feeder2_line117 | 3 | 99 | 4.9357e-08 | 6.4667e-07 | 4.9856e-08 | 6.532e-07
1080 | feeder2_line118 | 1 | 354.6 | 88.8454 | 88.8452 | 25.0551 | 25.0551
1080 | feeder2_line118 | 2 | 354.6 | 92.1407 | 92.1445 | 25.9844 | 25.9855
1080 | feeder2_line118 | 3 | 354.6 | 93.3971 | 93.3933 | 26.3387 | 26.3377
1080 | feeder2_line119 | 1 | 99 | 2.5589e-08 | 5.9576e-07 | 2.5848e-08 | 6.0178e-07
1080 | feeder2_line119 | 2 | 99 | 2.4399e-08 | 6.0555e-07 | 2.4646e-08 | 6.1166e-07
1080 | feeder2_line119 | 3 | 99 | 0.093128 | 0.09312 | 0.094069 | 0.09406
1080 | feeder2_line120 | 1 | 354.6 | 0.89544 | 0.89531 | 0.25252 | 0.25248
1080 | feeder2_line120 | 2 | 354.6 | 2.9425 | 2.9423 | 0.82981 | 0.82976
1080 | feeder2_line120 | 3 | 354.6 | 8.3074 | 8.3071 | 2.3427 | 2.3427
1080 | feeder2_line121 | 1 | 99 | 3.2096e-07 | 9.2258e-07 | 3.242e-07 | 9.3189e-07
1080 | feeder2_line121 | 2 | 99 | 0.68712 | 0.68713 | 0.69406 | 0.69407
1080 | feeder2_line121 | 3 | 99 | 3.2529e-07 | 9.4109e-07 | 3.2858e-07 | 9.506e-07
1080 | feeder2_line122 | 1 | 354.6 | 0.89542 | 0.89531 | 0.25251 | 0.25248
1080 | feeder2_line122 | 2 | 354.6 | 2.6301 | 2.63 | 0.74172 | 0.74169
1080 | feeder2_line122 | 3 | 354.6 | 8.3074 | 8.3071 | 2.3427 | 2.3427
1080 | feeder2_line123 | 1 | 99 | 5.6518e-07 | 9.5601e-07 | 5.7089e-07 | 9.6567e-07
1080 | feeder2_line123 | 2 | 99 | 5.7457e-07 | 9.7168e-07 | 5.8037e-07 | 9.8149e-07
1080 | feeder2_line123 | 3 | 99 | 0.80219 | 0.8022 | 0.8103 | 0.8103
1080 | feeder2_line124 | 1 | 354.6 | 0.89546 | 0.89531 | 0.25253 | 0.25248
1080 | feeder2_line124 | 2 | 354.6 | 2.6302 | 2.63 | 0.74173 | 0.74169
1080 | feeder2_line124 | 3 | 354.6 | 7.528 | 7.5278 | 2.1229 | 2.1229
1080 | feeder2_line125 | 1 | 99 | 5.6518e-07 | 8.8871e-07 | 5.7089e-07 | 8.9769e-07
1080 | feeder2_line125 | 2 | 99 | 5.7456e-07 | 9.0326e-07 | 5.8037e-07 | 9.1239e-07
1080 | feeder2_line125 | 3 | 99 | 2.9471 | 2.9471 | 2.9769 | 2.9769
1080 | feeder2_line126 | 1 | 354.6 | 0.89558 | 0.89531 | 0.25256 | 0.25249
1080 | feeder2_line126 | 2 | 354.6 | 2.6303 | 2.63 | 0.74177 | 0.74169
1080 | feeder2_line126 | 3 | 354.6 | 4.7705 | 4.7702 | 1.3453 | 1.3452
1080 | feeder2_line127 | 1 | 99 | 5.6519e-07 | 1.0639e-06 | 5.709e-07 | 1.0747e-06
1080 | feeder2_line127 | 2 | 99 | 5.7455e-07 | 1.0814e-06 | 5.8036e-07 | 1.0923e-06
1080 | feeder2_line127 | 3 | 99 | 3.2572 | 3.2572 | 3.2901 | 3.2901
1080 | feeder2_line128 | 1 | 354.6 | 0.89557 | 0.89531 | 0.25256 | 0.25249
1080 | feeder2_line128 | 2 | 354.6 | 2.6303 | 2.63 | 0.74176 | 0.74169
1080 | feeder2_line128 | 3 | 354.6 | 1.6825 | 1.6823 | 0.47449 | 0.47442
1080 | feeder2_line129 | 1 | 99 | 5.3961e-07 | 8.627e-07 | 5.4506e-07 | 8.7141e-07
1080 | feeder2_line129 | 2 | 99 | 2.63 | 2.63 | 2.6566 | 2.6566
1080 | feeder2_line129 | 3 | 99 | 5.519e-07 | 8.7989e-07 | 5.5748e-07 | 8.8878e-07
1080 | feeder2_line130 | 1 | 354.6 | 0.89561 | 0.89531 | 0.25257 | 0.25249
1080 | feeder2_line130 | 2 | 354.6 | 0.0003066 | 4.6385e-06 | 8.6463e-05 | 1.3081e-06
1080 | feeder2_line130 | 3 | 354.6 | 1.6825 | 1.6823 | 0.47449 | 0.47442
1080 | feeder2_line131 | 1 | 99 | 5.6518e-07 | 9.5617e-07 | 5.7089e-07 | 9.6583e-07
1080 | feeder2_line131 | 2 | 99 | 5.7456e-07 | 9.7182e-07 | 5.8036e-07 | 9.8163e-07
1080 | feeder2_line131 | 3 | 99 | 1.6065 | 1.6064 | 1.6227 | 1.6227
1080 | feeder2_line132 | 1 | 354.6 | 0.89543 | 0.89532 | 0.25252 | 0.25249
1080 | feeder2_line132 | 2 | 354.6 | 0.00012603 | 2.916e-06 | 3.5541e-05 | 8.2235e-07
1080 | feeder2_line132 | 3 | 354.6 | 0.076752 | 0.076679 | 0.021645 | 0.021624
1080 | feeder2_line133 | 1 | 99 | 0.89531 | 0.89532 | 0.90435 | 0.90436
1080 | feeder2_line133 | 2 | 99 | 2.9947e-07 | 9.7958e-07 | 3.025e-07 | 9.8947e-07
1080 | feeder2_line133 | 3 | 99 | 3.006e-07 | 9.8299e-07 | 3.0364e-07 | 9.9292e-07
1080 | feeder2_line134 | 1 | 354.6 | 7.635e-12 | 1.7594e-06 | 2.1531e-12 | 4.9616e-07
1080 | feeder2_line134 | 2 | 354.6 | 1.2462e-11 | 1.7853e-06 | 3.5144e-12 | 5.0347e-07
1080 | feeder2_line134 | 3 | 354.6 | 0.076682 | 0.076679 | 0.021625 | 0.021624
1080 | feeder2_line135 | 1 | 99 | 6.7558 | 6.7558 | 6.824 | 6.824
1080 | feeder2_line135 | 2 | 99 | 4.8904e-08 | 5.8689e-07 | 4.9398e-08 | 5.9282e-07
1080 | feeder2_line135 | 3 | 99 | 4.9373e-08 | 5.8948e-07 | 4.9872e-08 | 5.9544e-07
1080 | feeder2_line136 | 1 | 354.6 | 95.0894 | 95.0893 | 26.816 | 26.8159
1080 | feeder2_line136 | 2 | 354.6 | 92.1406 | 92.1445 | 25.9844 | 25.9855
1080 | feeder2_line136 | 3 | 354.6 | 93.3971 | 93.3933 | 26.3387 | 26.3377
1080 | feeder2_line137 | 1 | 99 | 1.1828 | 1.1828 | 1.1948 | 1.1948
1080 | feeder2_line137 | 2 | 99 | 8.5215e-07 | 1.5808e-06 | 8.6076e-07 | 1.5968e-06
1080 | feeder2_line137 | 3 | 99 | 8.5584e-07 | 1.5878e-06 | 8.6449e-07 | 1.6039e-06
1080 | feeder2_line138 | 1 | 354.6 | 95.6155 | 95.6153 | 26.9643 | 26.9643
1080 | feeder2_line138 | 2 | 354.6 | 92.1407 | 92.1445 | 25.9844 | 25.9855
1080 | feeder2_line138 | 3 | 354.6 | 93.3971 | 93.3933 | 26.3387 | 26.3377
1080 | feeder2_line139 | 1 | 99 | 5.1443e-08 | 4.8419e-07 | 5.1962e-08 | 4.8908e-07
1080 | feeder2_line139 | 2 | 99 | 4.8917e-08 | 4.9262e-07 | 4.9411e-08 | 4.976e-07
1080 | feeder2_line139 | 3 | 99 | 0.044415 | 0.044193 | 0.044863 | 0.044639
1080 | feeder2_line140 | 1 | 354.6 | 95.6156 | 95.6153 | 26.9643 | 26.9643
1080 | feeder2_line140 | 2 | 354.6 | 92.1408 | 92.1445 | 25.9844 | 25.9855
1080 | feeder2_line140 | 3 | 354.6 | 93.441 | 93.4369 | 26.3511 | 26.3499
1080 | feeder2_line141 | 1 | 99 | 2.4722e-06 | 4.7903e-07 | 2.4972e-06 | 4.8387e-07
1080 | feeder2_line141 | 2 | 99 | 1.1873 | 1.1873 | 1.1993 | 1.1992
1080 | feeder2_line141 | 3 | 99 | 2.5494e-06 | 4.895e-07 | 2.5751e-06 | 4.9445e-07
1080 | feeder2_line142 | 1 | 354.6 | 95.6154 | 95.6153 | 26.9643 | 26.9643
1080 | feeder2_line142 | 2 | 354.6 | 92.6357 | 92.6395 | 26.124 | 26.1251
1080 | feeder2_line142 | 3 | 354.6 | 93.4408 | 93.4369 | 26.351 | 26.3499
1080 | feeder2_line143 | 1 | 99 | 8.3689e-07 | 1.7023e-06 | 8.4534e-07 | 1.7194e-06
1080 | feeder2_line143 | 2 | 99 | 3.0153 | 3.0154 | 3.0458 | 3.0458
1080 | feeder2_line143 | 3 | 99 | 8.5617e-07 | 1.7395e-06 | 8.6482e-07 | 1.757e-06
1080 | feeder2_line144 | 1 | 354.6 | 95.6152 | 95.6153 | 26.9642 | 26.9643
1080 | feeder2_line144 | 2 | 354.6 | 95.5659 | 95.5699 | 26.9503 | 26.9515
1080 | feeder2_line144 | 3 | 354.6 | 93.4406 | 93.4369 | 26.351 | 26.3499
1080 | feeder2_line145 | 1 | 99 | 2.5728e-08 | 4.7733e-07 | 2.5988e-08 | 4.8215e-07
1080 | feeder2_line145 | 2 | 99 | 0.85573 | 0.85575 | 0.86437 | 0.86439
1080 | feeder2_line145 | 3 | 99 | 2.4703e-08 | 4.8777e-07 | 2.4953e-08 | 4.9269e-07
1080 | feeder2_line146 | 1 | 354.6 | 95.6151 | 95.6153 | 26.9642 | 26.9643
1080 | feeder2_line146 | 2 | 354.6 | 96.4047 | 96.4089 | 27.1869 | 27.1881
1080 | feeder2_line146 | 3 | 354.6 | 93.4405 | 93.4369 | 26.351 | 26.3499
1080 | feeder2_line147 | 1 | 99 | 1.8269 | 1.8268 | 1.8453 | 1.8453
1080 | feeder2_line147 | 2 | 99 | 1.1531e-06 | 2.24e-06 | 1.1648e-06 | 2.2626e-06
1080 | feeder2_line147 | 3 | 99 | 1.1582e-06 | 2.2499e-06 | 1.1699e-06 | 2.2726e-06
1080 | feeder2_line148 | 1 | 99 | 0.93892 | 0.93892 | 0.94841 | 0.94841
1080 | feeder2_line148 | 2 | 99 | 6.0101e-07 | 1.501e-06 | 6.0709e-07 | 1.5161e-06
1080 | feeder2_line148 | 3 | 99 | 6.0379e-07 | 1.5076e-06 | 6.0988e-07 | 1.5228e-06
1080 | feeder2_line149 | 1 | 354.6 | 98.3145 | 98.3145 | 27.7255 | 27.7255
1080 | feeder2_line149 | 2 | 354.6 | 96.4049 | 96.4089 | 27.1869 | 27.1881
1080 | feeder2_line149 | 3 | 354.6 | 93.4407 | 93.4369 | 26.351 | 26.3499
1080 | feeder2_line150 | 1 | 354.6 | 98.3146 | 98.3145 | 27.7255 | 27.7255
1080 | feeder2_line150 | 2 | 354.6 | 97.3305 | 97.3345 | 27.448 | 27.4491
1080 | feeder2_line150 | 3 | 354.6 | 93.4408 | 93.4369 | 26.351 | 26.3499
1080 | feeder2_line151 | 1 | 99 | 9.5391e-06 | 1.7527e-06 | 9.6355e-06 | 1.7704e-06
1080 | feeder2_line151 | 2 | 99 | 0.94207 | 0.94208 | 0.95158 | 0.9516
1080 | feeder2_line151 | 3 | 99 | 9.8501e-06 | 1.7909e-06 | 9.9496e-06 | 1.809e-06
1080 | feeder2_line152 | 1 | 354.6 | 7.1708e-12 | 1.1695e-06 | 2.0222e-12 | 3.2982e-07
1080 | feeder2_line152 | 2 | 354.6 | 2.6221e-11 | 1.1878e-06 | 7.3945e-12 | 3.3498e-07
1080 | feeder2_line152 | 3 | 354.6 | 0.076204 | 0.076201 | 0.02149 | 0.021489
1080 | feeder2_line153 | 1 | 99 | 0.68697 | 0.68697 | 0.69391 | 0.69391
1080 | feeder2_line153 | 2 | 99 | 4.8982e-08 | 5.9465e-07 | 4.9476e-08 | 6.0065e-07
1080 | feeder2_line153 | 3 | 99 | 4.9458e-08 | 5.9721e-07 | 4.9958e-08 | 6.0324e-07
1080 | feeder2_line154 | 1 | 99 | 5.6708e-07 | 8.6977e-07 | 5.7281e-07 | 8.7855e-07
1080 | feeder2_line154 | 2 | 99 | 5.7705e-07 | 8.8486e-07 | 5.8288e-07 | 8.938e-07
1080 | feeder2_line154 | 3 | 99 | 3.7157 | 3.7157 | 3.7533 | 3.7532
1080 | feeder2_line155 | 1 | 99 | 99 | 99 | 100 | 100
1080 | feeder2_line155 | 2 | 99 | 97.3305 | 97.3345 | 98.3136 | 98.3176
1080 | feeder2_line155 | 3 | 99 | 96.9952 | 96.9914 | 97.975 | 97.9711
1080 | feeder2_line156 | 1 | 99 | 5.926e-07 | 1.1445e-06 | 5.9859e-07 | 1.1561e-06
1080 | feeder2_line156 | 2 | 99 | 0.85304 | 0.85304 | 0.86166 | 0.86166
1080 | feeder2_line156 | 3 | 99 | 6.0403e-07 | 1.1694e-06 | 6.1013e-07 | 1.1812e-06
1080 | feeder2_line157 | 1 | 99 | 2.5742e-08 | 2.4846e-07 | 2.6002e-08 | 2.5097e-07
1080 | feeder2_line157 | 2 | 99 | 0.089166 | 0.089169 | 0.090067 | 0.09007
1080 | feeder2_line157 | 3 | 99 | 2.4717e-08 | 2.5388e-07 | 2.4966e-08 | 2.5644e-07
1110 | feeder2_line1 | 1 | 354.6 | 11.7288 | 11.728 | 3.3076 | 3.3074
1110 | feeder2_line1 | 2 | 354.6 | 17.1832 | 17.1802 | 4.8458 | 4.845
1110 | feeder2_line1 | 3 | 354.6 | 27.4182 | 27.424 | 7.7322 | 7.7338
1110 | feeder2_line2 | 1 | 354.6 | 9.8304 | 9.8328 | 2.7723 | 2.7729
1110 | feeder2_line2 | 2 | 354.6 | 17.1834 | 17.1802 | 4.8458 | 4.845
1110 | feeder2_line2 | 3 | 354.6 | 27.4184 | 27.424 | 7.7322 | 7.7338
1110 | feeder2_line3 | 1 | 80.1 | 20.5991 | 20.5991 | 25.7168 | 25.7167
1110 | feeder2_line3 | 2 | 80.1 | 5.705e-07 | 1.0543e-06 | 7.1224e-07 | 1.3162e-06
1110 | feeder2_line3 | 3 | 80.1 | 5.7147e-07 | 1.0561e-06 | 7.1345e-07 | 1.3185e-06
1110 | feeder2_line4 | 1 | 354.6 | 9.8306 | 9.8328 | 2.7723 | 2.7729
1110 | feeder2_line4 | 2 | 354.6 | 17.2174 | 17.2142 | 4.8554 | 4.8545
1110 | feeder2_line4 | 3 | 354.6 | 27.4186 | 27.424 | 7.7322 | 7.7338
1110 | feeder2_line5 | 1 | 80.1 | 5.7037e-07 | 9.9526e-07 | 7.1207e-07 | 1.2425e-06
1110 | feeder2_line5 | 2 | 80.1 | 0.090246 | 0.090244 | 0.11267 | 0.11266
1110 | feeder2_line5 | 3 | 80.1 | 5.7153e-07 | 9.9727e-07 | 7.1352e-07 | 1.245e-06
1110 | feeder2_line6 | 1 | 80.1 | 5.7037e-07 | 1.1708e-06 | 7.1208e-07 | 1.4617e-06
1110 | feeder2_line6 | 2 | 80.1 | 5.7052e-07 | 1.1711e-06 | 7.1225e-07 | 1.462e-06
1110 | feeder2_line6 | 3 | 80.1 | 3.632 | 3.632 | 4.5343 | 4.5343
1110 | feeder2_line7 | 1 | 354.6 | 9.8307 | 9.8328 | 2.7723 | 2.7729
1110 | feeder2_line7 | 2 | 354.6 | 17.2174 | 17.2142 | 4.8554 | 4.8545
1110 | feeder2_line7 | 3 | 354.6 | 29.6472 | 29.6527 | 8.3608 | 8.3623
1110 | feeder2_line8 | 1 | 80.1 | 1.9067 | 1.9067 | 2.3804 | 2.3804
1110 | feeder2_line8 | 2 | 80.1 | 5.7048e-07 | 1.1291e-06 | 7.1221e-07 | 1.4096e-06
1110 | feeder2_line8 | 3 | 80.1 | 5.7164e-07 | 1.1314e-06 | 7.1366e-07 | 1.4125e-06
1110 | feeder2_line9 | 1 | 354.6 | 11.7036 | 11.7056 | 3.3005 | 3.3011
1110 | feeder2_line9 | 2 | 354.6 | 17.2173 | 17.2142 | 4.8554 | 4.8545
1110 | feeder2_line9 | 3 | 354.6 | 29.6473 | 29.6527 | 8.3608 | 8.3623
1110 | feeder2_line10 | 1 | 80.1 | 8.4315e-07 | 1.4907e-06 | 1.0526e-06 | 1.861e-06
1110 | feeder2_line10 | 2 | 80.1 | 1.9062 | 1.9062 | 2.3798 | 2.3798
1110 | feeder2_line10 | 3 | 80.1 | 8.4508e-07 | 1.4939e-06 | 1.055e-06 | 1.8651e-06
1110 | feeder2_line11 | 1 | 354.6 | 11.7036 | 11.7056 | 3.3005 | 3.3011
1110 | feeder2_line11 | 2 | 354.6 | 18.0181 | 18.0142 | 5.0812 | 5.0802
1110 | feeder2_line11 | 3 | 354.6 | 29.6473 | 29.6527 | 8.3608 | 8.3623
1110 | feeder2_line12 | 1 | 80.1 | 5.4551e-07 | 9.8882e-07 | 6.8104e-07 | 1.2345e-06
1110 | feeder2_line12 | 2 | 80.1 | 5.457e-07 | 9.889e-07 | 6.8128e-07 | 1.2346e-06
1110 | feeder2_line12 | 3 | 80.1 | 0.46554 | 0.46554 | 0.5812 | 0.5812
1110 | feeder2_line13 | 1 | 354.6 | 11.7036 | 11.7056 | 3.3005 | 3.3011
1110 | feeder2_line13 | 2 | 354.6 | 18.0181 | 18.0142 | 5.0813 | 5.0802
1110 | feeder2_line13 | 3 | 354.6 | 30.1063 | 30.1118 | 8.4902 | 8.4918
1110 | feeder2_line14 | 1 | 80.1 | 15.3478 | 15.3477 | 19.1607 | 19.1607
1110 | feeder2_line14 | 2 | 80.1 | 2.976e-07 | 6.4482e-07 | 3.7153e-07 | 8.0501e-07
1110 | feeder2_line14 | 3 | 80.1 | 2.9825e-07 | 6.4625e-07 | 3.7234e-07 | 8.068e-07
1110 | feeder2_line15 | 1 | 354.6 | 26.8412 | 26.8428 | 7.5694 | 7.5699
1110 | feeder2_line15 | 2 | 354.6 | 18.0181 | 18.0142 | 5.0813 | 5.0802
1110 | feeder2_line15 | 3 | 354.6 | 30.1063 | 30.1118 | 8.4902 | 8.4918
1110 | feeder2_line16 | 1 | 80.1 | 5.7048e-07 | 1.0278e-06 | 7.1221e-07 | 1.2831e-06
1110 | feeder2_line16 | 2 | 80.1 | 2.3256 | 2.3256 | 2.9033 | 2.9033
1110 | feeder2_line16 | 3 | 80.1 | 5.7175e-07 | 1.03e-06 | 7.138e-07 | 1.2859e-06
1110 | feeder2_line17 | 1 | 354.6 | 26.8412 | 26.8428 | 7.5694 | 7.5699
1110 | feeder2_line17 | 2 | 354.6 | 19.0576 | 19.053 | 5.3744 | 5.3731
1110 | feeder2_line17 | 3 | 354.6 | 30.1064 | 30.1118 | 8.4902 | 8.4918
1110 | feeder2_line18 | 1 | 80.1 | 5.4588e-07 | 7.3604e-07 | 6.815e-07 | 9.1891e-07
1110 | feeder2_line18 | 2 | 80.1 | 5.4553e-07 | 7.3546e-07 | 6.8106e-07 | 9.1818e-07
1110 | feeder2_line18 | 3 | 80.1 | 1.3882 | 1.3882 | 1.7331 | 1.7331
1110 | feeder2_line19 | 1 | 354.6 | 26.8412 | 26.8428 | 7.5694 | 7.5699
1110 | feeder2_line19 | 2 | 354.6 | 19.0576 | 19.053 | 5.3744 | 5.3731
1110 | feeder2_line19 | 3 | 354.6 | 30.985 | 30.9903 | 8.738 | 8.7395
1110 | feeder2_line20 | 1 | 99 | 5.4598e-07 | 8.8264e-07 | 5.515e-07 | 8.9155e-07
1110 | feeder2_line20 | 2 | 99 | 5.4548e-07 | 8.8172e-07 | 5.5099e-07 | 8.9063e-07
1110 | feeder2_line20 | 3 | 99 | 2.298 | 2.298 | 2.3212 | 2.3212
1110 | feeder2_line21 | 1 | 354.6 | 26.8414 | 26.8428 | 7.5695 | 7.5699
1110 | feeder2_line21 | 2 | 354.6 | 19.0577 | 19.053 | 5.3744 | 5.3731
1110 | feeder2_line21 | 3 | 354.6 | 32.7622 | 32.7675 | 9.2392 | 9.2407
1110 | feeder2_line22 | 1 | 99 | 5.7092e-07 | 1.0119e-06 | 5.7669e-07 | 1.0222e-06
1110 | feeder2_line22 | 2 | 99 | 2.0157 | 2.0157 | 2.0361 | 2.036
1110 | feeder2_line22 | 3 | 99 | 5.7203e-07 | 1.0139e-06 | 5.7781e-07 | 1.0241e-06
1110 | feeder2_line23 | 1 | 99 | 5.7092e-07 | 9.4727e-07 | 5.7669e-07 | 9.5683e-07
1110 | feeder2_line23 | 2 | 99 | 5.7025e-07 | 9.4614e-07 | 5.7601e-07 | 9.5569e-07
1110 | feeder2_line23 | 3 | 99 | 1.3322 | 1.3322 | 1.3457 | 1.3457
1110 | feeder2_line24 | 1 | 354.6 | 26.8414 | 26.8428 | 7.5695 | 7.5699
1110 | feeder2_line24 | 2 | 354.6 | 20.0357 | 20.0305 | 5.6502 | 5.6488
1110 | feeder2_line24 | 3 | 354.6 | 34.0731 | 34.0783 | 9.6089 | 9.6104
1110 | feeder2_line25 | 1 | 99 | 2.0145 | 2.0144 | 2.0348 | 2.0348
1110 | feeder2_line25 | 2 | 99 | 4.9631e-08 | 6.8781e-07 | 5.0132e-08 | 6.9476e-07
1110 | feeder2_line25 | 3 | 99 | 4.9598e-08 | 6.9011e-07 | 5.0099e-08 | 6.9708e-07
1110 | feeder2_line26 | 1 | 99 | 1.3027 | 1.3027 | 1.3158 | 1.3158
1110 | feeder2_line26 | 2 | 99 | 5.454e-07 | 8.5216e-07 | 5.5091e-07 | 8.6077e-07
1110 | feeder2_line26 | 3 | 99 | 5.4732e-07 | 8.5501e-07 | 5.5285e-07 | 8.6364e-07
1110 | feeder2_line27 | 1 | 354.6 | 30.1287 | 30.13 | 8.4965 | 8.4969
1110 | feeder2_line27 | 2 | 354.6 | 20.0357 | 20.0305 | 5.6502 | 5.6488
1110 | feeder2_line27 | 3 | 354.6 | 34.0731 | 34.0783 | 9.6089 | 9.6104
1110 | feeder2_line28 | 1 | 99 | 2.5329e-06 | 7.0864e-07 | 2.5584e-06 | 7.158e-07
1110 | feeder2_line28 | 2 | 99 | 3.5854 | 3.5854 | 3.6216 | 3.6217
1110 | feeder2_line28 | 3 | 99 | 2.5389e-06 | 7.0991e-07 | 2.5646e-06 | 7.1708e-07
1110 | feeder2_line29 | 1 | 354.6 | 30.1287 | 30.13 | 8.4965 | 8.4969
1110 | feeder2_line29 | 2 | 354.6 | 20.8095 | 20.8034 | 5.8684 | 5.8667
1110 | feeder2_line29 | 3 | 354.6 | 34.0731 | 34.0783 | 9.6089 | 9.6104
1110 | feeder2_line30 | 1 | 266.4 | 10.1588 | 10.1585 | 3.8134 | 3.8133
1110 | feeder2_line30 | 2 | 266.4 | 6.2433 | 6.2432 | 2.3436 | 2.3435
1110 | feeder2_line30 | 3 | 266.4 | 17.0011 | 17.0007 | 6.3818 | 6.3817
1110 | feeder2_line31 | 1 | 354.6 | 40.1891 | 40.1901 | 11.3337 | 11.3339
1110 | feeder2_line31 | 2 | 354.6 | 23.4567 | 23.4492 | 6.615 | 6.6129
1110 | feeder2_line31 | 3 | 354.6 | 50.5522 | 50.5571 | 14.2561 | 14.2575
1110 | feeder2_line32 | 1 | 354.6 | 40.1892 | 40.1901 | 11.3337 | 11.3339
1110 | feeder2_line32 | 2 | 354.6 | 26.009 | 26.0015 | 7.3348 | 7.3326
1110 | feeder2_line32 | 3 | 354.6 | 50.5522 | 50.5571 | 14.2561 | 14.2575
1110 | feeder2_line33 | 1 | 99 | 4.9734e-08 | 6.8419e-07 | 5.0236e-08 | 6.911e-07
1110 | feeder2_line33 | 2 | 99 | 3.2621 | 3.262 | 3.295 | 3.295
1110 | feeder2_line33 | 3 | 99 | 4.9602e-08 | 6.8535e-07 | 5.0103e-08 | 6.9227e-07
1110 | feeder2_line34 | 1 | 354.6 | 40.1892 | 40.1901 | 11.3337 | 11.3339
1110 | feeder2_line34 | 2 | 354.6 | 26.009 | 26.0015 | 7.3348 | 7.3326
1110 | feeder2_line34 | 3 | 354.6 | 50.6378 | 50.6427 | 14.2803 | 14.2816
1110 | feeder2_line35 | 1 | 99 | 2.9832e-07 | 7.5775e-07 | 3.0133e-07 | 7.6541e-07
1110 | feeder2_line35 | 2 | 99 | 2.9747e-07 | 7.5551e-07 | 3.0047e-07 | 7.6314e-07
1110 | feeder2_line35 | 3 | 99 | 0.085679 | 0.085684 | 0.086545 | 0.086549
1110 | feeder2_line36 | 1 | 354.6 | 50.6767 | 50.6776 | 14.2912 | 14.2915
1110 | feeder2_line36 | 2 | 354.6 | 26.009 | 26.0015 | 7.3347 | 7.3326
1110 | feeder2_line36 | 3 | 354.6 | 50.6378 | 50.6427 | 14.2802 | 14.2816
1110 | feeder2_line37 | 1 | 99 | 10.5082 | 10.5082 | 10.6143 | 10.6143
1110 | feeder2_line37 | 2 | 99 | 2.9746e-07 | 8.3592e-07 | 3.0046e-07 | 8.4437e-07
1110 | feeder2_line37 | 3 | 99 | 2.9882e-07 | 8.4002e-07 | 3.0184e-07 | 8.4851e-07
1110 | feeder2_line38 | 1 | 99 | 3.2304e-07 | 7.7336e-07 | 3.263e-07 | 7.8117e-07
1110 | feeder2_line38 | 2 | 99 | 0.59496 | 0.59496 | 0.60097 | 0.60097
1110 | feeder2_line38 | 3 | 99 | 3.2341e-07 | 7.7459e-07 | 3.2668e-07 | 7.8242e-07
1110 | feeder2_line39 | 1 | 266.4 | 10.1588 | 10.1585 | 3.8134 | 3.8133
1110 | feeder2_line39 | 2 | 266.4 | 5.7232 | 5.7231 | 2.1484 | 2.1483
1110 | feeder2_line39 | 3 | 266.4 | 17.0011 | 17.0007 | 6.3818 | 6.3817
1110 | feeder2_line40 | 1 | 354.6 | 52.6813 | 52.6821 | 14.8565 | 14.8568
1110 | feeder2_line40 | 2 | 354.6 | 26.009 | 26.0015 | 7.3348 | 7.3326
1110 | feeder2_line40 | 3 | 354.6 | 50.6378 | 50.6427 | 14.2803 | 14.2816
1110 | feeder2_line41 | 1 | 99 | 2.0125 | 2.0125 | 2.0328 | 2.0328
1110 | feeder2_line41 | 2 | 99 | 4.978e-08 | 7.3044e-07 | 5.0283e-08 | 7.3782e-07
1110 | feeder2_line41 | 3 | 99 | 4.9599e-08 | 7.341e-07 | 5.01e-08 | 7.4152e-07
1110 | feeder2_line42 | 1 | 99 | 2.9815e-07 | 7.4641e-07 | 3.0116e-07 | 7.5395e-07
1110 | feeder2_line42 | 2 | 99 | 2.9746e-07 | 7.4462e-07 | 3.0046e-07 | 7.5214e-07
1110 | feeder2_line42 | 3 | 99 | 1.315 | 1.315 | 1.3282 | 1.3283
1110 | feeder2_line43 | 1 | 266.4 | 10.1588 | 10.1585 | 3.8133 | 3.8133
1110 | feeder2_line43 | 2 | 266.4 | 5.7232 | 5.7231 | 2.1484 | 2.1483
1110 | feeder2_line43 | 3 | 266.4 | 15.9465 | 15.9462 | 5.9859 | 5.9858
1110 | feeder2_line44 | 1 | 354.6 | 52.6814 | 52.6821 | 14.8566 | 14.8568
1110 | feeder2_line44 | 2 | 354.6 | 26.0091 | 26.0015 | 7.3348 | 7.3326
1110 | feeder2_line44 | 3 | 354.6 | 52.6041 | 52.6089 | 14.8348 | 14.8361
1110 | feeder2_line45 | 1 | 99 | 4.9737e-08 | 5.7801e-07 | 5.024e-08 | 5.8385e-07
1110 | feeder2_line45 | 2 | 99 | 4.9795e-08 | 5.7604e-07 | 5.0298e-08 | 5.8186e-07
1110 | feeder2_line45 | 3 | 99 | 2.2992 | 2.2992 | 2.3224 | 2.3225
1110 | feeder2_line46 | 1 | 99 | 5.7141e-07 | 1.3531e-06 | 5.7718e-07 | 1.3667e-06
1110 | feeder2_line46 | 2 | 99 | 5.7004e-07 | 1.3498e-06 | 5.758e-07 | 1.3635e-06
1110 | feeder2_line46 | 3 | 99 | 14.2183 | 14.2182 | 14.3619 | 14.3618
1110 | feeder2_line47 | 1 | 266.4 | 10.1588 | 10.1585 | 3.8134 | 3.8133
1110 | feeder2_line47 | 2 | 266.4 | 5.7233 | 5.7231 | 2.1484 | 2.1483
1110 | feeder2_line47 | 3 | 266.4 | 1.7392 | 1.7389 | 0.65283 | 0.65275
1110 | feeder2_line48 | 1 | 99 | 1.9739 | 1.9739 | 1.9939 | 1.9939
1110 | feeder2_line48 | 2 | 99 | 4.9685e-08 | 7.2678e-07 | 5.0187e-08 | 7.3412e-07
1110 | feeder2_line48 | 3 | 99 | 4.9618e-08 | 7.2963e-07 | 5.0119e-08 | 7.37e-07
1110 | feeder2_line49 | 1 | 266.4 | 8.205 | 8.2048 | 3.08 | 3.0799
1110 | feeder2_line49 | 2 | 266.4 | 5.7233 | 5.7231 | 2.1484 | 2.1483
1110 | feeder2_line49 | 3 | 266.4 | 1.7391 | 1.7389 | 0.65283 | 0.65275
1110 | feeder2_line50 | 1 | 99 | 5.7139e-07 | 1.2313e-06 | 5.7716e-07 | 1.2438e-06
1110 | feeder2_line50 | 2 | 99 | 3.6335 | 3.6334 | 3.6702 | 3.6701
1110 | feeder2_line50 | 3 | 99 | 5.723e-07 | 1.2333e-06 | 5.7808e-07 | 1.2457e-06
1110 | feeder2_line51 | 1 | 99 | 1.4219 | 1.422 | 1.4363 | 1.4363
1110 | feeder2_line51 | 2 | 99 | 5.7005e-07 | 1.3336e-06 | 5.758e-07 | 1.3471e-06
1110 | feeder2_line51 | 3 | 99 | 5.723e-07 | 1.3389e-06 | 5.7808e-07 | 1.3524e-06
1110 | feeder2_line52 | 1 | 266.4 | 6.7929 | 6.7928 | 2.5499 | 2.5498
1110 | feeder2_line52 | 2 | 266.4 | 2.1063 | 2.1063 | 0.79066 | 0.79064
1110 | feeder2_line52 | 3 | 266.4 | 1.739 | 1.7389 | 0.65278 | 0.65275
1110 | feeder2_line53 | 1 | 99 | 5.4653e-07 | 7.5151e-07 | 5.5206e-07 | 7.591e-07
1110 | feeder2_line53 | 2 | 99 | 2.1063 | 2.1063 | 2.1276 | 2.1275
1110 | feeder2_line53 | 3 | 99 | 5.4749e-07 | 7.5269e-07 | 5.5302e-07 | 7.6029e-07
1110 | feeder2_line54 | 1 | 266.4 | 6.7927 | 6.7928 | 2.5498 | 2.5498
1110 | feeder2_line54 | 2 | 266.4 | 8.5049e-05 | 4.5994e-06 | 3.1925e-05 | 1.7265e-06
1110 | feeder2_line54 | 3 | 266.4 | 1.7388 | 1.7389 | 0.65271 | 0.65275
1110 | feeder2_line55 | 1 | 99 | 1.7343 | 1.7343 | 1.7518 | 1.7518
1110 | feeder2_line55 | 2 | 99 | 4.9849e-08 | 7.2566e-07 | 5.0353e-08 | 7.3299e-07
1110 | feeder2_line55 | 3 | 99 | 4.9599e-08 | 7.2975e-07 | 5.01e-08 | 7.3712e-07
1110 | feeder2_line56 | 1 | 354.6 | 54.4106 | 54.4113 | 15.3442 | 15.3444
1110 | feeder2_line56 | 2 | 354.6 | 26.0091 | 26.0015 | 7.3348 | 7.3326
1110 | feeder2_line56 | 3 | 354.6 | 52.6041 | 52.6089 | 14.8348 | 14.8361
1110 | feeder2_line57 | 1 | 99 | 7.4581e-07 | 1.5393e-06 | 7.5334e-07 | 1.5548e-06
1110 | feeder2_line57 | 2 | 99 | 7.4523e-07 | 1.5357e-06 | 7.5276e-07 | 1.5512e-06
1110 | feeder2_line57 | 3 | 99 | 1.7389 | 1.7389 | 1.7565 | 1.7565
1110 | feeder2_line58 | 1 | 266.4 | 6.7928 | 6.7928 | 2.5499 | 2.5498
1110 | feeder2_line58 | 2 | 266.4 | 1.8836e-05 | 2.6704e-06 | 7.0706e-06 | 1.0024e-06
1110 | feeder2_line58 | 3 | 266.4 | 1.8918e-05 | 2.6807e-06 | 7.1014e-06 | 1.0063e-06
1110 | feeder2_line59 | 1 | 99 | 4.9721e-08 | 5.3506e-07 | 5.0223e-08 | 5.4047e-07
1110 | feeder2_line59 | 2 | 99 | 4.9688e-08 | 5.3383e-07 | 5.019e-08 | 5.3922e-07
1110 | feeder2_line59 | 3 | 99 | 1.2749 | 1.2749 | 1.2878 | 1.2878
1110 | feeder2_line60 | 1 | 99 | 2.9812e-07 | 8.0865e-07 | 3.0113e-07 | 8.1681e-07
1110 | feeder2_line60 | 2 | 99 | 2.9744e-07 | 8.0678e-07 | 3.0045e-07 | 8.1493e-07
1110 | feeder2_line60 | 3 | 99 | 0.46566 | 0.46566 | 0.47037 | 0.47037
1110 | feeder2_line61 | 1 | 266.4 | 2.2983 | 2.2985 | 0.86272 | 0.86279
1110 | feeder2_line61 | 2 | 266.4 | 17.5928 | 17.5931 | 6.6039 | 6.604
1110 | feeder2_line61 | 3 | 266.4 | 15.4953 | 15.4953 | 5.8166 | 5.8166
1110 | feeder2_line62 | 1 | 354.6 | 56.7088 | 56.7097 | 15.9923 | 15.9926
1110 | feeder2_line62 | 2 | 354.6 | 42.0587 | 42.0512 | 11.8609 | 11.8588
1110 | feeder2_line62 | 3 | 354.6 | 68.0747 | 68.0796 | 19.1976 | 19.199
1110 | feeder2_line63 | 1 | 99 | 0.089387 | 0.089388 | 0.09029 | 0.090291
1110 | feeder2_line63 | 2 | 99 | 5.7006e-07 | 1.213e-06 | 5.7582e-07 | 1.2252e-06
1110 | feeder2_line63 | 3 | 99 | 5.7231e-07 | 1.2178e-06 | 5.7809e-07 | 1.2301e-06
1110 | feeder2_line64 | 1 | 99 | 6.7049 | 6.7049 | 6.7727 | 6.7726
1110 | feeder2_line64 | 2 | 99 | 6.2963e-12 | 3.1952e-07 | 6.3599e-12 | 3.2275e-07
1110 | feeder2_line64 | 3 | 99 | 1.3271e-11 | 3.2078e-07 | 1.3405e-11 | 3.2402e-07
1110 | feeder2_line65 | 1 | 99 | 4.9731e-08 | 6.405e-07 | 5.0233e-08 | 6.4697e-07
1110 | feeder2_line65 | 2 | 99 | 0.090415 | 0.090407 | 0.091329 | 0.09132
1110 | feeder2_line65 | 3 | 99 | 4.96e-08 | 6.4147e-07 | 5.0101e-08 | 6.4795e-07
1110 | feeder2_line66 | 1 | 354.6 | 56.7087 | 56.7097 | 15.9923 | 15.9926
1110 | feeder2_line66 | 2 | 354.6 | 42.148 | 42.1406 | 11.8861 | 11.884
1110 | feeder2_line66 | 3 | 354.6 | 68.0746 | 68.0796 | 19.1976 | 19.199
1110 | feeder2_line67 | 1 | 99 | 2.4856e-08 | 3.6196e-07 | 2.5107e-08 | 3.6561e-07
1110 | feeder2_line67 | 2 | 99 | 2.4956e-08 | 3.6025e-07 | 2.5208e-08 | 3.6389e-07
1110 | feeder2_line67 | 3 | 99 | 2.0089 | 2.0089 | 2.0292 | 2.0292
1110 | feeder2_line68 | 1 | 266.4 | 2.2983 | 2.2985 | 0.86274 | 0.86279
1110 | feeder2_line68 | 2 | 266.4 | 17.5928 | 17.5931 | 6.6039 | 6.604
1110 | feeder2_line68 | 3 | 266.4 | 13.4899 | 13.4899 | 5.0638 | 5.0638
1110 | feeder2_line69 | 1 | 99 | 4.12 | 4.12 | 4.1616 | 4.1617
1110 | feeder2_line69 | 2 | 99 | 2.5256e-06 | 6.6167e-07 | 2.5511e-06 | 6.6836e-07
1110 | feeder2_line69 | 3 | 99 | 2.5469e-06 | 6.6606e-07 | 2.5727e-06 | 6.7278e-07
1110 | feeder2_line70 | 1 | 354.6 | 60.8284 | 60.8295 | 17.1541 | 17.1544
1110 | feeder2_line70 | 2 | 354.6 | 42.148 | 42.1406 | 11.8861 | 11.884
1110 | feeder2_line70 | 3 | 354.6 | 68.0746 | 68.0796 | 19.1976 | 19.199
1110 | feeder2_line71 | 1 | 99 | 4.9737e-08 | 7.1478e-07 | 5.024e-08 | 7.22e-07
1110 | feeder2_line71 | 2 | 99 | 2.5104 | 2.5104 | 2.5358 | 2.5358
1110 | feeder2_line71 | 3 | 99 | 4.96e-08 | 7.1589e-07 | 5.0101e-08 | 7.2312e-07
1110 | feeder2_line72 | 1 | 354.6 | 60.8285 | 60.8295 | 17.1541 | 17.1544
1110 | feeder2_line72 | 2 | 354.6 | 44.2094 | 44.202 | 12.4674 | 12.4653
1110 | feeder2_line72 | 3 | 354.6 | 68.0747 | 68.0796 | 19.1976 | 19.199
1110 | feeder2_line73 | 1 | 99 | 5.9749e-07 | 1.5324e-06 | 6.0352e-07 | 1.5479e-06
1110 | feeder2_line73 | 2 | 99 | 3.2638 | 3.2637 | 3.2967 | 3.2967
1110 | feeder2_line73 | 3 | 99 | 5.9812e-07 | 1.5342e-06 | 6.0416e-07 | 1.5497e-06
1110 | feeder2_line74 | 1 | 99 | 4.9688e-08 | 4.5706e-07 | 5.019e-08 | 4.6167e-07
1110 | feeder2_line74 | 2 | 99 | 13.3939 | 13.3941 | 13.5292 | 13.5294
1110 | feeder2_line74 | 3 | 99 | 4.959e-08 | 4.5759e-07 | 5.0091e-08 | 4.6221e-07
1110 | feeder2_line75 | 1 | 266.4 | 2.2984 | 2.2985 | 0.86278 | 0.86279
1110 | feeder2_line75 | 2 | 266.4 | 1.4744 | 1.4744 | 0.55344 | 0.55345
1110 | feeder2_line75 | 3 | 266.4 | 13.49 | 13.4899 | 5.0638 | 5.0638
1110 | feeder2_line76 | 1 | 99 | 2.2985 | 2.2985 | 2.3217 | 2.3217
1110 | feeder2_line76 | 2 | 99 | 8.4226e-07 | 1.573e-06 | 8.5077e-07 | 1.5889e-06
1110 | feeder2_line76 | 3 | 99 | 8.4753e-07 | 1.5825e-06 | 8.5609e-07 | 1.5985e-06
1110 | feeder2_line77 | 1 | 99 | 2.4841e-08 | 5.7437e-07 | 2.5092e-08 | 5.8017e-07
1110 | feeder2_line77 | 2 | 99 | 2.4954e-08 | 5.7156e-07 | 2.5206e-08 | 5.7733e-07
1110 | feeder2_line77 | 3 | 99 | 13.49 | 13.4899 | 13.6263 | 13.6262
1110 | feeder2_line78 | 1 | 266.4 | 1.796e-11 | 9.5252e-07 | 6.7419e-12 | 3.5755e-07
1110 | feeder2_line78 | 2 | 266.4 | 1.4744 | 1.4744 | 0.55345 | 0.55345
1110 | feeder2_line78 | 3 | 266.4 | 1.2493e-11 | 9.5347e-07 | 4.6896e-12 | 3.5791e-07
1110 | feeder2_line79 | 1 | 354.6 | 13.1757 | 13.1753 | 3.7156 | 3.7155
1110 | feeder2_line79 | 2 | 354.6 | 6.36 | 6.3595 | 1.7936 | 1.7934
1110 | feeder2_line79 | 3 | 354.6 | 24.9309 | 24.9305 | 7.0307 | 7.0306
1110 | feeder2_line80 | 1 | 354.6 | 74.0016 | 74.0021 | 20.869 | 20.8692
1110 | feeder2_line80 | 2 | 354.6 | 50.1632 | 50.1551 | 14.1464 | 14.1441
1110 | feeder2_line80 | 3 | 354.6 | 92.5677 | 92.572 | 26.1048 | 26.106
1110 | feeder2_line81 | 1 | 354.6 | 74.0016 | 74.0021 | 20.869 | 20.8692
1110 | feeder2_line81 | 2 | 354.6 | 50.1631 | 50.1551 | 14.1464 | 14.1441
1110 | feeder2_line81 | 3 | 354.6 | 93.1615 | 93.1658 | 26.2723 | 26.2735
1110 | feeder2_line82 | 1 | 354.6 | 2.8637e-11 | 7.3339e-07 | 8.0758e-12 | 2.0682e-07
1110 | feeder2_line82 | 2 | 354.6 | 2.802e-11 | 7.2943e-07 | 7.9018e-12 | 2.057e-07
1110 | feeder2_line82 | 3 | 354.6 | 0.59585 | 0.59585 | 0.16803 | 0.16803
1110 | feeder2_line83 | 1 | 354.6 | 74.0018 | 74.0021 | 20.8691 | 20.8692
1110 | feeder2_line83 | 2 | 354.6 | 51.7812 | 51.773 | 14.6027 | 14.6004
1110 | feeder2_line83 | 3 | 354.6 | 93.1617 | 93.1658 | 26.2723 | 26.2735
1110 | feeder2_line84 | 1 | 354.6 | 8.3399e-12 | 1.2965e-06 | 2.3519e-12 | 3.6562e-07
1110 | feeder2_line84 | 2 | 354.6 | 2.5705 | 2.5705 | 0.72489 | 0.72489
1110 | feeder2_line84 | 3 | 354.6 | 1.889e-11 | 1.2986e-06 | 5.3272e-12 | 3.6621e-07
1110 | feeder2_line85 | 1 | 99 | 0.59649 | 0.59649 | 0.60251 | 0.60252
1110 | feeder2_line85 | 2 | 99 | 5.008e-08 | 4.6002e-07 | 5.0586e-08 | 4.6467e-07
1110 | feeder2_line85 | 3 | 99 | 4.959e-08 | 4.6363e-07 | 5.0091e-08 | 4.6831e-07
1110 | feeder2_line86 | 1 | 354.6 | 74.5983 | 74.5986 | 21.0373 | 21.0374
1110 | feeder2_line86 | 2 | 354.6 | 51.7813 | 51.773 | 14.6027 | 14.6004
1110 | feeder2_line86 | 3 | 354.6 | 93.1618 | 93.1658 | 26.2724 | 26.2735
1110 | feeder2_line87 | 1 | 354.6 | 74.5985 | 74.5986 | 21.0374 | 21.0374
1110 | feeder2_line87 | 2 | 354.6 | 75.6951 | 75.687 | 21.3466 | 21.3443
1110 | feeder2_line87 | 3 | 354.6 | 93.2432 | 93.2471 | 26.2953 | 26.2964
1110 | feeder2_line88 | 1 | 354.6 | 0.00011338 | 3.3612e-06 | 3.1973e-05 | 9.4789e-07
1110 | feeder2_line88 | 2 | 354.6 | 24.2293 | 24.2296 | 6.8329 | 6.8329
1110 | feeder2_line88 | 3 | 354.6 | 0.081682 | 0.081582 | 0.023035 | 0.023007
1110 | feeder2_line89 | 1 | 354.6 | 74.5962 | 74.5986 | 21.0367 | 21.0374
1110 | feeder2_line89 | 2 | 354.6 | 77.573 | 77.5671 | 21.8762 | 21.8745
1110 | feeder2_line89 | 3 | 354.6 | 93.2409 | 93.2471 | 26.2947 | 26.2964
1110 | feeder2_line90 | 1 | 354.6 | 0.00072339 | 2.0286e-06 | 0.000204 | 5.7209e-07
1110 | feeder2_line90 | 2 | 354.6 | 2.6256 | 2.6256 | 0.74044 | 0.74043
1110 | feeder2_line90 | 3 | 354.6 | 0.00072652 | 2.0331e-06 | 0.00020489 | 5.7335e-07
1110 | feeder2_line91 | 1 | 354.6 | 74.5961 | 74.5986 | 21.0367 | 21.0374
1110 | feeder2_line91 | 2 | 354.6 | 77.5729 | 77.5671 | 21.8762 | 21.8745
1110 | feeder2_line91 | 3 | 354.6 | 93.7038 | 93.7101 | 26.4252 | 26.427
1110 | feeder2_line92 | 1 | 354.6 | 5.2328e-12 | 1.0236e-06 | 1.4757e-12 | 2.8868e-07
1110 | feeder2_line92 | 2 | 354.6 | 5.2328e-12 | 1.0176e-06 | 1.4757e-12 | 2.8696e-07
1110 | feeder2_line92 | 3 | 354.6 | 0.46633 | 0.46633 | 0.13151 | 0.13151
1110 | feeder2_line93 | 1 | 99 | 2.491e-08 | 3.417e-07 | 2.5162e-08 | 3.4515e-07
1110 | feeder2_line93 | 2 | 99 | 2.5705 | 2.5704 | 2.5964 | 2.5964
1110 | feeder2_line93 | 3 | 99 | 2.4796e-08 | 3.4243e-07 | 2.5047e-08 | 3.4589e-07
1110 | feeder2_line94 | 1 | 354.6 | 2.4909e-06 | 1.6635e-06 | 7.0246e-07 | 4.6912e-07
1110 | feeder2_line94 | 2 | 354.6 | 0.082334 | 0.082302 | 0.023219 | 0.02321
1110 | feeder2_line94 | 3 | 354.6 | 2.4795e-06 | 1.6668e-06 | 6.9923e-07 | 4.7005e-07
1110 | feeder2_line95 | 1 | 99 | 3.5674e-06 | 2.6064e-06 | 3.6034e-06 | 2.6328e-06
1110 | feeder2_line95 | 2 | 99 | 24.2293 | 24.2296 | 24.474 | 24.4743
1110 | feeder2_line95 | 3 | 99 | 3.571e-06 | 2.6115e-06 | 3.6071e-06 | 2.6378e-06
1110 | feeder2_line96 | 1 | 354.6 | 0.00012096 | 6.2126e-07 | 3.4112e-05 | 1.752e-07
1110 | feeder2_line96 | 2 | 354.6 | 0.00012017 | 6.1754e-07 | 3.3888e-05 | 1.7415e-07
1110 | feeder2_line96 | 3 | 354.6 | 0.081664 | 0.081582 | 0.02303 | 0.023007
1110 | feeder2_line97 | 1 | 354.6 | 77.2335 | 77.2358 | 21.7805 | 21.7811
1110 | feeder2_line97 | 2 | 354.6 | 77.573 | 77.5671 | 21.8762 | 21.8745
1110 | feeder2_line97 | 3 | 354.6 | 93.704 | 93.7101 | 26.4253 | 26.427
1110 | feeder2_line98 | 1 | 354.6 | 2.6433 | 2.6417 | 0.74543 | 0.74497
1110 | feeder2_line98 | 2 | 354.6 | 0.0016862 | 6.1868e-07 | 0.00047554 | 1.7447e-07
1110 | feeder2_line98 | 3 | 354.6 | 0.0017131 | 6.2492e-07 | 0.0004831 | 1.7623e-07
1110 | feeder2_line99 | 1 | 99 | 2.4901e-08 | 4.4669e-07 | 2.5152e-08 | 4.512e-07
1110 | feeder2_line99 | 2 | 99 | 2.5058e-08 | 4.439e-07 | 2.5311e-08 | 4.4839e-07
1110 | feeder2_line99 | 3 | 99 | 0.081573 | 0.081582 | 0.082397 | 0.082406
1110 | feeder2_line100 | 1 | 99 | 2.6416 | 2.6417 | 2.6683 | 2.6684
1110 | feeder2_line100 | 2 | 99 | 2.5078e-08 | 6.0966e-07 | 2.5331e-08 | 6.1581e-07
1110 | feeder2_line100 | 3 | 99 | 2.4796e-08 | 6.1486e-07 | 2.5046e-08 | 6.2107e-07
1110 | feeder2_line101 | 1 | 354.6 | 0.08226 | 0.081866 | 0.023198 | 0.023087
1110 | feeder2_line101 | 2 | 354.6 | 6.36 | 6.3595 | 1.7936 | 1.7934
1110 | feeder2_line101 | 3 | 354.6 | 24.9309 | 24.9305 | 7.0307 | 7.0306
1110 | feeder2_line102 | 1 | 99 | 13.0937 | 13.0937 | 13.2259 | 13.2259
1110 | feeder2_line102 | 2 | 99 | 2.3154e-06 | 8.7202e-07 | 2.3388e-06 | 8.8083e-07
1110 | feeder2_line102 | 3 | 99 | 2.3397e-06 | 8.7796e-07 | 2.3633e-06 | 8.8683e-07
1110 | feeder2_line103 | 1 | 99 | 5.4845e-07 | 8.0252e-07 | 5.5399e-07 | 8.1062e-07
1110 | feeder2_line103 | 2 | 99 | 1.6364 | 1.6364 | 1.6529 | 1.6529
1110 | feeder2_line103 | 3 | 99 | 5.4921e-07 | 8.035e-07 | 5.5476e-07 | 8.1162e-07
1110 | feeder2_line104 | 1 | 354.6 | 0.082155 | 0.081866 | 0.023168 | 0.023087
1110 | feeder2_line104 | 2 | 354.6 | 4.7649 | 4.7645 | 1.3437 | 1.3436
1110 | feeder2_line104 | 3 | 354.6 | 24.9308 | 24.9305 | 7.0307 | 7.0306
1110 | feeder2_line105 | 1 | 99 | 2.5435e-06 | 7.3844e-07 | 2.5692e-06 | 7.459e-07
1110 | feeder2_line105 | 2 | 99 | 2.5262e-06 | 7.3444e-07 | 2.5517e-06 | 7.4186e-07
1110 | feeder2_line105 | 3 | 99 | 1.3884 | 1.3884 | 1.4024 | 1.4025
1110 | feeder2_line106 | 1 | 354.6 | 0.082099 | 0.081866 | 0.023153 | 0.023087
1110 | feeder2_line106 | 2 | 354.6 | 4.7648 | 4.7645 | 1.3437 | 1.3436
1110 | feeder2_line106 | 3 | 354.6 | 23.6941 | 23.6938 | 6.6819 | 6.6818
1110 | feeder2_line107 | 1 | 99 | 3.2395e-07 | 8.9993e-07 | 3.2723e-07 | 9.0902e-07
1110 | feeder2_line107 | 2 | 99 | 3.2596 | 3.2595 | 3.2926 | 3.2925
1110 | feeder2_line107 | 3 | 99 | 3.2416e-07 | 9.0068e-07 | 3.2743e-07 | 9.0977e-07
1110 | feeder2_line108 | 1 | 354.6 | 0.082088 | 0.081866 | 0.02315 | 0.023087
1110 | feeder2_line108 | 2 | 354.6 | 1.5149 | 1.5147 | 0.42722 | 0.42716
1110 | feeder2_line108 | 3 | 354.6 | 23.6941 | 23.6938 | 6.6819 | 6.6818
1110 | feeder2_line109 | 1 | 354.6 | 89.5263 | 89.5274 | 25.2471 | 25.2474
1110 | feeder2_line109 | 2 | 354.6 | 77.5742 | 77.5671 | 21.8766 | 21.8745
1110 | feeder2_line109 | 3 | 354.6 | 93.7052 | 93.7101 | 26.4256 | 26.427
1110 | feeder2_line110 | 1 | 99 | 12.3503 | 12.3495 | 12.4751 | 12.4743
1110 | feeder2_line110 | 2 | 99 | 0.00079713 | 9.0207e-07 | 0.00080518 | 9.1118e-07
1110 | feeder2_line110 | 3 | 99 | 0.00080687 | 9.1004e-07 | 0.00081502 | 9.1923e-07
1110 | feeder2_line111 | 1 | 99 | 2.4874e-08 | 3.8149e-07 | 2.5125e-08 | 3.8534e-07
1110 | feeder2_line111 | 2 | 99 | 22.4643 | 22.4647 | 22.6912 | 22.6917
1110 | feeder2_line111 | 3 | 99 | 2.4767e-08 | 3.8221e-07 | 2.5017e-08 | 3.8607e-07
1110 | feeder2_line112 | 1 | 99 | 3.2421e-07 | 9.1672e-07 | 3.2748e-07 | 9.2598e-07
1110 | feeder2_line112 | 2 | 99 | 1.9 | 1.8999 | 1.9192 | 1.9191
1110 | feeder2_line112 | 3 | 99 | 3.2461e-07 | 9.1848e-07 | 3.2789e-07 | 9.2776e-07
1110 | feeder2_line113 | 1 | 99 | 10.4565 | 10.4565 | 10.5621 | 10.5621
1110 | feeder2_line113 | 2 | 99 | 3.23e-07 | 8.991e-07 | 3.2627e-07 | 9.0818e-07
1110 | feeder2_line113 | 3 | 99 | 3.2507e-07 | 9.0695e-07 | 3.2836e-07 | 9.1611e-07
1110 | feeder2_line114 | 1 | 99 | 1.6391 | 1.6391 | 1.6556 | 1.6556
1110 | feeder2_line114 | 2 | 99 | 2.4996e-08 | 4.3363e-07 | 2.5248e-08 | 4.3801e-07
1110 | feeder2_line114 | 3 | 99 | 2.4809e-08 | 4.3657e-07 | 2.5059e-08 | 4.4098e-07
1110 | feeder2_line115 | 1 | 99 | 2.4843e-08 | 5.6163e-07 | 2.5094e-08 | 5.673e-07
1110 | feeder2_line115 | 2 | 99 | 0.061441 | 0.061432 | 0.062062 | 0.062052
1110 | feeder2_line115 | 3 | 99 | 2.4839e-08 | 5.6191e-07 | 2.509e-08 | 5.6759e-07
1110 | feeder2_line116 | 1 | 354.6 | 0.082094 | 0.081866 | 0.023151 | 0.023087
1110 | feeder2_line116 | 2 | 354.6 | 1.4595 | 1.4592 | 0.41158 | 0.41152
1110 | feeder2_line116 | 3 | 354.6 | 23.6941 | 23.6938 | 6.6819 | 6.6818
1110 | feeder2_line117 | 1 | 99 | 4.9877e-08 | 6.4256e-07 | 5.0381e-08 | 6.4905e-07
1110 | feeder2_line117 | 2 | 99 | 14.1695 | 14.1697 | 14.3126 | 14.3129
1110 | feeder2_line117 | 3 | 99 | 4.9602e-08 | 6.4416e-07 | 5.0103e-08 | 6.5067e-07
1110 | feeder2_line118 | 1 | 354.6 | 89.5263 | 89.5274 | 25.2471 | 25.2474
1110 | feeder2_line118 | 2 | 354.6 | 91.6764 | 91.6695 | 25.8535 | 25.8515
1110 | feeder2_line118 | 3 | 354.6 | 93.7053 | 93.7101 | 26.4256 | 26.427
1110 | feeder2_line119 | 1 | 99 | 2.4829e-08 | 6.0436e-07 | 2.508e-08 | 6.1047e-07
1110 | feeder2_line119 | 2 | 99 | 2.4975e-08 | 6.0109e-07 | 2.5227e-08 | 6.0716e-07
1110 | feeder2_line119 | 3 | 99 | 12.4095 | 12.4093 | 12.5349 | 12.5347
1110 | feeder2_line120 | 1 | 354.6 | 0.082096 | 0.081866 | 0.023152 | 0.023087
1110 | feeder2_line120 | 2 | 354.6 | 1.4595 | 1.4592 | 0.41158 | 0.41152
1110 | feeder2_line120 | 3 | 354.6 | 11.5173 | 11.5172 | 3.248 | 3.2479
1110 | feeder2_line121 | 1 | 99 | 3.2396e-07 | 9.3591e-07 | 3.2723e-07 | 9.4536e-07
1110 | feeder2_line121 | 2 | 99 | 1.3788 | 1.3788 | 1.3928 | 1.3928
1110 | feeder2_line121 | 3 | 99 | 3.2399e-07 | 9.3587e-07 | 3.2726e-07 | 9.4532e-07
1110 | feeder2_line122 | 1 | 354.6 | 0.082084 | 0.081865 | 0.023148 | 0.023087
1110 | feeder2_line122 | 2 | 354.6 | 0.089982 | 0.089736 | 0.025376 | 0.025306
1110 | feeder2_line122 | 3 | 354.6 | 11.5173 | 11.5172 | 3.248 | 3.2479
1110 | feeder2_line123 | 1 | 99 | 5.7343e-07 | 9.6982e-07 | 5.7923e-07 | 9.7962e-07
1110 | feeder2_line123 | 2 | 99 | 5.7033e-07 | 9.6461e-07 | 5.7609e-07 | 9.7435e-07
1110 | feeder2_line123 | 3 | 99 | 3.5845 | 3.5845 | 3.6207 | 3.6207
1110 | feeder2_line124 | 1 | 354.6 | 0.081987 | 0.081865 | 0.023121 | 0.023087
1110 | feeder2_line124 | 2 | 354.6 | 0.089886 | 0.089736 | 0.025349 | 0.025306
1110 | feeder2_line124 | 3 | 354.6 | 8.0256 | 8.0255 | 2.2633 | 2.2633
1110 | feeder2_line125 | 1 | 99 | 5.7344e-07 | 9.0155e-07 | 5.7923e-07 | 9.1066e-07
1110 | feeder2_line125 | 2 | 99 | 5.7033e-07 | 8.9671e-07 | 5.7609e-07 | 9.0577e-07
1110 | feeder2_line125 | 3 | 99 | 2.6424 | 2.6424 | 2.6691 | 2.6691
1110 | feeder2_line126 | 1 | 354.6 | 0.082143 | 0.081865 | 0.023165 | 0.023087
1110 | feeder2_line126 | 2 | 354.6 | 0.090041 | 0.089736 | 0.025392 | 0.025306
1110 | feeder2_line126 | 3 | 354.6 | 5.4372 | 5.437 | 1.5333 | 1.5333
1110 | feeder2_line127 | 1 | 99 | 5.7344e-07 | 1.0793e-06 | 5.7923e-07 | 1.0902e-06
1110 | feeder2_line127 | 2 | 99 | 5.7034e-07 | 1.0735e-06 | 5.7611e-07 | 1.0844e-06
1110 | feeder2_line127 | 3 | 99 | 1.514 | 1.514 | 1.5293 | 1.5293
1110 | feeder2_line128 | 1 | 354.6 | 0.082057 | 0.081865 | 0.023141 | 0.023087
1110 | feeder2_line128 | 2 | 354.6 | 0.089957 | 0.089735 | 0.025368 | 0.025306
1110 | feeder2_line128 | 3 | 354.6 | 4.0338 | 4.0336 | 1.1376 | 1.1375
1110 | feeder2_line129 | 1 | 99 | 5.4862e-07 | 8.7517e-07 | 5.5416e-07 | 8.8401e-07
1110 | feeder2_line129 | 2 | 99 | 0.089742 | 0.089735 | 0.090648 | 0.090641
1110 | feeder2_line129 | 3 | 99 | 5.4844e-07 | 8.7496e-07 | 5.5398e-07 | 8.838e-07
1110 | feeder2_line130 | 1 | 354.6 | 0.082071 | 0.081865 | 0.023145 | 0.023087
1110 | feeder2_line130 | 2 | 354.6 | 0.00030653 | 4.6071e-06 | 8.6444e-05 | 1.2992e-06
1110 | feeder2_line130 | 3 | 354.6 | 4.0339 | 4.0336 | 1.1376 | 1.1375
1110 | feeder2_line131 | 1 | 99 | 5.7344e-07 | 9.6998e-07 | 5.7923e-07 | 9.7978e-07
1110 | feeder2_line131 | 2 | 99 | 5.7034e-07 | 9.6479e-07 | 5.7611e-07 | 9.7454e-07
1110 | feeder2_line131 | 3 | 99 | 3.4964 | 3.4964 | 3.5317 | 3.5317
1110 | feeder2_line132 | 1 | 354.6 | 0.081912 | 0.081865 | 0.0231 | 0.023086
1110 | feeder2_line132 | 2 | 354.6 | 0.00012473 | 2.8967e-06 | 3.5176e-05 | 8.1689e-07
1110 | feeder2_line132 | 3 | 354.6 | 0.59642 | 0.59635 | 0.1682 | 0.16817
1110 | feeder2_line133 | 1 | 99 | 0.081843 | 0.081864 | 0.082669 | 0.082691
1110 | feeder2_line133 | 2 | 99 | 2.9766e-07 | 9.725e-07 | 3.0067e-07 | 9.8233e-07
1110 | feeder2_line133 | 3 | 99 | 2.9908e-07 | 9.7747e-07 | 3.021e-07 | 9.8735e-07
1110 | feeder2_line134 | 1 | 354.6 | 1.4304e-12 | 1.7828e-06 | 4.0338e-13 | 5.0277e-07
1110 | feeder2_line134 | 2 | 354.6 | 8.9326e-12 | 1.7738e-06 | 2.5191e-12 | 5.0022e-07
1110 | feeder2_line134 | 3 | 354.6 | 0.59634 | 0.59635 | 0.16817 | 0.16817
1110 | feeder2_line135 | 1 | 99 | 2.5081 | 2.5082 | 2.5335 | 2.5335
1110 | feeder2_line135 | 2 | 99 | 5.0257e-08 | 5.8204e-07 | 5.0765e-08 | 5.8791e-07
1110 | feeder2_line135 | 3 | 99 | 4.9638e-08 | 5.8728e-07 | 5.014e-08 | 5.9321e-07
1110 | feeder2_line136 | 1 | 354.6 | 91.8433 | 91.8443 | 25.9005 | 25.9008
1110 | feeder2_line136 | 2 | 354.6 | 91.6763 | 91.6695 | 25.8535 | 25.8515
1110 | feeder2_line136 | 3 | 354.6 | 93.7052 | 93.7101 | 26.4256 | 26.427
1110 | feeder2_line137 | 1 | 99 | 1.0425 | 1.0426 | 1.0531 | 1.0531
1110 | feeder2_line137 | 2 | 99 | 8.4458e-07 | 1.5678e-06 | 8.5311e-07 | 1.5837e-06
1110 | feeder2_line137 | 3 | 99 | 8.5251e-07 | 1.5819e-06 | 8.6112e-07 | 1.5979e-06
1110 | feeder2_line138 | 1 | 354.6 | 92.6867 | 92.6877 | 26.1384 | 26.1387
1110 | feeder2_line138 | 2 | 354.6 | 91.6764 | 91.6695 | 25.8535 | 25.8515
1110 | feeder2_line138 | 3 | 354.6 | 93.7053 | 93.7101 | 26.4256 | 26.427
1110 | feeder2_line139 | 1 | 99 | 4.9937e-08 | 4.9173e-07 | 5.0442e-08 | 4.967e-07
1110 | feeder2_line139 | 2 | 99 | 5.0278e-08 | 4.8858e-07 | 5.0786e-08 | 4.9351e-07
1110 | feeder2_line139 | 3 | 99 | 0.044598 | 0.044878 | 0.045049 | 0.045331
1110 | feeder2_line140 | 1 | 354.6 | 92.6868 | 92.6877 | 26.1384 | 26.1387
1110 | feeder2_line140 | 2 | 354.6 | 91.6765 | 91.6695 | 25.8535 | 25.8515
1110 | feeder2_line140 | 3 | 354.6 | 93.7499 | 93.7549 | 26.4382 | 26.4396
1110 | feeder2_line141 | 1 | 99 | 2.5272e-06 | 4.8649e-07 | 2.5528e-06 | 4.914e-07
1110 | feeder2_line141 | 2 | 99 | 1.3153 | 1.3153 | 1.3286 | 1.3286
1110 | feeder2_line141 | 3 | 99 | 2.5366e-06 | 4.8772e-07 | 2.5622e-06 | 4.9265e-07
1110 | feeder2_line142 | 1 | 354.6 | 92.6866 | 92.6877 | 26.1384 | 26.1387
1110 | feeder2_line142 | 2 | 354.6 | 92.6537 | 92.6469 | 26.1291 | 26.1272
1110 | feeder2_line142 | 3 | 354.6 | 93.7497 | 93.7549 | 26.4382 | 26.4396
1110 | feeder2_line143 | 1 | 99 | 8.5063e-07 | 1.7288e-06 | 8.5923e-07 | 1.7462e-06
1110 | feeder2_line143 | 2 | 99 | 3.2567 | 3.2566 | 3.2896 | 3.2895
1110 | feeder2_line143 | 3 | 99 | 8.5292e-07 | 1.7332e-06 | 8.6154e-07 | 1.7507e-06
1110 | feeder2_line144 | 1 | 354.6 | 92.6864 | 92.6877 | 26.1383 | 26.1387
1110 | feeder2_line144 | 2 | 354.6 | 95.8431 | 95.8364 | 27.0285 | 27.0266
1110 | feeder2_line144 | 3 | 354.6 | 93.7495 | 93.7549 | 26.4381 | 26.4396
1110 | feeder2_line145 | 1 | 99 | 2.4981e-08 | 4.8478e-07 | 2.5233e-08 | 4.8968e-07
1110 | feeder2_line145 | 2 | 99 | 0.5945 | 0.5945 | 0.60051 | 0.6005
1110 | feeder2_line145 | 3 | 99 | 2.4838e-08 | 4.8602e-07 | 2.5089e-08 | 4.9093e-07
1110 | feeder2_line146 | 1 | 354.6 | 92.6863 | 92.6877 | 26.1383 | 26.1387
1110 | feeder2_line146 | 2 | 354.6 | 96.4355 | 96.4289 | 27.1956 | 27.1937
1110 | feeder2_line146 | 3 | 354.6 | 93.7494 | 93.7549 | 26.4381 | 26.4396
1110 | feeder2_line147 | 1 | 99 | 1.8964 | 1.8964 | 1.9155 | 1.9156
1110 | feeder2_line147 | 2 | 99 | 1.1436e-06 | 2.2218e-06 | 1.1552e-06 | 2.2443e-06
1110 | feeder2_line147 | 3 | 99 | 1.154e-06 | 2.2419e-06 | 1.1657e-06 | 2.2645e-06
1110 | feeder2_line148 | 1 | 99 | 1.3055 | 1.3055 | 1.3186 | 1.3186
1110 | feeder2_line148 | 2 | 99 | 5.9697e-07 | 1.4888e-06 | 6.03e-07 | 1.5038e-06
1110 | feeder2_line148 | 3 | 99 | 6.0185e-07 | 1.5022e-06 | 6.0793e-07 | 1.5174e-06
1110 | feeder2_line149 | 1 | 354.6 | 95.888 | 95.8892 | 27.0412 | 27.0415
1110 | feeder2_line149 | 2 | 354.6 | 96.4357 | 96.4289 | 27.1956 | 27.1937
1110 | feeder2_line149 | 3 | 354.6 | 93.7496 | 93.7549 | 26.4381 | 26.4396
1110 | feeder2_line150 | 1 | 354.6 | 95.8881 | 95.8892 | 27.0412 | 27.0415
1110 | feeder2_line150 | 2 | 354.6 | 99.0001 | 98.9932 | 27.9188 | 27.9169
1110 | feeder2_line150 | 3 | 354.6 | 93.7497 | 93.7549 | 26.4382 | 26.4396
1110 | feeder2_line151 | 1 | 99 | 9.7668e-06 | 1.7802e-06 | 9.8655e-06 | 1.7982e-06
1110 | feeder2_line151 | 2 | 99 | 2.794 | 2.794 | 2.8222 | 2.8222
1110 | feeder2_line151 | 3 | 99 | 9.8109e-06 | 1.7847e-06 | 9.91e-06 | 1.8027e-06
1110 | feeder2_line152 | 1 | 354.6 | 9.7636e-12 | 1.1866e-06 | 2.7534e-12 | 3.3464e-07
1110 | feeder2_line152 | 2 | 354.6 | 9.7636e-12 | 1.1795e-06 | 2.7534e-12 | 3.3262e-07
1110 | feeder2_line152 | 3 | 354.6 | 2.1451 | 2.1451 | 0.60494 | 0.60493
1110 | feeder2_line153 | 1 | 99 | 1.3814 | 1.3814 | 1.3954 | 1.3954
1110 | feeder2_line153 | 2 | 99 | 5.0352e-08 | 5.8994e-07 | 5.0861e-08 | 5.959e-07
1110 | feeder2_line153 | 3 | 99 | 4.9738e-08 | 5.952e-07 | 5.0241e-08 | 6.0121e-07
1110 | feeder2_line154 | 1 | 99 | 5.7611e-07 | 8.8348e-07 | 5.8193e-07 | 8.924e-07
1110 | feeder2_line154 | 2 | 99 | 5.7242e-07 | 8.7786e-07 | 5.782e-07 | 8.8672e-07
1110 | feeder2_line154 | 3 | 99 | 2.1319 | 2.132 | 2.1535 | 2.1535
1110 | feeder2_line155 | 1 | 99 | 97.1726 | 97.1738 | 98.1541 | 98.1553
1110 | feeder2_line155 | 2 | 99 | 99 | 98.9932 | 100 | 99.9932
1110 | feeder2_line155 | 3 | 99 | 97.8219 | 97.8272 | 98.81 | 98.8154
1110 | feeder2_line156 | 1 | 99 | 6.0083e-07 | 1.1625e-06 | 6.069e-07 | 1.1742e-06
1110 | feeder2_line156 | 2 | 99 | 1.6375 | 1.6375 | 1.6541 | 1.6541
1110 | feeder2_line156 | 3 | 99 | 6.0216e-07 | 1.1654e-06 | 6.0824e-07 | 1.1771e-06
1110 | feeder2_line157 | 1 | 99 | 2.4994e-08 | 2.5237e-07 | 2.5247e-08 | 2.5492e-07
1110 | feeder2_line157 | 2 | 99 | 1.4759 | 1.4759 | 1.4908 | 1.4908
1110 | feeder2_line157 | 3 | 99 | 2.4856e-08 | 2.53e-07 | 2.5107e-08 | 2.5556e-07
1140 | feeder2_line1 | 1 | 354.6 | 83.4189 | 83.4165 | 23.5248 | 23.5241
1140 | feeder2_line1 | 2 | 354.6 | 91.2071 | 91.202 | 25.7211 | 25.7197
1140 | feeder2_line1 | 3 | 354.6 | 86.4862 | 86.495 | 24.3898 | 24.3923
1140 | feeder2_line2 | 1 | 354.6 | 83.2932 | 83.2906 | 23.4893 | 23.4886
1140 | feeder2_line2 | 2 | 354.6 | 91.2072 | 91.202 | 25.7211 | 25.7197
1140 | feeder2_line2 | 3 | 354.6 | 86.4863 | 86.495 | 24.3898 | 24.3923
1140 | feeder2_line3 | 1 | 80.1 | 1.2438 | 1.2438 | 1.5529 | 1.5528
1140 | feeder2_line3 | 2 | 80.1 | 5.6773e-07 | 1.0492e-06 | 7.0878e-07 | 1.3098e-06
1140 | feeder2_line3 | 3 | 80.1 | 5.6751e-07 | 1.0488e-06 | 7.085e-07 | 1.3093e-06
1140 | feeder2_line4 | 1 | 354.6 | 83.2931 | 83.2906 | 23.4893 | 23.4886
1140 | feeder2_line4 | 2 | 354.6 | 90.02 | 90.0147 | 25.3864 | 25.3849
1140 | feeder2_line4 | 3 | 354.6 | 86.4862 | 86.495 | 24.3898 | 24.3923
1140 | feeder2_line5 | 1 | 80.1 | 5.6821e-07 | 9.9148e-07 | 7.0937e-07 | 1.2378e-06
1140 | feeder2_line5 | 2 | 80.1 | 10.351 | 10.3509 | 12.9225 | 12.9225
1140 | feeder2_line5 | 3 | 80.1 | 5.6743e-07 | 9.9014e-07 | 7.084e-07 | 1.2361e-06
1140 | feeder2_line6 | 1 | 80.1 | 5.6816e-07 | 1.1662e-06 | 7.0932e-07 | 1.456e-06
1140 | feeder2_line6 | 2 | 80.1 | 5.6762e-07 | 1.1651e-06 | 7.0864e-07 | 1.4546e-06
1140 | feeder2_line6 | 3 | 80.1 | 0.53125 | 0.53127 | 0.66323 | 0.66326
1140 | feeder2_line7 | 1 | 354.6 | 83.2931 | 83.2906 | 23.4893 | 23.4886
1140 | feeder2_line7 | 2 | 354.6 | 90.02 | 90.0147 | 25.3864 | 25.3849
1140 | feeder2_line7 | 3 | 354.6 | 86.4559 | 86.4648 | 24.3812 | 24.3837
1140 | feeder2_line8 | 1 | 80.1 | 1.2907 | 1.2907 | 1.6113 | 1.6113
1140 | feeder2_line8 | 2 | 80.1 | 5.6744e-07 | 1.1231e-06 | 7.0841e-07 | 1.4021e-06
1140 | feeder2_line8 | 3 | 80.1 | 5.6706e-07 | 1.1224e-06 | 7.0794e-07 | 1.4012e-06
1140 | feeder2_line9 | 1 | 354.6 | 83.3372 | 83.3346 | 23.5017 | 23.501
1140 | feeder2_line9 | 2 | 354.6 | 90.0199 | 90.0147 | 25.3863 | 25.3849
1140 | feeder2_line9 | 3 | 354.6 | 86.4557 | 86.4648 | 24.3812 | 24.3838
1140 | feeder2_line10 | 1 | 80.1 | 8.3966e-07 | 1.4843e-06 | 1.0483e-06 | 1.8531e-06
1140 | feeder2_line10 | 2 | 80.1 | 1.2905 | 1.2905 | 1.6111 | 1.6111
1140 | feeder2_line10 | 3 | 80.1 | 8.3816e-07 | 1.4818e-06 | 1.0464e-06 | 1.85e-06
1140 | feeder2_line11 | 1 | 354.6 | 83.3373 | 83.3346 | 23.5018 | 23.501
1140 | feeder2_line11 | 2 | 354.6 | 90.0988 | 90.0934 | 25.4086 | 25.4071
1140 | feeder2_line11 | 3 | 354.6 | 86.4559 | 86.4648 | 24.3812 | 24.3838
1140 | feeder2_line12 | 1 | 80.1 | 5.4331e-07 | 9.8446e-07 | 6.7829e-07 | 1.229e-06
1140 | feeder2_line12 | 2 | 80.1 | 5.4266e-07 | 9.835e-07 | 6.7748e-07 | 1.2278e-06
1140 | feeder2_line12 | 3 | 80.1 | 1.8375 | 1.8375 | 2.294 | 2.294
1140 | feeder2_line13 | 1 | 354.6 | 83.3373 | 83.3346 | 23.5018 | 23.501
1140 | feeder2_line13 | 2 | 354.6 | 90.0988 | 90.0934 | 25.4086 | 25.4071
1140 | feeder2_line13 | 3 | 354.6 | 85.3057 | 85.3148 | 24.0569 | 24.0594
1140 | feeder2_line14 | 1 | 80.1 | 2.161 | 2.161 | 2.6978 | 2.6978
1140 | feeder2_line14 | 2 | 80.1 | 2.9598e-07 | 6.4125e-07 | 3.6952e-07 | 8.0056e-07
1140 | feeder2_line14 | 3 | 80.1 | 2.9576e-07 | 6.4071e-07 | 3.6924e-07 | 7.9988e-07
1140 | feeder2_line15 | 1 | 354.6 | 82.1691 | 82.1661 | 23.1723 | 23.1715
1140 | feeder2_line15 | 2 | 354.6 | 90.0988 | 90.0934 | 25.4086 | 25.4071
1140 | feeder2_line15 | 3 | 354.6 | 85.3057 | 85.3148 | 24.0569 | 24.0594
1140 | feeder2_line16 | 1 | 80.1 | 5.6776e-07 | 1.0228e-06 | 7.0882e-07 | 1.277e-06
1140 | feeder2_line16 | 2 | 80.1 | 2.0194 | 2.0194 | 2.5211 | 2.5211
1140 | feeder2_line16 | 3 | 80.1 | 5.6663e-07 | 1.0208e-06 | 7.0741e-07 | 1.2745e-06
1140 | feeder2_line17 | 1 | 354.6 | 82.1692 | 82.1661 | 23.1723 | 23.1715
1140 | feeder2_line17 | 2 | 354.6 | 90.0883 | 90.0829 | 25.4056 | 25.4041
1140 | feeder2_line17 | 3 | 354.6 | 85.3057 | 85.3148 | 24.0569 | 24.0595
1140 | feeder2_line18 | 1 | 80.1 | 5.4283e-07 | 7.3165e-07 | 6.7769e-07 | 9.1342e-07
1140 | feeder2_line18 | 2 | 80.1 | 5.4211e-07 | 7.3088e-07 | 6.7679e-07 | 9.1246e-07
1140 | feeder2_line18 | 3 | 80.1 | 11.1314 | 11.1313 | 13.8969 | 13.8968
1140 | feeder2_line19 | 1 | 354.6 | 82.1692 | 82.1661 | 23.1724 | 23.1715
1140 | feeder2_line19 | 2 | 354.6 | 90.0883 | 90.0829 | 25.4056 | 25.4041
1140 | feeder2_line19 | 3 | 354.6 | 83.4935 | 83.5044 | 23.5458 | 23.5489
1140 | feeder2_line20 | 1 | 99 | 5.4269e-07 | 8.7697e-07 | 5.4818e-07 | 8.8583e-07
1140 | feeder2_line20 | 2 | 99 | 5.4196e-07 | 8.7603e-07 | 5.4743e-07 | 8.8488e-07
1140 | feeder2_line20 | 3 | 99 | 1.3825 | 1.3826 | 1.3965 | 1.3965
1140 | feeder2_line21 | 1 | 354.6 | 82.1692 | 82.1661 | 23.1724 | 23.1715
1140 | feeder2_line21 | 2 | 354.6 | 90.0883 | 90.0829 | 25.4056 | 25.4041
1140 | feeder2_line21 | 3 | 354.6 | 83.4376 | 83.4487 | 23.53 | 23.5332
1140 | feeder2_line22 | 1 | 99 | 5.6713e-07 | 1.0052e-06 | 5.7285e-07 | 1.0153e-06
1140 | feeder2_line22 | 2 | 99 | 0.094761 | 0.094762 | 0.095718 | 0.095719
1140 | feeder2_line22 | 3 | 99 | 5.6557e-07 | 1.0025e-06 | 5.7128e-07 | 1.0126e-06
1140 | feeder2_line23 | 1 | 99 | 5.6711e-07 | 9.4092e-07 | 5.7284e-07 | 9.5042e-07
1140 | feeder2_line23 | 2 | 99 | 5.6647e-07 | 9.3988e-07 | 5.722e-07 | 9.4938e-07
1140 | feeder2_line23 | 3 | 99 | 11.1258 | 11.1257 | 11.2382 | 11.238
1140 | feeder2_line24 | 1 | 354.6 | 82.1692 | 82.1661 | 23.1724 | 23.1715
1140 | feeder2_line24 | 2 | 354.6 | 90.0938 | 90.0883 | 25.4072 | 25.4056
1140 | feeder2_line24 | 3 | 354.6 | 82.7414 | 82.7541 | 23.3337 | 23.3373
1140 | feeder2_line25 | 1 | 99 | 0.094632 | 0.094628 | 0.095587 | 0.095584
1140 | feeder2_line25 | 2 | 99 | 4.9251e-08 | 6.8308e-07 | 4.9748e-08 | 6.8998e-07
1140 | feeder2_line25 | 3 | 99 | 4.9438e-08 | 6.8203e-07 | 4.9938e-08 | 6.8892e-07
1140 | feeder2_line26 | 1 | 99 | 0.45056 | 0.45054 | 0.45511 | 0.45509
1140 | feeder2_line26 | 2 | 99 | 5.4167e-07 | 8.463e-07 | 5.4714e-07 | 8.5485e-07
1140 | feeder2_line26 | 3 | 99 | 5.4069e-07 | 8.45e-07 | 5.4615e-07 | 8.5353e-07
1140 | feeder2_line27 | 1 | 354.6 | 82.16 | 82.1568 | 23.1698 | 23.1689
1140 | feeder2_line27 | 2 | 354.6 | 90.0938 | 90.0883 | 25.4072 | 25.4056
1140 | feeder2_line27 | 3 | 354.6 | 82.7414 | 82.7541 | 23.3337 | 23.3373
1140 | feeder2_line28 | 1 | 99 | 2.5148e-06 | 7.0293e-07 | 2.5402e-06 | 7.1003e-07
1140 | feeder2_line28 | 2 | 99 | 0.75375 | 0.75378 | 0.76137 | 0.76139
1140 | feeder2_line28 | 3 | 99 | 2.5045e-06 | 7.0109e-07 | 2.5298e-06 | 7.0818e-07
1140 | feeder2_line29 | 1 | 354.6 | 82.16 | 82.1568 | 23.1698 | 23.1689
1140 | feeder2_line29 | 2 | 354.6 | 89.5168 | 89.5112 | 25.2444 | 25.2429
1140 | feeder2_line29 | 3 | 354.6 | 82.7414 | 82.7541 | 23.3337 | 23.3373
1140 | feeder2_line30 | 1 | 266.4 | 4.4823 | 4.4816 | 1.6825 | 1.6823
1140 | feeder2_line30 | 2 | 266.4 | 16.2689 | 16.2686 | 6.1069 | 6.1068
1140 | feeder2_line30 | 3 | 266.4 | 5.1407 | 5.1405 | 1.9297 | 1.9296
1140 | feeder2_line31 | 1 | 354.6 | 82.2474 | 82.2431 | 23.1944 | 23.1932
1140 | feeder2_line31 | 2 | 354.6 | 87.9098 | 87.9036 | 24.7913 | 24.7895
1140 | feeder2_line31 | 3 | 354.6 | 82.071 | 82.0837 | 23.1447 | 23.1483
1140 | feeder2_line32 | 1 | 354.6 | 82.2474 | 82.2431 | 23.1944 | 23.1932
1140 | feeder2_line32 | 2 | 354.6 | 87.5793 | 87.5732 | 24.6981 | 24.6963
1140 | feeder2_line32 | 3 | 354.6 | 82.0709 | 82.0837 | 23.1447 | 23.1483
1140 | feeder2_line33 | 1 | 99 | 4.8936e-08 | 6.7738e-07 | 4.943e-08 | 6.8423e-07
1140 | feeder2_line33 | 2 | 99 | 2.9437 | 2.9437 | 2.9734 | 2.9734
1140 | feeder2_line33 | 3 | 99 | 4.9369e-08 | 6.7572e-07 | 4.9867e-08 | 6.8254e-07
1140 | feeder2_line34 | 1 | 354.6 | 82.2474 | 82.2431 | 23.1944 | 23.1932
1140 | feeder2_line34 | 2 | 354.6 | 87.5793 | 87.5732 | 24.6981 | 24.6963
1140 | feeder2_line34 | 3 | 354.6 | 82.0852 | 82.0981 | 23.1487 | 23.1523
1140 | feeder2_line35 | 1 | 99 | 2.9519e-07 | 7.4997e-07 | 2.9817e-07 | 7.5755e-07
1140 | feeder2_line35 | 2 | 99 | 2.9494e-07 | 7.4921e-07 | 2.9792e-07 | 7.5678e-07
1140 | feeder2_line35 | 3 | 99 | 0.086766 | 0.086776 | 0.087642 | 0.087652
1140 | feeder2_line36 | 1 | 354.6 | 83.4239 | 83.4182 | 23.5262 | 23.5246
1140 | feeder2_line36 | 2 | 354.6 | 87.5793 | 87.5732 | 24.6981 | 24.6963
1140 | feeder2_line36 | 3 | 354.6 | 82.0852 | 82.0981 | 23.1487 | 23.1523
1140 | feeder2_line37 | 1 | 99 | 11.2759 | 11.2758 | 11.3898 | 11.3897
1140 | feeder2_line37 | 2 | 99 | 2.9489e-07 | 8.2885e-07 | 2.9787e-07 | 8.3723e-07
1140 | feeder2_line37 | 3 | 99 | 2.9454e-07 | 8.2766e-07 | 2.9751e-07 | 8.3602e-07
1140 | feeder2_line38 | 1 | 99 | 3.1981e-07 | 7.662e-07 | 3.2304e-07 | 7.7394e-07
1140 | feeder2_line38 | 2 | 99 | 12.683 | 12.683 | 12.8112 | 12.8111
1140 | feeder2_line38 | 3 | 99 | 3.1939e-07 | 7.6425e-07 | 3.2262e-07 | 7.7197e-07
1140 | feeder2_line39 | 1 | 266.4 | 4.4823 | 4.4816 | 1.6825 | 1.6823
1140 | feeder2_line39 | 2 | 266.4 | 3.8774 | 3.8774 | 1.4555 | 1.4555
1140 | feeder2_line39 | 3 | 266.4 | 5.1407 | 5.1405 | 1.9297 | 1.9296
1140 | feeder2_line40 | 1 | 354.6 | 83.4453 | 83.4397 | 23.5322 | 23.5307
1140 | feeder2_line40 | 2 | 354.6 | 87.5793 | 87.5732 | 24.698 | 24.6963
1140 | feeder2_line40 | 3 | 354.6 | 82.0852 | 82.0981 | 23.1487 | 23.1523
1140 | feeder2_line41 | 1 | 99 | 0.0948 | 0.094794 | 0.095757 | 0.095752
1140 | feeder2_line41 | 2 | 99 | 4.9127e-08 | 7.2423e-07 | 4.9623e-08 | 7.3155e-07
1140 | feeder2_line41 | 3 | 99 | 4.9361e-08 | 7.2316e-07 | 4.986e-08 | 7.3047e-07
1140 | feeder2_line42 | 1 | 99 | 2.9534e-07 | 7.3955e-07 | 2.9832e-07 | 7.4702e-07
1140 | feeder2_line42 | 2 | 99 | 2.9501e-07 | 7.3855e-07 | 2.9799e-07 | 7.4601e-07
1140 | feeder2_line42 | 3 | 99 | 1.0301 | 1.0301 | 1.0405 | 1.0405
1140 | feeder2_line43 | 1 | 266.4 | 4.4822 | 4.4816 | 1.6825 | 1.6823
1140 | feeder2_line43 | 2 | 266.4 | 3.8774 | 3.8774 | 1.4555 | 1.4555
1140 | feeder2_line43 | 3 | 266.4 | 4.1555 | 4.1554 | 1.5599 | 1.5598
1140 | feeder2_line44 | 1 | 354.6 | 83.4454 | 83.4397 | 23.5322 | 23.5307
1140 | feeder2_line44 | 2 | 354.6 | 87.5793 | 87.5732 | 24.6981 | 24.6963
1140 | feeder2_line44 | 3 | 354.6 | 82.3283 | 82.3413 | 23.2172 | 23.2209
1140 | feeder2_line45 | 1 | 99 | 4.8918e-08 | 5.7162e-07 | 4.9413e-08 | 5.7739e-07
1140 | feeder2_line45 | 2 | 99 | 4.9121e-08 | 5.711e-07 | 4.9617e-08 | 5.7686e-07
1140 | feeder2_line45 | 3 | 99 | 1.3811 | 1.3812 | 1.395 | 1.3951
1140 | feeder2_line46 | 1 | 99 | 5.662e-07 | 1.3407e-06 | 5.7192e-07 | 1.3542e-06
1140 | feeder2_line46 | 2 | 99 | 5.6542e-07 | 1.3389e-06 | 5.7113e-07 | 1.3524e-06
1140 | feeder2_line46 | 3 | 99 | 2.2782 | 2.2783 | 2.3013 | 2.3013
1140 | feeder2_line47 | 1 | 266.4 | 4.4822 | 4.4816 | 1.6825 | 1.6823
1140 | feeder2_line47 | 2 | 266.4 | 3.8775 | 3.8774 | 1.4555 | 1.4555
1140 | feeder2_line47 | 3 | 266.4 | 1.9085 | 1.9083 | 0.71641 | 0.71634
1140 | feeder2_line48 | 1 | 99 | 3.0847 | 3.0846 | 3.1158 | 3.1158
1140 | feeder2_line48 | 2 | 99 | 4.9187e-08 | 7.2086e-07 | 4.9684e-08 | 7.2814e-07
1140 | feeder2_line48 | 3 | 99 | 4.9374e-08 | 7.1998e-07 | 4.9873e-08 | 7.2725e-07
1140 | feeder2_line49 | 1 | 266.4 | 1.3977 | 1.3972 | 0.52468 | 0.52447
1140 | feeder2_line49 | 2 | 266.4 | 3.8775 | 3.8774 | 1.4555 | 1.4555
1140 | feeder2_line49 | 3 | 266.4 | 1.9085 | 1.9083 | 0.7164 | 0.71634
1140 | feeder2_line50 | 1 | 99 | 5.6619e-07 | 1.2201e-06 | 5.7191e-07 | 1.2324e-06
1140 | feeder2_line50 | 2 | 99 | 0.53118 | 0.53114 | 0.53655 | 0.5365
1140 | feeder2_line50 | 3 | 99 | 5.6471e-07 | 1.217e-06 | 5.7042e-07 | 1.2292e-06
1140 | feeder2_line51 | 1 | 99 | 1.2827 | 1.2824 | 1.2956 | 1.2953
1140 | feeder2_line51 | 2 | 99 | 5.6541e-07 | 1.3227e-06 | 5.7112e-07 | 1.3361e-06
1140 | feeder2_line51 | 3 | 99 | 5.6471e-07 | 1.3211e-06 | 5.7042e-07 | 1.3345e-06
1140 | feeder2_line52 | 1 | 266.4 | 0.11509 | 0.11497 | 0.043203 | 0.043155
1140 | feeder2_line52 | 2 | 266.4 | 3.4937 | 3.4937 | 1.3114 | 1.3114
1140 | feeder2_line52 | 3 | 266.4 | 1.9084 | 1.9083 | 0.71636 | 0.71634
1140 | feeder2_line53 | 1 | 99 | 5.4172e-07 | 7.4464e-07 | 5.4719e-07 | 7.5216e-07
1140 | feeder2_line53 | 2 | 99 | 3.4937 | 3.4937 | 3.529 | 3.529
1140 | feeder2_line53 | 3 | 99 | 5.4003e-07 | 7.4273e-07 | 5.4548e-07 | 7.5023e-07
1140 | feeder2_line54 | 1 | 266.4 | 0.11491 | 0.11497 | 0.043135 | 0.043155
1140 | feeder2_line54 | 2 | 266.4 | 8.4328e-05 | 4.5618e-06 | 3.1655e-05 | 1.7124e-06
1140 | feeder2_line54 | 3 | 266.4 | 1.9083 | 1.9083 | 0.71632 | 0.71634
1140 | feeder2_line55 | 1 | 99 | 9.9745 | 9.9747 | 10.0752 | 10.0755
1140 | feeder2_line55 | 2 | 99 | 4.9088e-08 | 7.1923e-07 | 4.9584e-08 | 7.265e-07
1140 | feeder2_line55 | 3 | 99 | 4.9347e-08 | 7.1807e-07 | 4.9845e-08 | 7.2532e-07
1140 | feeder2_line56 | 1 | 354.6 | 85.6243 | 85.6175 | 24.1467 | 24.1448
1140 | feeder2_line56 | 2 | 354.6 | 87.5793 | 87.5732 | 24.6981 | 24.6963
1140 | feeder2_line56 | 3 | 354.6 | 82.3283 | 82.3413 | 23.2172 | 23.2209
1140 | feeder2_line57 | 1 | 99 | 7.341e-07 | 1.5253e-06 | 7.4151e-07 | 1.5407e-06
1140 | feeder2_line57 | 2 | 99 | 7.378e-07 | 1.5232e-06 | 7.4525e-07 | 1.5386e-06
1140 | feeder2_line57 | 3 | 99 | 1.9084 | 1.9083 | 1.9276 | 1.9276
1140 | feeder2_line58 | 1 | 266.4 | 0.11497 | 0.11497 | 0.043157 | 0.043155
1140 | feeder2_line58 | 2 | 266.4 | 1.8693e-05 | 2.6485e-06 | 7.017e-06 | 9.9419e-07
1140 | feeder2_line58 | 3 | 266.4 | 1.8654e-05 | 2.6455e-06 | 7.0023e-06 | 9.9304e-07
1140 | feeder2_line59 | 1 | 99 | 4.8944e-08 | 5.302e-07 | 4.9438e-08 | 5.3555e-07
1140 | feeder2_line59 | 2 | 99 | 4.9185e-08 | 5.2948e-07 | 4.9682e-08 | 5.3483e-07
1140 | feeder2_line59 | 3 | 99 | 0.08236 | 0.082364 | 0.083192 | 0.083196
1140 | feeder2_line60 | 1 | 99 | 2.9533e-07 | 8.013e-07 | 2.9831e-07 | 8.0939e-07
1140 | feeder2_line60 | 2 | 99 | 2.95e-07 | 8.002e-07 | 2.9798e-07 | 8.0828e-07
1140 | feeder2_line60 | 3 | 99 | 1.8367 | 1.8366 | 1.8552 | 1.8552
1140 | feeder2_line61 | 1 | 266.4 | 3.1145 | 3.1147 | 1.1691 | 1.1692
1140 | feeder2_line61 | 2 | 266.4 | 5.7198 | 5.72 | 2.1471 | 2.1471
1140 | feeder2_line61 | 3 | 266.4 | 0.19852 | 0.19875 | 0.07452 | 0.074607
1140 | feeder2_line62 | 1 | 354.6 | 85.5458 | 85.5387 | 24.1246 | 24.1226
1140 | feeder2_line62 | 2 | 354.6 | 88.1168 | 88.1108 | 24.8496 | 24.8479
1140 | feeder2_line62 | 3 | 354.6 | 82.3719 | 82.385 | 23.2295 | 23.2332
1140 | feeder2_line63 | 1 | 99 | 0.090034 | 0.09002 | 0.090944 | 0.09093
1140 | feeder2_line63 | 2 | 99 | 5.6541e-07 | 1.2031e-06 | 5.7112e-07 | 1.2152e-06
1140 | feeder2_line63 | 3 | 99 | 5.6471e-07 | 1.2016e-06 | 5.7041e-07 | 1.2137e-06
1140 | feeder2_line64 | 1 | 99 | 0.024955 | 0.024946 | 0.025208 | 0.025198
1140 | feeder2_line64 | 2 | 99 | 7.6917e-12 | 3.1691e-07 | 7.7694e-12 | 3.2011e-07
1140 | feeder2_line64 | 3 | 99 | 3.1144e-12 | 3.1653e-07 | 3.1459e-12 | 3.1973e-07
1140 | feeder2_line65 | 1 | 99 | 4.8822e-08 | 6.3199e-07 | 4.9315e-08 | 6.3837e-07
1140 | feeder2_line65 | 2 | 99 | 10.3033 | 10.3032 | 10.4074 | 10.4073
1140 | feeder2_line65 | 3 | 99 | 4.935e-08 | 6.3012e-07 | 4.9848e-08 | 6.3648e-07
1140 | feeder2_line66 | 1 | 354.6 | 85.5458 | 85.5387 | 24.1246 | 24.1226
1140 | feeder2_line66 | 2 | 354.6 | 91.4721 | 91.4664 | 25.7959 | 25.7942
1140 | feeder2_line66 | 3 | 354.6 | 82.3719 | 82.385 | 23.2295 | 23.2332
1140 | feeder2_line67 | 1 | 99 | 2.4432e-08 | 3.5736e-07 | 2.4679e-08 | 3.6096e-07
1140 | feeder2_line67 | 2 | 99 | 2.454e-08 | 3.57e-07 | 2.4788e-08 | 3.6061e-07
1140 | feeder2_line67 | 3 | 99 | 0.095204 | 0.095211 | 0.096166 | 0.096172
1140 | feeder2_line68 | 1 | 266.4 | 3.1145 | 3.1147 | 1.1691 | 1.1692
1140 | feeder2_line68 | 2 | 266.4 | 5.7199 | 5.72 | 2.1471 | 2.1471
1140 | feeder2_line68 | 3 | 266.4 | 0.10336 | 0.10355 | 0.038798 | 0.038869
1140 | feeder2_line69 | 1 | 99 | 4.2802 | 4.2802 | 4.3235 | 4.3235
1140 | feeder2_line69 | 2 | 99 | 2.5044e-06 | 6.5538e-07 | 2.5297e-06 | 6.62e-07
1140 | feeder2_line69 | 3 | 99 | 2.4965e-06 | 6.5402e-07 | 2.5217e-06 | 6.6063e-07
1140 | feeder2_line70 | 1 | 354.6 | 87.0172 | 87.0098 | 24.5395 | 24.5374
1140 | feeder2_line70 | 2 | 354.6 | 91.4722 | 91.4664 | 25.7959 | 25.7942
1140 | feeder2_line70 | 3 | 354.6 | 82.372 | 82.385 | 23.2296 | 23.2332
1140 | feeder2_line71 | 1 | 99 | 4.8807e-08 | 7.0494e-07 | 4.93e-08 | 7.1206e-07
1140 | feeder2_line71 | 2 | 99 | 2.0836 | 2.0836 | 2.1047 | 2.1046
1140 | feeder2_line71 | 3 | 99 | 4.9371e-08 | 7.0271e-07 | 4.9869e-08 | 7.098e-07
1140 | feeder2_line72 | 1 | 354.6 | 87.0173 | 87.0098 | 24.5396 | 24.5374
1140 | feeder2_line72 | 2 | 354.6 | 92.2912 | 92.2853 | 26.0268 | 26.0252
1140 | feeder2_line72 | 3 | 354.6 | 82.372 | 82.385 | 23.2296 | 23.2332
1140 | feeder2_line73 | 1 | 99 | 5.8977e-07 | 1.5129e-06 | 5.9572e-07 | 1.5281e-06
1140 | feeder2_line73 | 2 | 99 | 2.9448 | 2.9448 | 2.9746 | 2.9746
1140 | feeder2_line73 | 3 | 99 | 5.8849e-07 | 1.5089e-06 | 5.9444e-07 | 1.5241e-06
1140 | feeder2_line74 | 1 | 99 | 4.8863e-08 | 4.5122e-07 | 4.9357e-08 | 4.5577e-07
1140 | feeder2_line74 | 2 | 99 | 0.10325 | 0.10323 | 0.1043 | 0.10427
1140 | feeder2_line74 | 3 | 99 | 4.9344e-08 | 4.5003e-07 | 4.9843e-08 | 4.5457e-07
1140 | feeder2_line75 | 1 | 266.4 | 3.1146 | 3.1147 | 1.1692 | 1.1692
1140 | feeder2_line75 | 2 | 266.4 | 2.7434 | 2.7434 | 1.0298 | 1.0298
1140 | feeder2_line75 | 3 | 266.4 | 0.10345 | 0.10355 | 0.038834 | 0.038869
1140 | feeder2_line76 | 1 | 99 | 3.1147 | 3.1147 | 3.1461 | 3.1461
1140 | feeder2_line76 | 2 | 99 | 8.3484e-07 | 1.559e-06 | 8.4327e-07 | 1.5747e-06
1140 | feeder2_line76 | 3 | 99 | 8.334e-07 | 1.5565e-06 | 8.4181e-07 | 1.5722e-06
1140 | feeder2_line77 | 1 | 99 | 2.4433e-08 | 5.6703e-07 | 2.468e-08 | 5.7275e-07
1140 | feeder2_line77 | 2 | 99 | 2.4545e-08 | 5.6644e-07 | 2.4793e-08 | 5.7216e-07
1140 | feeder2_line77 | 3 | 99 | 0.10348 | 0.10355 | 0.10453 | 0.10459
1140 | feeder2_line78 | 1 | 266.4 | 6.2889e-12 | 9.402e-07 | 2.3607e-12 | 3.5293e-07
1140 | feeder2_line78 | 2 | 266.4 | 2.7434 | 2.7434 | 1.0298 | 1.0298
1140 | feeder2_line78 | 3 | 266.4 | 1.9761e-11 | 9.3813e-07 | 7.4178e-12 | 3.5215e-07
1140 | feeder2_line79 | 1 | 354.6 | 5.7944 | 5.794 | 1.6341 | 1.634
1140 | feeder2_line79 | 2 | 354.6 | 7.0415 | 7.0412 | 1.9858 | 1.9857
1140 | feeder2_line79 | 3 | 354.6 | 30.3249 | 30.3242 | 8.5519 | 8.5517
1140 | feeder2_line80 | 1 | 354.6 | 87.0486 | 87.0402 | 24.5484 | 24.546
1140 | feeder2_line80 | 2 | 354.6 | 91.8999 | 91.8939 | 25.9165 | 25.9148
1140 | feeder2_line80 | 3 | 354.6 | 90.426 | 90.4405 | 25.5009 | 25.5049
1140 | feeder2_line81 | 1 | 354.6 | 87.0484 | 87.0402 | 24.5483 | 24.546
1140 | feeder2_line81 | 2 | 354.6 | 91.8998 | 91.8939 | 25.9165 | 25.9148
1140 | feeder2_line81 | 3 | 354.6 | 90.5956 | 90.6103 | 25.5487 | 25.5528
1140 | feeder2_line82 | 1 | 354.6 | 2.1753e-11 | 7.226e-07 | 6.1346e-12 | 2.0378e-07
1140 | feeder2_line82 | 2 | 354.6 | 2.7296e-11 | 7.2207e-07 | 7.6976e-12 | 2.0363e-07
1140 | feeder2_line82 | 3 | 354.6 | 0.31128 | 0.31129 | 0.087784 | 0.087787
1140 | feeder2_line83 | 1 | 354.6 | 87.0485 | 87.0402 | 24.5484 | 24.546
1140 | feeder2_line83 | 2 | 354.6 | 91.7131 | 91.7071 | 25.8638 | 25.8621
1140 | feeder2_line83 | 3 | 354.6 | 90.5958 | 90.6103 | 25.5487 | 25.5528
1140 | feeder2_line84 | 1 | 354.6 | 1.2875e-11 | 1.2769e-06 | 3.6308e-12 | 3.6009e-07
1140 | feeder2_line84 | 2 | 354.6 | 1.2942 | 1.2942 | 0.36497 | 0.36497
1140 | feeder2_line84 | 3 | 354.6 | 6.8621e-12 | 1.273e-06 | 1.9352e-12 | 3.5899e-07
1140 | feeder2_line85 | 1 | 99 | 12.6893 | 12.6898 | 12.8175 | 12.818
1140 | feeder2_line85 | 2 | 99 | 4.9008e-08 | 4.5541e-07 | 4.9503e-08 | 4.6001e-07
1140 | feeder2_line85 | 3 | 99 | 4.9383e-08 | 4.5421e-07 | 4.9882e-08 | 4.588e-07
1140 | feeder2_line86 | 1 | 354.6 | 92.1192 | 92.1099 | 25.9783 | 25.9757
1140 | feeder2_line86 | 2 | 354.6 | 91.7131 | 91.7071 | 25.8638 | 25.8621
1140 | feeder2_line86 | 3 | 354.6 | 90.5958 | 90.6103 | 25.5487 | 25.5528
1140 | feeder2_line87 | 1 | 354.6 | 92.1193 | 92.1099 | 25.9784 | 25.9757
1140 | feeder2_line87 | 2 | 354.6 | 92.2647 | 92.2585 | 26.0194 | 26.0176
1140 | feeder2_line87 | 3 | 354.6 | 90.3824 | 90.397 | 25.4886 | 25.4927
1140 | feeder2_line88 | 1 | 354.6 | 0.00011335 | 3.3097e-06 | 3.1967e-05 | 9.3335e-07
1140 | feeder2_line88 | 2 | 354.6 | 3.2917 | 3.2915 | 0.92827 | 0.92823
1140 | feeder2_line88 | 3 | 354.6 | 1.201 | 1.201 | 0.33869 | 0.33869
1140 | feeder2_line89 | 1 | 354.6 | 92.1178 | 92.1099 | 25.978 | 25.9757
1140 | feeder2_line89 | 2 | 354.6 | 92.1912 | 92.1863 | 25.9986 | 25.9973
1140 | feeder2_line89 | 3 | 354.6 | 90.3811 | 90.397 | 25.4882 | 25.4927
1140 | feeder2_line90 | 1 | 354.6 | 0.00071332 | 1.9982e-06 | 0.00020116 | 5.635e-07
1140 | feeder2_line90 | 2 | 354.6 | 1.3569 | 1.357 | 0.38265 | 0.38269
1140 | feeder2_line90 | 3 | 354.6 | 0.00070834 | 1.9904e-06 | 0.00019976 | 5.6131e-07
1140 | feeder2_line91 | 1 | 354.6 | 92.1179 | 92.1099 | 25.978 | 25.9757
1140 | feeder2_line91 | 2 | 354.6 | 92.1913 | 92.1863 | 25.9987 | 25.9973
1140 | feeder2_line91 | 3 | 354.6 | 90.5168 | 90.5328 | 25.5265 | 25.531
1140 | feeder2_line92 | 1 | 354.6 | 2.4173e-11 | 1.0073e-06 | 6.8171e-12 | 2.8406e-07
1140 | feeder2_line92 | 2 | 354.6 | 2.1536e-11 | 1.0065e-06 | 6.0733e-12 | 2.8385e-07
1140 | feeder2_line92 | 3 | 354.6 | 1.836 | 1.8359 | 0.51776 | 0.51775
1140 | feeder2_line93 | 1 | 99 | 2.4382e-08 | 3.363e-07 | 2.4629e-08 | 3.397e-07
1140 | feeder2_line93 | 2 | 99 | 1.2942 | 1.2942 | 1.3072 | 1.3072
1140 | feeder2_line93 | 3 | 99 | 2.4696e-08 | 3.351e-07 | 2.4946e-08 | 3.3848e-07
1140 | feeder2_line94 | 1 | 354.6 | 2.4382e-06 | 1.637e-06 | 6.876e-07 | 4.6166e-07
1140 | feeder2_line94 | 2 | 354.6 | 0.082906 | 0.082865 | 0.02338 | 0.023369
1140 | feeder2_line94 | 3 | 354.6 | 2.4696e-06 | 1.6319e-06 | 6.9646e-07 | 4.6019e-07
1140 | feeder2_line95 | 1 | 99 | 3.5097e-06 | 2.5664e-06 | 3.5452e-06 | 2.5923e-06
1140 | feeder2_line95 | 2 | 99 | 3.2916 | 3.2915 | 3.3248 | 3.3248
1140 | feeder2_line95 | 3 | 99 | 3.4931e-06 | 2.5574e-06 | 3.5284e-06 | 2.5832e-06
1140 | feeder2_line96 | 1 | 354.6 | 0.00011916 | 6.1182e-07 | 3.3603e-05 | 1.7254e-07
1140 | feeder2_line96 | 2 | 354.6 | 0.00011899 | 6.1168e-07 | 3.3557e-05 | 1.725e-07
1140 | feeder2_line96 | 3 | 354.6 | 1.2009 | 1.201 | 0.33868 | 0.33869
1140 | feeder2_line97 | 1 | 354.6 | 93.6204 | 93.6119 | 26.4017 | 26.3993
1140 | feeder2_line97 | 2 | 354.6 | 92.1916 | 92.1863 | 25.9988 | 25.9973
1140 | feeder2_line97 | 3 | 354.6 | 90.5171 | 90.5328 | 25.5265 | 25.531
1140 | feeder2_line98 | 1 | 354.6 | 2.8526 | 2.8509 | 0.80446 | 0.80398
1140 | feeder2_line98 | 2 | 354.6 | 0.0016675 | 6.112e-07 | 0.00047024 | 1.7236e-07
1140 | feeder2_line98 | 3 | 354.6 | 0.0016641 | 6.1192e-07 | 0.00046929 | 1.7257e-07
1140 | feeder2_line99 | 1 | 99 | 2.4384e-08 | 4.3981e-07 | 2.463e-08 | 4.4425e-07
1140 | feeder2_line99 | 2 | 99 | 2.4508e-08 | 4.3942e-07 | 2.4755e-08 | 4.4386e-07
1140 | feeder2_line99 | 3 | 99 | 1.2009 | 1.201 | 1.2131 | 1.2131
1140 | feeder2_line100 | 1 | 99 | 2.851 | 2.8509 | 2.8798 | 2.8797
1140 | feeder2_line100 | 2 | 99 | 2.4506e-08 | 6.0309e-07 | 2.4754e-08 | 6.0919e-07
1140 | feeder2_line100 | 3 | 99 | 2.4696e-08 | 6.0145e-07 | 2.4946e-08 | 6.0752e-07
1140 | feeder2_line101 | 1 | 354.6 | 0.083123 | 0.082684 | 0.023441 | 0.023318
1140 | feeder2_line101 | 2 | 354.6 | 7.0415 | 7.0412 | 1.9858 | 1.9857
1140 | feeder2_line101 | 3 | 354.6 | 30.3249 | 30.3242 | 8.5519 | 8.5517
1140 | feeder2_line102 | 1 | 99 | 5.7208 | 5.7207 | 5.7786 | 5.7785
1140 | feeder2_line102 | 2 | 99 | 2.2939e-06 | 8.6343e-07 | 2.317e-06 | 8.7215e-07
1140 | feeder2_line102 | 3 | 99 | 2.2851e-06 | 8.6079e-07 | 2.3082e-06 | 8.6949e-07
1140 | feeder2_line103 | 1 | 99 | 5.4079e-07 | 7.9107e-07 | 5.4626e-07 | 7.9906e-07
1140 | feeder2_line103 | 2 | 99 | 2.3173 | 2.3173 | 2.3407 | 2.3407
1140 | feeder2_line103 | 3 | 99 | 5.3804e-07 | 7.8776e-07 | 5.4347e-07 | 7.9572e-07
1140 | feeder2_line104 | 1 | 354.6 | 0.083019 | 0.082684 | 0.023412 | 0.023318
1140 | feeder2_line104 | 2 | 354.6 | 4.7348 | 4.7346 | 1.3353 | 1.3352
1140 | feeder2_line104 | 3 | 354.6 | 30.3248 | 30.3242 | 8.5518 | 8.5517
1140 | feeder2_line105 | 1 | 99 | 2.5092e-06 | 7.2791e-07 | 2.5346e-06 | 7.3526e-07
1140 | feeder2_line105 | 2 | 99 | 2.5045e-06 | 7.2719e-07 | 2.5298e-06 | 7.3454e-07
1140 | feeder2_line105 | 3 | 99 | 11.0761 | 11.0759 | 11.188 | 11.1878
1140 | feeder2_line106 | 1 | 354.6 | 0.082964 | 0.082684 | 0.023396 | 0.023318
1140 | feeder2_line106 | 2 | 354.6 | 4.7348 | 4.7346 | 1.3353 | 1.3352
1140 | feeder2_line106 | 3 | 354.6 | 19.2675 | 19.2671 | 5.4336 | 5.4335
1140 | feeder2_line107 | 1 | 99 | 3.1912e-07 | 8.8711e-07 | 3.2235e-07 | 8.9607e-07
1140 | feeder2_line107 | 2 | 99 | 2.4019 | 2.4019 | 2.4261 | 2.4261
1140 | feeder2_line107 | 3 | 99 | 3.1838e-07 | 8.8305e-07 | 3.216e-07 | 8.9197e-07
1140 | feeder2_line108 | 1 | 354.6 | 0.082953 | 0.082684 | 0.023393 | 0.023318
1140 | feeder2_line108 | 2 | 354.6 | 2.4157 | 2.4156 | 0.68125 | 0.68121
1140 | feeder2_line108 | 3 | 354.6 | 19.2675 | 19.2671 | 5.4336 | 5.4335
1140 | feeder2_line109 | 1 | 354.6 | 94.2449 | 94.2357 | 26.5778 | 26.5752
1140 | feeder2_line109 | 2 | 354.6 | 92.1921 | 92.1864 | 25.9989 | 25.9973
1140 | feeder2_line109 | 3 | 354.6 | 90.5176 | 90.5328 | 25.5267 | 25.531
1140 | feeder2_line110 | 1 | 99 | 1.0193 | 1.0185 | 1.0296 | 1.0288
1140 | feeder2_line110 | 2 | 99 | 0.00078997 | 8.9205e-07 | 0.00079795 | 9.0106e-07
1140 | feeder2_line110 | 3 | 99 | 0.00078636 | 8.9002e-07 | 0.0007943 | 8.9901e-07
1140 | feeder2_line111 | 1 | 99 | 2.4376e-08 | 3.7563e-07 | 2.4622e-08 | 3.7942e-07
1140 | feeder2_line111 | 2 | 99 | 2.4017 | 2.4017 | 2.426 | 2.426
1140 | feeder2_line111 | 3 | 99 | 2.4693e-08 | 3.7431e-07 | 2.4942e-08 | 3.7809e-07
1140 | feeder2_line112 | 1 | 99 | 3.1907e-07 | 9.0265e-07 | 3.223e-07 | 9.1177e-07
1140 | feeder2_line112 | 2 | 99 | 0.97268 | 0.97258 | 0.98251 | 0.98241
1140 | feeder2_line112 | 3 | 99 | 3.1853e-07 | 8.9949e-07 | 3.2175e-07 | 9.0857e-07
1140 | feeder2_line113 | 1 | 99 | 0.93642 | 0.93642 | 0.94587 | 0.94588
1140 | feeder2_line113 | 2 | 99 | 3.1898e-07 | 8.8914e-07 | 3.222e-07 | 8.9812e-07
1140 | feeder2_line113 | 3 | 99 | 3.1848e-07 | 8.8668e-07 | 3.217e-07 | 8.9564e-07
1140 | feeder2_line114 | 1 | 99 | 2.3164 | 2.3164 | 2.3398 | 2.3398
1140 | feeder2_line114 | 2 | 99 | 2.4507e-08 | 4.2935e-07 | 2.4755e-08 | 4.3368e-07
1140 | feeder2_line114 | 3 | 99 | 2.4708e-08 | 4.2804e-07 | 2.4958e-08 | 4.3236e-07
1140 | feeder2_line115 | 1 | 99 | 2.4336e-08 | 5.5364e-07 | 2.4582e-08 | 5.5923e-07
1140 | feeder2_line115 | 2 | 99 | 1.6275 | 1.6275 | 1.6439 | 1.644
1140 | feeder2_line115 | 3 | 99 | 2.474e-08 | 5.5094e-07 | 2.499e-08 | 5.565e-07
1140 | feeder2_line116 | 1 | 354.6 | 0.082959 | 0.082684 | 0.023395 | 0.023317
1140 | feeder2_line116 | 2 | 354.6 | 0.79163 | 0.79148 | 0.22325 | 0.2232
1140 | feeder2_line116 | 3 | 354.6 | 19.2675 | 19.2671 | 5.4336 | 5.4335
1140 | feeder2_line117 | 1 | 99 | 4.8743e-08 | 6.3171e-07 | 4.9235e-08 | 6.3809e-07
1140 | feeder2_line117 | 2 | 99 | 2.2785 | 2.2785 | 2.3015 | 2.3015
1140 | feeder2_line117 | 3 | 99 | 4.9397e-08 | 6.2931e-07 | 4.9896e-08 | 6.3567e-07
1140 | feeder2_line118 | 1 | 354.6 | 94.2449 | 94.2357 | 26.5778 | 26.5752
1140 | feeder2_line118 | 2 | 354.6 | 93.0609 | 93.0552 | 26.2439 | 26.2423
1140 | feeder2_line118 | 3 | 354.6 | 90.5176 | 90.5328 | 25.5267 | 25.531
1140 | feeder2_line119 | 1 | 99 | 2.433e-08 | 5.9576e-07 | 2.4576e-08 | 6.0178e-07
1140 | feeder2_line119 | 2 | 99 | 2.4492e-08 | 5.9514e-07 | 2.474e-08 | 6.0115e-07
1140 | feeder2_line119 | 3 | 99 | 2.069 | 2.069 | 2.0899 | 2.0899
1140 | feeder2_line120 | 1 | 354.6 | 0.082961 | 0.082684 | 0.023396 | 0.023317
1140 | feeder2_line120 | 2 | 354.6 | 0.79163 | 0.79149 | 0.22325 | 0.22321
1140 | feeder2_line120 | 3 | 354.6 | 17.2145 | 17.2141 | 4.8546 | 4.8545
1140 | feeder2_line121 | 1 | 99 | 3.1913e-07 | 9.226e-07 | 3.2235e-07 | 9.3192e-07
1140 | feeder2_line121 | 2 | 99 | 0.73792 | 0.73791 | 0.74537 | 0.74537
1140 | feeder2_line121 | 3 | 99 | 3.1822e-07 | 9.1756e-07 | 3.2143e-07 | 9.2683e-07
1140 | feeder2_line122 | 1 | 354.6 | 0.082949 | 0.082683 | 0.023392 | 0.023317
1140 | feeder2_line122 | 2 | 354.6 | 0.090673 | 0.090438 | 0.025571 | 0.025504
1140 | feeder2_line122 | 3 | 354.6 | 17.2145 | 17.2141 | 4.8546 | 4.8545
1140 | feeder2_line123 | 1 | 99 | 5.6531e-07 | 9.5605e-07 | 5.7102e-07 | 9.6571e-07
1140 | feeder2_line123 | 2 | 99 | 5.6471e-07 | 9.5507e-07 | 5.7041e-07 | 9.6472e-07
1140 | feeder2_line123 | 3 | 99 | 0.75242 | 0.75243 | 0.76002 | 0.76003
1140 | feeder2_line124 | 1 | 354.6 | 0.082853 | 0.082683 | 0.023365 | 0.023317
1140 | feeder2_line124 | 2 | 354.6 | 0.090578 | 0.090438 | 0.025544 | 0.025504
1140 | feeder2_line124 | 3 | 354.6 | 16.679 | 16.6787 | 4.7036 | 4.7035
1140 | feeder2_line125 | 1 | 99 | 5.6531e-07 | 8.8875e-07 | 5.7102e-07 | 8.9773e-07
1140 | feeder2_line125 | 2 | 99 | 5.6472e-07 | 8.8785e-07 | 5.7042e-07 | 8.9682e-07
1140 | feeder2_line125 | 3 | 99 | 2.8602 | 2.8603 | 2.8891 | 2.8892
1140 | feeder2_line126 | 1 | 354.6 | 0.083007 | 0.082683 | 0.023409 | 0.023317
1140 | feeder2_line126 | 2 | 354.6 | 0.090732 | 0.090438 | 0.025587 | 0.025504
1140 | feeder2_line126 | 3 | 354.6 | 13.8224 | 13.8218 | 3.898 | 3.8978
1140 | feeder2_line127 | 1 | 99 | 5.6532e-07 | 1.064e-06 | 5.7103e-07 | 1.0748e-06
1140 | feeder2_line127 | 2 | 99 | 5.6474e-07 | 1.0629e-06 | 5.7044e-07 | 1.0737e-06
1140 | feeder2_line127 | 3 | 99 | 1.1857 | 1.1857 | 1.1977 | 1.1977
1140 | feeder2_line128 | 1 | 354.6 | 0.082922 | 0.082683 | 0.023385 | 0.023317
1140 | feeder2_line128 | 2 | 354.6 | 0.090648 | 0.090438 | 0.025563 | 0.025504
1140 | feeder2_line128 | 3 | 354.6 | 12.6468 | 12.6462 | 3.5665 | 3.5663
1140 | feeder2_line129 | 1 | 99 | 5.4102e-07 | 8.6276e-07 | 5.4648e-07 | 8.7148e-07
1140 | feeder2_line129 | 2 | 99 | 0.090436 | 0.090437 | 0.09135 | 0.091351
1140 | feeder2_line129 | 3 | 99 | 5.3719e-07 | 8.5771e-07 | 5.4261e-07 | 8.6637e-07
1140 | feeder2_line130 | 1 | 354.6 | 0.082935 | 0.082683 | 0.023388 | 0.023317
1140 | feeder2_line130 | 2 | 354.6 | 0.00030387 | 4.5611e-06 | 8.5692e-05 | 1.2863e-06
1140 | feeder2_line130 | 3 | 354.6 | 12.6468 | 12.6462 | 3.5665 | 3.5663
1140 | feeder2_line131 | 1 | 99 | 5.6534e-07 | 9.5625e-07 | 5.7105e-07 | 9.6591e-07
1140 | feeder2_line131 | 2 | 99 | 5.6476e-07 | 9.553e-07 | 5.7046e-07 | 9.6495e-07
1140 | feeder2_line131 | 3 | 99 | 0.050168 | 0.050176 | 0.050675 | 0.050683
1140 | feeder2_line132 | 1 | 354.6 | 0.082779 | 0.082683 | 0.023344 | 0.023317
1140 | feeder2_line132 | 2 | 354.6 | 0.00012365 | 2.8677e-06 | 3.4871e-05 | 8.087e-07
1140 | feeder2_line132 | 3 | 354.6 | 12.5967 | 12.5962 | 3.5524 | 3.5522
1140 | feeder2_line133 | 1 | 99 | 0.082711 | 0.082682 | 0.083546 | 0.083518
1140 | feeder2_line133 | 2 | 99 | 2.9462e-07 | 9.6293e-07 | 2.9759e-07 | 9.7266e-07
1140 | feeder2_line133 | 3 | 99 | 2.9334e-07 | 9.5812e-07 | 2.963e-07 | 9.6779e-07
1140 | feeder2_line134 | 1 | 354.6 | 4.4995e-12 | 1.7573e-06 | 1.2689e-12 | 4.9558e-07
1140 | feeder2_line134 | 2 | 354.6 | 6.0301e-12 | 1.7559e-06 | 1.7005e-12 | 4.9519e-07
1140 | feeder2_line134 | 3 | 354.6 | 12.5966 | 12.5962 | 3.5523 | 3.5522
1140 | feeder2_line135 | 1 | 99 | 2.0823 | 2.0822 | 2.1033 | 2.1032
1140 | feeder2_line135 | 2 | 99 | 4.9002e-08 | 5.7496e-07 | 4.9497e-08 | 5.8076e-07
1140 | feeder2_line135 | 3 | 99 | 4.9402e-08 | 5.7329e-07 | 4.9901e-08 | 5.7908e-07
1140 | feeder2_line136 | 1 | 354.6 | 95.4348 | 95.4256 | 26.9134 | 26.9108
1140 | feeder2_line136 | 2 | 354.6 | 93.0609 | 93.0552 | 26.2439 | 26.2423
1140 | feeder2_line136 | 3 | 354.6 | 90.5176 | 90.5328 | 25.5267 | 25.531
1140 | feeder2_line137 | 1 | 99 | 1.3767 | 1.3766 | 1.3906 | 1.3905
1140 | feeder2_line137 | 2 | 99 | 8.3435e-07 | 1.5485e-06 | 8.4278e-07 | 1.5641e-06
1140 | feeder2_line137 | 3 | 99 | 8.3174e-07 | 1.544e-06 | 8.4014e-07 | 1.5595e-06
1140 | feeder2_line138 | 1 | 354.6 | 95.6884 | 95.679 | 26.9849 | 26.9822
1140 | feeder2_line138 | 2 | 354.6 | 93.061 | 93.0552 | 26.2439 | 26.2423
1140 | feeder2_line138 | 3 | 354.6 | 90.5177 | 90.5328 | 25.5267 | 25.531
1140 | feeder2_line139 | 1 | 99 | 4.8728e-08 | 4.8295e-07 | 4.9221e-08 | 4.8783e-07
1140 | feeder2_line139 | 2 | 99 | 4.9004e-08 | 4.8246e-07 | 4.9499e-08 | 4.8733e-07
1140 | feeder2_line139 | 3 | 99 | 1.3046 | 1.3044 | 1.3178 | 1.3176
1140 | feeder2_line140 | 1 | 354.6 | 95.6884 | 95.679 | 26.9849 | 26.9822
1140 | feeder2_line140 | 2 | 354.6 | 93.0609 | 93.0552 | 26.2439 | 26.2423
1140 | feeder2_line140 | 3 | 354.6 | 90.0282 | 90.0445 | 25.3887 | 25.3933
1140 | feeder2_line141 | 1 | 99 | 2.484e-06 | 4.7771e-07 | 2.5091e-06 | 4.8254e-07
1140 | feeder2_line141 | 2 | 99 | 1.0297 | 1.0297 | 1.0401 | 1.0401
1140 | feeder2_line141 | 3 | 99 | 2.4676e-06 | 4.7578e-07 | 2.4925e-06 | 4.8059e-07
1140 | feeder2_line142 | 1 | 354.6 | 95.6884 | 95.679 | 26.9849 | 26.9822
1140 | feeder2_line142 | 2 | 354.6 | 93.6657 | 93.66 | 26.4145 | 26.4129
1140 | feeder2_line142 | 3 | 354.6 | 90.0282 | 90.0445 | 25.3887 | 25.3933
1140 | feeder2_line143 | 1 | 99 | 8.3534e-07 | 1.6975e-06 | 8.4378e-07 | 1.7146e-06
1140 | feeder2_line143 | 2 | 99 | 2.4023 | 2.4023 | 2.4266 | 2.4266
1140 | feeder2_line143 | 3 | 99 | 8.3167e-07 | 1.6906e-06 | 8.4007e-07 | 1.7077e-06
1140 | feeder2_line144 | 1 | 354.6 | 95.6882 | 95.679 | 26.9848 | 26.9822
1140 | feeder2_line144 | 2 | 354.6 | 94.2441 | 94.2386 | 26.5776 | 26.576
1140 | feeder2_line144 | 3 | 354.6 | 90.028 | 90.0445 | 25.3886 | 25.3933
1140 | feeder2_line145 | 1 | 99 | 2.4365e-08 | 4.7596e-07 | 2.4612e-08 | 4.8077e-07
1140 | feeder2_line145 | 2 | 99 | 0.31146 | 0.31146 | 0.31461 | 0.31461
1140 | feeder2_line145 | 3 | 99 | 2.4705e-08 | 4.7402e-07 | 2.4955e-08 | 4.7881e-07
1140 | feeder2_line146 | 1 | 354.6 | 95.6881 | 95.679 | 26.9848 | 26.9822
1140 | feeder2_line146 | 2 | 354.6 | 94.4453 | 94.4398 | 26.6343 | 26.6328
1140 | feeder2_line146 | 3 | 354.6 | 90.028 | 90.0445 | 25.3886 | 25.3933
1140 | feeder2_line147 | 1 | 99 | 0.08212 | 0.082109 | 0.08295 | 0.082938
1140 | feeder2_line147 | 2 | 99 | 1.1288e-06 | 2.1929e-06 | 1.1402e-06 | 2.215e-06
1140 | feeder2_line147 | 3 | 99 | 1.1253e-06 | 2.1863e-06 | 1.1367e-06 | 2.2084e-06
1140 | feeder2_line148 | 1 | 99 | 0.45188 | 0.45184 | 0.45644 | 0.45641
1140 | feeder2_line148 | 2 | 99 | 5.8889e-07 | 1.4694e-06 | 5.9484e-07 | 1.4842e-06
1140 | feeder2_line148 | 3 | 99 | 5.8737e-07 | 1.465e-06 | 5.933e-07 | 1.4798e-06
1140 | feeder2_line149 | 1 | 354.6 | 96.0122 | 96.0028 | 27.0762 | 27.0736
1140 | feeder2_line149 | 2 | 354.6 | 94.4454 | 94.4398 | 26.6344 | 26.6328
1140 | feeder2_line149 | 3 | 354.6 | 90.0281 | 90.0445 | 25.3886 | 25.3933
1140 | feeder2_line150 | 1 | 354.6 | 96.0122 | 96.0028 | 27.0762 | 27.0736
1140 | feeder2_line150 | 2 | 354.6 | 96.5856 | 96.5803 | 27.2379 | 27.2364
1140 | feeder2_line150 | 3 | 354.6 | 90.0282 | 90.0445 | 25.3887 | 25.3933
1140 | feeder2_line151 | 1 | 99 | 9.6004e-06 | 1.7468e-06 | 9.6974e-06 | 1.7644e-06
1140 | feeder2_line151 | 2 | 99 | 4.9442 | 4.9442 | 4.9941 | 4.9941
1140 | feeder2_line151 | 3 | 99 | 9.5262e-06 | 1.7394e-06 | 9.6225e-06 | 1.7569e-06
1140 | feeder2_line152 | 1 | 354.6 | 1.6902e-11 | 1.1636e-06 | 4.7666e-12 | 3.2816e-07
1140 | feeder2_line152 | 2 | 354.6 | 1.469e-11 | 1.1626e-06 | 4.1427e-12 | 3.2785e-07
1140 | feeder2_line152 | 3 | 354.6 | 1.9471 | 1.9471 | 0.54908 | 0.54909
1140 | feeder2_line153 | 1 | 99 | 0.73825 | 0.73826 | 0.74571 | 0.74572
1140 | feeder2_line153 | 2 | 99 | 4.9003e-08 | 5.8167e-07 | 4.9498e-08 | 5.8755e-07
1140 | feeder2_line153 | 3 | 99 | 4.9428e-08 | 5.7978e-07 | 4.9928e-08 | 5.8563e-07
1140 | feeder2_line154 | 1 | 99 | 5.6504e-07 | 8.6649e-07 | 5.7075e-07 | 8.7525e-07
1140 | feeder2_line154 | 2 | 99 | 5.6441e-07 | 8.6554e-07 | 5.7011e-07 | 8.7428e-07
1140 | feeder2_line154 | 3 | 99 | 11.4141 | 11.4138 | 11.5294 | 11.5291
1140 | feeder2_line155 | 1 | 99 | 95.8185 | 95.809 | 96.7863 | 96.7768
1140 | feeder2_line155 | 2 | 99 | 96.5856 | 96.5803 | 97.5612 | 97.5558
1140 | feeder2_line155 | 3 | 99 | 97.078 | 97.0943 | 98.0586 | 98.0751
1140 | feeder2_line156 | 1 | 99 | 5.8939e-07 | 1.1406e-06 | 5.9535e-07 | 1.1521e-06
1140 | feeder2_line156 | 2 | 99 | 2.3175 | 2.3175 | 2.3409 | 2.3409
1140 | feeder2_line156 | 3 | 99 | 5.8731e-07 | 1.1358e-06 | 5.9325e-07 | 1.1473e-06
1140 | feeder2_line157 | 1 | 99 | 2.4359e-08 | 2.4762e-07 | 2.4605e-08 | 2.5013e-07
1140 | feeder2_line157 | 2 | 99 | 2.7428 | 2.7428 | 2.7705 | 2.7705
1140 | feeder2_line157 | 3 | 99 | 2.4709e-08 | 2.4657e-07 | 2.4959e-08 | 2.4906e-07
1170 | feeder2_line1 | 1 | 354.6 | 110.2553 | 110.26 | 31.0929 | 31.0942
1170 | feeder2_line1 | 2 | 354.6 | 95.2524 | 95.248 | 26.8619 | 26.8607
1170 | feeder2_line1 | 3 | 354.6 | 113.86 | 113.8607 | 32.1094 | 32.1096
1170 | feeder2_line2 | 1 | 354.6 | 104.3766 | 104.3817 | 29.435 | 29.4365
1170 | feeder2_line2 | 2 | 354.6 | 95.2525 | 95.248 | 26.862 | 26.8607
1170 | feeder2_line2 | 3 | 354.6 | 113.8601 | 113.8608 | 32.1094 | 32.1096
1170 | feeder2_line3 | 1 | 80.1 | 11.6798 | 11.6798 | 14.5815 | 14.5816
1170 | feeder2_line3 | 2 | 80.1 | 5.6797e-07 | 1.0496e-06 | 7.0907e-07 | 1.3103e-06
1170 | feeder2_line3 | 3 | 80.1 | 5.6651e-07 | 1.0469e-06 | 7.0726e-07 | 1.307e-06
1170 | feeder2_line4 | 1 | 354.6 | 104.3765 | 104.3817 | 29.435 | 29.4365
1170 | feeder2_line4 | 2 | 354.6 | 95.2071 | 95.2027 | 26.8492 | 26.8479
1170 | feeder2_line4 | 3 | 354.6 | 113.86 | 113.8608 | 32.1094 | 32.1096
1170 | feeder2_line5 | 1 | 80.1 | 5.662e-07 | 9.8799e-07 | 7.0687e-07 | 1.2334e-06
1170 | feeder2_line5 | 2 | 80.1 | 0.91912 | 0.91911 | 1.1475 | 1.1474
1170 | feeder2_line5 | 3 | 80.1 | 5.6646e-07 | 9.8844e-07 | 7.0719e-07 | 1.234e-06
1170 | feeder2_line6 | 1 | 80.1 | 5.6608e-07 | 1.162e-06 | 7.0672e-07 | 1.4507e-06
1170 | feeder2_line6 | 2 | 80.1 | 5.6789e-07 | 1.1657e-06 | 7.0898e-07 | 1.4553e-06
1170 | feeder2_line6 | 3 | 80.1 | 1.1833 | 1.1833 | 1.4773 | 1.4773
1170 | feeder2_line7 | 1 | 354.6 | 104.3765 | 104.3817 | 29.435 | 29.4365
1170 | feeder2_line7 | 2 | 354.6 | 95.2071 | 95.2027 | 26.8492 | 26.8479
1170 | feeder2_line7 | 3 | 354.6 | 113.5583 | 113.5592 | 32.0243 | 32.0246
1170 | feeder2_line8 | 1 | 80.1 | 1.1114 | 1.1114 | 1.3875 | 1.3875
1170 | feeder2_line8 | 2 | 80.1 | 5.6772e-07 | 1.1236e-06 | 7.0877e-07 | 1.4028e-06
1170 | feeder2_line8 | 3 | 80.1 | 5.6594e-07 | 1.1202e-06 | 7.0655e-07 | 1.3984e-06
1170 | feeder2_line9 | 1 | 354.6 | 104.2145 | 104.2199 | 29.3893 | 29.3908
1170 | feeder2_line9 | 2 | 354.6 | 95.207 | 95.2027 | 26.8491 | 26.8479
1170 | feeder2_line9 | 3 | 354.6 | 113.5582 | 113.5592 | 32.0243 | 32.0246
1170 | feeder2_line10 | 1 | 80.1 | 8.3622e-07 | 1.4784e-06 | 1.044e-06 | 1.8457e-06
1170 | feeder2_line10 | 2 | 80.1 | 1.1094 | 1.1094 | 1.385 | 1.385
1170 | feeder2_line10 | 3 | 80.1 | 8.3648e-07 | 1.4789e-06 | 1.0443e-06 | 1.8463e-06
1170 | feeder2_line11 | 1 | 354.6 | 104.2146 | 104.2199 | 29.3893 | 29.3908
1170 | feeder2_line11 | 2 | 354.6 | 95.2342 | 95.2297 | 26.8568 | 26.8555
1170 | feeder2_line11 | 3 | 354.6 | 113.5583 | 113.5592 | 32.0243 | 32.0246
1170 | feeder2_line12 | 1 | 80.1 | 5.409e-07 | 9.8041e-07 | 6.7528e-07 | 1.224e-06
1170 | feeder2_line12 | 2 | 80.1 | 5.4314e-07 | 9.8398e-07 | 6.7807e-07 | 1.2284e-06
1170 | feeder2_line12 | 3 | 80.1 | 1.1654 | 1.1654 | 1.4549 | 1.4549
1170 | feeder2_line13 | 1 | 354.6 | 104.2147 | 104.2199 | 29.3894 | 29.3908
1170 | feeder2_line13 | 2 | 354.6 | 95.2343 | 95.2297 | 26.8568 | 26.8555
1170 | feeder2_line13 | 3 | 354.6 | 112.5064 | 112.5072 | 31.7277 | 31.7279
1170 | feeder2_line14 | 1 | 80.1 | 1.9823 | 1.9822 | 2.4747 | 2.4747
1170 | feeder2_line14 | 2 | 80.1 | 2.9603e-07 | 6.4157e-07 | 3.6958e-07 | 8.0097e-07
1170 | feeder2_line14 | 3 | 80.1 | 2.9515e-07 | 6.3935e-07 | 3.6848e-07 | 7.982e-07
1170 | feeder2_line15 | 1 | 354.6 | 103.0123 | 103.0176 | 29.0503 | 29.0518
1170 | feeder2_line15 | 2 | 354.6 | 95.2343 | 95.2297 | 26.8568 | 26.8555
1170 | feeder2_line15 | 3 | 354.6 | 112.5064 | 112.5072 | 31.7277 | 31.7279
1170 | feeder2_line16 | 1 | 80.1 | 5.6526e-07 | 1.0184e-06 | 7.0569e-07 | 1.2714e-06
1170 | feeder2_line16 | 2 | 80.1 | 1.5346 | 1.5346 | 1.9158 | 1.9158
1170 | feeder2_line16 | 3 | 80.1 | 5.6538e-07 | 1.0186e-06 | 7.0585e-07 | 1.2717e-06
1170 | feeder2_line17 | 1 | 354.6 | 103.0123 | 103.0176 | 29.0503 | 29.0518
1170 | feeder2_line17 | 2 | 354.6 | 95.103 | 95.0983 | 26.8198 | 26.8185
1170 | feeder2_line17 | 3 | 354.6 | 112.5064 | 112.5072 | 31.7277 | 31.7279
1170 | feeder2_line18 | 1 | 80.1 | 5.398e-07 | 7.2789e-07 | 6.7391e-07 | 9.0873e-07
1170 | feeder2_line18 | 2 | 80.1 | 5.4267e-07 | 7.3127e-07 | 6.775e-07 | 9.1295e-07
1170 | feeder2_line18 | 3 | 80.1 | 9.2305 | 9.2304 | 11.5237 | 11.5236
1170 | feeder2_line19 | 1 | 354.6 | 103.0123 | 103.0176 | 29.0503 | 29.0518
1170 | feeder2_line19 | 2 | 354.6 | 95.103 | 95.0983 | 26.8198 | 26.8185
1170 | feeder2_line19 | 3 | 354.6 | 109.4939 | 109.495 | 30.8782 | 30.8785
1170 | feeder2_line20 | 1 | 99 | 5.3951e-07 | 8.7223e-07 | 5.4496e-07 | 8.8104e-07
1170 | feeder2_line20 | 2 | 99 | 5.4254e-07 | 8.7652e-07 | 5.4802e-07 | 8.8537e-07
1170 | feeder2_line20 | 3 | 99 | 2.9938 | 2.9939 | 3.0241 | 3.0241
1170 | feeder2_line21 | 1 | 354.6 | 103.0123 | 103.0176 | 29.0503 | 29.0518
1170 | feeder2_line21 | 2 | 354.6 | 95.103 | 95.0983 | 26.8198 | 26.8185
1170 | feeder2_line21 | 3 | 354.6 | 107.6951 | 107.6962 | 30.3709 | 30.3712
1170 | feeder2_line22 | 1 | 99 | 5.6394e-07 | 9.9957e-07 | 5.6963e-07 | 1.0097e-06
1170 | feeder2_line22 | 2 | 99 | 1.2933 | 1.2933 | 1.3064 | 1.3064
1170 | feeder2_line22 | 3 | 99 | 5.6393e-07 | 9.9956e-07 | 5.6963e-07 | 1.0097e-06
1170 | feeder2_line23 | 1 | 99 | 5.6394e-07 | 9.3567e-07 | 5.6964e-07 | 9.4512e-07
1170 | feeder2_line23 | 2 | 99 | 5.6683e-07 | 9.4043e-07 | 5.7256e-07 | 9.4993e-07
1170 | feeder2_line23 | 3 | 99 | 1.1781 | 1.1781 | 1.19 | 1.19
1170 | feeder2_line24 | 1 | 354.6 | 103.0123 | 103.0176 | 29.0503 | 29.0518
1170 | feeder2_line24 | 2 | 354.6 | 94.9598 | 94.955 | 26.7794 | 26.7781
1170 | feeder2_line24 | 3 | 354.6 | 106.7032 | 106.7043 | 30.0911 | 30.0914
1170 | feeder2_line25 | 1 | 99 | 1.2902 | 1.2902 | 1.3032 | 1.3032
1170 | feeder2_line25 | 2 | 99 | 4.8706e-08 | 6.8351e-07 | 4.9198e-08 | 6.9042e-07
1170 | feeder2_line25 | 3 | 99 | 4.9354e-08 | 6.7988e-07 | 4.9852e-08 | 6.8675e-07
1170 | feeder2_line26 | 1 | 99 | 0.82799 | 0.82799 | 0.83635 | 0.83635
1170 | feeder2_line26 | 2 | 99 | 5.4231e-07 | 8.4682e-07 | 5.4779e-07 | 8.5538e-07
1170 | feeder2_line26 | 3 | 99 | 5.3895e-07 | 8.4233e-07 | 5.4439e-07 | 8.5084e-07
1170 | feeder2_line27 | 1 | 354.6 | 102.4425 | 102.4478 | 28.8896 | 28.8911
1170 | feeder2_line27 | 2 | 354.6 | 94.9598 | 94.955 | 26.7794 | 26.7781
1170 | feeder2_line27 | 3 | 354.6 | 106.7032 | 106.7043 | 30.0911 | 30.0914
1170 | feeder2_line28 | 1 | 99 | 2.4954e-06 | 6.9851e-07 | 2.5206e-06 | 7.0556e-07
1170 | feeder2_line28 | 2 | 99 | 0.077796 | 0.077794 | 0.078582 | 0.07858
1170 | feeder2_line28 | 3 | 99 | 2.4949e-06 | 6.9856e-07 | 2.5201e-06 | 7.0562e-07
1170 | feeder2_line29 | 1 | 354.6 | 102.4425 | 102.4478 | 28.8896 | 28.8911
1170 | feeder2_line29 | 2 | 354.6 | 94.9581 | 94.9533 | 26.7789 | 26.7776
1170 | feeder2_line29 | 3 | 354.6 | 106.7032 | 106.7043 | 30.0911 | 30.0914
1170 | feeder2_line30 | 1 | 266.4 | 8.8988 | 8.8986 | 3.3404 | 3.3403
1170 | feeder2_line30 | 2 | 266.4 | 3.8191 | 3.8187 | 1.4336 | 1.4334
1170 | feeder2_line30 | 3 | 266.4 | 5.1115 | 5.1113 | 1.9187 | 1.9187
1170 | feeder2_line31 | 1 | 354.6 | 99.6051 | 99.6104 | 28.0894 | 28.0909
1170 | feeder2_line31 | 2 | 354.6 | 95.0171 | 95.0115 | 26.7956 | 26.794
1170 | feeder2_line31 | 3 | 354.6 | 104.7783 | 104.779 | 29.5483 | 29.5485
1170 | feeder2_line32 | 1 | 354.6 | 99.6051 | 99.6105 | 28.0894 | 28.0909
1170 | feeder2_line32 | 2 | 354.6 | 94.946 | 94.9403 | 26.7755 | 26.7739
1170 | feeder2_line32 | 3 | 354.6 | 104.7783 | 104.779 | 29.5483 | 29.5485
1170 | feeder2_line33 | 1 | 99 | 4.9169e-08 | 6.7257e-07 | 4.9665e-08 | 6.7937e-07
1170 | feeder2_line33 | 2 | 99 | 1.8038 | 1.8037 | 1.822 | 1.822
1170 | feeder2_line33 | 3 | 99 | 4.9283e-08 | 6.7263e-07 | 4.9781e-08 | 6.7943e-07
1170 | feeder2_line34 | 1 | 354.6 | 99.605 | 99.6105 | 28.0894 | 28.0909
1170 | feeder2_line34 | 2 | 354.6 | 94.9459 | 94.9403 | 26.7755 | 26.7739
1170 | feeder2_line34 | 3 | 354.6 | 104.7569 | 104.7577 | 29.5423 | 29.5425
1170 | feeder2_line35 | 1 | 99 | 2.9319e-07 | 7.4457e-07 | 2.9615e-07 | 7.5209e-07
1170 | feeder2_line35 | 2 | 99 | 2.9496e-07 | 7.4966e-07 | 2.9794e-07 | 7.5724e-07
1170 | feeder2_line35 | 3 | 99 | 0.25026 | 0.25027 | 0.25279 | 0.2528
1170 | feeder2_line36 | 1 | 354.6 | 98.3251 | 98.3309 | 27.7284 | 27.7301
1170 | feeder2_line36 | 2 | 354.6 | 94.946 | 94.9403 | 26.7755 | 26.7739
1170 | feeder2_line36 | 3 | 354.6 | 104.757 | 104.7577 | 29.5423 | 29.5425
1170 | feeder2_line37 | 1 | 99 | 10.5939 | 10.5939 | 10.701 | 10.7009
1170 | feeder2_line37 | 2 | 99 | 2.9489e-07 | 8.2931e-07 | 2.9787e-07 | 8.3769e-07
1170 | feeder2_line37 | 3 | 99 | 2.9313e-07 | 8.2361e-07 | 2.9609e-07 | 8.3192e-07
1170 | feeder2_line38 | 1 | 99 | 3.1802e-07 | 7.6088e-07 | 3.2123e-07 | 7.6857e-07
1170 | feeder2_line38 | 2 | 99 | 1.4536 | 1.4536 | 1.4683 | 1.4683
1170 | feeder2_line38 | 3 | 99 | 3.1814e-07 | 7.6101e-07 | 3.2136e-07 | 7.687e-07
1170 | feeder2_line39 | 1 | 266.4 | 8.8988 | 8.8986 | 3.3404 | 3.3403
1170 | feeder2_line39 | 2 | 266.4 | 2.3674 | 2.367 | 0.88866 | 0.88851
1170 | feeder2_line39 | 3 | 266.4 | 5.1115 | 5.1113 | 1.9187 | 1.9187
1170 | feeder2_line40 | 1 | 354.6 | 98.2302 | 98.2361 | 27.7017 | 27.7034
1170 | feeder2_line40 | 2 | 354.6 | 94.9459 | 94.9403 | 26.7755 | 26.7739
1170 | feeder2_line40 | 3 | 354.6 | 104.7569 | 104.7577 | 29.5423 | 29.5425
1170 | feeder2_line41 | 1 | 99 | 1.2887 | 1.2887 | 1.3017 | 1.3017
1170 | feeder2_line41 | 2 | 99 | 4.8425e-08 | 7.246e-07 | 4.8914e-08 | 7.3192e-07
1170 | feeder2_line41 | 3 | 99 | 4.927e-08 | 7.1955e-07 | 4.9767e-08 | 7.2681e-07
1170 | feeder2_line42 | 1 | 99 | 2.934e-07 | 7.3436e-07 | 2.9636e-07 | 7.4178e-07
1170 | feeder2_line42 | 2 | 99 | 2.9511e-07 | 7.3921e-07 | 2.9809e-07 | 7.4668e-07
1170 | feeder2_line42 | 3 | 99 | 1.0959 | 1.0959 | 1.1069 | 1.1069
1170 | feeder2_line43 | 1 | 266.4 | 8.8987 | 8.8986 | 3.3404 | 3.3403
1170 | feeder2_line43 | 2 | 266.4 | 2.3673 | 2.367 | 0.88862 | 0.88851
1170 | feeder2_line43 | 3 | 266.4 | 4.0414 | 4.0413 | 1.517 | 1.517
1170 | feeder2_line44 | 1 | 354.6 | 98.2302 | 98.2361 | 27.7017 | 27.7034
1170 | feeder2_line44 | 2 | 354.6 | 94.9459 | 94.9403 | 26.7755 | 26.7739
1170 | feeder2_line44 | 3 | 354.6 | 103.1641 | 103.1649 | 29.0931 | 29.0933
1170 | feeder2_line45 | 1 | 99 | 4.913e-08 | 5.6735e-07 | 4.9627e-08 | 5.7308e-07
1170 | feeder2_line45 | 2 | 99 | 4.8411e-08 | 5.7136e-07 | 4.89e-08 | 5.7714e-07
1170 | feeder2_line45 | 3 | 99 | 2.99 | 2.9901 | 3.0202 | 3.0203
1170 | feeder2_line46 | 1 | 99 | 5.622e-07 | 1.3313e-06 | 5.6788e-07 | 1.3447e-06
1170 | feeder2_line46 | 2 | 99 | 5.6596e-07 | 1.3401e-06 | 5.7168e-07 | 1.3536e-06
1170 | feeder2_line46 | 3 | 99 | 1.8649 | 1.8649 | 1.8837 | 1.8837
1170 | feeder2_line47 | 1 | 266.4 | 8.8988 | 8.8986 | 3.3404 | 3.3403
1170 | feeder2_line47 | 2 | 266.4 | 2.3673 | 2.367 | 0.88862 | 0.88851
1170 | feeder2_line47 | 3 | 266.4 | 2.2296 | 2.2294 | 0.83693 | 0.83687
1170 | feeder2_line48 | 1 | 99 | 2.91 | 2.91 | 2.9394 | 2.9394
1170 | feeder2_line48 | 2 | 99 | 4.8514e-08 | 7.2152e-07 | 4.9004e-08 | 7.288e-07
1170 | feeder2_line48 | 3 | 99 | 4.9287e-08 | 7.1694e-07 | 4.9785e-08 | 7.2418e-07
1170 | feeder2_line49 | 1 | 266.4 | 6.0539 | 6.0537 | 2.2725 | 2.2724
1170 | feeder2_line49 | 2 | 266.4 | 2.3673 | 2.367 | 0.88861 | 0.88851
1170 | feeder2_line49 | 3 | 266.4 | 2.2296 | 2.2294 | 0.83692 | 0.83687
1170 | feeder2_line50 | 1 | 99 | 5.6216e-07 | 1.2115e-06 | 5.6784e-07 | 1.2237e-06
1170 | feeder2_line50 | 2 | 99 | 1.1822 | 1.1822 | 1.1942 | 1.1941
1170 | feeder2_line50 | 3 | 99 | 5.6232e-07 | 1.2118e-06 | 5.68e-07 | 1.2241e-06
1170 | feeder2_line51 | 1 | 99 | 5.9382 | 5.9382 | 5.9982 | 5.9982
1170 | feeder2_line51 | 2 | 99 | 5.6595e-07 | 1.3239e-06 | 5.7166e-07 | 1.3373e-06
1170 | feeder2_line51 | 3 | 99 | 5.6232e-07 | 1.3156e-06 | 5.68e-07 | 1.3288e-06
1170 | feeder2_line52 | 1 | 266.4 | 0.11597 | 0.11587 | 0.043533 | 0.043495
1170 | feeder2_line52 | 2 | 266.4 | 1.1894 | 1.1893 | 0.44647 | 0.44643
1170 | feeder2_line52 | 3 | 266.4 | 2.2294 | 2.2294 | 0.83688 | 0.83687
1170 | feeder2_line53 | 1 | 99 | 5.3757e-07 | 7.3938e-07 | 5.43e-07 | 7.4685e-07
1170 | feeder2_line53 | 2 | 99 | 1.1893 | 1.1893 | 1.2013 | 1.2013
1170 | feeder2_line53 | 3 | 99 | 5.3768e-07 | 7.3959e-07 | 5.4311e-07 | 7.4706e-07
1170 | feeder2_line54 | 1 | 266.4 | 0.11579 | 0.11587 | 0.043465 | 0.043495
1170 | feeder2_line54 | 2 | 266.4 | 8.4347e-05 | 4.5653e-06 | 3.1662e-05 | 1.7137e-06
1170 | feeder2_line54 | 3 | 266.4 | 2.2293 | 2.2294 | 0.83683 | 0.83687
1170 | feeder2_line55 | 1 | 99 | 2.0757 | 2.0757 | 2.0967 | 2.0967
1170 | feeder2_line55 | 2 | 99 | 4.8364e-08 | 7.1945e-07 | 4.8853e-08 | 7.2671e-07
1170 | feeder2_line55 | 3 | 99 | 4.9251e-08 | 7.141e-07 | 4.9749e-08 | 7.2131e-07
1170 | feeder2_line56 | 1 | 354.6 | 97.7861 | 97.7921 | 27.5764 | 27.5781
1170 | feeder2_line56 | 2 | 354.6 | 94.9459 | 94.9403 | 26.7755 | 26.7739
1170 | feeder2_line56 | 3 | 354.6 | 103.1641 | 103.1649 | 29.0931 | 29.0933
1170 | feeder2_line57 | 1 | 99 | 7.3791e-07 | 1.5145e-06 | 7.4537e-07 | 1.5298e-06
1170 | feeder2_line57 | 2 | 99 | 7.277e-07 | 1.5246e-06 | 7.3505e-07 | 1.54e-06
1170 | feeder2_line57 | 3 | 99 | 2.2294 | 2.2294 | 2.2519 | 2.2519
1170 | feeder2_line58 | 1 | 266.4 | 0.11585 | 0.11587 | 0.043488 | 0.043495
1170 | feeder2_line58 | 2 | 266.4 | 1.8722e-05 | 2.6504e-06 | 7.028e-06 | 9.949e-07
1170 | feeder2_line58 | 3 | 266.4 | 1.8588e-05 | 2.6344e-06 | 6.9775e-06 | 9.8888e-07
1170 | feeder2_line59 | 1 | 99 | 4.9188e-08 | 5.2645e-07 | 4.9685e-08 | 5.3177e-07
1170 | feeder2_line59 | 2 | 99 | 4.8516e-08 | 5.2996e-07 | 4.9007e-08 | 5.3531e-07
1170 | feeder2_line59 | 3 | 99 | 1.2409 | 1.2409 | 1.2535 | 1.2535
1170 | feeder2_line60 | 1 | 99 | 2.9338e-07 | 7.9563e-07 | 2.9634e-07 | 8.0366e-07
1170 | feeder2_line60 | 2 | 99 | 2.9511e-07 | 8.0094e-07 | 2.9809e-07 | 8.0903e-07
1170 | feeder2_line60 | 3 | 99 | 1.1649 | 1.1649 | 1.1766 | 1.1766
1170 | feeder2_line61 | 1 | 266.4 | 2.188 | 2.1881 | 0.82131 | 0.82137
1170 | feeder2_line61 | 2 | 266.4 | 2.5282 | 2.5283 | 0.94901 | 0.94906
1170 | feeder2_line61 | 3 | 266.4 | 1.9544 | 1.9546 | 0.73364 | 0.73372
1170 | feeder2_line62 | 1 | 354.6 | 97.8803 | 97.8862 | 27.603 | 27.6047
1170 | feeder2_line62 | 2 | 354.6 | 94.2909 | 94.285 | 26.5908 | 26.5891
1170 | feeder2_line62 | 3 | 354.6 | 102.2183 | 102.219 | 28.8264 | 28.8266
1170 | feeder2_line63 | 1 | 99 | 0.090771 | 0.090771 | 0.091687 | 0.091688
1170 | feeder2_line63 | 2 | 99 | 5.6596e-07 | 1.2042e-06 | 5.7168e-07 | 1.2164e-06
1170 | feeder2_line63 | 3 | 99 | 5.6232e-07 | 1.1965e-06 | 5.68e-07 | 1.2086e-06
1170 | feeder2_line64 | 1 | 99 | 0.0251 | 0.0251 | 0.025353 | 0.025354
1170 | feeder2_line64 | 2 | 99 | 3.9759e-12 | 3.172e-07 | 4.016e-12 | 3.204e-07
1170 | feeder2_line64 | 3 | 99 | 3.0663e-12 | 3.1519e-07 | 3.0973e-12 | 3.1838e-07
1170 | feeder2_line65 | 1 | 99 | 4.9034e-08 | 6.2672e-07 | 4.9529e-08 | 6.3305e-07
1170 | feeder2_line65 | 2 | 99 | 0.91957 | 0.91955 | 0.92886 | 0.92884
1170 | feeder2_line65 | 3 | 99 | 4.9233e-08 | 6.2625e-07 | 4.973e-08 | 6.3258e-07
1170 | feeder2_line66 | 1 | 354.6 | 97.8803 | 97.8862 | 27.603 | 27.6047
1170 | feeder2_line66 | 2 | 354.6 | 94.3804 | 94.3744 | 26.616 | 26.6143
1170 | feeder2_line66 | 3 | 354.6 | 102.2183 | 102.219 | 28.8264 | 28.8266
1170 | feeder2_line67 | 1 | 99 | 2.4531e-08 | 3.5449e-07 | 2.4778e-08 | 3.5807e-07
1170 | feeder2_line67 | 2 | 99 | 2.4163e-08 | 3.5706e-07 | 2.4407e-08 | 3.6067e-07
1170 | feeder2_line67 | 3 | 99 | 1.2878 | 1.2878 | 1.3008 | 1.3008
1170 | feeder2_line68 | 1 | 266.4 | 2.188 | 2.1881 | 0.82132 | 0.82137
1170 | feeder2_line68 | 2 | 266.4 | 2.5282 | 2.5283 | 0.94903 | 0.94906
1170 | feeder2_line68 | 3 | 266.4 | 0.83618 | 0.83634 | 0.31388 | 0.31394
1170 | feeder2_line69 | 1 | 99 | 6.6114 | 6.6114 | 6.6782 | 6.6782
1170 | feeder2_line69 | 2 | 99 | 2.5092e-06 | 6.5527e-07 | 2.5346e-06 | 6.6189e-07
1170 | feeder2_line69 | 3 | 99 | 2.4797e-06 | 6.4993e-07 | 2.5048e-06 | 6.5649e-07
1170 | feeder2_line70 | 1 | 354.6 | 95.7788 | 95.7849 | 27.0104 | 27.0121
1170 | feeder2_line70 | 2 | 354.6 | 94.3804 | 94.3744 | 26.616 | 26.6143
1170 | feeder2_line70 | 3 | 354.6 | 102.2184 | 102.219 | 28.8264 | 28.8266
1170 | feeder2_line71 | 1 | 99 | 4.9007e-08 | 6.9891e-07 | 4.9502e-08 | 7.0597e-07
1170 | feeder2_line71 | 2 | 99 | 2.4946 | 2.4946 | 2.5198 | 2.5198
1170 | feeder2_line71 | 3 | 99 | 4.9227e-08 | 6.9824e-07 | 4.9724e-08 | 7.053e-07
1170 | feeder2_line72 | 1 | 354.6 | 95.7789 | 95.7849 | 27.0104 | 27.0121
1170 | feeder2_line72 | 2 | 354.6 | 94.4967 | 94.4905 | 26.6488 | 26.6471
1170 | feeder2_line72 | 3 | 354.6 | 102.2184 | 102.219 | 28.8264 | 28.8266
1170 | feeder2_line73 | 1 | 99 | 5.8531e-07 | 1.5007e-06 | 5.9123e-07 | 1.5159e-06
1170 | feeder2_line73 | 2 | 99 | 1.8047 | 1.8047 | 1.823 | 1.8229
1170 | feeder2_line73 | 3 | 99 | 5.8511e-07 | 1.5e-06 | 5.9102e-07 | 1.5151e-06
1170 | feeder2_line74 | 1 | 99 | 4.9068e-08 | 4.476e-07 | 4.9564e-08 | 4.5212e-07
1170 | feeder2_line74 | 2 | 99 | 0.83801 | 0.83802 | 0.84647 | 0.84648
1170 | feeder2_line74 | 3 | 99 | 4.9242e-08 | 4.4738e-07 | 4.9739e-08 | 4.519e-07
1170 | feeder2_line75 | 1 | 266.4 | 2.1881 | 2.1881 | 0.82136 | 0.82137
1170 | feeder2_line75 | 2 | 266.4 | 0.090745 | 0.090774 | 0.034064 | 0.034075
1170 | feeder2_line75 | 3 | 266.4 | 0.83626 | 0.83634 | 0.31391 | 0.31394
1170 | feeder2_line76 | 1 | 99 | 2.1881 | 2.1881 | 2.2102 | 2.2102
1170 | feeder2_line76 | 2 | 99 | 8.3527e-07 | 1.5593e-06 | 8.4371e-07 | 1.5751e-06
1170 | feeder2_line76 | 3 | 99 | 8.2844e-07 | 1.5473e-06 | 8.368e-07 | 1.5629e-06
1170 | feeder2_line77 | 1 | 99 | 2.4531e-08 | 5.6248e-07 | 2.4778e-08 | 5.6816e-07
1170 | feeder2_line77 | 2 | 99 | 2.4163e-08 | 5.6658e-07 | 2.4407e-08 | 5.723e-07
1170 | feeder2_line77 | 3 | 99 | 0.8363 | 0.83634 | 0.84475 | 0.84479
1170 | feeder2_line78 | 1 | 266.4 | 5.7418e-12 | 9.3307e-07 | 2.1553e-12 | 3.5025e-07
1170 | feeder2_line78 | 2 | 266.4 | 0.090777 | 0.090774 | 0.034076 | 0.034074
1170 | feeder2_line78 | 3 | 266.4 | 1.5338e-11 | 9.3271e-07 | 5.7576e-12 | 3.5012e-07
1170 | feeder2_line79 | 1 | 354.6 | 4.4402 | 4.4399 | 1.2522 | 1.2521
1170 | feeder2_line79 | 2 | 354.6 | 8.1606 | 8.1602 | 2.3014 | 2.3012
1170 | feeder2_line79 | 3 | 354.6 | 29.409 | 29.4085 | 8.2936 | 8.2934
1170 | feeder2_line80 | 1 | 354.6 | 95.5885 | 95.5945 | 26.9567 | 26.9584
1170 | feeder2_line80 | 2 | 354.6 | 93.2914 | 93.2846 | 26.3089 | 26.307
1170 | feeder2_line80 | 3 | 354.6 | 97.8066 | 97.8081 | 27.5822 | 27.5827
1170 | feeder2_line81 | 1 | 354.6 | 95.5884 | 95.5945 | 26.9567 | 26.9584
1170 | feeder2_line81 | 2 | 354.6 | 93.2913 | 93.2846 | 26.3089 | 26.307
1170 | feeder2_line81 | 3 | 354.6 | 97.921 | 97.9226 | 27.6145 | 27.615
1170 | feeder2_line82 | 1 | 354.6 | 2.0251e-11 | 7.1637e-07 | 5.7111e-12 | 2.0202e-07
1170 | feeder2_line82 | 2 | 354.6 | 8.833e-12 | 7.2127e-07 | 2.491e-12 | 2.034e-07
1170 | feeder2_line82 | 3 | 354.6 | 0.76184 | 0.76185 | 0.21484 | 0.21485
1170 | feeder2_line83 | 1 | 354.6 | 95.5884 | 95.5945 | 26.9567 | 26.9584
1170 | feeder2_line83 | 2 | 354.6 | 93.5895 | 93.5827 | 26.393 | 26.391
1170 | feeder2_line83 | 3 | 354.6 | 97.921 | 97.9226 | 27.6145 | 27.615
1170 | feeder2_line84 | 1 | 354.6 | 8.8433e-12 | 1.2657e-06 | 2.4939e-12 | 3.5695e-07
1170 | feeder2_line84 | 2 | 354.6 | 1.8655 | 1.8655 | 0.5261 | 0.52609
1170 | feeder2_line84 | 3 | 354.6 | 5.487e-12 | 1.2643e-06 | 1.5474e-12 | 3.5655e-07
1170 | feeder2_line85 | 1 | 99 | 1.4475 | 1.4475 | 1.4621 | 1.4621
1170 | feeder2_line85 | 2 | 99 | 4.82e-08 | 4.5503e-07 | 4.8686e-08 | 4.5962e-07
1170 | feeder2_line85 | 3 | 99 | 4.9206e-08 | 4.5107e-07 | 4.9703e-08 | 4.5563e-07
1170 | feeder2_line86 | 1 | 354.6 | 95.9249 | 95.931 | 27.0516 | 27.0533
1170 | feeder2_line86 | 2 | 354.6 | 93.5895 | 93.5827 | 26.393 | 26.391
1170 | feeder2_line86 | 3 | 354.6 | 97.921 | 97.9226 | 27.6145 | 27.615
1170 | feeder2_line87 | 1 | 354.6 | 95.9249 | 95.931 | 27.0516 | 27.0533
1170 | feeder2_line87 | 2 | 354.6 | 92.9764 | 92.9694 | 26.2201 | 26.2181
1170 | feeder2_line87 | 3 | 354.6 | 95.673 | 95.6746 | 26.9805 | 26.981
1170 | feeder2_line88 | 1 | 354.6 | 0.00011169 | 3.2788e-06 | 3.1497e-05 | 9.2464e-07
1170 | feeder2_line88 | 2 | 354.6 | 2.7655 | 2.7653 | 0.77988 | 0.77983
1170 | feeder2_line88 | 3 | 354.6 | 10.2469 | 10.2466 | 2.8897 | 2.8896
1170 | feeder2_line89 | 1 | 354.6 | 95.9244 | 95.931 | 27.0514 | 27.0533
1170 | feeder2_line89 | 2 | 354.6 | 93.3878 | 93.3814 | 26.3361 | 26.3343
1170 | feeder2_line89 | 3 | 354.6 | 95.6722 | 95.6747 | 26.9803 | 26.981
1170 | feeder2_line90 | 1 | 354.6 | 0.00070492 | 1.9789e-06 | 0.00019879 | 5.5806e-07
1170 | feeder2_line90 | 2 | 354.6 | 1.9477 | 1.9482 | 0.54928 | 0.5494
1170 | feeder2_line90 | 3 | 354.6 | 0.00070235 | 1.9751e-06 | 0.00019807 | 5.5699e-07
1170 | feeder2_line91 | 1 | 354.6 | 95.9246 | 95.931 | 27.0515 | 27.0533
1170 | feeder2_line91 | 2 | 354.6 | 93.3879 | 93.3814 | 26.3361 | 26.3343
1170 | feeder2_line91 | 3 | 354.6 | 95.1163 | 95.1186 | 26.8235 | 26.8242
1170 | feeder2_line92 | 1 | 354.6 | 9.3446e-12 | 9.9789e-07 | 2.6353e-12 | 2.8141e-07
1170 | feeder2_line92 | 2 | 354.6 | 1.0674e-11 | 1.0049e-06 | 3.01e-12 | 2.8338e-07
1170 | feeder2_line92 | 3 | 354.6 | 1.1644 | 1.1644 | 0.32838 | 0.32838
1170 | feeder2_line93 | 1 | 99 | 2.4465e-08 | 3.3308e-07 | 2.4712e-08 | 3.3644e-07
1170 | feeder2_line93 | 2 | 99 | 1.8656 | 1.8655 | 1.8844 | 1.8844
1170 | feeder2_line93 | 3 | 99 | 2.4585e-08 | 3.3271e-07 | 2.4833e-08 | 3.3607e-07
1170 | feeder2_line94 | 1 | 354.6 | 2.4472e-06 | 1.6218e-06 | 6.9014e-07 | 4.5736e-07
1170 | feeder2_line94 | 2 | 354.6 | 0.082826 | 0.082791 | 0.023358 | 0.023348
1170 | feeder2_line94 | 3 | 354.6 | 2.4585e-06 | 1.6203e-06 | 6.9332e-07 | 4.5693e-07
1170 | feeder2_line95 | 1 | 99 | 3.4706e-06 | 2.5425e-06 | 3.5057e-06 | 2.5682e-06
1170 | feeder2_line95 | 2 | 99 | 2.7654 | 2.7653 | 2.7933 | 2.7932
1170 | feeder2_line95 | 3 | 99 | 3.4715e-06 | 2.5393e-06 | 3.5066e-06 | 2.565e-06
1170 | feeder2_line96 | 1 | 354.6 | 0.000118 | 6.0612e-07 | 3.3277e-05 | 1.7093e-07
1170 | feeder2_line96 | 2 | 354.6 | 0.00011897 | 6.1085e-07 | 3.3551e-05 | 1.7226e-07
1170 | feeder2_line96 | 3 | 354.6 | 10.2469 | 10.2466 | 2.8897 | 2.8896
1170 | feeder2_line97 | 1 | 354.6 | 95.3149 | 95.3212 | 26.8796 | 26.8813
1170 | feeder2_line97 | 2 | 354.6 | 93.3882 | 93.3814 | 26.3362 | 26.3343
1170 | feeder2_line97 | 3 | 354.6 | 95.1165 | 95.1186 | 26.8236 | 26.8242
1170 | feeder2_line98 | 1 | 354.6 | 3.5877 | 3.5863 | 1.0118 | 1.0114
1170 | feeder2_line98 | 2 | 354.6 | 0.001677 | 6.0901e-07 | 0.00047292 | 1.7175e-07
1170 | feeder2_line98 | 3 | 354.6 | 0.001642 | 6.0541e-07 | 0.00046305 | 1.7073e-07
1170 | feeder2_line99 | 1 | 99 | 2.4472e-08 | 4.3571e-07 | 2.4719e-08 | 4.4011e-07
1170 | feeder2_line99 | 2 | 99 | 2.4095e-08 | 4.3899e-07 | 2.4339e-08 | 4.4343e-07
1170 | feeder2_line99 | 3 | 99 | 10.2468 | 10.2466 | 10.3503 | 10.3501
1170 | feeder2_line100 | 1 | 99 | 3.5862 | 3.5863 | 3.6225 | 3.6225
1170 | feeder2_line100 | 2 | 99 | 2.4082e-08 | 6.0226e-07 | 2.4325e-08 | 6.0834e-07
1170 | feeder2_line100 | 3 | 99 | 2.4576e-08 | 5.9711e-07 | 2.4824e-08 | 6.0314e-07
1170 | feeder2_line101 | 1 | 354.6 | 0.083848 | 0.08347 | 0.023646 | 0.023539
1170 | feeder2_line101 | 2 | 354.6 | 8.1606 | 8.1602 | 2.3014 | 2.3012
1170 | feeder2_line101 | 3 | 354.6 | 29.409 | 29.4085 | 8.2936 | 8.2934
1170 | feeder2_line102 | 1 | 99 | 4.3583 | 4.3584 | 4.4024 | 4.4024
1170 | feeder2_line102 | 2 | 99 | 2.3024e-06 | 8.6292e-07 | 2.3257e-06 | 8.7164e-07
1170 | feeder2_line102 | 3 | 99 | 2.2633e-06 | 8.5507e-07 | 2.2861e-06 | 8.6371e-07
1170 | feeder2_line103 | 1 | 99 | 5.3567e-07 | 7.8406e-07 | 5.4108e-07 | 7.9198e-07
1170 | feeder2_line103 | 2 | 99 | 1.4231 | 1.4231 | 1.4375 | 1.4375
1170 | feeder2_line103 | 3 | 99 | 5.3437e-07 | 7.8253e-07 | 5.3977e-07 | 7.9043e-07
1170 | feeder2_line104 | 1 | 354.6 | 0.083744 | 0.08347 | 0.023617 | 0.023539
1170 | feeder2_line104 | 2 | 354.6 | 6.7895 | 6.7892 | 1.9147 | 1.9146
1170 | feeder2_line104 | 3 | 354.6 | 29.4089 | 29.4085 | 8.2935 | 8.2934
1170 | feeder2_line105 | 1 | 99 | 2.4829e-06 | 7.2147e-07 | 2.5079e-06 | 7.2875e-07
1170 | feeder2_line105 | 2 | 99 | 2.5082e-06 | 7.2676e-07 | 2.5335e-06 | 7.341e-07
1170 | feeder2_line105 | 3 | 99 | 9.1325 | 9.1324 | 9.2247 | 9.2246
1170 | feeder2_line106 | 1 | 354.6 | 0.08369 | 0.083469 | 0.023601 | 0.023539
1170 | feeder2_line106 | 2 | 354.6 | 6.7895 | 6.7892 | 1.9147 | 1.9146
1170 | feeder2_line106 | 3 | 354.6 | 20.3829 | 20.3826 | 5.7481 | 5.7481
1170 | feeder2_line107 | 1 | 99 | 3.1675e-07 | 8.7925e-07 | 3.1995e-07 | 8.8813e-07
1170 | feeder2_line107 | 2 | 99 | 3.1718 | 3.1718 | 3.2039 | 3.2038
1170 | feeder2_line107 | 3 | 99 | 3.1637e-07 | 8.7717e-07 | 3.1957e-07 | 8.8603e-07
1170 | feeder2_line108 | 1 | 354.6 | 0.08368 | 0.083469 | 0.023598 | 0.023539
1170 | feeder2_line108 | 2 | 354.6 | 3.6191 | 3.6188 | 1.0206 | 1.0205
1170 | feeder2_line108 | 3 | 354.6 | 20.3829 | 20.3826 | 5.7481 | 5.7481
1170 | feeder2_line109 | 1 | 354.6 | 94.547 | 94.5532 | 26.663 | 26.6648
1170 | feeder2_line109 | 2 | 354.6 | 93.3883 | 93.3814 | 26.3363 | 26.3343
1170 | feeder2_line109 | 3 | 354.6 | 95.1167 | 95.1186 | 26.8237 | 26.8242
1170 | feeder2_line110 | 1 | 99 | 2.2318 | 2.2311 | 2.2544 | 2.2537
1170 | feeder2_line110 | 2 | 99 | 0.00079083 | 8.8967e-07 | 0.00079882 | 8.9866e-07
1170 | feeder2_line110 | 3 | 99 | 0.00078034 | 8.8347e-07 | 0.00078823 | 8.9239e-07
1170 | feeder2_line111 | 1 | 99 | 2.4467e-08 | 3.7212e-07 | 2.4714e-08 | 3.7588e-07
1170 | feeder2_line111 | 2 | 99 | 1.0399 | 1.0399 | 1.0504 | 1.0504
1170 | feeder2_line111 | 3 | 99 | 2.4597e-08 | 3.7167e-07 | 2.4845e-08 | 3.7542e-07
1170 | feeder2_line112 | 1 | 99 | 3.1655e-07 | 8.9424e-07 | 3.1975e-07 | 9.0327e-07
1170 | feeder2_line112 | 2 | 99 | 1.8506 | 1.8505 | 1.8693 | 1.8692
1170 | feeder2_line112 | 3 | 99 | 3.164e-07 | 8.9314e-07 | 3.1959e-07 | 9.0216e-07
1170 | feeder2_line113 | 1 | 99 | 2.163 | 2.163 | 2.1848 | 2.1848
1170 | feeder2_line113 | 2 | 99 | 3.1791e-07 | 8.8774e-07 | 3.2112e-07 | 8.967e-07
1170 | feeder2_line113 | 3 | 99 | 3.1622e-07 | 8.802e-07 | 3.1942e-07 | 8.8909e-07
1170 | feeder2_line114 | 1 | 99 | 1.4181 | 1.4181 | 1.4324 | 1.4324
1170 | feeder2_line114 | 2 | 99 | 2.4108e-08 | 4.2911e-07 | 2.4351e-08 | 4.3344e-07
1170 | feeder2_line114 | 3 | 99 | 2.4627e-08 | 4.2519e-07 | 2.4875e-08 | 4.2949e-07
1170 | feeder2_line115 | 1 | 99 | 2.4443e-08 | 5.4874e-07 | 2.4689e-08 | 5.5428e-07
1170 | feeder2_line115 | 2 | 99 | 0.71236 | 0.71234 | 0.71955 | 0.71953
1170 | feeder2_line115 | 3 | 99 | 2.4653e-08 | 5.4727e-07 | 2.4902e-08 | 5.5279e-07
1170 | feeder2_line116 | 1 | 354.6 | 0.083685 | 0.083469 | 0.0236 | 0.023539
1170 | feeder2_line116 | 2 | 354.6 | 3.014 | 3.0138 | 0.84997 | 0.84991
1170 | feeder2_line116 | 3 | 354.6 | 20.3829 | 20.3826 | 5.7481 | 5.7481
1170 | feeder2_line117 | 1 | 99 | 4.8929e-08 | 6.251e-07 | 4.9423e-08 | 6.3141e-07
1170 | feeder2_line117 | 2 | 99 | 1.8653 | 1.8653 | 1.8841 | 1.8841
1170 | feeder2_line117 | 3 | 99 | 4.9113e-08 | 6.2463e-07 | 4.9609e-08 | 6.3094e-07
1170 | feeder2_line118 | 1 | 354.6 | 94.547 | 94.5532 | 26.663 | 26.6648
1170 | feeder2_line118 | 2 | 354.6 | 93.7176 | 93.7105 | 26.4291 | 26.4271
1170 | feeder2_line118 | 3 | 354.6 | 95.1167 | 95.1186 | 26.8237 | 26.8242
1170 | feeder2_line119 | 1 | 99 | 2.4433e-08 | 5.9048e-07 | 2.468e-08 | 5.9644e-07
1170 | feeder2_line119 | 2 | 99 | 2.4088e-08 | 5.9476e-07 | 2.4331e-08 | 6.0077e-07
1170 | feeder2_line119 | 3 | 99 | 2.6068 | 2.6068 | 2.6331 | 2.6332
1170 | feeder2_line120 | 1 | 354.6 | 0.083687 | 0.083469 | 0.0236 | 0.023539
1170 | feeder2_line120 | 2 | 354.6 | 3.014 | 3.0138 | 0.84997 | 0.84991
1170 | feeder2_line120 | 3 | 354.6 | 17.8344 | 17.8341 | 5.0294 | 5.0293
1170 | feeder2_line121 | 1 | 99 | 3.1675e-07 | 9.1443e-07 | 3.1995e-07 | 9.2366e-07
1170 | feeder2_line121 | 2 | 99 | 1.89 | 1.89 | 1.9091 | 1.9091
1170 | feeder2_line121 | 3 | 99 | 3.162e-07 | 9.1141e-07 | 3.1939e-07 | 9.2062e-07
1170 | feeder2_line122 | 1 | 354.6 | 0.083676 | 0.083469 | 0.023597 | 0.023539
1170 | feeder2_line122 | 2 | 354.6 | 1.4715 | 1.4714 | 0.41496 | 0.41494
1170 | feeder2_line122 | 3 | 354.6 | 17.8344 | 17.8341 | 5.0294 | 5.0293
1170 | feeder2_line123 | 1 | 99 | 5.6028e-07 | 9.4758e-07 | 5.6593e-07 | 9.5716e-07
1170 | feeder2_line123 | 2 | 99 | 5.6437e-07 | 9.5444e-07 | 5.7007e-07 | 9.6408e-07
1170 | feeder2_line123 | 3 | 99 | 0.079112 | 0.079116 | 0.079911 | 0.079915
1170 | feeder2_line124 | 1 | 354.6 | 0.08358 | 0.083469 | 0.02357 | 0.023539
1170 | feeder2_line124 | 2 | 354.6 | 1.4715 | 1.4714 | 0.41498 | 0.41494
1170 | feeder2_line124 | 3 | 354.6 | 17.7573 | 17.7571 | 5.0077 | 5.0076
1170 | feeder2_line125 | 1 | 99 | 5.6028e-07 | 8.8088e-07 | 5.6594e-07 | 8.8978e-07
1170 | feeder2_line125 | 2 | 99 | 5.6437e-07 | 8.8726e-07 | 5.7007e-07 | 8.9622e-07
1170 | feeder2_line125 | 3 | 99 | 3.5917 | 3.5917 | 3.628 | 3.628
1170 | feeder2_line126 | 1 | 354.6 | 0.083732 | 0.083468 | 0.023613 | 0.023539
1170 | feeder2_line126 | 2 | 354.6 | 1.4716 | 1.4714 | 0.41501 | 0.41494
1170 | feeder2_line126 | 3 | 354.6 | 14.2143 | 14.2138 | 4.0085 | 4.0084
1170 | feeder2_line127 | 1 | 99 | 5.6027e-07 | 1.0546e-06 | 5.6593e-07 | 1.0652e-06
1170 | feeder2_line127 | 2 | 99 | 5.6437e-07 | 1.0622e-06 | 5.7007e-07 | 1.0729e-06
1170 | feeder2_line127 | 3 | 99 | 11.9514 | 11.9513 | 12.0721 | 12.072
1170 | feeder2_line128 | 1 | 354.6 | 0.083648 | 0.083468 | 0.023589 | 0.023539
1170 | feeder2_line128 | 2 | 354.6 | 1.4716 | 1.4714 | 0.41501 | 0.41494
1170 | feeder2_line128 | 3 | 354.6 | 2.3326 | 2.3324 | 0.65782 | 0.65775
1170 | feeder2_line129 | 1 | 99 | 5.3589e-07 | 8.5512e-07 | 5.413e-07 | 8.6375e-07
1170 | feeder2_line129 | 2 | 99 | 1.4714 | 1.4714 | 1.4862 | 1.4862
1170 | feeder2_line129 | 3 | 99 | 5.3352e-07 | 8.5197e-07 | 5.3891e-07 | 8.6058e-07
1170 | feeder2_line130 | 1 | 354.6 | 0.083661 | 0.083468 | 0.023593 | 0.023539
1170 | feeder2_line130 | 2 | 354.6 | 0.00030305 | 4.5568e-06 | 8.5462e-05 | 1.2851e-06
1170 | feeder2_line130 | 3 | 354.6 | 2.3326 | 2.3324 | 0.65782 | 0.65775
1170 | feeder2_line131 | 1 | 99 | 5.6029e-07 | 9.4777e-07 | 5.6595e-07 | 9.5734e-07
1170 | feeder2_line131 | 2 | 99 | 5.6438e-07 | 9.5462e-07 | 5.7008e-07 | 9.6426e-07
1170 | feeder2_line131 | 3 | 99 | 1.2346 | 1.2347 | 1.2471 | 1.2471
1170 | feeder2_line132 | 1 | 354.6 | 0.083506 | 0.083468 | 0.023549 | 0.023539
1170 | feeder2_line132 | 2 | 354.6 | 0.00012377 | 2.8648e-06 | 3.4905e-05 | 8.0789e-07
1170 | feeder2_line132 | 3 | 354.6 | 1.4455 | 1.4454 | 0.40764 | 0.40763
1170 | feeder2_line133 | 1 | 99 | 0.083439 | 0.083468 | 0.084282 | 0.084311
1170 | feeder2_line133 | 2 | 99 | 2.9423e-07 | 9.6225e-07 | 2.9721e-07 | 9.7197e-07
1170 | feeder2_line133 | 3 | 99 | 2.9144e-07 | 9.518e-07 | 2.9438e-07 | 9.6141e-07
1170 | feeder2_line134 | 1 | 354.6 | 8.9037e-12 | 1.7423e-06 | 2.5109e-12 | 4.9133e-07
1170 | feeder2_line134 | 2 | 354.6 | 8.9037e-12 | 1.754e-06 | 2.5109e-12 | 4.9463e-07
1170 | feeder2_line134 | 3 | 354.6 | 1.4454 | 1.4454 | 0.40763 | 0.40763
1170 | feeder2_line135 | 1 | 99 | 2.5081 | 2.5082 | 2.5335 | 2.5335
1170 | feeder2_line135 | 2 | 99 | 4.8132e-08 | 5.7372e-07 | 4.8618e-08 | 5.7951e-07
1170 | feeder2_line135 | 3 | 99 | 4.909e-08 | 5.6893e-07 | 4.9586e-08 | 5.7468e-07
1170 | feeder2_line136 | 1 | 354.6 | 95.0868 | 95.0931 | 26.8152 | 26.817
1170 | feeder2_line136 | 2 | 354.6 | 93.7176 | 93.7105 | 26.4291 | 26.4271
1170 | feeder2_line136 | 3 | 354.6 | 95.1167 | 95.1186 | 26.8237 | 26.8242
1170 | feeder2_line137 | 1 | 99 | 2.8289 | 2.8289 | 2.8574 | 2.8574
1170 | feeder2_line137 | 2 | 99 | 8.3273e-07 | 1.545e-06 | 8.4114e-07 | 1.5606e-06
1170 | feeder2_line137 | 3 | 99 | 8.2537e-07 | 1.5322e-06 | 8.3371e-07 | 1.5476e-06
1170 | feeder2_line138 | 1 | 354.6 | 94.1806 | 94.1868 | 26.5597 | 26.5614
1170 | feeder2_line138 | 2 | 354.6 | 93.7176 | 93.7105 | 26.4291 | 26.4271
1170 | feeder2_line138 | 3 | 354.6 | 95.1168 | 95.1186 | 26.8237 | 26.8242
1170 | feeder2_line139 | 1 | 99 | 4.8915e-08 | 4.7763e-07 | 4.9409e-08 | 4.8246e-07
1170 | feeder2_line139 | 2 | 99 | 4.8123e-08 | 4.8134e-07 | 4.8609e-08 | 4.862e-07
1170 | feeder2_line139 | 3 | 99 | 0.045884 | 0.046195 | 0.046348 | 0.046662
1170 | feeder2_line140 | 1 | 354.6 | 94.1806 | 94.1868 | 26.5597 | 26.5614
1170 | feeder2_line140 | 2 | 354.6 | 93.7176 | 93.7105 | 26.4291 | 26.4271
1170 | feeder2_line140 | 3 | 354.6 | 95.1308 | 95.1325 | 26.8276 | 26.8281
1170 | feeder2_line141 | 1 | 99 | 2.4511e-06 | 4.7239e-07 | 2.4759e-06 | 4.7716e-07
1170 | feeder2_line141 | 2 | 99 | 1.0923 | 1.0923 | 1.1034 | 1.1033
1170 | feeder2_line141 | 3 | 99 | 2.4482e-06 | 4.721e-07 | 2.4729e-06 | 4.7687e-07
1170 | feeder2_line142 | 1 | 354.6 | 94.1806 | 94.1868 | 26.5597 | 26.5614
1170 | feeder2_line142 | 2 | 354.6 | 94.0007 | 93.9935 | 26.5089 | 26.5069
1170 | feeder2_line142 | 3 | 354.6 | 95.1309 | 95.1325 | 26.8277 | 26.8281
1170 | feeder2_line143 | 1 | 99 | 8.2575e-07 | 1.6785e-06 | 8.3409e-07 | 1.6954e-06
1170 | feeder2_line143 | 2 | 99 | 3.1736 | 3.1736 | 3.2057 | 3.2056
1170 | feeder2_line143 | 3 | 99 | 8.252e-07 | 1.6775e-06 | 8.3354e-07 | 1.6944e-06
1170 | feeder2_line144 | 1 | 354.6 | 94.1805 | 94.1868 | 26.5596 | 26.5614
1170 | feeder2_line144 | 2 | 354.6 | 93.8182 | 93.811 | 26.4575 | 26.4555
1170 | feeder2_line144 | 3 | 354.6 | 95.1307 | 95.1325 | 26.8276 | 26.8281
1170 | feeder2_line145 | 1 | 99 | 2.4456e-08 | 4.7062e-07 | 2.4703e-08 | 4.7537e-07
1170 | feeder2_line145 | 2 | 99 | 0.75712 | 0.7571 | 0.76477 | 0.76475
1170 | feeder2_line145 | 3 | 99 | 2.4534e-08 | 4.7033e-07 | 2.4782e-08 | 4.7508e-07
1170 | feeder2_line146 | 1 | 354.6 | 94.1805 | 94.1868 | 26.5596 | 26.5614
1170 | feeder2_line146 | 2 | 354.6 | 94.0296 | 94.0224 | 26.5171 | 26.5151
1170 | feeder2_line146 | 3 | 354.6 | 95.1307 | 95.1325 | 26.8276 | 26.8281
1170 | feeder2_line147 | 1 | 99 | 0.083145 | 0.083145 | 0.083985 | 0.083985
1170 | feeder2_line147 | 2 | 99 | 1.126e-06 | 2.1873e-06 | 1.1373e-06 | 2.2094e-06
1170 | feeder2_line147 | 3 | 99 | 1.1165e-06 | 2.1692e-06 | 1.1278e-06 | 2.1911e-06
1170 | feeder2_line148 | 1 | 99 | 0.8236 | 0.8236 | 0.83192 | 0.83192
1170 | feeder2_line148 | 2 | 99 | 5.8704e-07 | 1.4657e-06 | 5.9297e-07 | 1.4805e-06
1170 | feeder2_line148 | 3 | 99 | 5.828e-07 | 1.4535e-06 | 5.8868e-07 | 1.4682e-06
1170 | feeder2_line149 | 1 | 354.6 | 94.4122 | 94.4184 | 26.625 | 26.6267
1170 | feeder2_line149 | 2 | 354.6 | 94.0298 | 94.0224 | 26.5171 | 26.5151
1170 | feeder2_line149 | 3 | 354.6 | 95.1308 | 95.1325 | 26.8276 | 26.8281
1170 | feeder2_line150 | 1 | 354.6 | 94.4122 | 94.4184 | 26.625 | 26.6267
1170 | feeder2_line150 | 2 | 354.6 | 94.4759 | 94.4685 | 26.6429 | 26.6409
1170 | feeder2_line150 | 3 | 354.6 | 95.1308 | 95.1325 | 26.8277 | 26.8281
1170 | feeder2_line151 | 1 | 99 | 9.4649e-06 | 1.7265e-06 | 9.5605e-06 | 1.744e-06
1170 | feeder2_line151 | 2 | 99 | 1.5128 | 1.5128 | 1.528 | 1.5281
1170 | feeder2_line151 | 3 | 99 | 9.4449e-06 | 1.7255e-06 | 9.5403e-06 | 1.7429e-06
1170 | feeder2_line152 | 1 | 354.6 | 1.3652e-11 | 1.1503e-06 | 3.85e-12 | 3.244e-07
1170 | feeder2_line152 | 2 | 354.6 | 6.9467e-12 | 1.1586e-06 | 1.959e-12 | 3.2674e-07
1170 | feeder2_line152 | 3 | 354.6 | 2.0604 | 2.0604 | 0.58105 | 0.58106
1170 | feeder2_line153 | 1 | 99 | 1.8983 | 1.8983 | 1.9174 | 1.9174
1170 | feeder2_line153 | 2 | 99 | 4.8081e-08 | 5.7993e-07 | 4.8566e-08 | 5.8579e-07
1170 | feeder2_line153 | 3 | 99 | 4.9044e-08 | 5.7509e-07 | 4.9539e-08 | 5.809e-07
1170 | feeder2_line154 | 1 | 99 | 5.5834e-07 | 8.5625e-07 | 5.6398e-07 | 8.649e-07
1170 | feeder2_line154 | 2 | 99 | 5.6276e-07 | 8.6296e-07 | 5.6845e-07 | 8.7168e-07
1170 | feeder2_line154 | 3 | 99 | 0.73803 | 0.73803 | 0.74549 | 0.74549
1170 | feeder2_line155 | 1 | 99 | 94.9395 | 94.9457 | 95.8985 | 95.9048
1170 | feeder2_line155 | 2 | 99 | 94.4759 | 94.4685 | 95.4302 | 95.4227
1170 | feeder2_line155 | 3 | 99 | 95.6797 | 95.6814 | 96.6461 | 96.6479
1170 | feeder2_line156 | 1 | 99 | 5.829e-07 | 1.1274e-06 | 5.8879e-07 | 1.1388e-06
1170 | feeder2_line156 | 2 | 99 | 1.4219 | 1.4219 | 1.4363 | 1.4363
1170 | feeder2_line156 | 3 | 99 | 5.8265e-07 | 1.1267e-06 | 5.8854e-07 | 1.1381e-06
1170 | feeder2_line157 | 1 | 99 | 2.4455e-08 | 2.4475e-07 | 2.4702e-08 | 2.4722e-07
1170 | feeder2_line157 | 2 | 99 | 0.091036 | 0.091031 | 0.091955 | 0.09195
1170 | feeder2_line157 | 3 | 99 | 2.4527e-08 | 2.4461e-07 | 2.4774e-08 | 2.4708e-07
1200 | feeder2_line1 | 1 | 354.6 | 119.1338 | 119.126 | 33.5967 | 33.5945
1200 | feeder2_line1 | 2 | 354.6 | 130.3422 | 130.3506 | 36.7575 | 36.7599
1200 | feeder2_line1 | 3 | 354.6 | 137.303 | 137.3052 | 38.7205 | 38.7212
1200 | feeder2_line2 | 1 | 354.6 | 115.1702 | 115.1621 | 32.4789 | 32.4766
1200 | feeder2_line2 | 2 | 354.6 | 130.3421 | 130.3506 | 36.7575 | 36.7599
1200 | feeder2_line2 | 3 | 354.6 | 137.303 | 137.3052 | 38.7205 | 38.7212
1200 | feeder2_line3 | 1 | 80.1 | 5.9651 | 5.9651 | 7.4471 | 7.4471
1200 | feeder2_line3 | 2 | 80.1 | 5.6587e-07 | 1.0457e-06 | 7.0645e-07 | 1.3055e-06
1200 | feeder2_line3 | 3 | 80.1 | 5.6524e-07 | 1.0446e-06 | 7.0566e-07 | 1.3041e-06
1200 | feeder2_line4 | 1 | 354.6 | 115.1701 | 115.1621 | 32.4789 | 32.4766
1200 | feeder2_line4 | 2 | 354.6 | 128.5504 | 128.5592 | 36.2522 | 36.2547
1200 | feeder2_line4 | 3 | 354.6 | 137.3028 | 137.3052 | 38.7205 | 38.7212
1200 | feeder2_line5 | 1 | 80.1 | 5.6642e-07 | 9.8835e-07 | 7.0714e-07 | 1.2339e-06
1200 | feeder2_line5 | 2 | 80.1 | 1.9783 | 1.9783 | 2.4698 | 2.4698
1200 | feeder2_line5 | 3 | 80.1 | 5.6514e-07 | 9.8613e-07 | 7.0554e-07 | 1.2311e-06
1200 | feeder2_line6 | 1 | 80.1 | 5.6631e-07 | 1.1624e-06 | 7.07e-07 | 1.4512e-06
1200 | feeder2_line6 | 2 | 80.1 | 5.6563e-07 | 1.161e-06 | 7.0615e-07 | 1.4495e-06
1200 | feeder2_line6 | 3 | 80.1 | 1.0414 | 1.0414 | 1.3001 | 1.3001
1200 | feeder2_line7 | 1 | 354.6 | 115.1701 | 115.1621 | 32.4789 | 32.4766
1200 | feeder2_line7 | 2 | 354.6 | 128.5503 | 128.5592 | 36.2522 | 36.2547
1200 | feeder2_line7 | 3 | 354.6 | 136.7195 | 136.7219 | 38.556 | 38.5567
1200 | feeder2_line8 | 1 | 80.1 | 0.84029 | 0.8403 | 1.0491 | 1.0491
1200 | feeder2_line8 | 2 | 80.1 | 5.6518e-07 | 1.1186e-06 | 7.0559e-07 | 1.3965e-06
1200 | feeder2_line8 | 3 | 80.1 | 5.6441e-07 | 1.1171e-06 | 7.0463e-07 | 1.3946e-06
1200 | feeder2_line9 | 1 | 354.6 | 114.8633 | 114.8554 | 32.3924 | 32.3901
1200 | feeder2_line9 | 2 | 354.6 | 128.5502 | 128.5592 | 36.2522 | 36.2547
1200 | feeder2_line9 | 3 | 354.6 | 136.7193 | 136.7219 | 38.5559 | 38.5567
1200 | feeder2_line10 | 1 | 80.1 | 8.3668e-07 | 1.479e-06 | 1.0445e-06 | 1.8464e-06
1200 | feeder2_line10 | 2 | 80.1 | 0.84071 | 0.84071 | 1.0496 | 1.0496
1200 | feeder2_line10 | 3 | 80.1 | 8.3419e-07 | 1.4748e-06 | 1.0414e-06 | 1.8412e-06
1200 | feeder2_line11 | 1 | 354.6 | 114.8634 | 114.8554 | 32.3924 | 32.3901
1200 | feeder2_line11 | 2 | 354.6 | 128.1468 | 128.1559 | 36.1384 | 36.141
1200 | feeder2_line11 | 3 | 354.6 | 136.7194 | 136.7219 | 38.556 | 38.5567
1200 | feeder2_line12 | 1 | 80.1 | 5.4133e-07 | 9.8081e-07 | 6.7582e-07 | 1.2245e-06
1200 | feeder2_line12 | 2 | 80.1 | 5.4032e-07 | 9.7931e-07 | 6.7456e-07 | 1.2226e-06
1200 | feeder2_line12 | 3 | 80.1 | 9.4689 | 9.4691 | 11.8214 | 11.8215
1200 | feeder2_line13 | 1 | 354.6 | 114.8635 | 114.8554 | 32.3924 | 32.3901
1200 | feeder2_line13 | 2 | 354.6 | 128.1469 | 128.1559 | 36.1384 | 36.141
1200 | feeder2_line13 | 3 | 354.6 | 130.766 | 130.7678 | 36.877 | 36.8775
1200 | feeder2_line14 | 1 | 80.1 | 1.6813 | 1.6813 | 2.099 | 2.099
1200 | feeder2_line14 | 2 | 80.1 | 2.9469e-07 | 6.3841e-07 | 3.679e-07 | 7.9702e-07
1200 | feeder2_line14 | 3 | 80.1 | 2.9427e-07 | 6.3748e-07 | 3.6738e-07 | 7.9585e-07
1200 | feeder2_line15 | 1 | 354.6 | 114.1217 | 114.1135 | 32.1832 | 32.1809
1200 | feeder2_line15 | 2 | 354.6 | 128.1469 | 128.1559 | 36.1384 | 36.141
1200 | feeder2_line15 | 3 | 354.6 | 130.766 | 130.7678 | 36.877 | 36.8775
1200 | feeder2_line16 | 1 | 80.1 | 5.655e-07 | 1.0188e-06 | 7.0599e-07 | 1.2719e-06
1200 | feeder2_line16 | 2 | 80.1 | 11.0937 | 11.0936 | 13.8498 | 13.8497
1200 | feeder2_line16 | 3 | 80.1 | 5.6364e-07 | 1.0155e-06 | 7.0367e-07 | 1.2677e-06
1200 | feeder2_line17 | 1 | 354.6 | 114.1217 | 114.1135 | 32.1832 | 32.1809
1200 | feeder2_line17 | 2 | 354.6 | 121.7578 | 121.7684 | 34.3367 | 34.3397
1200 | feeder2_line17 | 3 | 354.6 | 130.766 | 130.7678 | 36.877 | 36.8775
1200 | feeder2_line18 | 1 | 80.1 | 5.4029e-07 | 7.2816e-07 | 6.7452e-07 | 9.0907e-07
1200 | feeder2_line18 | 2 | 80.1 | 5.3896e-07 | 7.267e-07 | 6.7286e-07 | 9.0724e-07
1200 | feeder2_line18 | 3 | 80.1 | 6.6754 | 6.6755 | 8.3339 | 8.334
1200 | feeder2_line19 | 1 | 354.6 | 114.1217 | 114.1135 | 32.1832 | 32.1809
1200 | feeder2_line19 | 2 | 354.6 | 121.7578 | 121.7684 | 34.3367 | 34.3397
1200 | feeder2_line19 | 3 | 354.6 | 126.1277 | 126.1291 | 35.569 | 35.5694
1200 | feeder2_line20 | 1 | 99 | 5.4e-07 | 8.7253e-07 | 5.4545e-07 | 8.8135e-07
1200 | feeder2_line20 | 2 | 99 | 5.386e-07 | 8.7068e-07 | 5.4404e-07 | 8.7948e-07
1200 | feeder2_line20 | 3 | 99 | 1.3358 | 1.3358 | 1.3493 | 1.3493
1200 | feeder2_line21 | 1 | 354.6 | 114.1217 | 114.1135 | 32.1832 | 32.1809
1200 | feeder2_line21 | 2 | 354.6 | 121.7577 | 121.7684 | 34.3366 | 34.3397
1200 | feeder2_line21 | 3 | 354.6 | 125.3796 | 125.381 | 35.358 | 35.3584
1200 | feeder2_line22 | 1 | 99 | 5.6415e-07 | 9.9991e-07 | 5.6985e-07 | 1.01e-06
1200 | feeder2_line22 | 2 | 99 | 1.4276 | 1.4276 | 1.442 | 1.442
1200 | feeder2_line22 | 3 | 99 | 5.617e-07 | 9.956e-07 | 5.6737e-07 | 1.0057e-06
1200 | feeder2_line23 | 1 | 99 | 5.6416e-07 | 9.36e-07 | 5.6985e-07 | 9.4545e-07
1200 | feeder2_line23 | 2 | 99 | 5.6289e-07 | 9.3394e-07 | 5.6858e-07 | 9.4337e-07
1200 | feeder2_line23 | 3 | 99 | 3.4867 | 3.4868 | 3.522 | 3.5221
1200 | feeder2_line24 | 1 | 354.6 | 114.1217 | 114.1135 | 32.1832 | 32.1809
1200 | feeder2_line24 | 2 | 354.6 | 121.0334 | 121.0443 | 34.1324 | 34.1354
1200 | feeder2_line24 | 3 | 354.6 | 121.9852 | 121.9864 | 34.4008 | 34.4011
1200 | feeder2_line25 | 1 | 99 | 1.4284 | 1.4284 | 1.4428 | 1.4428
1200 | feeder2_line25 | 2 | 99 | 4.902e-08 | 6.785e-07 | 4.9515e-08 | 6.8536e-07
1200 | feeder2_line25 | 3 | 99 | 4.9092e-08 | 6.7702e-07 | 4.9588e-08 | 6.8386e-07
1200 | feeder2_line26 | 1 | 99 | 0.87383 | 0.87383 | 0.88266 | 0.88266
1200 | feeder2_line26 | 2 | 99 | 5.3798e-07 | 8.4062e-07 | 5.4341e-07 | 8.4911e-07
1200 | feeder2_line26 | 3 | 99 | 5.3671e-07 | 8.3879e-07 | 5.4213e-07 | 8.4726e-07
1200 | feeder2_line27 | 1 | 354.6 | 113.0775 | 113.0692 | 31.8888 | 31.8864
1200 | feeder2_line27 | 2 | 354.6 | 121.0334 | 121.0443 | 34.1324 | 34.1354
1200 | feeder2_line27 | 3 | 354.6 | 121.9852 | 121.9864 | 34.4008 | 34.4011
1200 | feeder2_line28 | 1 | 99 | 2.5007e-06 | 6.9872e-07 | 2.526e-06 | 7.0578e-07
1200 | feeder2_line28 | 2 | 99 | 1.2494 | 1.2494 | 1.262 | 1.262
1200 | feeder2_line28 | 3 | 99 | 2.4838e-06 | 6.9535e-07 | 2.5089e-06 | 7.0238e-07
1200 | feeder2_line29 | 1 | 354.6 | 113.0775 | 113.0692 | 31.8888 | 31.8864
1200 | feeder2_line29 | 2 | 354.6 | 119.7921 | 119.803 | 33.7823 | 33.7854
1200 | feeder2_line29 | 3 | 354.6 | 121.9852 | 121.9864 | 34.4008 | 34.4011
1200 | feeder2_line30 | 1 | 266.4 | 6.8512 | 6.8515 | 2.5718 | 2.5719
1200 | feeder2_line30 | 2 | 266.4 | 3.7327 | 3.7324 | 1.4011 | 1.401
1200 | feeder2_line30 | 3 | 266.4 | 25.5846 | 25.5849 | 9.6038 | 9.6039
1200 | feeder2_line31 | 1 | 354.6 | 107.6925 | 107.683 | 30.3701 | 30.3674
1200 | feeder2_line31 | 2 | 354.6 | 118.1356 | 118.1467 | 33.3152 | 33.3183
1200 | feeder2_line31 | 3 | 354.6 | 108.9777 | 108.9761 | 30.7326 | 30.7321
1200 | feeder2_line32 | 1 | 354.6 | 107.6924 | 107.683 | 30.3701 | 30.3674
1200 | feeder2_line32 | 2 | 354.6 | 117.0604 | 117.0718 | 33.0119 | 33.0152
1200 | feeder2_line32 | 3 | 354.6 | 108.9777 | 108.9761 | 30.7326 | 30.7321
1200 | feeder2_line33 | 1 | 99 | 4.8399e-08 | 6.727e-07 | 4.8888e-08 | 6.7949e-07
1200 | feeder2_line33 | 2 | 99 | 2.1426 | 2.1426 | 2.1642 | 2.1642
1200 | feeder2_line33 | 3 | 99 | 4.8941e-08 | 6.6914e-07 | 4.9435e-08 | 6.7589e-07
1200 | feeder2_line34 | 1 | 354.6 | 107.6924 | 107.683 | 30.3701 | 30.3674
1200 | feeder2_line34 | 2 | 354.6 | 117.0604 | 117.0718 | 33.0119 | 33.0152
1200 | feeder2_line34 | 3 | 354.6 | 108.3611 | 108.3594 | 30.5587 | 30.5582
1200 | feeder2_line35 | 1 | 99 | 2.9305e-07 | 7.4467e-07 | 2.9601e-07 | 7.522e-07
1200 | feeder2_line35 | 2 | 99 | 2.9227e-07 | 7.4232e-07 | 2.9522e-07 | 7.4982e-07
1200 | feeder2_line35 | 3 | 99 | 1.6431 | 1.6431 | 1.6597 | 1.6597
1200 | feeder2_line36 | 1 | 354.6 | 102.5231 | 102.5127 | 28.9123 | 28.9094
1200 | feeder2_line36 | 2 | 354.6 | 117.0604 | 117.0718 | 33.012 | 33.0152
1200 | feeder2_line36 | 3 | 354.6 | 108.3611 | 108.3594 | 30.5587 | 30.5582
1200 | feeder2_line37 | 1 | 99 | 10.9923 | 10.9924 | 11.1033 | 11.1034
1200 | feeder2_line37 | 2 | 99 | 2.9213e-07 | 8.2095e-07 | 2.9508e-07 | 8.2925e-07
1200 | feeder2_line37 | 3 | 99 | 2.9157e-07 | 8.1929e-07 | 2.9451e-07 | 8.2756e-07
1200 | feeder2_line38 | 1 | 99 | 3.1755e-07 | 7.6112e-07 | 3.2076e-07 | 7.6881e-07
1200 | feeder2_line38 | 2 | 99 | 0.93426 | 0.93426 | 0.9437 | 0.94369
1200 | feeder2_line38 | 3 | 99 | 3.1643e-07 | 7.5698e-07 | 3.1963e-07 | 7.6463e-07
1200 | feeder2_line39 | 1 | 266.4 | 6.8512 | 6.8515 | 2.5718 | 2.5719
1200 | feeder2_line39 | 2 | 266.4 | 2.8069 | 2.8067 | 1.0536 | 1.0535
1200 | feeder2_line39 | 3 | 266.4 | 25.5846 | 25.5849 | 9.6038 | 9.6039
1200 | feeder2_line40 | 1 | 354.6 | 102.0851 | 102.0747 | 28.7888 | 28.7859
1200 | feeder2_line40 | 2 | 354.6 | 117.0603 | 117.0718 | 33.0119 | 33.0152
1200 | feeder2_line40 | 3 | 354.6 | 108.361 | 108.3594 | 30.5587 | 30.5582
1200 | feeder2_line41 | 1 | 99 | 1.4274 | 1.4274 | 1.4418 | 1.4418
1200 | feeder2_line41 | 2 | 99 | 4.8849e-08 | 7.1718e-07 | 4.9342e-08 | 7.2443e-07
1200 | feeder2_line41 | 3 | 99 | 4.8884e-08 | 7.1577e-07 | 4.9378e-08 | 7.23e-07
1200 | feeder2_line42 | 1 | 99 | 2.9333e-07 | 7.3463e-07 | 2.9629e-07 | 7.4205e-07
1200 | feeder2_line42 | 2 | 99 | 2.9264e-07 | 7.3259e-07 | 2.956e-07 | 7.3999e-07
1200 | feeder2_line42 | 3 | 99 | 2.263 | 2.263 | 2.2859 | 2.2858
1200 | feeder2_line43 | 1 | 266.4 | 6.8512 | 6.8515 | 2.5718 | 2.5719
1200 | feeder2_line43 | 2 | 266.4 | 2.8068 | 2.8067 | 1.0536 | 1.0535
1200 | feeder2_line43 | 3 | 266.4 | 23.4949 | 23.4953 | 8.8194 | 8.8196
1200 | feeder2_line44 | 1 | 354.6 | 102.0851 | 102.0747 | 28.7888 | 28.7859
1200 | feeder2_line44 | 2 | 354.6 | 117.0603 | 117.0718 | 33.0119 | 33.0152
1200 | feeder2_line44 | 3 | 354.6 | 107.8789 | 107.8773 | 30.4227 | 30.4222
1200 | feeder2_line45 | 1 | 99 | 4.8328e-08 | 5.6737e-07 | 4.8816e-08 | 5.731e-07
1200 | feeder2_line45 | 2 | 99 | 4.8838e-08 | 5.6542e-07 | 4.9332e-08 | 5.7113e-07
1200 | feeder2_line45 | 3 | 99 | 1.3321 | 1.332 | 1.3455 | 1.3455
1200 | feeder2_line46 | 1 | 99 | 5.6241e-07 | 1.3317e-06 | 5.6809e-07 | 1.3452e-06
1200 | feeder2_line46 | 2 | 99 | 5.6084e-07 | 1.328e-06 | 5.665e-07 | 1.3415e-06
1200 | feeder2_line46 | 3 | 99 | 12.4371 | 12.4375 | 12.5627 | 12.5631
1200 | feeder2_line47 | 1 | 266.4 | 6.8513 | 6.8515 | 2.5718 | 2.5719
1200 | feeder2_line47 | 2 | 266.4 | 2.8068 | 2.8067 | 1.0536 | 1.0535
1200 | feeder2_line47 | 3 | 266.4 | 11.0583 | 11.0584 | 4.151 | 4.151
1200 | feeder2_line48 | 1 | 99 | 2.6823 | 2.6823 | 2.7094 | 2.7094
1200 | feeder2_line48 | 2 | 99 | 4.8887e-08 | 7.1504e-07 | 4.9381e-08 | 7.2227e-07
1200 | feeder2_line48 | 3 | 99 | 4.9003e-08 | 7.1293e-07 | 4.9498e-08 | 7.2013e-07
1200 | feeder2_line49 | 1 | 266.4 | 4.1962 | 4.1966 | 1.5752 | 1.5753
1200 | feeder2_line49 | 2 | 266.4 | 2.8068 | 2.8067 | 1.0536 | 1.0535
1200 | feeder2_line49 | 3 | 266.4 | 11.0583 | 11.0584 | 4.151 | 4.151
1200 | feeder2_line50 | 1 | 99 | 5.6242e-07 | 1.212e-06 | 5.681e-07 | 1.2242e-06
1200 | feeder2_line50 | 2 | 99 | 1.0455 | 1.0456 | 1.0561 | 1.0562
1200 | feeder2_line50 | 3 | 99 | 5.5917e-07 | 1.205e-06 | 5.6482e-07 | 1.2172e-06
1200 | feeder2_line51 | 1 | 99 | 2.1935 | 2.1937 | 2.2157 | 2.2159
1200 | feeder2_line51 | 2 | 99 | 5.6085e-07 | 1.3121e-06 | 5.6651e-07 | 1.3253e-06
1200 | feeder2_line51 | 3 | 99 | 5.5917e-07 | 1.3082e-06 | 5.6481e-07 | 1.3214e-06
1200 | feeder2_line52 | 1 | 266.4 | 2.4102 | 2.4103 | 0.90472 | 0.90476
1200 | feeder2_line52 | 2 | 266.4 | 1.7651 | 1.765 | 0.66258 | 0.66254
1200 | feeder2_line52 | 3 | 266.4 | 11.0582 | 11.0584 | 4.151 | 4.151
1200 | feeder2_line53 | 1 | 99 | 5.3822e-07 | 7.3968e-07 | 5.4365e-07 | 7.4715e-07
1200 | feeder2_line53 | 2 | 99 | 1.765 | 1.765 | 1.7828 | 1.7828
1200 | feeder2_line53 | 3 | 99 | 5.3466e-07 | 7.3543e-07 | 5.4006e-07 | 7.4286e-07
1200 | feeder2_line54 | 1 | 266.4 | 2.4102 | 2.4103 | 0.90471 | 0.90476
1200 | feeder2_line54 | 2 | 266.4 | 8.365e-05 | 4.5252e-06 | 3.14e-05 | 1.6986e-06
1200 | feeder2_line54 | 3 | 266.4 | 11.058 | 11.0584 | 4.1509 | 4.151
1200 | feeder2_line55 | 1 | 99 | 4.7731 | 4.7731 | 4.8213 | 4.8213
1200 | feeder2_line55 | 2 | 99 | 4.8818e-08 | 7.1144e-07 | 4.9311e-08 | 7.1862e-07
1200 | feeder2_line55 | 3 | 99 | 4.8807e-08 | 7.1028e-07 | 4.93e-08 | 7.1745e-07
1200 | feeder2_line56 | 1 | 354.6 | 98.9427 | 98.9321 | 27.9026 | 27.8996
1200 | feeder2_line56 | 2 | 354.6 | 117.0603 | 117.0718 | 33.0119 | 33.0152
1200 | feeder2_line56 | 3 | 354.6 | 107.8789 | 107.8773 | 30.4227 | 30.4222
1200 | feeder2_line57 | 1 | 99 | 7.2606e-07 | 1.5151e-06 | 7.3339e-07 | 1.5304e-06
1200 | feeder2_line57 | 2 | 99 | 7.3317e-07 | 1.5109e-06 | 7.4058e-07 | 1.5262e-06
1200 | feeder2_line57 | 3 | 99 | 11.0581 | 11.0584 | 11.1698 | 11.1701
1200 | feeder2_line58 | 1 | 266.4 | 2.4102 | 2.4103 | 0.90474 | 0.90476
1200 | feeder2_line58 | 2 | 266.4 | 1.8545e-05 | 2.6273e-06 | 6.9612e-06 | 9.8621e-07
1200 | feeder2_line58 | 3 | 266.4 | 1.8464e-05 | 2.6194e-06 | 6.9309e-06 | 9.8328e-07
1200 | feeder2_line59 | 1 | 99 | 4.8402e-08 | 5.2666e-07 | 4.8891e-08 | 5.3198e-07
1200 | feeder2_line59 | 2 | 99 | 4.8877e-08 | 5.2521e-07 | 4.9371e-08 | 5.3052e-07
1200 | feeder2_line59 | 3 | 99 | 1.675 | 1.675 | 1.6919 | 1.6919
1200 | feeder2_line60 | 1 | 99 | 2.933e-07 | 7.9593e-07 | 2.9626e-07 | 8.0397e-07
1200 | feeder2_line60 | 2 | 99 | 2.9264e-07 | 7.9375e-07 | 2.9559e-07 | 8.0177e-07
1200 | feeder2_line60 | 3 | 99 | 9.3831 | 9.3833 | 9.4778 | 9.4781
1200 | feeder2_line61 | 1 | 266.4 | 1.7616 | 1.7617 | 0.66125 | 0.66131
1200 | feeder2_line61 | 2 | 266.4 | 4.0339 | 4.0342 | 1.5142 | 1.5143
1200 | feeder2_line61 | 3 | 266.4 | 2.0643 | 2.0645 | 0.7749 | 0.77495
1200 | feeder2_line62 | 1 | 354.6 | 98.5241 | 98.5134 | 27.7846 | 27.7815
1200 | feeder2_line62 | 2 | 354.6 | 113.7645 | 113.7761 | 32.0825 | 32.0858
1200 | feeder2_line62 | 3 | 354.6 | 106.6306 | 106.6286 | 30.0707 | 30.0701
1200 | feeder2_line63 | 1 | 99 | 1.4003 | 1.4004 | 1.4145 | 1.4145
1200 | feeder2_line63 | 2 | 99 | 5.6086e-07 | 1.1934e-06 | 5.6652e-07 | 1.2055e-06
1200 | feeder2_line63 | 3 | 99 | 5.5913e-07 | 1.1898e-06 | 5.6478e-07 | 1.2018e-06
1200 | feeder2_line64 | 1 | 99 | 1.0103 | 1.0102 | 1.0205 | 1.0205
1200 | feeder2_line64 | 2 | 99 | 1.2611e-12 | 3.1436e-07 | 1.2738e-12 | 3.1754e-07
1200 | feeder2_line64 | 3 | 99 | 6.8852e-12 | 3.1341e-07 | 6.9547e-12 | 3.1658e-07
1200 | feeder2_line65 | 1 | 99 | 4.8147e-08 | 6.2657e-07 | 4.8633e-08 | 6.329e-07
1200 | feeder2_line65 | 2 | 99 | 1.9847 | 1.9847 | 2.0048 | 2.0048
1200 | feeder2_line65 | 3 | 99 | 4.873e-08 | 6.228e-07 | 4.9222e-08 | 6.2909e-07
1200 | feeder2_line66 | 1 | 354.6 | 98.5241 | 98.5134 | 27.7846 | 27.7815
1200 | feeder2_line66 | 2 | 354.6 | 112.1425 | 112.1543 | 31.6251 | 31.6284
1200 | feeder2_line66 | 3 | 354.6 | 106.6306 | 106.6286 | 30.0707 | 30.0701
1200 | feeder2_line67 | 1 | 99 | 2.4107e-08 | 3.5443e-07 | 2.435e-08 | 3.5801e-07
1200 | feeder2_line67 | 2 | 99 | 2.4405e-08 | 3.5287e-07 | 2.4651e-08 | 3.5644e-07
1200 | feeder2_line67 | 3 | 99 | 1.4248 | 1.4249 | 1.4392 | 1.4392
1200 | feeder2_line68 | 1 | 266.4 | 1.7616 | 1.7617 | 0.66127 | 0.66131
1200 | feeder2_line68 | 2 | 266.4 | 4.034 | 4.0342 | 1.5143 | 1.5143
1200 | feeder2_line68 | 3 | 266.4 | 0.83556 | 0.83565 | 0.31365 | 0.31368
1200 | feeder2_line69 | 1 | 99 | 5.7065 | 5.7064 | 5.7641 | 5.764
1200 | feeder2_line69 | 2 | 99 | 2.4703e-06 | 6.4707e-07 | 2.4953e-06 | 6.536e-07
1200 | feeder2_line69 | 3 | 99 | 2.4676e-06 | 6.4633e-07 | 2.4926e-06 | 6.5286e-07
1200 | feeder2_line70 | 1 | 354.6 | 96.9315 | 96.9204 | 27.3354 | 27.3323
1200 | feeder2_line70 | 2 | 354.6 | 112.1426 | 112.1543 | 31.6251 | 31.6284
1200 | feeder2_line70 | 3 | 354.6 | 106.6307 | 106.6286 | 30.0707 | 30.0701
1200 | feeder2_line71 | 1 | 99 | 4.8101e-08 | 6.9869e-07 | 4.8587e-08 | 7.0575e-07
1200 | feeder2_line71 | 2 | 99 | 2.7412 | 2.7413 | 2.7688 | 2.769
1200 | feeder2_line71 | 3 | 99 | 4.8698e-08 | 6.9436e-07 | 4.919e-08 | 7.0137e-07
1200 | feeder2_line72 | 1 | 354.6 | 96.9315 | 96.9204 | 27.3354 | 27.3323
1200 | feeder2_line72 | 2 | 354.6 | 110.9693 | 110.9814 | 31.2942 | 31.2976
1200 | feeder2_line72 | 3 | 354.6 | 106.6307 | 106.6286 | 30.0707 | 30.0701
1200 | feeder2_line73 | 1 | 99 | 5.8484e-07 | 1.5005e-06 | 5.9075e-07 | 1.5157e-06
1200 | feeder2_line73 | 2 | 99 | 2.1449 | 2.1449 | 2.1666 | 2.1666
1200 | feeder2_line73 | 3 | 99 | 5.8184e-07 | 1.4918e-06 | 5.8772e-07 | 1.5069e-06
1200 | feeder2_line74 | 1 | 99 | 4.8204e-08 | 4.4754e-07 | 4.8691e-08 | 4.5206e-07
1200 | feeder2_line74 | 2 | 99 | 0.83586 | 0.83591 | 0.8443 | 0.84435
1200 | feeder2_line74 | 3 | 99 | 4.8771e-08 | 4.4495e-07 | 4.9264e-08 | 4.4944e-07
1200 | feeder2_line75 | 1 | 266.4 | 1.7617 | 1.7617 | 0.6613 | 0.66131
1200 | feeder2_line75 | 2 | 266.4 | 1.4659 | 1.4659 | 0.55025 | 0.55025
1200 | feeder2_line75 | 3 | 266.4 | 0.83564 | 0.83565 | 0.31368 | 0.31368
1200 | feeder2_line76 | 1 | 99 | 1.7617 | 1.7617 | 1.7795 | 1.7795
1200 | feeder2_line76 | 2 | 99 | 8.2513e-07 | 1.541e-06 | 8.3347e-07 | 1.5566e-06
1200 | feeder2_line76 | 3 | 99 | 8.24e-07 | 1.5389e-06 | 8.3233e-07 | 1.5544e-06
1200 | feeder2_line77 | 1 | 99 | 2.4097e-08 | 5.6241e-07 | 2.4341e-08 | 5.6809e-07
1200 | feeder2_line77 | 2 | 99 | 2.4408e-08 | 5.5992e-07 | 2.4655e-08 | 5.6557e-07
1200 | feeder2_line77 | 3 | 99 | 0.83568 | 0.83565 | 0.84412 | 0.84409
1200 | feeder2_line78 | 1 | 266.4 | 7.6767e-12 | 9.324e-07 | 2.8817e-12 | 3.5e-07
1200 | feeder2_line78 | 2 | 266.4 | 1.4659 | 1.4659 | 0.55026 | 0.55025
1200 | feeder2_line78 | 3 | 266.4 | 2.0778e-11 | 9.2752e-07 | 7.7995e-12 | 3.4817e-07
1200 | feeder2_line79 | 1 | 354.6 | 13.7489 | 13.7482 | 3.8773 | 3.8771
1200 | feeder2_line79 | 2 | 354.6 | 17.9058 | 17.9052 | 5.0496 | 5.0494
1200 | feeder2_line79 | 3 | 354.6 | 23.0306 | 23.0308 | 6.4948 | 6.4949
1200 | feeder2_line80 | 1 | 354.6 | 94.7939 | 94.7826 | 26.7326 | 26.7294
1200 | feeder2_line80 | 2 | 354.6 | 102.7009 | 102.7154 | 28.9625 | 28.9666
1200 | feeder2_line80 | 3 | 354.6 | 99.131 | 99.1266 | 27.9557 | 27.9545
1200 | feeder2_line81 | 1 | 354.6 | 94.7937 | 94.7826 | 26.7326 | 26.7294
1200 | feeder2_line81 | 2 | 354.6 | 102.7007 | 102.7155 | 28.9624 | 28.9666
1200 | feeder2_line81 | 3 | 354.6 | 98.1341 | 98.1297 | 27.6746 | 27.6733
1200 | feeder2_line82 | 1 | 354.6 | 1.948e-11 | 7.1571e-07 | 5.4936e-12 | 2.0184e-07
1200 | feeder2_line82 | 2 | 354.6 | 1.8242e-11 | 7.1198e-07 | 5.1445e-12 | 2.0078e-07
1200 | feeder2_line82 | 3 | 354.6 | 1.6398 | 1.6398 | 0.46245 | 0.46243
1200 | feeder2_line83 | 1 | 354.6 | 94.7937 | 94.7826 | 26.7326 | 26.7294
1200 | feeder2_line83 | 2 | 354.6 | 101.4288 | 101.4438 | 28.6037 | 28.6079
1200 | feeder2_line83 | 3 | 354.6 | 98.1341 | 98.1297 | 27.6746 | 27.6733
1200 | feeder2_line84 | 1 | 354.6 | 8.4773e-12 | 1.2646e-06 | 2.3907e-12 | 3.5662e-07
1200 | feeder2_line84 | 2 | 354.6 | 2.4042 | 2.4043 | 0.67801 | 0.67804
1200 | feeder2_line84 | 3 | 354.6 | 1.2001e-11 | 1.2568e-06 | 3.3843e-12 | 3.5443e-07
1200 | feeder2_line85 | 1 | 99 | 0.93428 | 0.93427 | 0.94372 | 0.94371
1200 | feeder2_line85 | 2 | 99 | 4.8755e-08 | 4.4876e-07 | 4.9248e-08 | 4.533e-07
1200 | feeder2_line85 | 3 | 99 | 4.8623e-08 | 4.4844e-07 | 4.9114e-08 | 4.5297e-07
1200 | feeder2_line86 | 1 | 354.6 | 94.9072 | 94.8961 | 26.7646 | 26.7615
1200 | feeder2_line86 | 2 | 354.6 | 101.4287 | 101.4438 | 28.6037 | 28.6079
1200 | feeder2_line86 | 3 | 354.6 | 98.1341 | 98.1297 | 27.6746 | 27.6733
1200 | feeder2_line87 | 1 | 354.6 | 94.9072 | 94.8961 | 26.7646 | 26.7615
1200 | feeder2_line87 | 2 | 354.6 | 101.0539 | 101.0692 | 28.498 | 28.5023
1200 | feeder2_line87 | 3 | 354.6 | 95.7942 | 95.7895 | 27.0147 | 27.0134
1200 | feeder2_line88 | 1 | 354.6 | 0.00011246 | 3.2772e-06 | 3.1715e-05 | 9.2419e-07
1200 | feeder2_line88 | 2 | 354.6 | 1.3346 | 1.3348 | 0.37637 | 0.37643
1200 | feeder2_line88 | 3 | 354.6 | 4.6269 | 4.6267 | 1.3048 | 1.3048
1200 | feeder2_line89 | 1 | 354.6 | 94.9071 | 94.8961 | 26.7645 | 26.7615
1200 | feeder2_line89 | 2 | 354.6 | 99.8388 | 99.8541 | 28.1553 | 28.1597
1200 | feeder2_line89 | 3 | 354.6 | 95.7942 | 95.7895 | 27.0147 | 27.0134
1200 | feeder2_line90 | 1 | 354.6 | 0.00070682 | 1.9764e-06 | 0.00019933 | 5.5737e-07
1200 | feeder2_line90 | 2 | 354.6 | 2.4838 | 2.4844 | 0.70046 | 0.70061
1200 | feeder2_line90 | 3 | 354.6 | 0.00069979 | 1.9637e-06 | 0.00019735 | 5.5379e-07
1200 | feeder2_line91 | 1 | 354.6 | 94.9073 | 94.8961 | 26.7646 | 26.7615
1200 | feeder2_line91 | 2 | 354.6 | 99.839 | 99.8541 | 28.1554 | 28.1597
1200 | feeder2_line91 | 3 | 354.6 | 95.3569 | 95.3512 | 26.8914 | 26.8898
1200 | feeder2_line92 | 1 | 354.6 | 2.6815e-11 | 9.9696e-07 | 7.5621e-12 | 2.8115e-07
1200 | feeder2_line92 | 2 | 354.6 | 8.9522e-12 | 9.9111e-07 | 2.5246e-12 | 2.795e-07
1200 | feeder2_line92 | 3 | 354.6 | 9.3302 | 9.3307 | 2.6312 | 2.6313
1200 | feeder2_line93 | 1 | 99 | 2.3976e-08 | 3.3292e-07 | 2.4218e-08 | 3.3628e-07
1200 | feeder2_line93 | 2 | 99 | 2.4051 | 2.4052 | 2.4294 | 2.4295
1200 | feeder2_line93 | 3 | 99 | 2.4286e-08 | 3.3067e-07 | 2.4531e-08 | 3.3401e-07
1200 | feeder2_line94 | 1 | 354.6 | 2.3973e-06 | 1.6203e-06 | 6.7606e-07 | 4.5693e-07
1200 | feeder2_line94 | 2 | 354.6 | 0.08407 | 0.084166 | 0.023708 | 0.023735
1200 | feeder2_line94 | 3 | 354.6 | 2.4286e-06 | 1.6101e-06 | 6.8489e-07 | 4.5407e-07
1200 | feeder2_line95 | 1 | 99 | 3.4792e-06 | 2.5414e-06 | 3.5143e-06 | 2.5671e-06
1200 | feeder2_line95 | 2 | 99 | 1.3345 | 1.3348 | 1.348 | 1.3483
1200 | feeder2_line95 | 3 | 99 | 3.4467e-06 | 2.5243e-06 | 3.4815e-06 | 2.5498e-06
1200 | feeder2_line96 | 1 | 354.6 | 0.00011801 | 6.0573e-07 | 3.3281e-05 | 1.7082e-07
1200 | feeder2_line96 | 2 | 354.6 | 0.00011716 | 6.0232e-07 | 3.3039e-05 | 1.6986e-07
1200 | feeder2_line96 | 3 | 354.6 | 4.6268 | 4.6267 | 1.3048 | 1.3048
1200 | feeder2_line97 | 1 | 354.6 | 94.6711 | 94.6596 | 26.698 | 26.6948
1200 | feeder2_line97 | 2 | 354.6 | 99.8392 | 99.8541 | 28.1555 | 28.1597
1200 | feeder2_line97 | 3 | 354.6 | 95.3571 | 95.3512 | 26.8914 | 26.8898
1200 | feeder2_line98 | 1 | 354.6 | 1.9047 | 1.903 | 0.53714 | 0.53667
1200 | feeder2_line98 | 2 | 354.6 | 0.0016344 | 6.0007e-07 | 0.00046092 | 1.6922e-07
1200 | feeder2_line98 | 3 | 354.6 | 0.0016492 | 6.0163e-07 | 0.00046508 | 1.6967e-07
1200 | feeder2_line99 | 1 | 99 | 2.3986e-08 | 4.3552e-07 | 2.4228e-08 | 4.3991e-07
1200 | feeder2_line99 | 2 | 99 | 2.4377e-08 | 4.3285e-07 | 2.4623e-08 | 4.3722e-07
1200 | feeder2_line99 | 3 | 99 | 4.6268 | 4.6267 | 4.6735 | 4.6735
1200 | feeder2_line100 | 1 | 99 | 1.9031 | 1.903 | 1.9223 | 1.9222
1200 | feeder2_line100 | 2 | 99 | 2.4375e-08 | 5.9349e-07 | 2.4621e-08 | 5.9948e-07
1200 | feeder2_line100 | 3 | 99 | 2.4273e-08 | 5.9339e-07 | 2.4519e-08 | 5.9938e-07
1200 | feeder2_line101 | 1 | 354.6 | 0.083696 | 0.08324 | 0.023603 | 0.023474
1200 | feeder2_line101 | 2 | 354.6 | 17.9058 | 17.9052 | 5.0496 | 5.0494
1200 | feeder2_line101 | 3 | 354.6 | 23.0306 | 23.0308 | 6.4948 | 6.4949
1200 | feeder2_line102 | 1 | 99 | 13.6655 | 13.6653 | 13.8035 | 13.8034
1200 | feeder2_line102 | 2 | 99 | 2.2567e-06 | 8.5127e-07 | 2.2795e-06 | 8.5987e-07
1200 | feeder2_line102 | 3 | 99 | 2.2617e-06 | 8.5038e-07 | 2.2846e-06 | 8.5897e-07
1200 | feeder2_line103 | 1 | 99 | 5.3586e-07 | 7.8367e-07 | 5.4128e-07 | 7.9159e-07
1200 | feeder2_line103 | 2 | 99 | 11.4838 | 11.4834 | 11.5998 | 11.5994
1200 | feeder2_line103 | 3 | 99 | 5.3165e-07 | 7.7827e-07 | 5.3702e-07 | 7.8613e-07
1200 | feeder2_line104 | 1 | 354.6 | 0.083592 | 0.08324 | 0.023574 | 0.023474
1200 | feeder2_line104 | 2 | 354.6 | 6.551 | 6.5509 | 1.8474 | 1.8474
1200 | feeder2_line104 | 3 | 354.6 | 23.0305 | 23.0308 | 6.4948 | 6.4949
1200 | feeder2_line105 | 1 | 99 | 2.4875e-06 | 7.211e-07 | 2.5126e-06 | 7.2838e-07
1200 | feeder2_line105 | 2 | 99 | 2.4661e-06 | 7.169e-07 | 2.491e-06 | 7.2414e-07
1200 | feeder2_line105 | 3 | 99 | 6.6109 | 6.6111 | 6.6777 | 6.6779
1200 | feeder2_line106 | 1 | 354.6 | 0.083537 | 0.083239 | 0.023558 | 0.023474
1200 | feeder2_line106 | 2 | 354.6 | 6.5509 | 6.5509 | 1.8474 | 1.8474
1200 | feeder2_line106 | 3 | 354.6 | 16.4379 | 16.4379 | 4.6356 | 4.6356
1200 | feeder2_line107 | 1 | 99 | 3.1595e-07 | 8.7881e-07 | 3.1914e-07 | 8.8768e-07
1200 | feeder2_line107 | 2 | 99 | 2.951 | 2.9511 | 2.9808 | 2.9809
1200 | feeder2_line107 | 3 | 99 | 3.1443e-07 | 8.7248e-07 | 3.1761e-07 | 8.8129e-07
1200 | feeder2_line108 | 1 | 354.6 | 0.083527 | 0.083239 | 0.023555 | 0.023474
1200 | feeder2_line108 | 2 | 354.6 | 3.6041 | 3.6039 | 1.0164 | 1.0163
1200 | feeder2_line108 | 3 | 354.6 | 16.4378 | 16.4379 | 4.6356 | 4.6356
1200 | feeder2_line109 | 1 | 354.6 | 92.7532 | 92.742 | 26.1571 | 26.154
1200 | feeder2_line109 | 2 | 354.6 | 99.8388 | 99.8541 | 28.1553 | 28.1597
1200 | feeder2_line109 | 3 | 354.6 | 95.357 | 95.3512 | 26.8914 | 26.8898
1200 | feeder2_line110 | 1 | 99 | 2.7669 | 2.7663 | 2.7949 | 2.7943
1200 | feeder2_line110 | 2 | 99 | 0.00077554 | 8.7839e-07 | 0.00078337 | 8.8727e-07
1200 | feeder2_line110 | 3 | 99 | 0.00077627 | 8.7795e-07 | 0.00078412 | 8.8682e-07
1200 | feeder2_line111 | 1 | 99 | 2.3984e-08 | 3.7197e-07 | 2.4226e-08 | 3.7573e-07
1200 | feeder2_line111 | 2 | 99 | 0.49007 | 0.49016 | 0.49502 | 0.49511
1200 | feeder2_line111 | 3 | 99 | 2.4302e-08 | 3.6947e-07 | 2.4547e-08 | 3.732e-07
1200 | feeder2_line112 | 1 | 99 | 3.1573e-07 | 8.9387e-07 | 3.1892e-07 | 9.029e-07
1200 | feeder2_line112 | 2 | 99 | 0.84444 | 0.84467 | 0.85297 | 0.8532
1200 | feeder2_line112 | 3 | 99 | 3.143e-07 | 8.8785e-07 | 3.1748e-07 | 8.9682e-07
1200 | feeder2_line113 | 1 | 99 | 1.6815 | 1.6815 | 1.6984 | 1.6985
1200 | feeder2_line113 | 2 | 99 | 3.1414e-07 | 8.7456e-07 | 3.1732e-07 | 8.8339e-07
1200 | feeder2_line113 | 3 | 99 | 3.14e-07 | 8.7463e-07 | 3.1717e-07 | 8.8347e-07
1200 | feeder2_line114 | 1 | 99 | 11.5793 | 11.5792 | 11.6962 | 11.6961
1200 | feeder2_line114 | 2 | 99 | 2.4375e-08 | 4.233e-07 | 2.4621e-08 | 4.2757e-07
1200 | feeder2_line114 | 3 | 99 | 2.4327e-08 | 4.2286e-07 | 2.4573e-08 | 4.2713e-07
1200 | feeder2_line115 | 1 | 99 | 2.3982e-08 | 5.4845e-07 | 2.4224e-08 | 5.5399e-07
1200 | feeder2_line115 | 2 | 99 | 0.93942 | 0.93943 | 0.94891 | 0.94892
1200 | feeder2_line115 | 3 | 99 | 2.435e-08 | 5.4437e-07 | 2.4596e-08 | 5.4987e-07
1200 | feeder2_line116 | 1 | 354.6 | 0.083532 | 0.083239 | 0.023557 | 0.023474
1200 | feeder2_line116 | 2 | 354.6 | 2.7719 | 2.7717 | 0.78169 | 0.78165
1200 | feeder2_line116 | 3 | 354.6 | 16.4379 | 16.4379 | 4.6356 | 4.6356
1200 | feeder2_line117 | 1 | 99 | 4.7875e-08 | 6.2477e-07 | 4.8359e-08 | 6.3108e-07
1200 | feeder2_line117 | 2 | 99 | 12.3408 | 12.3404 | 12.4655 | 12.465
1200 | feeder2_line117 | 3 | 99 | 4.8464e-08 | 6.2058e-07 | 4.8953e-08 | 6.2685e-07
1200 | feeder2_line118 | 1 | 354.6 | 92.7532 | 92.742 | 26.1571 | 26.154
1200 | feeder2_line118 | 2 | 354.6 | 97.6315 | 97.6484 | 27.5329 | 27.5376
1200 | feeder2_line118 | 3 | 354.6 | 95.357 | 95.3512 | 26.8914 | 26.8898
1200 | feeder2_line119 | 1 | 99 | 2.3977e-08 | 5.9018e-07 | 2.4219e-08 | 5.9614e-07
1200 | feeder2_line119 | 2 | 99 | 2.4374e-08 | 5.8666e-07 | 2.462e-08 | 5.9258e-07
1200 | feeder2_line119 | 3 | 99 | 1.5858 | 1.5858 | 1.6018 | 1.6018
1200 | feeder2_line120 | 1 | 354.6 | 0.083534 | 0.083239 | 0.023557 | 0.023474
1200 | feeder2_line120 | 2 | 354.6 | 2.7719 | 2.7717 | 0.78169 | 0.78165
1200 | feeder2_line120 | 3 | 354.6 | 14.852 | 14.8521 | 4.1884 | 4.1884
1200 | feeder2_line121 | 1 | 99 | 3.1595e-07 | 9.1397e-07 | 3.1914e-07 | 9.2321e-07
1200 | feeder2_line121 | 2 | 99 | 1.8388 | 1.8389 | 1.8574 | 1.8574
1200 | feeder2_line121 | 3 | 99 | 3.143e-07 | 9.0668e-07 | 3.1747e-07 | 9.1584e-07
1200 | feeder2_line122 | 1 | 354.6 | 0.083523 | 0.083239 | 0.023554 | 0.023474
1200 | feeder2_line122 | 2 | 354.6 | 1.1813 | 1.1812 | 0.33314 | 0.33311
1200 | feeder2_line122 | 3 | 354.6 | 14.852 | 14.8521 | 4.1884 | 4.1884
1200 | feeder2_line123 | 1 | 99 | 5.6003e-07 | 9.4711e-07 | 5.6568e-07 | 9.5668e-07
1200 | feeder2_line123 | 2 | 99 | 5.5661e-07 | 9.4142e-07 | 5.6223e-07 | 9.5092e-07
1200 | feeder2_line123 | 3 | 99 | 1.2454 | 1.2454 | 1.258 | 1.258
1200 | feeder2_line124 | 1 | 354.6 | 0.083427 | 0.083239 | 0.023527 | 0.023474
1200 | feeder2_line124 | 2 | 354.6 | 1.1814 | 1.1812 | 0.33315 | 0.33311
1200 | feeder2_line124 | 3 | 354.6 | 14.0504 | 14.0506 | 3.9623 | 3.9624
1200 | feeder2_line125 | 1 | 99 | 5.6003e-07 | 8.8044e-07 | 5.6569e-07 | 8.8934e-07
1200 | feeder2_line125 | 2 | 99 | 5.5661e-07 | 8.7515e-07 | 5.6224e-07 | 8.8399e-07
1200 | feeder2_line125 | 3 | 99 | 1.9146 | 1.9145 | 1.934 | 1.9338
1200 | feeder2_line126 | 1 | 354.6 | 0.083579 | 0.083238 | 0.02357 | 0.023474
1200 | feeder2_line126 | 2 | 354.6 | 1.1815 | 1.1812 | 0.33319 | 0.33311
1200 | feeder2_line126 | 3 | 354.6 | 12.1429 | 12.1431 | 3.4244 | 3.4245
1200 | feeder2_line127 | 1 | 99 | 5.6002e-07 | 1.054e-06 | 5.6568e-07 | 1.0647e-06
1200 | feeder2_line127 | 2 | 99 | 5.5661e-07 | 1.0477e-06 | 5.6223e-07 | 1.0583e-06
1200 | feeder2_line127 | 3 | 99 | 11.1732 | 11.1737 | 11.2861 | 11.2866
1200 | feeder2_line128 | 1 | 354.6 | 0.083495 | 0.083238 | 0.023546 | 0.023474
1200 | feeder2_line128 | 2 | 354.6 | 1.1815 | 1.1812 | 0.33318 | 0.33312
1200 | feeder2_line128 | 3 | 354.6 | 0.98343 | 0.98321 | 0.27733 | 0.27727
1200 | feeder2_line129 | 1 | 99 | 5.3609e-07 | 8.547e-07 | 5.4151e-07 | 8.6333e-07
1200 | feeder2_line129 | 2 | 99 | 1.1812 | 1.1812 | 1.1931 | 1.1932
1200 | feeder2_line129 | 3 | 99 | 5.3099e-07 | 8.4761e-07 | 5.3635e-07 | 8.5617e-07
1200 | feeder2_line130 | 1 | 354.6 | 0.083508 | 0.083238 | 0.02355 | 0.023474
1200 | feeder2_line130 | 2 | 354.6 | 0.00029973 | 4.4961e-06 | 8.4527e-05 | 1.2679e-06
1200 | feeder2_line130 | 3 | 354.6 | 0.98344 | 0.98321 | 0.27734 | 0.27727
1200 | feeder2_line131 | 1 | 99 | 5.6005e-07 | 9.473e-07 | 5.657e-07 | 9.5687e-07
1200 | feeder2_line131 | 2 | 99 | 5.5662e-07 | 9.4158e-07 | 5.6225e-07 | 9.5109e-07
1200 | feeder2_line131 | 3 | 99 | 0.050522 | 0.05051 | 0.051033 | 0.05102
1200 | feeder2_line132 | 1 | 354.6 | 0.083354 | 0.083238 | 0.023506 | 0.023474
1200 | feeder2_line132 | 2 | 354.6 | 0.00012174 | 2.8269e-06 | 3.4333e-05 | 7.972e-07
1200 | feeder2_line132 | 3 | 354.6 | 0.93366 | 0.93358 | 0.2633 | 0.26328
1200 | feeder2_line133 | 1 | 99 | 0.083287 | 0.083238 | 0.084128 | 0.084079
1200 | feeder2_line133 | 2 | 99 | 2.905e-07 | 9.4909e-07 | 2.9343e-07 | 9.5868e-07
1200 | feeder2_line133 | 3 | 99 | 2.8987e-07 | 9.4694e-07 | 2.928e-07 | 9.565e-07
1200 | feeder2_line134 | 1 | 354.6 | 8.4451e-12 | 1.7406e-06 | 2.3816e-12 | 4.9087e-07
1200 | feeder2_line134 | 2 | 354.6 | 6.2085e-12 | 1.7311e-06 | 1.7509e-12 | 4.8819e-07
1200 | feeder2_line134 | 3 | 354.6 | 0.9336 | 0.93358 | 0.26328 | 0.26328
1200 | feeder2_line135 | 1 | 99 | 2.7362 | 2.7361 | 2.7638 | 2.7637
1200 | feeder2_line135 | 2 | 99 | 4.8724e-08 | 5.648e-07 | 4.9217e-08 | 5.705e-07
1200 | feeder2_line135 | 3 | 99 | 4.844e-08 | 5.6515e-07 | 4.893e-08 | 5.7085e-07
1200 | feeder2_line136 | 1 | 354.6 | 92.786 | 92.7748 | 26.1664 | 26.1632
1200 | feeder2_line136 | 2 | 354.6 | 97.6315 | 97.6484 | 27.5329 | 27.5376
1200 | feeder2_line136 | 3 | 354.6 | 95.3569 | 95.3512 | 26.8914 | 26.8898
1200 | feeder2_line137 | 1 | 99 | 1.3724 | 1.3723 | 1.3862 | 1.3862
1200 | feeder2_line137 | 2 | 99 | 8.1929e-07 | 1.5209e-06 | 8.2757e-07 | 1.5362e-06
1200 | feeder2_line137 | 3 | 99 | 8.1996e-07 | 1.5219e-06 | 8.2824e-07 | 1.5373e-06
1200 | feeder2_line138 | 1 | 354.6 | 92.8712 | 92.8598 | 26.1904 | 26.1872
1200 | feeder2_line138 | 2 | 354.6 | 97.6316 | 97.6484 | 27.5329 | 27.5376
1200 | feeder2_line138 | 3 | 354.6 | 95.357 | 95.3512 | 26.8914 | 26.8898
1200 | feeder2_line139 | 1 | 99 | 4.7839e-08 | 4.7732e-07 | 4.8323e-08 | 4.8214e-07
1200 | feeder2_line139 | 2 | 99 | 4.8716e-08 | 4.7377e-07 | 4.9208e-08 | 4.7856e-07
1200 | feeder2_line139 | 3 | 99 | 0.046098 | 0.045119 | 0.046564 | 0.045575
1200 | feeder2_line140 | 1 | 354.6 | 92.8711 | 92.8598 | 26.1904 | 26.1872
1200 | feeder2_line140 | 2 | 354.6 | 97.6315 | 97.6484 | 27.5329 | 27.5376
1200 | feeder2_line140 | 3 | 354.6 | 95.3597 | 95.3543 | 26.8922 | 26.8907
1200 | feeder2_line141 | 1 | 99 | 2.4569e-06 | 4.7206e-07 | 2.4817e-06 | 4.7683e-07
1200 | feeder2_line141 | 2 | 99 | 2.2674 | 2.2674 | 2.2903 | 2.2903
1200 | feeder2_line141 | 3 | 99 | 2.4339e-06 | 4.6889e-07 | 2.4585e-06 | 4.7362e-07
1200 | feeder2_line142 | 1 | 354.6 | 92.8712 | 92.8598 | 26.1904 | 26.1872
1200 | feeder2_line142 | 2 | 354.6 | 96.5031 | 96.52 | 27.2146 | 27.2194
1200 | feeder2_line142 | 3 | 354.6 | 95.3598 | 95.3543 | 26.8922 | 26.8907
1200 | feeder2_line143 | 1 | 99 | 8.2548e-07 | 1.6772e-06 | 8.3381e-07 | 1.6942e-06
1200 | feeder2_line143 | 2 | 99 | 2.9533 | 2.9535 | 2.9832 | 2.9833
1200 | feeder2_line143 | 3 | 99 | 8.1966e-07 | 1.666e-06 | 8.2794e-07 | 1.6828e-06
1200 | feeder2_line144 | 1 | 354.6 | 92.8711 | 92.8598 | 26.1904 | 26.1872
1200 | feeder2_line144 | 2 | 354.6 | 95.3904 | 95.4078 | 26.9009 | 26.9058
1200 | feeder2_line144 | 3 | 354.6 | 95.3597 | 95.3543 | 26.8922 | 26.8907
1200 | feeder2_line145 | 1 | 99 | 2.3912e-08 | 4.7027e-07 | 2.4154e-08 | 4.7502e-07
1200 | feeder2_line145 | 2 | 99 | 1.6414 | 1.6414 | 1.6579 | 1.6579
1200 | feeder2_line145 | 3 | 99 | 2.4203e-08 | 4.671e-07 | 2.4448e-08 | 4.7182e-07
1200 | feeder2_line146 | 1 | 354.6 | 92.8711 | 92.8598 | 26.1904 | 26.1872
1200 | feeder2_line146 | 2 | 354.6 | 94.4908 | 94.5084 | 26.6472 | 26.6521
1200 | feeder2_line146 | 3 | 354.6 | 95.3597 | 95.3543 | 26.8922 | 26.8907
1200 | feeder2_line147 | 1 | 99 | 1.1082 | 1.1082 | 1.1194 | 1.1194
1200 | feeder2_line147 | 2 | 99 | 1.1079e-06 | 2.1524e-06 | 1.1191e-06 | 2.1742e-06
1200 | feeder2_line147 | 3 | 99 | 1.1089e-06 | 2.1542e-06 | 1.1201e-06 | 2.176e-06
1200 | feeder2_line148 | 1 | 99 | 0.86936 | 0.86935 | 0.87814 | 0.87813
1200 | feeder2_line148 | 2 | 99 | 5.783e-07 | 1.4423e-06 | 5.8414e-07 | 1.4569e-06
1200 | feeder2_line148 | 3 | 99 | 5.7863e-07 | 1.4435e-06 | 5.8448e-07 | 1.4581e-06
1200 | feeder2_line149 | 1 | 354.6 | 92.0601 | 92.0487 | 25.9617 | 25.9585
1200 | feeder2_line149 | 2 | 354.6 | 94.4909 | 94.5084 | 26.6472 | 26.6521
1200 | feeder2_line149 | 3 | 354.6 | 95.3598 | 95.3543 | 26.8922 | 26.8907
1200 | feeder2_line150 | 1 | 354.6 | 92.0601 | 92.0487 | 25.9617 | 25.9585
1200 | feeder2_line150 | 2 | 354.6 | 93.321 | 93.3396 | 26.3173 | 26.3225
1200 | feeder2_line150 | 3 | 354.6 | 95.3598 | 95.3543 | 26.8922 | 26.8907
1200 | feeder2_line151 | 1 | 99 | 9.4891e-06 | 1.725e-06 | 9.585e-06 | 1.7425e-06
1200 | feeder2_line151 | 2 | 99 | 12.4006 | 12.4001 | 12.5259 | 12.5253
1200 | feeder2_line151 | 3 | 99 | 9.3979e-06 | 1.7133e-06 | 9.4928e-06 | 1.7306e-06
1200 | feeder2_line152 | 1 | 354.6 | 3.3748e-12 | 1.1486e-06 | 9.5173e-13 | 3.2391e-07
1200 | feeder2_line152 | 2 | 354.6 | 3.3748e-12 | 1.1406e-06 | 9.5173e-13 | 3.2165e-07
1200 | feeder2_line152 | 3 | 354.6 | 0.0796 | 0.079587 | 0.022448 | 0.022444
1200 | feeder2_line153 | 1 | 99 | 1.8313 | 1.8313 | 1.8498 | 1.8498
1200 | feeder2_line153 | 2 | 99 | 4.8676e-08 | 5.7049e-07 | 4.9168e-08 | 5.7625e-07
1200 | feeder2_line153 | 3 | 99 | 4.8367e-08 | 5.7096e-07 | 4.8856e-08 | 5.7673e-07
1200 | feeder2_line154 | 1 | 99 | 5.5785e-07 | 8.5544e-07 | 5.6348e-07 | 8.6408e-07
1200 | feeder2_line154 | 2 | 99 | 5.5353e-07 | 8.489e-07 | 5.5912e-07 | 8.5748e-07
1200 | feeder2_line154 | 3 | 99 | 6.0457 | 6.0455 | 6.1067 | 6.1065
1200 | feeder2_line155 | 1 | 99 | 92.0707 | 92.0594 | 93.0007 | 92.9893
1200 | feeder2_line155 | 2 | 99 | 93.321 | 93.3396 | 94.2636 | 94.2824
1200 | feeder2_line155 | 3 | 99 | 93.1382 | 93.132 | 94.079 | 94.0727
1200 | feeder2_line156 | 1 | 99 | 5.8189e-07 | 1.1264e-06 | 5.8777e-07 | 1.1378e-06
1200 | feeder2_line156 | 2 | 99 | 11.4173 | 11.4167 | 11.5326 | 11.5321
1200 | feeder2_line156 | 3 | 99 | 5.7836e-07 | 1.1188e-06 | 5.842e-07 | 1.1301e-06
1200 | feeder2_line157 | 1 | 99 | 2.3894e-08 | 2.4454e-07 | 2.4135e-08 | 2.4701e-07
1200 | feeder2_line157 | 2 | 99 | 1.4625 | 1.4624 | 1.4772 | 1.4772
1200 | feeder2_line157 | 3 | 99 | 2.4188e-08 | 2.4289e-07 | 2.4433e-08 | 2.4534e-07
1230 | feeder2_line1 | 1 | 354.6 | 115.243 | 115.2438 | 32.4994 | 32.4997
1230 | feeder2_line1 | 2 | 354.6 | 133.5189 | 133.5227 | 37.6534 | 37.6545
1230 | feeder2_line1 | 3 | 354.6 | 122.9141 | 122.9114 | 34.6627 | 34.662
1230 | feeder2_line2 | 1 | 354.6 | 112.4316 | 112.4325 | 31.7066 | 31.7068
1230 | feeder2_line2 | 2 | 354.6 | 133.5189 | 133.5227 | 37.6534 | 37.6545
1230 | feeder2_line2 | 3 | 354.6 | 122.9141 | 122.9114 | 34.6627 | 34.662
1230 | feeder2_line3 | 1 | 80.1 | 3.5709 | 3.5709 | 4.458 | 4.458
1230 | feeder2_line3 | 2 | 80.1 | 5.6547e-07 | 1.045e-06 | 7.0595e-07 | 1.3046e-06
1230 | feeder2_line3 | 3 | 80.1 | 5.6597e-07 | 1.0459e-06 | 7.0658e-07 | 1.3058e-06
1230 | feeder2_line4 | 1 | 354.6 | 112.4315 | 112.4325 | 31.7066 | 31.7068
1230 | feeder2_line4 | 2 | 354.6 | 132.9875 | 132.9914 | 37.5035 | 37.5046
1230 | feeder2_line4 | 3 | 354.6 | 122.914 | 122.9114 | 34.6627 | 34.662
1230 | feeder2_line5 | 1 | 80.1 | 5.6668e-07 | 9.8881e-07 | 7.0747e-07 | 1.2345e-06
1230 | feeder2_line5 | 2 | 80.1 | 0.98003 | 0.98003 | 1.2235 | 1.2235
1230 | feeder2_line5 | 3 | 80.1 | 5.6589e-07 | 9.8744e-07 | 7.0649e-07 | 1.2328e-06
1230 | feeder2_line6 | 1 | 80.1 | 5.6655e-07 | 1.163e-06 | 7.073e-07 | 1.4519e-06
1230 | feeder2_line6 | 2 | 80.1 | 5.6516e-07 | 1.1601e-06 | 7.0556e-07 | 1.4483e-06
1230 | feeder2_line6 | 3 | 80.1 | 11.2995 | 11.2995 | 14.1067 | 14.1067
1230 | feeder2_line7 | 1 | 354.6 | 112.4315 | 112.4325 | 31.7066 | 31.7068
1230 | feeder2_line7 | 2 | 354.6 | 132.9874 | 132.9914 | 37.5035 | 37.5046
1230 | feeder2_line7 | 3 | 354.6 | 116.3822 | 116.3793 | 32.8207 | 32.8199
1230 | feeder2_line8 | 1 | 80.1 | 0.53682 | 0.53682 | 0.67019 | 0.67018
1230 | feeder2_line8 | 2 | 80.1 | 5.6466e-07 | 1.1176e-06 | 7.0495e-07 | 1.3953e-06
1230 | feeder2_line8 | 3 | 80.1 | 5.6537e-07 | 1.119e-06 | 7.0583e-07 | 1.397e-06
1230 | feeder2_line9 | 1 | 354.6 | 112.1988 | 112.2 | 31.6409 | 31.6413
1230 | feeder2_line9 | 2 | 354.6 | 132.9873 | 132.9914 | 37.5035 | 37.5046
1230 | feeder2_line9 | 3 | 354.6 | 116.3821 | 116.3793 | 32.8207 | 32.8199
1230 | feeder2_line10 | 1 | 80.1 | 8.3707e-07 | 1.4797e-06 | 1.045e-06 | 1.8474e-06
1230 | feeder2_line10 | 2 | 80.1 | 0.53681 | 0.53681 | 0.67018 | 0.67017
1230 | feeder2_line10 | 3 | 80.1 | 8.3571e-07 | 1.4774e-06 | 1.0433e-06 | 1.8444e-06
1230 | feeder2_line11 | 1 | 354.6 | 112.1989 | 112.2 | 31.641 | 31.6413
1230 | feeder2_line11 | 2 | 354.6 | 132.6755 | 132.6796 | 37.4155 | 37.4167
1230 | feeder2_line11 | 3 | 354.6 | 116.3822 | 116.3793 | 32.8207 | 32.8199
1230 | feeder2_line12 | 1 | 80.1 | 5.4158e-07 | 9.8131e-07 | 6.7612e-07 | 1.2251e-06
1230 | feeder2_line12 | 2 | 80.1 | 5.3971e-07 | 9.7836e-07 | 6.7379e-07 | 1.2214e-06
1230 | feeder2_line12 | 3 | 80.1 | 4.9339 | 4.9339 | 6.1597 | 6.1597
1230 | feeder2_line13 | 1 | 354.6 | 112.199 | 112.2 | 31.641 | 31.6413
1230 | feeder2_line13 | 2 | 354.6 | 132.6756 | 132.6796 | 37.4156 | 37.4167
1230 | feeder2_line13 | 3 | 354.6 | 113.2517 | 113.2484 | 31.9379 | 31.937
1230 | feeder2_line14 | 1 | 80.1 | 1.6856 | 1.6856 | 2.1044 | 2.1044
1230 | feeder2_line14 | 2 | 80.1 | 2.9443e-07 | 6.3777e-07 | 3.6757e-07 | 7.9621e-07
1230 | feeder2_line14 | 3 | 80.1 | 2.9479e-07 | 6.3872e-07 | 3.6803e-07 | 7.974e-07
1230 | feeder2_line15 | 1 | 354.6 | 111.5295 | 111.5305 | 31.4522 | 31.4525
1230 | feeder2_line15 | 2 | 354.6 | 132.6756 | 132.6796 | 37.4156 | 37.4167
1230 | feeder2_line15 | 3 | 354.6 | 113.2516 | 113.2484 | 31.9379 | 31.937
1230 | feeder2_line16 | 1 | 80.1 | 5.6581e-07 | 1.0193e-06 | 7.0638e-07 | 1.2726e-06
1230 | feeder2_line16 | 2 | 80.1 | 1.8251 | 1.8251 | 2.2785 | 2.2785
1230 | feeder2_line16 | 3 | 80.1 | 5.6485e-07 | 1.0176e-06 | 7.0518e-07 | 1.2704e-06
1230 | feeder2_line17 | 1 | 354.6 | 111.5295 | 111.5306 | 31.4522 | 31.4525
1230 | feeder2_line17 | 2 | 354.6 | 131.4506 | 131.4546 | 37.0701 | 37.0712
1230 | feeder2_line17 | 3 | 354.6 | 113.2516 | 113.2484 | 31.9379 | 31.937
1230 | feeder2_line18 | 1 | 80.1 | 5.406e-07 | 7.2864e-07 | 6.749e-07 | 9.0967e-07
1230 | feeder2_line18 | 2 | 80.1 | 5.3794e-07 | 7.2552e-07 | 6.7158e-07 | 9.0577e-07
1230 | feeder2_line18 | 3 | 80.1 | 0.0408 | 0.040783 | 0.050936 | 0.050916
1230 | feeder2_line19 | 1 | 354.6 | 111.5295 | 111.5306 | 31.4522 | 31.4525
1230 | feeder2_line19 | 2 | 354.6 | 131.4506 | 131.4546 | 37.0701 | 37.0712
1230 | feeder2_line19 | 3 | 354.6 | 113.2346 | 113.2314 | 31.933 | 31.9321
1230 | feeder2_line20 | 1 | 99 | 5.4033e-07 | 8.7315e-07 | 5.4579e-07 | 8.8197e-07
1230 | feeder2_line20 | 2 | 99 | 5.3746e-07 | 8.691e-07 | 5.4289e-07 | 8.7788e-07
1230 | feeder2_line20 | 3 | 99 | 1.354 | 1.3539 | 1.3676 | 1.3676
1230 | feeder2_line21 | 1 | 354.6 | 111.5295 | 111.5306 | 31.4522 | 31.4525
1230 | feeder2_line21 | 2 | 354.6 | 131.4505 | 131.4546 | 37.0701 | 37.0712
1230 | feeder2_line21 | 3 | 354.6 | 112.6735 | 112.6703 | 31.7748 | 31.7739
1230 | feeder2_line22 | 1 | 99 | 5.6457e-07 | 1.0007e-06 | 5.7027e-07 | 1.0108e-06
1230 | feeder2_line22 | 2 | 99 | 1.7535 | 1.7535 | 1.7712 | 1.7712
1230 | feeder2_line22 | 3 | 99 | 5.6347e-07 | 9.987e-07 | 5.6916e-07 | 1.0088e-06
1230 | feeder2_line23 | 1 | 99 | 5.6457e-07 | 9.3669e-07 | 5.7027e-07 | 9.4616e-07
1230 | feeder2_line23 | 2 | 99 | 5.6181e-07 | 9.3215e-07 | 5.6748e-07 | 9.4156e-07
1230 | feeder2_line23 | 3 | 99 | 0.28441 | 0.28441 | 0.28729 | 0.28729
1230 | feeder2_line24 | 1 | 354.6 | 111.5295 | 111.5306 | 31.4522 | 31.4525
1230 | feeder2_line24 | 2 | 354.6 | 130.3775 | 130.3816 | 36.7675 | 36.7687
1230 | feeder2_line24 | 3 | 354.6 | 112.5894 | 112.5862 | 31.7511 | 31.7502
1230 | feeder2_line25 | 1 | 99 | 1.7505 | 1.7505 | 1.7682 | 1.7682
1230 | feeder2_line25 | 2 | 99 | 4.9277e-08 | 6.7707e-07 | 4.9774e-08 | 6.8391e-07
1230 | feeder2_line25 | 3 | 99 | 4.8804e-08 | 6.7926e-07 | 4.9297e-08 | 6.8612e-07
1230 | feeder2_line26 | 1 | 99 | 0.32012 | 0.32012 | 0.32335 | 0.32336
1230 | feeder2_line26 | 2 | 99 | 5.3665e-07 | 8.3885e-07 | 5.4207e-07 | 8.4733e-07
1230 | feeder2_line26 | 3 | 99 | 5.3873e-07 | 8.4156e-07 | 5.4417e-07 | 8.5006e-07
1230 | feeder2_line27 | 1 | 354.6 | 110.6177 | 110.6189 | 31.1951 | 31.1954
1230 | feeder2_line27 | 2 | 354.6 | 130.3775 | 130.3817 | 36.7675 | 36.7687
1230 | feeder2_line27 | 3 | 354.6 | 112.5894 | 112.5862 | 31.7511 | 31.7502
1230 | feeder2_line28 | 1 | 99 | 2.5024e-06 | 6.9934e-07 | 2.5276e-06 | 7.064e-07
1230 | feeder2_line28 | 2 | 99 | 0.078781 | 0.07878 | 0.079577 | 0.079576
1230 | feeder2_line28 | 3 | 99 | 2.4961e-06 | 6.9786e-07 | 2.5213e-06 | 7.0491e-07
1230 | feeder2_line29 | 1 | 354.6 | 110.6177 | 110.6189 | 31.1951 | 31.1954
1230 | feeder2_line29 | 2 | 354.6 | 130.3362 | 130.3403 | 36.7558 | 36.757
1230 | feeder2_line29 | 3 | 354.6 | 112.5894 | 112.5862 | 31.7511 | 31.7502
1230 | feeder2_line30 | 1 | 266.4 | 3.8872 | 3.887 | 1.4592 | 1.4591
1230 | feeder2_line30 | 2 | 266.4 | 13.869 | 13.8687 | 5.2061 | 5.206
1230 | feeder2_line30 | 3 | 266.4 | 12.458 | 12.4578 | 4.6764 | 4.6764
1230 | feeder2_line31 | 1 | 354.6 | 108.953 | 108.9537 | 30.7256 | 30.7258
1230 | feeder2_line31 | 2 | 354.6 | 122.2318 | 122.2358 | 34.4703 | 34.4715
1230 | feeder2_line31 | 3 | 354.6 | 104.1128 | 104.1087 | 29.3606 | 29.3595
1230 | feeder2_line32 | 1 | 354.6 | 108.953 | 108.9537 | 30.7256 | 30.7258
1230 | feeder2_line32 | 2 | 354.6 | 121.2797 | 121.2839 | 34.2018 | 34.203
1230 | feeder2_line32 | 3 | 354.6 | 104.1127 | 104.1087 | 29.3606 | 29.3595
1230 | feeder2_line33 | 1 | 99 | 4.8525e-08 | 6.7341e-07 | 4.9016e-08 | 6.8022e-07
1230 | feeder2_line33 | 2 | 99 | 1.9131 | 1.9131 | 1.9324 | 1.9324
1230 | feeder2_line33 | 3 | 99 | 4.857e-08 | 6.7189e-07 | 4.906e-08 | 6.7868e-07
1230 | feeder2_line34 | 1 | 354.6 | 108.953 | 108.9537 | 30.7256 | 30.7258
1230 | feeder2_line34 | 2 | 354.6 | 121.2797 | 121.2839 | 34.2018 | 34.203
1230 | feeder2_line34 | 3 | 354.6 | 103.6761 | 103.672 | 29.2375 | 29.2363
1230 | feeder2_line35 | 1 | 99 | 2.9338e-07 | 7.4548e-07 | 2.9635e-07 | 7.5301e-07
1230 | feeder2_line35 | 2 | 99 | 2.9152e-07 | 7.4011e-07 | 2.9446e-07 | 7.4759e-07
1230 | feeder2_line35 | 3 | 99 | 1.2977 | 1.2977 | 1.3108 | 1.3108
1230 | feeder2_line36 | 1 | 354.6 | 107.3579 | 107.3586 | 30.2758 | 30.276
1230 | feeder2_line36 | 2 | 354.6 | 121.2798 | 121.2839 | 34.2019 | 34.203
1230 | feeder2_line36 | 3 | 354.6 | 103.6761 | 103.672 | 29.2375 | 29.2363
1230 | feeder2_line37 | 1 | 99 | 2.2149 | 2.215 | 2.2373 | 2.2374
1230 | feeder2_line37 | 2 | 99 | 2.9137e-07 | 8.1847e-07 | 2.9432e-07 | 8.2674e-07
1230 | feeder2_line37 | 3 | 99 | 2.9266e-07 | 8.2272e-07 | 2.9561e-07 | 8.3103e-07
1230 | feeder2_line38 | 1 | 99 | 3.1794e-07 | 7.6191e-07 | 3.2115e-07 | 7.6961e-07
1230 | feeder2_line38 | 2 | 99 | 1.1056 | 1.1056 | 1.1168 | 1.1168
1230 | feeder2_line38 | 3 | 99 | 3.1732e-07 | 7.6011e-07 | 3.2052e-07 | 7.6779e-07
1230 | feeder2_line39 | 1 | 266.4 | 3.8872 | 3.887 | 1.4592 | 1.4591
1230 | feeder2_line39 | 2 | 266.4 | 12.7942 | 12.7939 | 4.8026 | 4.8025
1230 | feeder2_line39 | 3 | 266.4 | 12.458 | 12.4578 | 4.6764 | 4.6764
1230 | feeder2_line40 | 1 | 354.6 | 106.6568 | 106.6575 | 30.0781 | 30.0783
1230 | feeder2_line40 | 2 | 354.6 | 121.2797 | 121.2839 | 34.2018 | 34.203
1230 | feeder2_line40 | 3 | 354.6 | 103.676 | 103.672 | 29.2375 | 29.2363
1230 | feeder2_line41 | 1 | 99 | 1.752 | 1.752 | 1.7697 | 1.7697
1230 | feeder2_line41 | 2 | 99 | 4.9216e-08 | 7.1499e-07 | 4.9713e-08 | 7.2222e-07
1230 | feeder2_line41 | 3 | 99 | 4.8503e-08 | 7.1878e-07 | 4.8993e-08 | 7.2604e-07
1230 | feeder2_line42 | 1 | 99 | 2.9366e-07 | 7.3541e-07 | 2.9662e-07 | 7.4284e-07
1230 | feeder2_line42 | 2 | 99 | 2.9187e-07 | 7.3034e-07 | 2.9482e-07 | 7.3772e-07
1230 | feeder2_line42 | 3 | 99 | 2.3318 | 2.3318 | 2.3554 | 2.3554
1230 | feeder2_line43 | 1 | 266.4 | 3.8871 | 3.887 | 1.4591 | 1.4591
1230 | feeder2_line43 | 2 | 266.4 | 12.7941 | 12.7939 | 4.8026 | 4.8025
1230 | feeder2_line43 | 3 | 266.4 | 10.1333 | 10.1331 | 3.8038 | 3.8037
1230 | feeder2_line44 | 1 | 354.6 | 106.6568 | 106.6575 | 30.0781 | 30.0783
1230 | feeder2_line44 | 2 | 354.6 | 121.2797 | 121.2839 | 34.2018 | 34.203
1230 | feeder2_line44 | 3 | 354.6 | 103.2567 | 103.2526 | 29.1192 | 29.118
1230 | feeder2_line45 | 1 | 99 | 4.8453e-08 | 5.6799e-07 | 4.8943e-08 | 5.7373e-07
1230 | feeder2_line45 | 2 | 99 | 4.9213e-08 | 5.6367e-07 | 4.971e-08 | 5.6936e-07
1230 | feeder2_line45 | 3 | 99 | 1.3528 | 1.3527 | 1.3665 | 1.3664
1230 | feeder2_line46 | 1 | 99 | 5.6304e-07 | 1.3332e-06 | 5.6872e-07 | 1.3466e-06
1230 | feeder2_line46 | 2 | 99 | 5.591e-07 | 1.324e-06 | 5.6475e-07 | 1.3374e-06
1230 | feeder2_line46 | 3 | 99 | 3.9547 | 3.9547 | 3.9947 | 3.9946
1230 | feeder2_line47 | 1 | 266.4 | 3.8871 | 3.887 | 1.4591 | 1.4591
1230 | feeder2_line47 | 2 | 266.4 | 12.7941 | 12.7939 | 4.8026 | 4.8025
1230 | feeder2_line47 | 3 | 266.4 | 6.4247 | 6.4245 | 2.4117 | 2.4116
1230 | feeder2_line48 | 1 | 99 | 2.3072 | 2.3072 | 2.3305 | 2.3305
1230 | feeder2_line48 | 2 | 99 | 4.9243e-08 | 7.1282e-07 | 4.974e-08 | 7.2002e-07
1230 | feeder2_line48 | 3 | 99 | 4.8615e-08 | 7.1601e-07 | 4.9106e-08 | 7.2324e-07
1230 | feeder2_line49 | 1 | 266.4 | 1.5844 | 1.5843 | 0.59473 | 0.59472
1230 | feeder2_line49 | 2 | 266.4 | 12.7941 | 12.7939 | 4.8026 | 4.8025
1230 | feeder2_line49 | 3 | 266.4 | 6.4247 | 6.4245 | 2.4117 | 2.4116
1230 | feeder2_line50 | 1 | 99 | 5.6302e-07 | 1.2133e-06 | 5.687e-07 | 1.2255e-06
1230 | feeder2_line50 | 2 | 99 | 11.1887 | 11.1887 | 11.3017 | 11.3017
1230 | feeder2_line50 | 3 | 99 | 5.6159e-07 | 1.2102e-06 | 5.6727e-07 | 1.2224e-06
1230 | feeder2_line51 | 1 | 99 | 1.4698 | 1.47 | 1.4847 | 1.4848
1230 | feeder2_line51 | 2 | 99 | 5.5906e-07 | 1.3079e-06 | 5.647e-07 | 1.3212e-06
1230 | feeder2_line51 | 3 | 99 | 5.6161e-07 | 1.3138e-06 | 5.6729e-07 | 1.3271e-06
1230 | feeder2_line52 | 1 | 266.4 | 0.1156 | 0.11551 | 0.043394 | 0.04336
1230 | feeder2_line52 | 2 | 266.4 | 1.6102 | 1.6101 | 0.60443 | 0.6044
1230 | feeder2_line52 | 3 | 266.4 | 6.4245 | 6.4245 | 2.4116 | 2.4116
1230 | feeder2_line53 | 1 | 99 | 5.3876e-07 | 7.4049e-07 | 5.442e-07 | 7.4797e-07
1230 | feeder2_line53 | 2 | 99 | 1.6101 | 1.6101 | 1.6264 | 1.6264
1230 | feeder2_line53 | 3 | 99 | 5.373e-07 | 7.3862e-07 | 5.4273e-07 | 7.4608e-07
1230 | feeder2_line54 | 1 | 266.4 | 0.11542 | 0.11551 | 0.043327 | 0.04336
1230 | feeder2_line54 | 2 | 266.4 | 8.3454e-05 | 4.5114e-06 | 3.1327e-05 | 1.6935e-06
1230 | feeder2_line54 | 3 | 266.4 | 6.4244 | 6.4245 | 2.4116 | 2.4116
1230 | feeder2_line55 | 1 | 99 | 2.2147 | 2.2147 | 2.2371 | 2.2371
1230 | feeder2_line55 | 2 | 99 | 4.9201e-08 | 7.0918e-07 | 4.9698e-08 | 7.1634e-07
1230 | feeder2_line55 | 3 | 99 | 4.8417e-08 | 7.1338e-07 | 4.8906e-08 | 7.2059e-07
1230 | feeder2_line56 | 1 | 354.6 | 105.602 | 105.6028 | 29.7806 | 29.7808
1230 | feeder2_line56 | 2 | 354.6 | 121.2797 | 121.2839 | 34.2018 | 34.203
1230 | feeder2_line56 | 3 | 354.6 | 103.2567 | 103.2526 | 29.1192 | 29.118
1230 | feeder2_line57 | 1 | 99 | 7.2823e-07 | 1.5168e-06 | 7.3559e-07 | 1.5321e-06
1230 | feeder2_line57 | 2 | 99 | 7.3862e-07 | 1.5061e-06 | 7.4608e-07 | 1.5214e-06
1230 | feeder2_line57 | 3 | 99 | 6.4245 | 6.4245 | 6.4894 | 6.4893
1230 | feeder2_line58 | 1 | 266.4 | 0.11548 | 0.11551 | 0.043349 | 0.04336
1230 | feeder2_line58 | 2 | 266.4 | 1.8465e-05 | 2.6194e-06 | 6.9314e-06 | 9.8324e-07
1230 | feeder2_line58 | 3 | 266.4 | 1.8554e-05 | 2.6304e-06 | 6.9647e-06 | 9.8738e-07
1230 | feeder2_line59 | 1 | 99 | 4.8549e-08 | 5.2723e-07 | 4.9039e-08 | 5.3256e-07
1230 | feeder2_line59 | 2 | 99 | 4.9243e-08 | 5.2355e-07 | 4.9741e-08 | 5.2884e-07
1230 | feeder2_line59 | 3 | 99 | 1.5213 | 1.5213 | 1.5367 | 1.5366
1230 | feeder2_line60 | 1 | 99 | 2.9365e-07 | 7.9682e-07 | 2.9662e-07 | 8.0486e-07
1230 | feeder2_line60 | 2 | 99 | 2.9184e-07 | 7.9125e-07 | 2.9478e-07 | 7.9924e-07
1230 | feeder2_line60 | 3 | 99 | 4.9316 | 4.9316 | 4.9814 | 4.9814
1230 | feeder2_line61 | 1 | 266.4 | 2.3305 | 2.3307 | 0.87481 | 0.87488
1230 | feeder2_line61 | 2 | 266.4 | 2.1128 | 2.1129 | 0.79308 | 0.79314
1230 | feeder2_line61 | 3 | 266.4 | 1.857 | 1.8571 | 0.69707 | 0.69712
1230 | feeder2_line62 | 1 | 354.6 | 103.8887 | 103.8895 | 29.2974 | 29.2976
1230 | feeder2_line62 | 2 | 354.6 | 120.2719 | 120.276 | 33.9176 | 33.9188
1230 | feeder2_line62 | 3 | 354.6 | 102.6062 | 102.6019 | 28.9358 | 28.9345
1230 | feeder2_line63 | 1 | 99 | 0.090462 | 0.090467 | 0.091375 | 0.091381
1230 | feeder2_line63 | 2 | 99 | 5.5906e-07 | 1.1896e-06 | 5.6471e-07 | 1.2016e-06
1230 | feeder2_line63 | 3 | 99 | 5.6159e-07 | 1.1949e-06 | 5.6726e-07 | 1.207e-06
1230 | feeder2_line64 | 1 | 99 | 0.025039 | 0.025043 | 0.025292 | 0.025296
1230 | feeder2_line64 | 2 | 99 | 1.1006e-11 | 3.1337e-07 | 1.1117e-11 | 3.1654e-07
1230 | feeder2_line64 | 3 | 99 | 9.1393e-13 | 3.1477e-07 | 9.2316e-13 | 3.1795e-07
1230 | feeder2_line65 | 1 | 99 | 4.8281e-08 | 6.2711e-07 | 4.8769e-08 | 6.3345e-07
1230 | feeder2_line65 | 2 | 99 | 0.98066 | 0.98066 | 0.99056 | 0.99056
1230 | feeder2_line65 | 3 | 99 | 4.831e-08 | 6.2566e-07 | 4.8798e-08 | 6.3198e-07
1230 | feeder2_line66 | 1 | 354.6 | 103.8887 | 103.8895 | 29.2974 | 29.2976
1230 | feeder2_line66 | 2 | 354.6 | 119.876 | 119.88 | 33.806 | 33.8071
1230 | feeder2_line66 | 3 | 354.6 | 102.6063 | 102.6019 | 28.9358 | 28.9346
1230 | feeder2_line67 | 1 | 99 | 2.4166e-08 | 3.5477e-07 | 2.441e-08 | 3.5835e-07
1230 | feeder2_line67 | 2 | 99 | 2.4598e-08 | 3.5173e-07 | 2.4846e-08 | 3.5528e-07
1230 | feeder2_line67 | 3 | 99 | 1.7539 | 1.7539 | 1.7716 | 1.7716
1230 | feeder2_line68 | 1 | 266.4 | 2.3306 | 2.3307 | 0.87483 | 0.87488
1230 | feeder2_line68 | 2 | 266.4 | 2.1128 | 2.1129 | 0.79309 | 0.79314
1230 | feeder2_line68 | 3 | 266.4 | 0.10378 | 0.10388 | 0.038956 | 0.038994
1230 | feeder2_line69 | 1 | 99 | 15.7924 | 15.7924 | 15.9519 | 15.9519
1230 | feeder2_line69 | 2 | 99 | 2.4581e-06 | 6.4485e-07 | 2.4829e-06 | 6.5136e-07
1230 | feeder2_line69 | 3 | 99 | 2.4834e-06 | 6.4932e-07 | 2.5085e-06 | 6.5588e-07
1230 | feeder2_line70 | 1 | 354.6 | 98.5893 | 98.5904 | 27.803 | 27.8033
1230 | feeder2_line70 | 2 | 354.6 | 119.8761 | 119.88 | 33.806 | 33.8071
1230 | feeder2_line70 | 3 | 354.6 | 102.6064 | 102.6019 | 28.9358 | 28.9346
1230 | feeder2_line71 | 1 | 99 | 4.8229e-08 | 6.993e-07 | 4.8716e-08 | 7.0636e-07
1230 | feeder2_line71 | 2 | 99 | 2.4918 | 2.4918 | 2.5169 | 2.517
1230 | feeder2_line71 | 3 | 99 | 4.8272e-08 | 6.9759e-07 | 4.876e-08 | 7.0464e-07
1230 | feeder2_line72 | 1 | 354.6 | 98.5893 | 98.5904 | 27.8029 | 27.8033
1230 | feeder2_line72 | 2 | 354.6 | 118.762 | 118.7661 | 33.4918 | 33.493
1230 | feeder2_line72 | 3 | 354.6 | 102.6063 | 102.6019 | 28.9358 | 28.9346
1230 | feeder2_line73 | 1 | 99 | 5.8541e-07 | 1.5019e-06 | 5.9133e-07 | 1.5171e-06
1230 | feeder2_line73 | 2 | 99 | 1.9164 | 1.9164 | 1.9358 | 1.9358
1230 | feeder2_line73 | 3 | 99 | 5.8417e-07 | 1.4985e-06 | 5.9007e-07 | 1.5137e-06
1230 | feeder2_line74 | 1 | 99 | 4.8338e-08 | 4.4795e-07 | 4.8827e-08 | 4.5247e-07
1230 | feeder2_line74 | 2 | 99 | 0.10479 | 0.10481 | 0.10585 | 0.10587
1230 | feeder2_line74 | 3 | 99 | 4.836e-08 | 4.4695e-07 | 4.8849e-08 | 4.5147e-07
1230 | feeder2_line75 | 1 | 266.4 | 2.3307 | 2.3307 | 0.87487 | 0.87488
1230 | feeder2_line75 | 2 | 266.4 | 0.092255 | 0.092286 | 0.03463 | 0.034642
1230 | feeder2_line75 | 3 | 266.4 | 0.10387 | 0.10388 | 0.038991 | 0.038994
1230 | feeder2_line76 | 1 | 99 | 2.3307 | 2.3307 | 2.3542 | 2.3542
1230 | feeder2_line76 | 2 | 99 | 8.2231e-07 | 1.536e-06 | 8.3061e-07 | 1.5515e-06
1230 | feeder2_line76 | 3 | 99 | 8.2791e-07 | 1.5458e-06 | 8.3627e-07 | 1.5615e-06
1230 | feeder2_line77 | 1 | 99 | 2.4164e-08 | 5.6291e-07 | 2.4408e-08 | 5.686e-07
1230 | feeder2_line77 | 2 | 99 | 2.4599e-08 | 5.581e-07 | 2.4848e-08 | 5.6374e-07
1230 | feeder2_line77 | 3 | 99 | 0.1039 | 0.10388 | 0.10495 | 0.10493
1230 | feeder2_line78 | 1 | 266.4 | 3.2495e-12 | 9.3327e-07 | 1.2198e-12 | 3.5033e-07
1230 | feeder2_line78 | 2 | 266.4 | 0.092286 | 0.092285 | 0.034642 | 0.034642
1230 | feeder2_line78 | 3 | 266.4 | 1.4715e-11 | 9.3131e-07 | 5.5236e-12 | 3.4959e-07
1230 | feeder2_line79 | 1 | 354.6 | 2.7829 | 2.7826 | 0.78481 | 0.78471
1230 | feeder2_line79 | 2 | 354.6 | 19.5044 | 19.504 | 5.5004 | 5.5003
1230 | feeder2_line79 | 3 | 354.6 | 16.4575 | 16.4572 | 4.6411 | 4.6411
1230 | feeder2_line80 | 1 | 354.6 | 97.5758 | 97.5769 | 27.5171 | 27.5175
1230 | feeder2_line80 | 2 | 354.6 | 107.652 | 107.6562 | 30.3587 | 30.3599
1230 | feeder2_line80 | 3 | 354.6 | 97.7345 | 97.7293 | 27.5619 | 27.5604
1230 | feeder2_line81 | 1 | 354.6 | 97.5756 | 97.5769 | 27.5171 | 27.5175
1230 | feeder2_line81 | 2 | 354.6 | 107.6518 | 107.6562 | 30.3587 | 30.3599
1230 | feeder2_line81 | 3 | 354.6 | 97.5757 | 97.5706 | 27.5171 | 27.5157
1230 | feeder2_line82 | 1 | 354.6 | 2.2644e-11 | 7.1644e-07 | 6.3857e-12 | 2.0204e-07
1230 | feeder2_line82 | 2 | 354.6 | 2.3821e-11 | 7.0959e-07 | 6.7176e-12 | 2.0011e-07
1230 | feeder2_line82 | 3 | 354.6 | 0.97547 | 0.97546 | 0.27509 | 0.27509
1230 | feeder2_line83 | 1 | 354.6 | 97.5756 | 97.5769 | 27.5171 | 27.5175
1230 | feeder2_line83 | 2 | 354.6 | 103.4508 | 103.4552 | 29.1739 | 29.1752
1230 | feeder2_line83 | 3 | 354.6 | 97.5758 | 97.5706 | 27.5171 | 27.5157
1230 | feeder2_line84 | 1 | 354.6 | 1.4018e-11 | 1.2658e-06 | 3.9533e-12 | 3.5695e-07
1230 | feeder2_line84 | 2 | 354.6 | 12.0996 | 12.0997 | 3.4122 | 3.4122
1230 | feeder2_line84 | 3 | 354.6 | 1.0173e-11 | 1.2623e-06 | 2.8687e-12 | 3.5599e-07
1230 | feeder2_line85 | 1 | 99 | 1.1064 | 1.1064 | 1.1176 | 1.1176
1230 | feeder2_line85 | 2 | 99 | 4.9172e-08 | 4.4712e-07 | 4.9669e-08 | 4.5164e-07
1230 | feeder2_line85 | 3 | 99 | 4.8191e-08 | 4.5056e-07 | 4.8678e-08 | 4.5512e-07
1230 | feeder2_line86 | 1 | 354.6 | 97.6015 | 97.6029 | 27.5244 | 27.5248
1230 | feeder2_line86 | 2 | 354.6 | 103.4508 | 103.4552 | 29.1739 | 29.1752
1230 | feeder2_line86 | 3 | 354.6 | 97.5757 | 97.5706 | 27.5171 | 27.5157
1230 | feeder2_line87 | 1 | 354.6 | 97.6015 | 97.6029 | 27.5244 | 27.5248
1230 | feeder2_line87 | 2 | 354.6 | 101.096 | 101.1006 | 28.5099 | 28.5112
1230 | feeder2_line87 | 3 | 354.6 | 96.1975 | 96.1923 | 27.1285 | 27.127
1230 | feeder2_line88 | 1 | 354.6 | 0.0001114 | 3.2798e-06 | 3.1415e-05 | 9.2493e-07
1230 | feeder2_line88 | 2 | 354.6 | 4.2624 | 4.2624 | 1.202 | 1.202
1230 | feeder2_line88 | 3 | 354.6 | 4.4337 | 4.4335 | 1.2503 | 1.2503
1230 | feeder2_line89 | 1 | 354.6 | 97.6015 | 97.6029 | 27.5244 | 27.5248
1230 | feeder2_line89 | 2 | 354.6 | 98.6295 | 98.6341 | 27.8143 | 27.8156
1230 | feeder2_line89 | 3 | 354.6 | 96.1975 | 96.1923 | 27.1284 | 27.127
1230 | feeder2_line90 | 1 | 354.6 | 0.00070663 | 1.979e-06 | 0.00019927 | 5.5808e-07
1230 | feeder2_line90 | 2 | 354.6 | 12.1741 | 12.1747 | 3.4332 | 3.4334
1230 | feeder2_line90 | 3 | 354.6 | 0.00070518 | 1.974e-06 | 0.00019887 | 5.5668e-07
1230 | feeder2_line91 | 1 | 354.6 | 97.6017 | 97.6029 | 27.5245 | 27.5248
1230 | feeder2_line91 | 2 | 354.6 | 98.6296 | 98.6341 | 27.8143 | 27.8156
1230 | feeder2_line91 | 3 | 354.6 | 94.7833 | 94.7778 | 26.7297 | 26.7281
1230 | feeder2_line92 | 1 | 354.6 | 1.1398e-11 | 9.9772e-07 | 3.2142e-12 | 2.8136e-07
1230 | feeder2_line92 | 2 | 354.6 | 1.3821e-11 | 9.8794e-07 | 3.8977e-12 | 2.7861e-07
1230 | feeder2_line92 | 3 | 354.6 | 4.9296 | 4.9296 | 1.3902 | 1.3902
1230 | feeder2_line93 | 1 | 99 | 2.4034e-08 | 3.3317e-07 | 2.4277e-08 | 3.3654e-07
1230 | feeder2_line93 | 2 | 99 | 12.0914 | 12.0915 | 12.2135 | 12.2136
1230 | feeder2_line93 | 3 | 99 | 2.4072e-08 | 3.3222e-07 | 2.4315e-08 | 3.3558e-07
1230 | feeder2_line94 | 1 | 354.6 | 2.4034e-06 | 1.6215e-06 | 6.7777e-07 | 4.5729e-07
1230 | feeder2_line94 | 2 | 354.6 | 0.084438 | 0.084459 | 0.023812 | 0.023818
1230 | feeder2_line94 | 3 | 354.6 | 2.4074e-06 | 1.6171e-06 | 6.7892e-07 | 4.5604e-07
1230 | feeder2_line95 | 1 | 99 | 3.4851e-06 | 2.5435e-06 | 3.5203e-06 | 2.5691e-06
1230 | feeder2_line95 | 2 | 99 | 4.2624 | 4.2624 | 4.3054 | 4.3054
1230 | feeder2_line95 | 3 | 99 | 3.4654e-06 | 2.5362e-06 | 3.5004e-06 | 2.5618e-06
1230 | feeder2_line96 | 1 | 354.6 | 0.00011808 | 6.0616e-07 | 3.3298e-05 | 1.7094e-07
1230 | feeder2_line96 | 2 | 354.6 | 0.00011669 | 6.0019e-07 | 3.2907e-05 | 1.6926e-07
1230 | feeder2_line96 | 3 | 354.6 | 4.4336 | 4.4335 | 1.2503 | 1.2503
1230 | feeder2_line97 | 1 | 354.6 | 97.2037 | 97.2046 | 27.4122 | 27.4125
1230 | feeder2_line97 | 2 | 354.6 | 98.6299 | 98.6341 | 27.8144 | 27.8156
1230 | feeder2_line97 | 3 | 354.6 | 94.7836 | 94.7778 | 26.7297 | 26.7281
1230 | feeder2_line98 | 1 | 354.6 | 1.9282 | 1.9266 | 0.54376 | 0.54332
1230 | feeder2_line98 | 2 | 354.6 | 0.0016275 | 5.9865e-07 | 0.00045896 | 1.6883e-07
1230 | feeder2_line98 | 3 | 354.6 | 0.0016666 | 6.0444e-07 | 0.00046998 | 1.7046e-07
1230 | feeder2_line99 | 1 | 99 | 2.4043e-08 | 4.3587e-07 | 2.4286e-08 | 4.4028e-07
1230 | feeder2_line99 | 2 | 99 | 2.4577e-08 | 4.3128e-07 | 2.4825e-08 | 4.3564e-07
1230 | feeder2_line99 | 3 | 99 | 4.4336 | 4.4335 | 4.4784 | 4.4783
1230 | feeder2_line100 | 1 | 99 | 1.9266 | 1.9266 | 1.946 | 1.9461
1230 | feeder2_line100 | 2 | 99 | 2.4564e-08 | 5.9148e-07 | 2.4812e-08 | 5.9746e-07
1230 | feeder2_line100 | 3 | 99 | 2.4066e-08 | 5.9615e-07 | 2.431e-08 | 6.0217e-07
1230 | feeder2_line101 | 1 | 354.6 | 0.083616 | 0.08322 | 0.02358 | 0.023469
1230 | feeder2_line101 | 2 | 354.6 | 19.5044 | 19.504 | 5.5004 | 5.5003
1230 | feeder2_line101 | 3 | 354.6 | 16.4575 | 16.4572 | 4.6411 | 4.6411
1230 | feeder2_line102 | 1 | 99 | 2.7028 | 2.7028 | 2.7301 | 2.7301
1230 | feeder2_line102 | 2 | 99 | 2.2442e-06 | 8.4812e-07 | 2.2668e-06 | 8.5669e-07
1230 | feeder2_line102 | 3 | 99 | 2.2817e-06 | 8.5446e-07 | 2.3048e-06 | 8.6309e-07
1230 | feeder2_line103 | 1 | 99 | 5.3644e-07 | 7.8454e-07 | 5.4186e-07 | 7.9246e-07
1230 | feeder2_line103 | 2 | 99 | 0.81497 | 0.81496 | 0.8232 | 0.8232
1230 | feeder2_line103 | 3 | 99 | 5.3458e-07 | 7.8203e-07 | 5.3998e-07 | 7.8993e-07
1230 | feeder2_line104 | 1 | 354.6 | 0.083513 | 0.083219 | 0.023551 | 0.023469
1230 | feeder2_line104 | 2 | 354.6 | 18.7167 | 18.7165 | 5.2783 | 5.2782
1230 | feeder2_line104 | 3 | 354.6 | 16.4574 | 16.4572 | 4.6411 | 4.6411
1230 | feeder2_line105 | 1 | 99 | 2.49e-06 | 7.2191e-07 | 2.5151e-06 | 7.292e-07
1230 | feeder2_line105 | 2 | 99 | 2.4524e-06 | 7.1418e-07 | 2.4772e-06 | 7.214e-07
1230 | feeder2_line105 | 3 | 99 | 0.04116 | 0.04112 | 0.041576 | 0.041535
1230 | feeder2_line106 | 1 | 354.6 | 0.083458 | 0.083219 | 0.023536 | 0.023469
1230 | feeder2_line106 | 2 | 354.6 | 18.7167 | 18.7165 | 5.2783 | 5.2782
1230 | feeder2_line106 | 3 | 354.6 | 16.4163 | 16.4162 | 4.6295 | 4.6295
1230 | feeder2_line107 | 1 | 99 | 3.1633e-07 | 8.7981e-07 | 3.1953e-07 | 8.887e-07
1230 | feeder2_line107 | 2 | 99 | 1.9569 | 1.9569 | 1.9767 | 1.9766
1230 | feeder2_line107 | 3 | 99 | 3.1547e-07 | 8.7673e-07 | 3.1865e-07 | 8.8559e-07
1230 | feeder2_line108 | 1 | 354.6 | 0.083447 | 0.083219 | 0.023533 | 0.023468
1230 | feeder2_line108 | 2 | 354.6 | 17.2482 | 17.248 | 4.8641 | 4.8641
1230 | feeder2_line108 | 3 | 354.6 | 16.4163 | 16.4162 | 4.6295 | 4.6295
1230 | feeder2_line109 | 1 | 354.6 | 96.2581 | 96.2595 | 27.1455 | 27.1459
1230 | feeder2_line109 | 2 | 354.6 | 98.6297 | 98.6341 | 27.8143 | 27.8156
1230 | feeder2_line109 | 3 | 354.6 | 94.7834 | 94.7778 | 26.7297 | 26.7281
1230 | feeder2_line110 | 1 | 99 | 1.6804 | 1.6797 | 1.6974 | 1.6967
1230 | feeder2_line110 | 2 | 99 | 0.00077162 | 8.753e-07 | 0.00077941 | 8.8414e-07
1230 | feeder2_line110 | 3 | 99 | 0.00078154 | 8.8169e-07 | 0.00078943 | 8.906e-07
1230 | feeder2_line111 | 1 | 99 | 2.404e-08 | 3.7226e-07 | 2.4283e-08 | 3.7602e-07
1230 | feeder2_line111 | 2 | 99 | 2.2039 | 2.2039 | 2.2261 | 2.2261
1230 | feeder2_line111 | 3 | 99 | 2.4086e-08 | 3.7121e-07 | 2.433e-08 | 3.7496e-07
1230 | feeder2_line112 | 1 | 99 | 3.1603e-07 | 8.9458e-07 | 3.1922e-07 | 9.0361e-07
1230 | feeder2_line112 | 2 | 99 | 2.0621 | 2.0621 | 2.0829 | 2.0829
1230 | feeder2_line112 | 3 | 99 | 3.153e-07 | 8.9204e-07 | 3.1849e-07 | 9.0105e-07
1230 | feeder2_line113 | 1 | 99 | 0.79591 | 0.79591 | 0.80394 | 0.80395
1230 | feeder2_line113 | 2 | 99 | 3.1352e-07 | 8.7175e-07 | 3.1669e-07 | 8.8055e-07
1230 | feeder2_line113 | 3 | 99 | 3.1498e-07 | 8.7865e-07 | 3.1817e-07 | 8.8752e-07
1230 | feeder2_line114 | 1 | 99 | 0.8132 | 0.81321 | 0.82142 | 0.82142
1230 | feeder2_line114 | 2 | 99 | 2.4596e-08 | 4.2174e-07 | 2.4845e-08 | 4.26e-07
1230 | feeder2_line114 | 3 | 99 | 2.4115e-08 | 4.2489e-07 | 2.4358e-08 | 4.2918e-07
1230 | feeder2_line115 | 1 | 99 | 2.4029e-08 | 5.491e-07 | 2.4271e-08 | 5.5464e-07
1230 | feeder2_line115 | 2 | 99 | 10.1082 | 10.1082 | 10.2103 | 10.2103
1230 | feeder2_line115 | 3 | 99 | 2.4117e-08 | 5.4703e-07 | 2.436e-08 | 5.5255e-07
1230 | feeder2_line116 | 1 | 354.6 | 0.083453 | 0.083219 | 0.023534 | 0.023468
1230 | feeder2_line116 | 2 | 354.6 | 7.4054 | 7.4052 | 2.0884 | 2.0883
1230 | feeder2_line116 | 3 | 354.6 | 16.4163 | 16.4162 | 4.6295 | 4.6295
1230 | feeder2_line117 | 1 | 99 | 4.8014e-08 | 6.2503e-07 | 4.8499e-08 | 6.3134e-07
1230 | feeder2_line117 | 2 | 99 | 3.9562 | 3.9562 | 3.9962 | 3.9962
1230 | feeder2_line117 | 3 | 99 | 4.8093e-08 | 6.2338e-07 | 4.8579e-08 | 6.2968e-07
1230 | feeder2_line118 | 1 | 354.6 | 96.2581 | 96.2595 | 27.1455 | 27.1459
1230 | feeder2_line118 | 2 | 354.6 | 96.2635 | 96.2681 | 27.1471 | 27.1484
1230 | feeder2_line118 | 3 | 354.6 | 94.7834 | 94.7778 | 26.7297 | 26.7281
1230 | feeder2_line119 | 1 | 99 | 2.4012e-08 | 5.909e-07 | 2.4255e-08 | 5.9687e-07
1230 | feeder2_line119 | 2 | 99 | 2.4614e-08 | 5.8422e-07 | 2.4863e-08 | 5.9013e-07
1230 | feeder2_line119 | 3 | 99 | 1.1468 | 1.1467 | 1.1583 | 1.1583
1230 | feeder2_line120 | 1 | 354.6 | 0.083454 | 0.083219 | 0.023535 | 0.023468
1230 | feeder2_line120 | 2 | 354.6 | 7.4054 | 7.4052 | 2.0884 | 2.0883
1230 | feeder2_line120 | 3 | 354.6 | 15.2698 | 15.2697 | 4.3062 | 4.3062
1230 | feeder2_line121 | 1 | 99 | 3.1635e-07 | 9.1509e-07 | 3.1954e-07 | 9.2434e-07
1230 | feeder2_line121 | 2 | 99 | 6.4111 | 6.4111 | 6.4758 | 6.4759
1230 | feeder2_line121 | 3 | 99 | 3.1532e-07 | 9.1113e-07 | 3.185e-07 | 9.2033e-07
1230 | feeder2_line122 | 1 | 354.6 | 0.083443 | 0.083219 | 0.023532 | 0.023468
1230 | feeder2_line122 | 2 | 354.6 | 1.1796 | 1.1796 | 0.33267 | 0.33264
1230 | feeder2_line122 | 3 | 354.6 | 15.2698 | 15.2697 | 4.3062 | 4.3062
1230 | feeder2_line123 | 1 | 99 | 5.6071e-07 | 9.4828e-07 | 5.6638e-07 | 9.5786e-07
1230 | feeder2_line123 | 2 | 99 | 5.5424e-07 | 9.3744e-07 | 5.5984e-07 | 9.4691e-07
1230 | feeder2_line123 | 3 | 99 | 0.078891 | 0.078888 | 0.079688 | 0.079685
1230 | feeder2_line124 | 1 | 354.6 | 0.083347 | 0.083218 | 0.023505 | 0.023468
1230 | feeder2_line124 | 2 | 354.6 | 1.1797 | 1.1796 | 0.33268 | 0.33265
1230 | feeder2_line124 | 3 | 354.6 | 15.1914 | 15.1914 | 4.2841 | 4.2841
1230 | feeder2_line125 | 1 | 99 | 5.6072e-07 | 8.8154e-07 | 5.6638e-07 | 8.9044e-07
1230 | feeder2_line125 | 2 | 99 | 5.5424e-07 | 8.7146e-07 | 5.5984e-07 | 8.8026e-07
1230 | feeder2_line125 | 3 | 99 | 1.9299 | 1.9298 | 1.9494 | 1.9493
1230 | feeder2_line126 | 1 | 354.6 | 0.0835 | 0.083218 | 0.023548 | 0.023468
1230 | feeder2_line126 | 2 | 354.6 | 1.1798 | 1.1796 | 0.33271 | 0.33265
1230 | feeder2_line126 | 3 | 354.6 | 13.262 | 13.2619 | 3.74 | 3.74
1230 | feeder2_line127 | 1 | 99 | 5.6071e-07 | 1.0553e-06 | 5.6638e-07 | 1.066e-06
1230 | feeder2_line127 | 2 | 99 | 5.5424e-07 | 1.0433e-06 | 5.5984e-07 | 1.0538e-06
1230 | feeder2_line127 | 3 | 99 | 11.4036 | 11.4038 | 11.5188 | 11.519
1230 | feeder2_line128 | 1 | 354.6 | 0.083415 | 0.083218 | 0.023524 | 0.023468
1230 | feeder2_line128 | 2 | 354.6 | 1.1798 | 1.1796 | 0.33271 | 0.33265
1230 | feeder2_line128 | 3 | 354.6 | 2.0016 | 2.0014 | 0.56447 | 0.5644
1230 | feeder2_line129 | 1 | 99 | 5.3674e-07 | 8.5575e-07 | 5.4217e-07 | 8.6439e-07
1230 | feeder2_line129 | 2 | 99 | 1.1795 | 1.1796 | 1.1915 | 1.1915
1230 | feeder2_line129 | 3 | 99 | 5.3396e-07 | 8.5175e-07 | 5.3935e-07 | 8.6035e-07
1230 | feeder2_line130 | 1 | 354.6 | 0.083428 | 0.083218 | 0.023527 | 0.023468
1230 | feeder2_line130 | 2 | 354.6 | 0.00029843 | 4.4782e-06 | 8.416e-05 | 1.2629e-06
1230 | feeder2_line130 | 3 | 354.6 | 2.0017 | 2.0014 | 0.56448 | 0.5644
1230 | feeder2_line131 | 1 | 99 | 5.6074e-07 | 9.4846e-07 | 5.664e-07 | 9.5804e-07
1230 | feeder2_line131 | 2 | 99 | 5.5425e-07 | 9.3761e-07 | 5.5985e-07 | 9.4709e-07
1230 | feeder2_line131 | 3 | 99 | 1.2359 | 1.2359 | 1.2483 | 1.2484
1230 | feeder2_line132 | 1 | 354.6 | 0.083274 | 0.083218 | 0.023484 | 0.023468
1230 | feeder2_line132 | 2 | 354.6 | 0.00012103 | 2.8158e-06 | 3.4132e-05 | 7.9406e-07
1230 | feeder2_line132 | 3 | 354.6 | 1.1058 | 1.1057 | 0.31184 | 0.31182
1230 | feeder2_line133 | 1 | 99 | 0.083207 | 0.083218 | 0.084048 | 0.084058
1230 | feeder2_line133 | 2 | 99 | 2.8943e-07 | 9.451e-07 | 2.9236e-07 | 9.5465e-07
1230 | feeder2_line133 | 3 | 99 | 2.9112e-07 | 9.5155e-07 | 2.9406e-07 | 9.6116e-07
1230 | feeder2_line134 | 1 | 354.6 | 6.8103e-12 | 1.7428e-06 | 1.9205e-12 | 4.9147e-07
1230 | feeder2_line134 | 2 | 354.6 | 5.4709e-12 | 1.7244e-06 | 1.5428e-12 | 4.863e-07
1230 | feeder2_line134 | 3 | 354.6 | 1.1057 | 1.1057 | 0.31183 | 0.31182
1230 | feeder2_line135 | 1 | 99 | 2.4847 | 2.4848 | 2.5098 | 2.5099
1230 | feeder2_line135 | 2 | 99 | 4.9051e-08 | 5.632e-07 | 4.9547e-08 | 5.6888e-07
1230 | feeder2_line135 | 3 | 99 | 4.8067e-08 | 5.6766e-07 | 4.8553e-08 | 5.7339e-07
1230 | feeder2_line136 | 1 | 354.6 | 96.0532 | 96.0546 | 27.0877 | 27.0882
1230 | feeder2_line136 | 2 | 354.6 | 96.2635 | 96.2681 | 27.1471 | 27.1484
1230 | feeder2_line136 | 3 | 354.6 | 94.7834 | 94.7778 | 26.7297 | 26.7281
1230 | feeder2_line137 | 1 | 99 | 1.3773 | 1.3773 | 1.3912 | 1.3912
1230 | feeder2_line137 | 2 | 99 | 8.1687e-07 | 1.5166e-06 | 8.2512e-07 | 1.5319e-06
1230 | feeder2_line137 | 3 | 99 | 8.2376e-07 | 1.5286e-06 | 8.3208e-07 | 1.5441e-06
1230 | feeder2_line138 | 1 | 354.6 | 95.9906 | 95.992 | 27.0701 | 27.0705
1230 | feeder2_line138 | 2 | 354.6 | 96.2636 | 96.2681 | 27.1471 | 27.1484
1230 | feeder2_line138 | 3 | 354.6 | 94.7834 | 94.7778 | 26.7297 | 26.7281
1230 | feeder2_line139 | 1 | 99 | 4.7984e-08 | 4.7742e-07 | 4.8468e-08 | 4.8224e-07
1230 | feeder2_line139 | 2 | 99 | 4.9037e-08 | 4.7247e-07 | 4.9533e-08 | 4.7724e-07
1230 | feeder2_line139 | 3 | 99 | 1.3015 | 1.3016 | 1.3147 | 1.3148
1230 | feeder2_line140 | 1 | 354.6 | 95.9905 | 95.992 | 27.0701 | 27.0705
1230 | feeder2_line140 | 2 | 354.6 | 96.2635 | 96.2681 | 27.1471 | 27.1484
1230 | feeder2_line140 | 3 | 354.6 | 93.7072 | 93.7014 | 26.4262 | 26.4245
1230 | feeder2_line141 | 1 | 99 | 2.4563e-06 | 4.7213e-07 | 2.4811e-06 | 4.769e-07
1230 | feeder2_line141 | 2 | 99 | 2.3354 | 2.3354 | 2.359 | 2.359
1230 | feeder2_line141 | 3 | 99 | 2.4488e-06 | 4.7095e-07 | 2.4735e-06 | 4.7571e-07
1230 | feeder2_line142 | 1 | 354.6 | 95.9907 | 95.992 | 27.0701 | 27.0705
1230 | feeder2_line142 | 2 | 354.6 | 95.3081 | 95.3126 | 26.8776 | 26.8789
1230 | feeder2_line142 | 3 | 354.6 | 93.7074 | 93.7014 | 26.4262 | 26.4245
1230 | feeder2_line143 | 1 | 99 | 8.2556e-07 | 1.6775e-06 | 8.339e-07 | 1.6944e-06
1230 | feeder2_line143 | 2 | 99 | 1.9552 | 1.9551 | 1.9749 | 1.9749
1230 | feeder2_line143 | 3 | 99 | 8.2345e-07 | 1.6733e-06 | 8.3177e-07 | 1.6902e-06
1230 | feeder2_line144 | 1 | 354.6 | 95.9906 | 95.992 | 27.0701 | 27.0705
1230 | feeder2_line144 | 2 | 354.6 | 93.7741 | 93.7787 | 26.445 | 26.4463
1230 | feeder2_line144 | 3 | 354.6 | 93.7073 | 93.7014 | 26.4262 | 26.4245
1230 | feeder2_line145 | 1 | 99 | 2.3989e-08 | 4.7032e-07 | 2.4231e-08 | 4.7507e-07
1230 | feeder2_line145 | 2 | 99 | 0.9801 | 0.98009 | 0.99 | 0.98999
1230 | feeder2_line145 | 3 | 99 | 2.402e-08 | 4.6915e-07 | 2.4263e-08 | 4.7389e-07
1230 | feeder2_line146 | 1 | 354.6 | 95.9906 | 95.992 | 27.0701 | 27.0705
1230 | feeder2_line146 | 2 | 354.6 | 93.7813 | 93.7859 | 26.4471 | 26.4484
1230 | feeder2_line146 | 3 | 354.6 | 93.7073 | 93.7014 | 26.4262 | 26.4245
1230 | feeder2_line147 | 1 | 99 | 1.1081 | 1.1081 | 1.1193 | 1.1193
1230 | feeder2_line147 | 2 | 99 | 1.1049e-06 | 2.1467e-06 | 1.1161e-06 | 2.1684e-06
1230 | feeder2_line147 | 3 | 99 | 1.1138e-06 | 2.1637e-06 | 1.125e-06 | 2.1855e-06
1230 | feeder2_line148 | 1 | 99 | 0.32328 | 0.3233 | 0.32655 | 0.32656
1230 | feeder2_line148 | 2 | 99 | 5.7698e-07 | 1.4385e-06 | 5.828e-07 | 1.453e-06
1230 | feeder2_line148 | 3 | 99 | 5.809e-07 | 1.4498e-06 | 5.8677e-07 | 1.4645e-06
1230 | feeder2_line149 | 1 | 354.6 | 95.1011 | 95.1025 | 26.8193 | 26.8197
1230 | feeder2_line149 | 2 | 354.6 | 93.7814 | 93.7859 | 26.4471 | 26.4484
1230 | feeder2_line149 | 3 | 354.6 | 93.7074 | 93.7014 | 26.4262 | 26.4245
1230 | feeder2_line150 | 1 | 354.6 | 95.1011 | 95.1025 | 26.8193 | 26.8197
1230 | feeder2_line150 | 2 | 354.6 | 93.8486 | 93.8531 | 26.4661 | 26.4673
1230 | feeder2_line150 | 3 | 354.6 | 93.7074 | 93.7014 | 26.4262 | 26.4245
1230 | feeder2_line151 | 1 | 99 | 9.4807e-06 | 1.7251e-06 | 9.5765e-06 | 1.7425e-06
1230 | feeder2_line151 | 2 | 99 | 0.90828 | 0.90829 | 0.91746 | 0.91746
1230 | feeder2_line151 | 3 | 99 | 9.4598e-06 | 1.7208e-06 | 9.5554e-06 | 1.7382e-06
1230 | feeder2_line152 | 1 | 354.6 | 1.1905e-11 | 1.1486e-06 | 3.3574e-12 | 3.2392e-07
1230 | feeder2_line152 | 2 | 354.6 | 1.0906e-11 | 1.1379e-06 | 3.0756e-12 | 3.2089e-07
1230 | feeder2_line152 | 3 | 354.6 | 1.1752 | 1.1752 | 0.33142 | 0.33141
1230 | feeder2_line153 | 1 | 99 | 6.3903 | 6.3903 | 6.4548 | 6.4549
1230 | feeder2_line153 | 2 | 99 | 4.8967e-08 | 5.6902e-07 | 4.9461e-08 | 5.7476e-07
1230 | feeder2_line153 | 3 | 99 | 4.8e-08 | 5.7344e-07 | 4.8485e-08 | 5.7923e-07
1230 | feeder2_line154 | 1 | 99 | 5.578e-07 | 8.5537e-07 | 5.6343e-07 | 8.6401e-07
1230 | feeder2_line154 | 2 | 99 | 5.521e-07 | 8.4672e-07 | 5.5768e-07 | 8.5528e-07
1230 | feeder2_line154 | 3 | 99 | 6.337 | 6.3369 | 6.401 | 6.4009
1230 | feeder2_line155 | 1 | 99 | 93.2935 | 93.2951 | 94.2359 | 94.2375
1230 | feeder2_line155 | 2 | 99 | 93.8486 | 93.8531 | 94.7966 | 94.8012
1230 | feeder2_line155 | 3 | 99 | 92.7244 | 92.7183 | 93.6611 | 93.6548
1230 | feeder2_line156 | 1 | 99 | 5.82e-07 | 1.1264e-06 | 5.8788e-07 | 1.1378e-06
1230 | feeder2_line156 | 2 | 99 | 0.81544 | 0.81543 | 0.82367 | 0.82367
1230 | feeder2_line156 | 3 | 99 | 5.8065e-07 | 1.1237e-06 | 5.8652e-07 | 1.135e-06
1230 | feeder2_line157 | 1 | 99 | 2.3972e-08 | 2.4454e-07 | 2.4214e-08 | 2.4701e-07
1230 | feeder2_line157 | 2 | 99 | 0.092895 | 0.092894 | 0.093834 | 0.093833
1230 | feeder2_line157 | 3 | 99 | 2.4009e-08 | 2.4395e-07 | 2.4252e-08 | 2.4641e-07
1260 | feeder2_line1 | 1 | 354.6 | 46.7812 | 46.7798 | 13.1927 | 13.1923
1260 | feeder2_line1 | 2 | 354.6 | 49.7296 | 49.7197 | 14.0241 | 14.0213
1260 | feeder2_line1 | 3 | 354.6 | 53.2809 | 53.2917 | 15.0256 | 15.0287
1260 | feeder2_line2 | 1 | 354.6 | 48.789 | 48.7874 | 13.7589 | 13.7584
1260 | feeder2_line2 | 2 | 354.6 | 49.7298 | 49.7197 | 14.0242 | 14.0213
1260 | feeder2_line2 | 3 | 354.6 | 53.2811 | 53.2917 | 15.0257 | 15.0287
1260 | feeder2_line3 | 1 | 80.1 | 2.008 | 2.008 | 2.5069 | 2.5069
1260 | feeder2_line3 | 2 | 80.1 | 5.719e-07 | 1.0569e-06 | 7.1399e-07 | 1.3194e-06
1260 | feeder2_line3 | 3 | 80.1 | 5.7201e-07 | 1.0571e-06 | 7.1412e-07 | 1.3197e-06
1260 | feeder2_line4 | 1 | 354.6 | 48.7891 | 48.7874 | 13.7589 | 13.7584
1260 | feeder2_line4 | 2 | 354.6 | 51.1955 | 51.1853 | 14.4375 | 14.4347
1260 | feeder2_line4 | 3 | 354.6 | 53.2812 | 53.2917 | 15.0257 | 15.0287
1260 | feeder2_line5 | 1 | 80.1 | 5.7186e-07 | 9.9785e-07 | 7.1393e-07 | 1.2458e-06
1260 | feeder2_line5 | 2 | 80.1 | 1.4772 | 1.4772 | 1.8442 | 1.8442
1260 | feeder2_line5 | 3 | 80.1 | 5.7204e-07 | 9.9817e-07 | 7.1416e-07 | 1.2462e-06
1260 | feeder2_line6 | 1 | 80.1 | 5.7191e-07 | 1.1739e-06 | 7.1399e-07 | 1.4656e-06
1260 | feeder2_line6 | 2 | 80.1 | 5.7198e-07 | 1.1741e-06 | 7.1408e-07 | 1.4658e-06
1260 | feeder2_line6 | 3 | 80.1 | 2.1945 | 2.1945 | 2.7397 | 2.7397
1260 | feeder2_line7 | 1 | 354.6 | 48.7892 | 48.7874 | 13.7589 | 13.7584
1260 | feeder2_line7 | 2 | 354.6 | 51.1956 | 51.1853 | 14.4376 | 14.4347
1260 | feeder2_line7 | 3 | 354.6 | 55.2369 | 55.2473 | 15.5773 | 15.5802
1260 | feeder2_line8 | 1 | 80.1 | 0.55094 | 0.55094 | 0.68782 | 0.68782
1260 | feeder2_line8 | 2 | 80.1 | 5.7212e-07 | 1.1324e-06 | 7.1426e-07 | 1.4137e-06
1260 | feeder2_line8 | 3 | 80.1 | 5.7226e-07 | 1.1326e-06 | 7.1443e-07 | 1.414e-06
1260 | feeder2_line9 | 1 | 354.6 | 49.3401 | 49.3382 | 13.9143 | 13.9138
1260 | feeder2_line9 | 2 | 354.6 | 51.1957 | 51.1853 | 14.4376 | 14.4347
1260 | feeder2_line9 | 3 | 354.6 | 55.237 | 55.2473 | 15.5773 | 15.5802
1260 | feeder2_line10 | 1 | 80.1 | 8.4562e-07 | 1.495e-06 | 1.0557e-06 | 1.8664e-06
1260 | feeder2_line10 | 2 | 80.1 | 0.55087 | 0.55087 | 0.68773 | 0.68772
1260 | feeder2_line10 | 3 | 80.1 | 8.4598e-07 | 1.4956e-06 | 1.0562e-06 | 1.8671e-06
1260 | feeder2_line11 | 1 | 354.6 | 49.3401 | 49.3382 | 13.9143 | 13.9138
1260 | feeder2_line11 | 2 | 354.6 | 51.7458 | 51.7354 | 14.5927 | 14.5898
1260 | feeder2_line11 | 3 | 354.6 | 55.237 | 55.2473 | 15.5773 | 15.5802
1260 | feeder2_line12 | 1 | 80.1 | 5.472e-07 | 9.9174e-07 | 6.8314e-07 | 1.2381e-06
1260 | feeder2_line12 | 2 | 80.1 | 5.4733e-07 | 9.919e-07 | 6.8331e-07 | 1.2383e-06
1260 | feeder2_line12 | 3 | 80.1 | 1.4142 | 1.4142 | 1.7656 | 1.7656
1260 | feeder2_line13 | 1 | 354.6 | 49.3401 | 49.3382 | 13.9143 | 13.9138
1260 | feeder2_line13 | 2 | 354.6 | 51.7457 | 51.7354 | 14.5927 | 14.5898
1260 | feeder2_line13 | 3 | 354.6 | 56.649 | 56.6593 | 15.9755 | 15.9784
1260 | feeder2_line14 | 1 | 80.1 | 2.633 | 2.633 | 3.2871 | 3.2871
1260 | feeder2_line14 | 2 | 80.1 | 2.9855e-07 | 6.4685e-07 | 3.7273e-07 | 8.0756e-07
1260 | feeder2_line14 | 3 | 80.1 | 2.9864e-07 | 6.4703e-07 | 3.7283e-07 | 8.0778e-07
1260 | feeder2_line15 | 1 | 354.6 | 51.9693 | 51.9675 | 14.6558 | 14.6552
1260 | feeder2_line15 | 2 | 354.6 | 51.7458 | 51.7354 | 14.5927 | 14.5898
1260 | feeder2_line15 | 3 | 354.6 | 56.649 | 56.6593 | 15.9755 | 15.9784
1260 | feeder2_line16 | 1 | 80.1 | 5.722e-07 | 1.0309e-06 | 7.1435e-07 | 1.287e-06
1260 | feeder2_line16 | 2 | 80.1 | 11.6846 | 11.6846 | 14.5875 | 14.5876
1260 | feeder2_line16 | 3 | 80.1 | 5.7247e-07 | 1.0314e-06 | 7.1469e-07 | 1.2876e-06
1260 | feeder2_line17 | 1 | 354.6 | 51.9693 | 51.9675 | 14.6558 | 14.6552
1260 | feeder2_line17 | 2 | 354.6 | 63.29 | 63.2798 | 17.8483 | 17.8454
1260 | feeder2_line17 | 3 | 354.6 | 56.649 | 56.6593 | 15.9755 | 15.9784
1260 | feeder2_line18 | 1 | 80.1 | 5.476e-07 | 7.3832e-07 | 6.8364e-07 | 9.2174e-07
1260 | feeder2_line18 | 2 | 80.1 | 5.4795e-07 | 7.3869e-07 | 6.8409e-07 | 9.2221e-07
1260 | feeder2_line18 | 3 | 80.1 | 0.040179 | 0.040195 | 0.050161 | 0.050181
1260 | feeder2_line19 | 1 | 354.6 | 51.9694 | 51.9675 | 14.6558 | 14.6552
1260 | feeder2_line19 | 2 | 354.6 | 63.29 | 63.2798 | 17.8483 | 17.8454
1260 | feeder2_line19 | 3 | 354.6 | 56.6891 | 56.6994 | 15.9868 | 15.9897
1260 | feeder2_line20 | 1 | 99 | 5.477e-07 | 8.8538e-07 | 5.5323e-07 | 8.9432e-07
1260 | feeder2_line20 | 2 | 99 | 5.4813e-07 | 8.8593e-07 | 5.5367e-07 | 8.9488e-07
1260 | feeder2_line20 | 3 | 99 | 2.6725 | 2.6725 | 2.6994 | 2.6995
1260 | feeder2_line21 | 1 | 354.6 | 51.9695 | 51.9675 | 14.6558 | 14.6552
1260 | feeder2_line21 | 2 | 354.6 | 63.2902 | 63.2798 | 17.8483 | 17.8454
1260 | feeder2_line21 | 3 | 354.6 | 59.0677 | 59.0778 | 16.6575 | 16.6604
1260 | feeder2_line22 | 1 | 99 | 5.7271e-07 | 1.0151e-06 | 5.785e-07 | 1.0254e-06
1260 | feeder2_line22 | 2 | 99 | 1.7815 | 1.7815 | 1.7995 | 1.7994
1260 | feeder2_line22 | 3 | 99 | 5.731e-07 | 1.0158e-06 | 5.7889e-07 | 1.026e-06
1260 | feeder2_line23 | 1 | 99 | 5.7271e-07 | 9.5022e-07 | 5.785e-07 | 9.5982e-07
1260 | feeder2_line23 | 2 | 99 | 5.7312e-07 | 9.5089e-07 | 5.7891e-07 | 9.6049e-07
1260 | feeder2_line23 | 3 | 99 | 1.2331 | 1.2331 | 1.2456 | 1.2456
1260 | feeder2_line24 | 1 | 354.6 | 51.9695 | 51.9675 | 14.6558 | 14.6552
1260 | feeder2_line24 | 2 | 354.6 | 65.0503 | 65.0398 | 18.3447 | 18.3418
1260 | feeder2_line24 | 3 | 354.6 | 60.2986 | 60.3087 | 17.0047 | 17.0075
1260 | feeder2_line25 | 1 | 99 | 1.7815 | 1.7815 | 1.7995 | 1.7995
1260 | feeder2_line25 | 2 | 99 | 4.9751e-08 | 6.9156e-07 | 5.0253e-08 | 6.9854e-07
1260 | feeder2_line25 | 3 | 99 | 4.9844e-08 | 6.915e-07 | 5.0348e-08 | 6.9848e-07
1260 | feeder2_line26 | 1 | 99 | 1.0863 | 1.0863 | 1.0972 | 1.0972
1260 | feeder2_line26 | 2 | 99 | 5.4845e-07 | 8.568e-07 | 5.5399e-07 | 8.6545e-07
1260 | feeder2_line26 | 3 | 99 | 5.4835e-07 | 8.5673e-07 | 5.5388e-07 | 8.6538e-07
1260 | feeder2_line27 | 1 | 354.6 | 54.8165 | 54.8144 | 15.4587 | 15.4581
1260 | feeder2_line27 | 2 | 354.6 | 65.0503 | 65.0398 | 18.3447 | 18.3418
1260 | feeder2_line27 | 3 | 354.6 | 60.2986 | 60.3087 | 17.0047 | 17.0075
1260 | feeder2_line28 | 1 | 99 | 2.5406e-06 | 7.1089e-07 | 2.5662e-06 | 7.1807e-07
1260 | feeder2_line28 | 2 | 99 | 0.7561 | 0.75612 | 0.76373 | 0.76376
1260 | feeder2_line28 | 3 | 99 | 2.5435e-06 | 7.115e-07 | 2.5692e-06 | 7.1869e-07
1260 | feeder2_line29 | 1 | 354.6 | 54.8166 | 54.8144 | 15.4587 | 15.4581
1260 | feeder2_line29 | 2 | 354.6 | 65.4907 | 65.4803 | 18.4689 | 18.466
1260 | feeder2_line29 | 3 | 354.6 | 60.2986 | 60.3087 | 17.0047 | 17.0075
1260 | feeder2_line30 | 1 | 266.4 | 4.2921 | 4.2917 | 1.6111 | 1.611
1260 | feeder2_line30 | 2 | 266.4 | 5.2186 | 5.2182 | 1.9589 | 1.9588
1260 | feeder2_line30 | 3 | 266.4 | 5.3775 | 5.3773 | 2.0186 | 2.0185
1260 | feeder2_line31 | 1 | 354.6 | 59.0962 | 59.0937 | 16.6656 | 16.6649
1260 | feeder2_line31 | 2 | 354.6 | 70.6408 | 70.63 | 19.9213 | 19.9182
1260 | feeder2_line31 | 3 | 354.6 | 65.532 | 65.5418 | 18.4805 | 18.4833
1260 | feeder2_line32 | 1 | 354.6 | 59.0962 | 59.0937 | 16.6656 | 16.6649
1260 | feeder2_line32 | 2 | 354.6 | 71.9114 | 71.9006 | 20.2796 | 20.2765
1260 | feeder2_line32 | 3 | 354.6 | 65.532 | 65.5418 | 18.4806 | 18.4833
1260 | feeder2_line33 | 1 | 99 | 5.0022e-08 | 6.864e-07 | 5.0527e-08 | 6.9333e-07
1260 | feeder2_line33 | 2 | 99 | 1.272 | 1.272 | 1.2848 | 1.2848
1260 | feeder2_line33 | 3 | 99 | 4.9933e-08 | 6.8715e-07 | 5.0438e-08 | 6.9409e-07
1260 | feeder2_line34 | 1 | 354.6 | 59.0962 | 59.0937 | 16.6656 | 16.6649
1260 | feeder2_line34 | 2 | 354.6 | 71.9114 | 71.9006 | 20.2796 | 20.2765
1260 | feeder2_line34 | 3 | 354.6 | 65.8071 | 65.8168 | 18.5581 | 18.5609
1260 | feeder2_line35 | 1 | 99 | 2.9931e-07 | 7.602e-07 | 3.0234e-07 | 7.6788e-07
1260 | feeder2_line35 | 2 | 99 | 2.9971e-07 | 7.614e-07 | 3.0273e-07 | 7.6909e-07
1260 | feeder2_line35 | 3 | 99 | 0.27533 | 0.27534 | 0.27811 | 0.27812
1260 | feeder2_line36 | 1 | 354.6 | 60.4014 | 60.3989 | 17.0337 | 17.033
1260 | feeder2_line36 | 2 | 354.6 | 71.9114 | 71.9006 | 20.2796 | 20.2765
1260 | feeder2_line36 | 3 | 354.6 | 65.807 | 65.8168 | 18.5581 | 18.5609
1260 | feeder2_line37 | 1 | 99 | 1.3053 | 1.3052 | 1.3184 | 1.3184
1260 | feeder2_line37 | 2 | 99 | 2.9978e-07 | 8.4267e-07 | 3.028e-07 | 8.5118e-07
1260 | feeder2_line37 | 3 | 99 | 2.9968e-07 | 8.4227e-07 | 3.0271e-07 | 8.5078e-07
1260 | feeder2_line38 | 1 | 99 | 3.2417e-07 | 7.7588e-07 | 3.2744e-07 | 7.8372e-07
1260 | feeder2_line38 | 2 | 99 | 1.3081 | 1.3081 | 1.3214 | 1.3213
1260 | feeder2_line38 | 3 | 99 | 3.2439e-07 | 7.7665e-07 | 3.2767e-07 | 7.845e-07
1260 | feeder2_line39 | 1 | 266.4 | 4.2921 | 4.2917 | 1.6111 | 1.611
1260 | feeder2_line39 | 2 | 266.4 | 3.9678 | 3.9675 | 1.4894 | 1.4893
1260 | feeder2_line39 | 3 | 266.4 | 5.3775 | 5.3773 | 2.0186 | 2.0185
1260 | feeder2_line40 | 1 | 354.6 | 62.1657 | 62.1631 | 17.5312 | 17.5305
1260 | feeder2_line40 | 2 | 354.6 | 71.9114 | 71.9006 | 20.2796 | 20.2765
1260 | feeder2_line40 | 3 | 354.6 | 65.8071 | 65.8168 | 18.5581 | 18.5609
1260 | feeder2_line41 | 1 | 99 | 1.7815 | 1.7815 | 1.7995 | 1.7994
1260 | feeder2_line41 | 2 | 99 | 4.9794e-08 | 7.3643e-07 | 5.0297e-08 | 7.4387e-07
1260 | feeder2_line41 | 3 | 99 | 4.9962e-08 | 7.3607e-07 | 5.0467e-08 | 7.4351e-07
1260 | feeder2_line42 | 1 | 99 | 2.9916e-07 | 7.4888e-07 | 3.0218e-07 | 7.5645e-07
1260 | feeder2_line42 | 2 | 99 | 2.9949e-07 | 7.4987e-07 | 3.0252e-07 | 7.5745e-07
1260 | feeder2_line42 | 3 | 99 | 1.762 | 1.762 | 1.7798 | 1.7798
1260 | feeder2_line43 | 1 | 266.4 | 4.292 | 4.2917 | 1.6111 | 1.611
1260 | feeder2_line43 | 2 | 266.4 | 3.9678 | 3.9675 | 1.4894 | 1.4893
1260 | feeder2_line43 | 3 | 266.4 | 3.654 | 3.6538 | 1.3716 | 1.3716
1260 | feeder2_line44 | 1 | 354.6 | 62.1657 | 62.1631 | 17.5312 | 17.5305
1260 | feeder2_line44 | 2 | 354.6 | 71.9115 | 71.9006 | 20.2796 | 20.2765
1260 | feeder2_line44 | 3 | 354.6 | 68.2351 | 68.2449 | 19.2428 | 19.2456
1260 | feeder2_line45 | 1 | 99 | 5.007e-08 | 5.7985e-07 | 5.0576e-08 | 5.857e-07
1260 | feeder2_line45 | 2 | 99 | 4.9798e-08 | 5.8085e-07 | 5.0301e-08 | 5.8672e-07
1260 | feeder2_line45 | 3 | 99 | 2.6729 | 2.673 | 2.6999 | 2.7
1260 | feeder2_line46 | 1 | 99 | 5.7333e-07 | 1.3576e-06 | 5.7912e-07 | 1.3713e-06
1260 | feeder2_line46 | 2 | 99 | 5.741e-07 | 1.3594e-06 | 5.799e-07 | 1.3731e-06
1260 | feeder2_line46 | 3 | 99 | 1.2564 | 1.2565 | 1.2691 | 1.2692
1260 | feeder2_line47 | 1 | 266.4 | 4.292 | 4.2917 | 1.6111 | 1.611
1260 | feeder2_line47 | 2 | 266.4 | 3.9678 | 3.9675 | 1.4894 | 1.4893
1260 | feeder2_line47 | 3 | 266.4 | 2.7769 | 2.7767 | 1.0424 | 1.0423
1260 | feeder2_line48 | 1 | 99 | 1.7447 | 1.7447 | 1.7623 | 1.7623
1260 | feeder2_line48 | 2 | 99 | 4.9769e-08 | 7.3191e-07 | 5.0271e-08 | 7.393e-07
1260 | feeder2_line48 | 3 | 99 | 4.9911e-08 | 7.3166e-07 | 5.0416e-08 | 7.3905e-07
1260 | feeder2_line49 | 1 | 266.4 | 2.5517 | 2.5514 | 0.95785 | 0.95775
1260 | feeder2_line49 | 2 | 266.4 | 3.9678 | 3.9675 | 1.4894 | 1.4893
1260 | feeder2_line49 | 3 | 266.4 | 2.7769 | 2.7767 | 1.0424 | 1.0423
1260 | feeder2_line50 | 1 | 99 | 5.7331e-07 | 1.2355e-06 | 5.791e-07 | 1.248e-06
1260 | feeder2_line50 | 2 | 99 | 2.1938 | 2.1937 | 2.216 | 2.2159
1260 | feeder2_line50 | 3 | 99 | 5.7388e-07 | 1.2367e-06 | 5.7968e-07 | 1.2492e-06
1260 | feeder2_line51 | 1 | 99 | 0.044837 | 0.044797 | 0.04529 | 0.04525
1260 | feeder2_line51 | 2 | 99 | 5.7409e-07 | 1.343e-06 | 5.7988e-07 | 1.3566e-06
1260 | feeder2_line51 | 3 | 99 | 5.7388e-07 | 1.3426e-06 | 5.7968e-07 | 1.3561e-06
1260 | feeder2_line52 | 1 | 266.4 | 2.5069 | 2.5068 | 0.94102 | 0.94098
1260 | feeder2_line52 | 2 | 266.4 | 1.8484 | 1.8483 | 0.69385 | 0.69381
1260 | feeder2_line52 | 3 | 266.4 | 2.7768 | 2.7767 | 1.0423 | 1.0423
1260 | feeder2_line53 | 1 | 99 | 5.4832e-07 | 7.5404e-07 | 5.5386e-07 | 7.6165e-07
1260 | feeder2_line53 | 2 | 99 | 1.8483 | 1.8483 | 1.867 | 1.867
1260 | feeder2_line53 | 3 | 99 | 5.4892e-07 | 7.5477e-07 | 5.5447e-07 | 7.624e-07
1260 | feeder2_line54 | 1 | 266.4 | 2.5067 | 2.5068 | 0.94095 | 0.94098
1260 | feeder2_line54 | 2 | 266.4 | 8.5622e-05 | 4.6316e-06 | 3.214e-05 | 1.7386e-06
1260 | feeder2_line54 | 3 | 266.4 | 2.7766 | 2.7767 | 1.0423 | 1.0423
1260 | feeder2_line55 | 1 | 99 | 1.4981 | 1.4981 | 1.5132 | 1.5132
1260 | feeder2_line55 | 2 | 99 | 4.9814e-08 | 7.3222e-07 | 5.0318e-08 | 7.3962e-07
1260 | feeder2_line55 | 3 | 99 | 4.9998e-08 | 7.3181e-07 | 5.0503e-08 | 7.392e-07
1260 | feeder2_line56 | 1 | 354.6 | 63.6553 | 63.6526 | 17.9513 | 17.9505
1260 | feeder2_line56 | 2 | 354.6 | 71.9115 | 71.9006 | 20.2796 | 20.2765
1260 | feeder2_line56 | 3 | 354.6 | 68.2352 | 68.2449 | 19.2429 | 19.2456
1260 | feeder2_line57 | 1 | 99 | 7.4989e-07 | 1.5445e-06 | 7.5747e-07 | 1.5601e-06
1260 | feeder2_line57 | 2 | 99 | 7.4651e-07 | 1.5466e-06 | 7.5406e-07 | 1.5622e-06
1260 | feeder2_line57 | 3 | 99 | 2.7767 | 2.7767 | 2.8047 | 2.8047
1260 | feeder2_line58 | 1 | 266.4 | 2.5068 | 2.5068 | 0.94098 | 0.94098
1260 | feeder2_line58 | 2 | 266.4 | 1.8976e-05 | 2.689e-06 | 7.1232e-06 | 1.0094e-06
1260 | feeder2_line58 | 3 | 266.4 | 1.897e-05 | 2.6882e-06 | 7.121e-06 | 1.0091e-06
1260 | feeder2_line59 | 1 | 99 | 4.9996e-08 | 5.3687e-07 | 5.0501e-08 | 5.423e-07
1260 | feeder2_line59 | 2 | 99 | 4.9771e-08 | 5.376e-07 | 5.0273e-08 | 5.4303e-07
1260 | feeder2_line59 | 3 | 99 | 1.361 | 1.361 | 1.3748 | 1.3748
1260 | feeder2_line60 | 1 | 99 | 2.9915e-07 | 8.1139e-07 | 3.0217e-07 | 8.1958e-07
1260 | feeder2_line60 | 2 | 99 | 2.9948e-07 | 8.1247e-07 | 3.0251e-07 | 8.2068e-07
1260 | feeder2_line60 | 3 | 99 | 1.4159 | 1.4158 | 1.4302 | 1.4301
1260 | feeder2_line61 | 1 | 266.4 | 2.2069 | 2.2071 | 0.82843 | 0.82849
1260 | feeder2_line61 | 2 | 266.4 | 2.9377 | 2.9378 | 1.1028 | 1.1028
1260 | feeder2_line61 | 3 | 266.4 | 3.376 | 3.3762 | 1.2673 | 1.2674
1260 | feeder2_line62 | 1 | 354.6 | 65.8618 | 65.8594 | 18.5736 | 18.5729
1260 | feeder2_line62 | 2 | 354.6 | 74.7713 | 74.7606 | 21.0861 | 21.0831
1260 | feeder2_line62 | 3 | 354.6 | 71.5195 | 71.5295 | 20.1691 | 20.1719
1260 | feeder2_line63 | 1 | 99 | 2.0919 | 2.0919 | 2.113 | 2.113
1260 | feeder2_line63 | 2 | 99 | 5.7409e-07 | 1.2215e-06 | 5.7988e-07 | 1.2339e-06
1260 | feeder2_line63 | 3 | 99 | 5.7388e-07 | 1.2211e-06 | 5.7967e-07 | 1.2334e-06
1260 | feeder2_line64 | 1 | 99 | 0.41633 | 0.41633 | 0.42053 | 0.42053
1260 | feeder2_line64 | 2 | 99 | 8.8022e-12 | 3.2178e-07 | 8.8911e-12 | 3.2503e-07
1260 | feeder2_line64 | 3 | 99 | 1.2642e-11 | 3.2166e-07 | 1.277e-11 | 3.2491e-07
1260 | feeder2_line65 | 1 | 99 | 5.0162e-08 | 6.4234e-07 | 5.0668e-08 | 6.4883e-07
1260 | feeder2_line65 | 2 | 99 | 1.4804 | 1.4805 | 1.4954 | 1.4954
1260 | feeder2_line65 | 3 | 99 | 5.0045e-08 | 6.4332e-07 | 5.0551e-08 | 6.4981e-07
1260 | feeder2_line66 | 1 | 354.6 | 65.8618 | 65.8594 | 18.5735 | 18.5729
1260 | feeder2_line66 | 2 | 354.6 | 76.2498 | 76.2392 | 21.5031 | 21.5001
1260 | feeder2_line66 | 3 | 354.6 | 71.5195 | 71.5295 | 20.1691 | 20.1719
1260 | feeder2_line67 | 1 | 99 | 2.5069e-08 | 3.6301e-07 | 2.5322e-08 | 3.6668e-07
1260 | feeder2_line67 | 2 | 99 | 2.4917e-08 | 3.6373e-07 | 2.5169e-08 | 3.674e-07
1260 | feeder2_line67 | 3 | 99 | 1.7815 | 1.7814 | 1.7995 | 1.7994
1260 | feeder2_line68 | 1 | 266.4 | 2.207 | 2.2071 | 0.82844 | 0.82849
1260 | feeder2_line68 | 2 | 266.4 | 2.9378 | 2.9378 | 1.1028 | 1.1028
1260 | feeder2_line68 | 3 | 266.4 | 1.6257 | 1.6259 | 0.61023 | 0.61031
1260 | feeder2_line69 | 1 | 99 | 14.2317 | 14.2317 | 14.3754 | 14.3755
1260 | feeder2_line69 | 2 | 99 | 2.5554e-06 | 6.684e-07 | 2.5812e-06 | 6.7515e-07
1260 | feeder2_line69 | 3 | 99 | 2.5521e-06 | 6.6797e-07 | 2.5779e-06 | 6.7471e-07
1260 | feeder2_line70 | 1 | 354.6 | 80.0743 | 80.072 | 22.5816 | 22.5809
1260 | feeder2_line70 | 2 | 354.6 | 76.2497 | 76.2392 | 21.503 | 21.5001
1260 | feeder2_line70 | 3 | 354.6 | 71.5194 | 71.5295 | 20.169 | 20.1719
1260 | feeder2_line71 | 1 | 99 | 5.0179e-08 | 7.1685e-07 | 5.0686e-08 | 7.2409e-07
1260 | feeder2_line71 | 2 | 99 | 3.9354 | 3.9353 | 3.9751 | 3.975
1260 | feeder2_line71 | 3 | 99 | 5.0068e-08 | 7.1793e-07 | 5.0574e-08 | 7.2518e-07
1260 | feeder2_line72 | 1 | 354.6 | 80.0744 | 80.072 | 22.5816 | 22.5809
1260 | feeder2_line72 | 2 | 354.6 | 79.605 | 79.5943 | 22.4492 | 22.4462
1260 | feeder2_line72 | 3 | 354.6 | 71.5195 | 71.5295 | 20.1691 | 20.1719
1260 | feeder2_line73 | 1 | 99 | 5.9933e-07 | 1.5368e-06 | 6.0538e-07 | 1.5523e-06
1260 | feeder2_line73 | 2 | 99 | 1.2714 | 1.2713 | 1.2842 | 1.2842
1260 | feeder2_line73 | 3 | 99 | 6.0009e-07 | 1.539e-06 | 6.0615e-07 | 1.5545e-06
1260 | feeder2_line74 | 1 | 99 | 5.0127e-08 | 4.5835e-07 | 5.0633e-08 | 4.6298e-07
1260 | feeder2_line74 | 2 | 99 | 1.6245 | 1.6245 | 1.641 | 1.6409
1260 | feeder2_line74 | 3 | 99 | 5.0022e-08 | 4.59e-07 | 5.0527e-08 | 4.6364e-07
1260 | feeder2_line75 | 1 | 266.4 | 2.2071 | 2.2071 | 0.82848 | 0.82849
1260 | feeder2_line75 | 2 | 266.4 | 0.089526 | 0.089553 | 0.033606 | 0.033616
1260 | feeder2_line75 | 3 | 266.4 | 1.6258 | 1.6259 | 0.61027 | 0.61031
1260 | feeder2_line76 | 1 | 99 | 2.2071 | 2.2071 | 2.2294 | 2.2294
1260 | feeder2_line76 | 2 | 99 | 8.507e-07 | 1.5885e-06 | 8.5929e-07 | 1.6045e-06
1260 | feeder2_line76 | 3 | 99 | 8.5011e-07 | 1.5875e-06 | 8.587e-07 | 1.6035e-06
1260 | feeder2_line77 | 1 | 99 | 2.5065e-08 | 5.7599e-07 | 2.5318e-08 | 5.8181e-07
1260 | feeder2_line77 | 2 | 99 | 2.4915e-08 | 5.7716e-07 | 2.5167e-08 | 5.8299e-07
1260 | feeder2_line77 | 3 | 99 | 1.6258 | 1.6259 | 1.6422 | 1.6423
1260 | feeder2_line78 | 1 | 266.4 | 1.4785e-11 | 9.5538e-07 | 5.55e-12 | 3.5863e-07
1260 | feeder2_line78 | 2 | 266.4 | 0.089558 | 0.089553 | 0.033618 | 0.033616
1260 | feeder2_line78 | 3 | 266.4 | 3.7488e-12 | 9.5665e-07 | 1.4072e-12 | 3.591e-07
1260 | feeder2_line79 | 1 | 354.6 | 5.3577 | 5.3574 | 1.5109 | 1.5108
1260 | feeder2_line79 | 2 | 354.6 | 5.5664 | 5.566 | 1.5698 | 1.5697
1260 | feeder2_line79 | 3 | 354.6 | 17.473 | 17.4725 | 4.9275 | 4.9274
1260 | feeder2_line80 | 1 | 354.6 | 85.3124 | 85.3094 | 24.0588 | 24.0579
1260 | feeder2_line80 | 2 | 354.6 | 84.6902 | 84.679 | 23.8833 | 23.8801
1260 | feeder2_line80 | 3 | 354.6 | 88.8546 | 88.864 | 25.0577 | 25.0603
1260 | feeder2_line81 | 1 | 354.6 | 85.3123 | 85.3094 | 24.0587 | 24.0579
1260 | feeder2_line81 | 2 | 354.6 | 84.6902 | 84.679 | 23.8833 | 23.8801
1260 | feeder2_line81 | 3 | 354.6 | 90.2745 | 90.2839 | 25.4581 | 25.4608
1260 | feeder2_line82 | 1 | 354.6 | 2.3534e-11 | 7.3572e-07 | 6.6366e-12 | 2.0748e-07
1260 | feeder2_line82 | 2 | 354.6 | 2.0099e-11 | 7.3716e-07 | 5.668e-12 | 2.0789e-07
1260 | feeder2_line82 | 3 | 354.6 | 1.4199 | 1.4199 | 0.40043 | 0.40044
1260 | feeder2_line83 | 1 | 354.6 | 85.3125 | 85.3094 | 24.0588 | 24.0579
1260 | feeder2_line83 | 2 | 354.6 | 86.8337 | 86.8222 | 24.4878 | 24.4845
1260 | feeder2_line83 | 3 | 354.6 | 90.2747 | 90.2839 | 25.4582 | 25.4608
1260 | feeder2_line84 | 1 | 354.6 | 1.1296e-11 | 1.3005e-06 | 3.1856e-12 | 3.6676e-07
1260 | feeder2_line84 | 2 | 354.6 | 2.1442 | 2.1441 | 0.60469 | 0.60466
1260 | feeder2_line84 | 3 | 354.6 | 1.1402e-11 | 1.3023e-06 | 3.2154e-12 | 3.6727e-07
1260 | feeder2_line85 | 1 | 99 | 1.3085 | 1.3085 | 1.3217 | 1.3217
1260 | feeder2_line85 | 2 | 99 | 4.9929e-08 | 4.6518e-07 | 5.0433e-08 | 4.6988e-07
1260 | feeder2_line85 | 3 | 99 | 5.0121e-08 | 4.6486e-07 | 5.0627e-08 | 4.6956e-07
1260 | feeder2_line86 | 1 | 354.6 | 86.6112 | 86.608 | 24.4251 | 24.4242
1260 | feeder2_line86 | 2 | 354.6 | 86.8338 | 86.8222 | 24.4878 | 24.4845
1260 | feeder2_line86 | 3 | 354.6 | 90.2748 | 90.2839 | 25.4582 | 25.4608
1260 | feeder2_line87 | 1 | 354.6 | 86.6114 | 86.608 | 24.4251 | 24.4242
1260 | feeder2_line87 | 2 | 354.6 | 90.3051 | 90.2931 | 25.4667 | 25.4634
1260 | feeder2_line87 | 3 | 354.6 | 94.2828 | 94.2917 | 26.5885 | 26.591
1260 | feeder2_line88 | 1 | 354.6 | 0.00011395 | 3.3714e-06 | 3.2134e-05 | 9.5076e-07
1260 | feeder2_line88 | 2 | 354.6 | 3.4724 | 3.472 | 0.97923 | 0.97914
1260 | feeder2_line88 | 3 | 354.6 | 4.0089 | 4.0088 | 1.1305 | 1.1305
1260 | feeder2_line89 | 1 | 354.6 | 86.6091 | 86.608 | 24.4245 | 24.4242
1260 | feeder2_line89 | 2 | 354.6 | 93.3875 | 93.3777 | 26.336 | 26.3332
1260 | feeder2_line89 | 3 | 354.6 | 94.2805 | 94.2917 | 26.5878 | 26.591
1260 | feeder2_line90 | 1 | 354.6 | 0.00072512 | 2.0367e-06 | 0.00020449 | 5.7435e-07
1260 | feeder2_line90 | 2 | 354.6 | 3.0845 | 3.0849 | 0.86986 | 0.86996
1260 | feeder2_line90 | 3 | 354.6 | 0.00072672 | 2.0397e-06 | 0.00020494 | 5.7522e-07
1260 | feeder2_line91 | 1 | 354.6 | 86.609 | 86.608 | 24.4244 | 24.4242
1260 | feeder2_line91 | 2 | 354.6 | 93.3874 | 93.3777 | 26.336 | 26.3332
1260 | feeder2_line91 | 3 | 354.6 | 95.6978 | 95.7092 | 26.9875 | 26.9907
1260 | feeder2_line92 | 1 | 354.6 | 6.5582e-12 | 1.0269e-06 | 1.8495e-12 | 2.8959e-07
1260 | feeder2_line92 | 2 | 354.6 | 6.5582e-12 | 1.029e-06 | 1.8495e-12 | 2.9019e-07
1260 | feeder2_line92 | 3 | 354.6 | 1.4191 | 1.419 | 0.40019 | 0.40018
1260 | feeder2_line93 | 1 | 99 | 2.5143e-08 | 3.4272e-07 | 2.5397e-08 | 3.4619e-07
1260 | feeder2_line93 | 2 | 99 | 2.1432 | 2.1431 | 2.1648 | 2.1647
1260 | feeder2_line93 | 3 | 99 | 2.5072e-08 | 3.4331e-07 | 2.5325e-08 | 3.4677e-07
1260 | feeder2_line94 | 1 | 354.6 | 2.5143e-06 | 1.6688e-06 | 7.0904e-07 | 4.7062e-07
1260 | feeder2_line94 | 2 | 354.6 | 0.9483 | 0.94824 | 0.26743 | 0.26741
1260 | feeder2_line94 | 3 | 354.6 | 2.5073e-06 | 1.6714e-06 | 7.0707e-07 | 4.7135e-07
1260 | feeder2_line95 | 1 | 99 | 3.5726e-06 | 2.6144e-06 | 3.6087e-06 | 2.6408e-06
1260 | feeder2_line95 | 2 | 99 | 3.4723 | 3.472 | 3.5073 | 3.5071
1260 | feeder2_line95 | 3 | 99 | 3.581e-06 | 2.6184e-06 | 3.6172e-06 | 2.6448e-06
1260 | feeder2_line96 | 1 | 354.6 | 0.00012131 | 6.2313e-07 | 3.4212e-05 | 1.7573e-07
1260 | feeder2_line96 | 2 | 354.6 | 0.00012162 | 6.2461e-07 | 3.4299e-05 | 1.7614e-07
1260 | feeder2_line96 | 3 | 354.6 | 4.0089 | 4.0088 | 1.1305 | 1.1305
1260 | feeder2_line97 | 1 | 354.6 | 86.7625 | 86.7614 | 24.4677 | 24.4674
1260 | feeder2_line97 | 2 | 354.6 | 93.3876 | 93.3777 | 26.336 | 26.3332
1260 | feeder2_line97 | 3 | 354.6 | 95.698 | 95.7092 | 26.9876 | 26.9907
1260 | feeder2_line98 | 1 | 354.6 | 0.1566 | 0.15494 | 0.044162 | 0.043693
1260 | feeder2_line98 | 2 | 354.6 | 0.0017133 | 6.2205e-07 | 0.00048318 | 1.7542e-07
1260 | feeder2_line98 | 3 | 354.6 | 0.001706 | 6.2587e-07 | 0.00048111 | 1.765e-07
1260 | feeder2_line99 | 1 | 99 | 2.5125e-08 | 4.4802e-07 | 2.5379e-08 | 4.5255e-07
1260 | feeder2_line99 | 2 | 99 | 2.4966e-08 | 4.4901e-07 | 2.5218e-08 | 4.5354e-07
1260 | feeder2_line99 | 3 | 99 | 4.0088 | 4.0088 | 4.0493 | 4.0493
1260 | feeder2_line100 | 1 | 99 | 0.1549 | 0.15494 | 0.15646 | 0.1565
1260 | feeder2_line100 | 2 | 99 | 2.4991e-08 | 6.1677e-07 | 2.5244e-08 | 6.23e-07
1260 | feeder2_line100 | 3 | 99 | 2.5079e-08 | 6.1643e-07 | 2.5333e-08 | 6.2266e-07
1260 | feeder2_line101 | 1 | 354.6 | 0.94874 | 0.94835 | 0.26755 | 0.26744
1260 | feeder2_line101 | 2 | 354.6 | 5.5664 | 5.566 | 1.5698 | 1.5697
1260 | feeder2_line101 | 3 | 354.6 | 17.473 | 17.4725 | 4.9275 | 4.9274
1260 | feeder2_line102 | 1 | 99 | 4.4502 | 4.4502 | 4.4952 | 4.4952
1260 | feeder2_line102 | 2 | 99 | 2.3468e-06 | 8.8137e-07 | 2.3705e-06 | 8.9028e-07
1260 | feeder2_line102 | 3 | 99 | 2.3394e-06 | 8.8049e-07 | 2.363e-06 | 8.8938e-07
1260 | feeder2_line103 | 1 | 99 | 5.4998e-07 | 8.0499e-07 | 5.5554e-07 | 8.1312e-07
1260 | feeder2_line103 | 2 | 99 | 1.3902 | 1.3901 | 1.4042 | 1.4042
1260 | feeder2_line103 | 3 | 99 | 5.5062e-07 | 8.0584e-07 | 5.5618e-07 | 8.1398e-07
1260 | feeder2_line104 | 1 | 354.6 | 0.94864 | 0.94835 | 0.26752 | 0.26744
1260 | feeder2_line104 | 2 | 354.6 | 4.3655 | 4.3653 | 1.2311 | 1.231
1260 | feeder2_line104 | 3 | 354.6 | 17.4729 | 17.4725 | 4.9275 | 4.9274
1260 | feeder2_line105 | 1 | 99 | 2.5493e-06 | 7.4071e-07 | 2.5751e-06 | 7.4819e-07
1260 | feeder2_line105 | 2 | 99 | 2.5575e-06 | 7.423e-07 | 2.5833e-06 | 7.498e-07
1260 | feeder2_line105 | 3 | 99 | 0.039995 | 0.040032 | 0.040399 | 0.040436
1260 | feeder2_line106 | 1 | 354.6 | 0.94858 | 0.94835 | 0.26751 | 0.26744
1260 | feeder2_line106 | 2 | 354.6 | 4.3655 | 4.3653 | 1.2311 | 1.231
1260 | feeder2_line106 | 3 | 354.6 | 17.4333 | 17.4329 | 4.9163 | 4.9162
1260 | feeder2_line107 | 1 | 99 | 3.2517e-07 | 9.027e-07 | 3.2846e-07 | 9.1182e-07
1260 | feeder2_line107 | 2 | 99 | 0.084585 | 0.084504 | 0.08544 | 0.085358
1260 | feeder2_line107 | 3 | 99 | 3.2538e-07 | 9.0338e-07 | 3.2867e-07 | 9.1251e-07
1260 | feeder2_line108 | 1 | 354.6 | 0.94857 | 0.94835 | 0.2675 | 0.26744
1260 | feeder2_line108 | 2 | 354.6 | 4.2964 | 4.2962 | 1.2116 | 1.2116
1260 | feeder2_line108 | 3 | 354.6 | 17.4333 | 17.4329 | 4.9163 | 4.9162
1260 | feeder2_line109 | 1 | 354.6 | 90.587 | 90.5846 | 25.5462 | 25.5456
1260 | feeder2_line109 | 2 | 354.6 | 93.3888 | 93.3777 | 26.3364 | 26.3332
1260 | feeder2_line109 | 3 | 354.6 | 95.6992 | 95.7092 | 26.9879 | 26.9907
1260 | feeder2_line110 | 1 | 99 | 4.1546 | 4.1539 | 4.1965 | 4.1959
1260 | feeder2_line110 | 2 | 99 | 0.00080862 | 9.1234e-07 | 0.00081679 | 9.2156e-07
1260 | feeder2_line110 | 3 | 99 | 0.00080769 | 9.1275e-07 | 0.00081585 | 9.2197e-07
1260 | feeder2_line111 | 1 | 99 | 2.5123e-08 | 3.8265e-07 | 2.5377e-08 | 3.8652e-07
1260 | feeder2_line111 | 2 | 99 | 1.7538 | 1.7537 | 1.7715 | 1.7714
1260 | feeder2_line111 | 3 | 99 | 2.5064e-08 | 3.8323e-07 | 2.5317e-08 | 3.8711e-07
1260 | feeder2_line112 | 1 | 99 | 3.2545e-07 | 9.1952e-07 | 3.2874e-07 | 9.288e-07
1260 | feeder2_line112 | 2 | 99 | 1.7186 | 1.7184 | 1.7359 | 1.7358
1260 | feeder2_line112 | 3 | 99 | 3.258e-07 | 9.2093e-07 | 3.2909e-07 | 9.3023e-07
1260 | feeder2_line113 | 1 | 99 | 4.0613 | 4.0614 | 4.1023 | 4.1024
1260 | feeder2_line113 | 2 | 99 | 3.2626e-07 | 9.097e-07 | 3.2956e-07 | 9.1889e-07
1260 | feeder2_line113 | 3 | 99 | 3.2623e-07 | 9.0925e-07 | 3.2952e-07 | 9.1843e-07
1260 | feeder2_line114 | 1 | 99 | 1.3911 | 1.3911 | 1.4051 | 1.4051
1260 | feeder2_line114 | 2 | 99 | 2.4939e-08 | 4.3827e-07 | 2.5191e-08 | 4.427e-07
1260 | feeder2_line114 | 3 | 99 | 2.5057e-08 | 4.3783e-07 | 2.531e-08 | 4.4225e-07
1260 | feeder2_line115 | 1 | 99 | 2.5074e-08 | 5.6335e-07 | 2.5328e-08 | 5.6904e-07
1260 | feeder2_line115 | 2 | 99 | 2.4448 | 2.4448 | 2.4695 | 2.4695
1260 | feeder2_line115 | 3 | 99 | 2.508e-08 | 5.6364e-07 | 2.5333e-08 | 5.6934e-07
1260 | feeder2_line116 | 1 | 354.6 | 0.94858 | 0.94835 | 0.26751 | 0.26744
1260 | feeder2_line116 | 2 | 354.6 | 1.9378 | 1.9377 | 0.54647 | 0.54644
1260 | feeder2_line116 | 3 | 354.6 | 17.4333 | 17.4329 | 4.9163 | 4.9162
1260 | feeder2_line117 | 1 | 99 | 5.0368e-08 | 6.4451e-07 | 5.0877e-08 | 6.5102e-07
1260 | feeder2_line117 | 2 | 99 | 1.2596 | 1.2596 | 1.2723 | 1.2723
1260 | feeder2_line117 | 3 | 99 | 5.0194e-08 | 6.4579e-07 | 5.0701e-08 | 6.5231e-07
1260 | feeder2_line118 | 1 | 354.6 | 90.587 | 90.5846 | 25.5463 | 25.5456
1260 | feeder2_line118 | 2 | 354.6 | 94.1675 | 94.1563 | 26.556 | 26.5528
1260 | feeder2_line118 | 3 | 354.6 | 95.6992 | 95.7092 | 26.9879 | 26.9907
1260 | feeder2_line119 | 1 | 99 | 2.5063e-08 | 6.0621e-07 | 2.5317e-08 | 6.1233e-07
1260 | feeder2_line119 | 2 | 99 | 2.4926e-08 | 6.0747e-07 | 2.5178e-08 | 6.1361e-07
1260 | feeder2_line119 | 3 | 99 | 2.9729 | 2.9729 | 3.0029 | 3.003
1260 | feeder2_line120 | 1 | 354.6 | 0.94858 | 0.94835 | 0.26751 | 0.26744
1260 | feeder2_line120 | 2 | 354.6 | 1.9378 | 1.9377 | 0.54647 | 0.54644
1260 | feeder2_line120 | 3 | 354.6 | 14.6029 | 14.6024 | 4.1181 | 4.118
1260 | feeder2_line121 | 1 | 99 | 3.2517e-07 | 9.3877e-07 | 3.2845e-07 | 9.4826e-07
1260 | feeder2_line121 | 2 | 99 | 0.50149 | 0.5015 | 0.50656 | 0.50656
1260 | feeder2_line121 | 3 | 99 | 3.2524e-07 | 9.3878e-07 | 3.2852e-07 | 9.4827e-07
1260 | feeder2_line122 | 1 | 354.6 | 0.94857 | 0.94835 | 0.2675 | 0.26744
1260 | feeder2_line122 | 2 | 354.6 | 1.4803 | 1.4802 | 0.41745 | 0.41743
1260 | feeder2_line122 | 3 | 354.6 | 14.6029 | 14.6024 | 4.1181 | 4.118
1260 | feeder2_line123 | 1 | 99 | 5.7518e-07 | 9.7281e-07 | 5.8099e-07 | 9.8263e-07
1260 | feeder2_line123 | 2 | 99 | 5.764e-07 | 9.7483e-07 | 5.8222e-07 | 9.8468e-07
1260 | feeder2_line123 | 3 | 99 | 0.75639 | 0.7564 | 0.76403 | 0.76404
1260 | feeder2_line124 | 1 | 354.6 | 0.94847 | 0.94835 | 0.26748 | 0.26744
1260 | feeder2_line124 | 2 | 354.6 | 1.4803 | 1.4802 | 0.41746 | 0.41743
1260 | feeder2_line124 | 3 | 354.6 | 14.0962 | 14.0958 | 3.9752 | 3.9751
1260 | feeder2_line125 | 1 | 99 | 5.7519e-07 | 9.0433e-07 | 5.81e-07 | 9.1347e-07
1260 | feeder2_line125 | 2 | 99 | 5.7641e-07 | 9.0622e-07 | 5.8223e-07 | 9.1537e-07
1260 | feeder2_line125 | 3 | 99 | 0.15503 | 0.15506 | 0.1566 | 0.15662
1260 | feeder2_line126 | 1 | 354.6 | 0.94862 | 0.94835 | 0.26752 | 0.26744
1260 | feeder2_line126 | 2 | 354.6 | 1.4804 | 1.4802 | 0.4175 | 0.41743
1260 | feeder2_line126 | 3 | 354.6 | 13.9444 | 13.9438 | 3.9324 | 3.9323
1260 | feeder2_line127 | 1 | 99 | 5.7518e-07 | 1.0826e-06 | 5.8099e-07 | 1.0936e-06
1260 | feeder2_line127 | 2 | 99 | 5.764e-07 | 1.0849e-06 | 5.8222e-07 | 1.0958e-06
1260 | feeder2_line127 | 3 | 99 | 12.0378 | 12.0375 | 12.1594 | 12.1591
1260 | feeder2_line128 | 1 | 354.6 | 0.94854 | 0.94835 | 0.2675 | 0.26744
1260 | feeder2_line128 | 2 | 354.6 | 1.4804 | 1.4802 | 0.41749 | 0.41743
1260 | feeder2_line128 | 3 | 354.6 | 1.9266 | 1.9264 | 0.54332 | 0.54326
1260 | feeder2_line129 | 1 | 99 | 5.5016e-07 | 8.7787e-07 | 5.5571e-07 | 8.8674e-07
1260 | feeder2_line129 | 2 | 99 | 1.4802 | 1.4802 | 1.4951 | 1.4952
1260 | feeder2_line129 | 3 | 99 | 5.4992e-07 | 8.7761e-07 | 5.5547e-07 | 8.8648e-07
1260 | feeder2_line130 | 1 | 354.6 | 0.94855 | 0.94835 | 0.2675 | 0.26744
1260 | feeder2_line130 | 2 | 354.6 | 0.00030952 | 4.655e-06 | 8.7286e-05 | 1.3127e-06
1260 | feeder2_line130 | 3 | 354.6 | 1.9266 | 1.9264 | 0.54333 | 0.54326
1260 | feeder2_line131 | 1 | 99 | 5.752e-07 | 9.7298e-07 | 5.8101e-07 | 9.8281e-07
1260 | feeder2_line131 | 2 | 99 | 5.7642e-07 | 9.7501e-07 | 5.8224e-07 | 9.8486e-07
1260 | feeder2_line131 | 3 | 99 | 0.62233 | 0.62233 | 0.62862 | 0.62861
1260 | feeder2_line132 | 1 | 354.6 | 0.94839 | 0.94835 | 0.26745 | 0.26744
1260 | feeder2_line132 | 2 | 354.6 | 0.00012623 | 2.9267e-06 | 3.5597e-05 | 8.2534e-07
1260 | feeder2_line132 | 3 | 354.6 | 1.3084 | 1.3083 | 0.36897 | 0.36895
1260 | feeder2_line133 | 1 | 99 | 0.94832 | 0.94835 | 0.9579 | 0.95793
1260 | feeder2_line133 | 2 | 99 | 3.0067e-07 | 9.828e-07 | 3.037e-07 | 9.9272e-07
1260 | feeder2_line133 | 3 | 99 | 3.0006e-07 | 9.8045e-07 | 3.0309e-07 | 9.9035e-07
1260 | feeder2_line134 | 1 | 354.6 | 9.2289e-12 | 1.7886e-06 | 2.6026e-12 | 5.044e-07
1260 | feeder2_line134 | 2 | 354.6 | 6.331e-12 | 1.792e-06 | 1.7854e-12 | 5.0536e-07
1260 | feeder2_line134 | 3 | 354.6 | 1.3083 | 1.3083 | 0.36895 | 0.36895
1260 | feeder2_line135 | 1 | 99 | 3.9354 | 3.9354 | 3.9752 | 3.9752
1260 | feeder2_line135 | 2 | 99 | 5.0061e-08 | 5.8901e-07 | 5.0567e-08 | 5.9496e-07
1260 | feeder2_line135 | 3 | 99 | 5.0214e-08 | 5.8877e-07 | 5.0721e-08 | 5.9472e-07
1260 | feeder2_line136 | 1 | 354.6 | 93.992 | 93.9896 | 26.5065 | 26.5058
1260 | feeder2_line136 | 2 | 354.6 | 94.1675 | 94.1563 | 26.556 | 26.5528
1260 | feeder2_line136 | 3 | 354.6 | 95.6992 | 95.7092 | 26.9879 | 26.9907
1260 | feeder2_line137 | 1 | 99 | 2.6689 | 2.6689 | 2.6959 | 2.6959
1260 | feeder2_line137 | 2 | 99 | 8.5495e-07 | 1.5866e-06 | 8.6359e-07 | 1.6026e-06
1260 | feeder2_line137 | 3 | 99 | 8.5454e-07 | 1.586e-06 | 8.6317e-07 | 1.602e-06
1260 | feeder2_line138 | 1 | 354.6 | 96.2005 | 96.198 | 27.1293 | 27.1286
1260 | feeder2_line138 | 2 | 354.6 | 94.1676 | 94.1563 | 26.556 | 26.5528
1260 | feeder2_line138 | 3 | 354.6 | 95.6993 | 95.7092 | 26.9879 | 26.9907
1260 | feeder2_line139 | 1 | 99 | 5.0431e-08 | 4.9321e-07 | 5.094e-08 | 4.9819e-07
1260 | feeder2_line139 | 2 | 99 | 5.0074e-08 | 4.9444e-07 | 5.058e-08 | 4.9943e-07
1260 | feeder2_line139 | 3 | 99 | 2.2682 | 2.2687 | 2.2911 | 2.2916
1260 | feeder2_line140 | 1 | 354.6 | 96.2006 | 96.198 | 27.1293 | 27.1286
1260 | feeder2_line140 | 2 | 354.6 | 94.1677 | 94.1563 | 26.556 | 26.5528
1260 | feeder2_line140 | 3 | 354.6 | 97.112 | 97.1225 | 27.3864 | 27.3893
1260 | feeder2_line141 | 1 | 99 | 2.5324e-06 | 4.8794e-07 | 2.5579e-06 | 4.9287e-07
1260 | feeder2_line141 | 2 | 99 | 1.7628 | 1.7628 | 1.7806 | 1.7806
1260 | feeder2_line141 | 3 | 99 | 2.5399e-06 | 4.8897e-07 | 2.5655e-06 | 4.9391e-07
1260 | feeder2_line142 | 1 | 354.6 | 96.2004 | 96.198 | 27.1293 | 27.1286
1260 | feeder2_line142 | 2 | 354.6 | 95.9296 | 95.9184 | 27.0529 | 27.0498
1260 | feeder2_line142 | 3 | 354.6 | 97.1118 | 97.1225 | 27.3863 | 27.3893
1260 | feeder2_line143 | 1 | 99 | 8.5311e-07 | 1.734e-06 | 8.6172e-07 | 1.7515e-06
1260 | feeder2_line143 | 2 | 99 | 0.084297 | 0.084192 | 0.085149 | 0.085042
1260 | feeder2_line143 | 3 | 99 | 8.5499e-07 | 1.7376e-06 | 8.6362e-07 | 1.7552e-06
1260 | feeder2_line144 | 1 | 354.6 | 96.2003 | 96.198 | 27.1292 | 27.1286
1260 | feeder2_line144 | 2 | 354.6 | 96.0135 | 96.0024 | 27.0766 | 27.0734
1260 | feeder2_line144 | 3 | 354.6 | 97.1116 | 97.1225 | 27.3863 | 27.3893
1260 | feeder2_line145 | 1 | 99 | 2.522e-08 | 4.8625e-07 | 2.5475e-08 | 4.9116e-07
1260 | feeder2_line145 | 2 | 99 | 1.4198 | 1.4198 | 1.4342 | 1.4341
1260 | feeder2_line145 | 3 | 99 | 2.5127e-08 | 4.8727e-07 | 2.538e-08 | 4.9219e-07
1260 | feeder2_line146 | 1 | 354.6 | 96.2001 | 96.198 | 27.1292 | 27.1286
1260 | feeder2_line146 | 2 | 354.6 | 97.4329 | 97.4219 | 27.4768 | 27.4737
1260 | feeder2_line146 | 3 | 354.6 | 97.1115 | 97.1225 | 27.3862 | 27.3893
1260 | feeder2_line147 | 1 | 99 | 0.10772 | 0.10772 | 0.10881 | 0.10881
1260 | feeder2_line147 | 2 | 99 | 1.1574e-06 | 2.2485e-06 | 1.1691e-06 | 2.2712e-06
1260 | feeder2_line147 | 3 | 99 | 1.157e-06 | 2.2477e-06 | 1.1687e-06 | 2.2704e-06
1260 | feeder2_line148 | 1 | 99 | 1.0809 | 1.0809 | 1.0918 | 1.0918
1260 | feeder2_line148 | 2 | 99 | 6.0376e-07 | 1.5067e-06 | 6.0986e-07 | 1.5219e-06
1260 | feeder2_line148 | 3 | 99 | 6.0361e-07 | 1.5061e-06 | 6.0971e-07 | 1.5213e-06
1260 | feeder2_line149 | 1 | 354.6 | 97.3846 | 97.3824 | 27.4632 | 27.4626
1260 | feeder2_line149 | 2 | 354.6 | 97.433 | 97.4219 | 27.4769 | 27.4737
1260 | feeder2_line149 | 3 | 354.6 | 97.1117 | 97.1225 | 27.3863 | 27.3893
1260 | feeder2_line150 | 1 | 354.6 | 97.3847 | 97.3824 | 27.4633 | 27.4626
1260 | feeder2_line150 | 2 | 354.6 | 98.9078 | 98.8965 | 27.8928 | 27.8896
1260 | feeder2_line150 | 3 | 354.6 | 97.1118 | 97.1225 | 27.3863 | 27.3893
1260 | feeder2_line151 | 1 | 99 | 9.7877e-06 | 1.7856e-06 | 9.8866e-06 | 1.8036e-06
1260 | feeder2_line151 | 2 | 99 | 1.4781 | 1.4781 | 1.493 | 1.493
1260 | feeder2_line151 | 3 | 99 | 9.8171e-06 | 1.7894e-06 | 9.9163e-06 | 1.8074e-06
1260 | feeder2_line152 | 1 | 354.6 | 3.3927e-12 | 1.1905e-06 | 9.5676e-13 | 3.3572e-07
1260 | feeder2_line152 | 2 | 354.6 | 9.6202e-12 | 1.1931e-06 | 2.713e-12 | 3.3647e-07
1260 | feeder2_line152 | 3 | 354.6 | 0.076448 | 0.076455 | 0.021559 | 0.021561
1260 | feeder2_line153 | 1 | 99 | 0.50133 | 0.50134 | 0.5064 | 0.50641
1260 | feeder2_line153 | 2 | 99 | 5.0153e-08 | 5.9701e-07 | 5.066e-08 | 6.0304e-07
1260 | feeder2_line153 | 3 | 99 | 5.0311e-08 | 5.9677e-07 | 5.0819e-08 | 6.028e-07
1260 | feeder2_line154 | 1 | 99 | 5.7784e-07 | 8.8616e-07 | 5.8368e-07 | 8.9511e-07
1260 | feeder2_line154 | 2 | 99 | 5.7931e-07 | 8.8838e-07 | 5.8516e-07 | 8.9735e-07
1260 | feeder2_line154 | 3 | 99 | 1.8165 | 1.8165 | 1.8348 | 1.8349
1260 | feeder2_line155 | 1 | 99 | 97.845 | 97.8428 | 98.8334 | 98.8311
1260 | feeder2_line155 | 2 | 99 | 98.9077 | 98.8965 | 99.9068 | 99.8955
1260 | feeder2_line155 | 3 | 99 | 99 | 99.0108 | 100 | 100.0109
1260 | feeder2_line156 | 1 | 99 | 6.0282e-07 | 1.166e-06 | 6.0891e-07 | 1.1778e-06
1260 | feeder2_line156 | 2 | 99 | 1.389 | 1.389 | 1.4031 | 1.403
1260 | feeder2_line156 | 3 | 99 | 6.0394e-07 | 1.1684e-06 | 6.1004e-07 | 1.1802e-06
1260 | feeder2_line157 | 1 | 99 | 2.5245e-08 | 2.5314e-07 | 2.55e-08 | 2.5569e-07
1260 | feeder2_line157 | 2 | 99 | 0.089112 | 0.089104 | 0.090012 | 0.090004
1260 | feeder2_line157 | 3 | 99 | 2.5143e-08 | 2.5366e-07 | 2.5397e-08 | 2.5622e-07
1290 | feeder2_line1 | 1 | 354.6 | 33.5742 | 33.5819 | 9.4682 | 9.4704
1290 | feeder2_line1 | 2 | 354.6 | 22.3392 | 22.3475 | 6.2998 | 6.3022
1290 | feeder2_line1 | 3 | 354.6 | 49.133 | 49.1213 | 13.8559 | 13.8526
1290 | feeder2_line2 | 1 | 354.6 | 36.0485 | 36.056 | 10.166 | 10.1681
1290 | feeder2_line2 | 2 | 354.6 | 22.3393 | 22.3475 | 6.2999 | 6.3022
1290 | feeder2_line2 | 3 | 354.6 | 49.1331 | 49.1213 | 13.8559 | 13.8526
1290 | feeder2_line3 | 1 | 80.1 | 2.5355 | 2.5355 | 3.1654 | 3.1654
1290 | feeder2_line3 | 2 | 80.1 | 5.7058e-07 | 1.0544e-06 | 7.1234e-07 | 1.3164e-06
1290 | feeder2_line3 | 3 | 80.1 | 5.7199e-07 | 1.057e-06 | 7.1409e-07 | 1.3196e-06
1290 | feeder2_line4 | 1 | 354.6 | 36.0486 | 36.056 | 10.166 | 10.1681
1290 | feeder2_line4 | 2 | 354.6 | 23.2397 | 23.2478 | 6.5538 | 6.5561
1290 | feeder2_line4 | 3 | 354.6 | 49.1333 | 49.1213 | 13.856 | 13.8526
1290 | feeder2_line5 | 1 | 80.1 | 5.7148e-07 | 9.9719e-07 | 7.1346e-07 | 1.2449e-06
1290 | feeder2_line5 | 2 | 80.1 | 1.0877 | 1.0877 | 1.358 | 1.358
1290 | feeder2_line5 | 3 | 80.1 | 5.7202e-07 | 9.9812e-07 | 7.1414e-07 | 1.2461e-06
1290 | feeder2_line6 | 1 | 80.1 | 5.7151e-07 | 1.1731e-06 | 7.1349e-07 | 1.4646e-06
1290 | feeder2_line6 | 2 | 80.1 | 5.7056e-07 | 1.1712e-06 | 7.1231e-07 | 1.4622e-06
1290 | feeder2_line6 | 3 | 80.1 | 3.6814 | 3.6814 | 4.5961 | 4.596
1290 | feeder2_line7 | 1 | 354.6 | 36.0487 | 36.056 | 10.166 | 10.1681
1290 | feeder2_line7 | 2 | 354.6 | 23.2398 | 23.2478 | 6.5538 | 6.5561
1290 | feeder2_line7 | 3 | 354.6 | 52.372 | 52.3599 | 14.7693 | 14.7659
1290 | feeder2_line8 | 1 | 80.1 | 0.95307 | 0.95307 | 1.1898 | 1.1898
1290 | feeder2_line8 | 2 | 80.1 | 5.7053e-07 | 1.1292e-06 | 7.1227e-07 | 1.4098e-06
1290 | feeder2_line8 | 3 | 80.1 | 5.7227e-07 | 1.1326e-06 | 7.1445e-07 | 1.414e-06
1290 | feeder2_line9 | 1 | 354.6 | 36.9644 | 36.9717 | 10.4243 | 10.4263
1290 | feeder2_line9 | 2 | 354.6 | 23.2398 | 23.2478 | 6.5538 | 6.5561
1290 | feeder2_line9 | 3 | 354.6 | 52.372 | 52.3599 | 14.7693 | 14.7659
1290 | feeder2_line10 | 1 | 80.1 | 8.4498e-07 | 1.4938e-06 | 1.0549e-06 | 1.865e-06
1290 | feeder2_line10 | 2 | 80.1 | 0.95438 | 0.95438 | 1.1915 | 1.1915
1290 | feeder2_line10 | 3 | 80.1 | 8.4607e-07 | 1.4956e-06 | 1.0563e-06 | 1.8672e-06
1290 | feeder2_line11 | 1 | 354.6 | 36.9644 | 36.9717 | 10.4243 | 10.4263
1290 | feeder2_line11 | 2 | 354.6 | 24.0311 | 24.039 | 6.777 | 6.7792
1290 | feeder2_line11 | 3 | 354.6 | 52.372 | 52.3599 | 14.7693 | 14.7659
1290 | feeder2_line12 | 1 | 80.1 | 5.4677e-07 | 9.9096e-07 | 6.826e-07 | 1.2372e-06
1290 | feeder2_line12 | 2 | 80.1 | 5.456e-07 | 9.89e-07 | 6.8115e-07 | 1.2347e-06
1290 | feeder2_line12 | 3 | 80.1 | 1.4097 | 1.4097 | 1.7599 | 1.7599
1290 | feeder2_line13 | 1 | 354.6 | 36.9644 | 36.9717 | 10.4243 | 10.4263
1290 | feeder2_line13 | 2 | 354.6 | 24.0312 | 24.039 | 6.777 | 6.7792
1290 | feeder2_line13 | 3 | 354.6 | 53.7733 | 53.7612 | 15.1645 | 15.1611
1290 | feeder2_line14 | 1 | 80.1 | 3.5063 | 3.5063 | 4.3774 | 4.3774
1290 | feeder2_line14 | 2 | 80.1 | 2.9771e-07 | 6.4489e-07 | 3.7167e-07 | 8.0511e-07
1290 | feeder2_line14 | 3 | 80.1 | 2.9859e-07 | 6.4707e-07 | 3.7277e-07 | 8.0782e-07
1290 | feeder2_line15 | 1 | 354.6 | 39.9009 | 39.9083 | 11.2524 | 11.2545
1290 | feeder2_line15 | 2 | 354.6 | 24.0312 | 24.039 | 6.777 | 6.7792
1290 | feeder2_line15 | 3 | 354.6 | 53.7733 | 53.7612 | 15.1645 | 15.1611
1290 | feeder2_line16 | 1 | 80.1 | 5.7172e-07 | 1.03e-06 | 7.1376e-07 | 1.2859e-06
1290 | feeder2_line16 | 2 | 80.1 | 10.7167 | 10.7167 | 13.3791 | 13.3791
1290 | feeder2_line16 | 3 | 80.1 | 5.7253e-07 | 1.0314e-06 | 7.1477e-07 | 1.2877e-06
1290 | feeder2_line17 | 1 | 354.6 | 39.9009 | 39.9083 | 11.2524 | 11.2545
1290 | feeder2_line17 | 2 | 354.6 | 33.0957 | 33.103 | 9.3333 | 9.3353
1290 | feeder2_line17 | 3 | 354.6 | 53.7733 | 53.7612 | 15.1645 | 15.1611
1290 | feeder2_line18 | 1 | 80.1 | 5.4709e-07 | 7.3762e-07 | 6.83e-07 | 9.2087e-07
1290 | feeder2_line18 | 2 | 80.1 | 5.4557e-07 | 7.3575e-07 | 6.8111e-07 | 9.1854e-07
1290 | feeder2_line18 | 3 | 80.1 | 1.5239 | 1.5238 | 1.9025 | 1.9024
1290 | feeder2_line19 | 1 | 354.6 | 39.9009 | 39.9083 | 11.2524 | 11.2545
1290 | feeder2_line19 | 2 | 354.6 | 33.0958 | 33.103 | 9.3333 | 9.3353
1290 | feeder2_line19 | 3 | 354.6 | 54.9091 | 54.8969 | 15.4848 | 15.4814
1290 | feeder2_line20 | 1 | 99 | 5.4717e-07 | 8.845e-07 | 5.5269e-07 | 8.9344e-07
1290 | feeder2_line20 | 2 | 99 | 5.4558e-07 | 8.8215e-07 | 5.5109e-07 | 8.9106e-07
1290 | feeder2_line20 | 3 | 99 | 1.6315 | 1.6315 | 1.648 | 1.648
1290 | feeder2_line21 | 1 | 354.6 | 39.901 | 39.9083 | 11.2524 | 11.2545
1290 | feeder2_line21 | 2 | 354.6 | 33.0959 | 33.103 | 9.3333 | 9.3353
1290 | feeder2_line21 | 3 | 354.6 | 56.5328 | 56.5204 | 15.9427 | 15.9392
1290 | feeder2_line22 | 1 | 99 | 5.7213e-07 | 1.0141e-06 | 5.7791e-07 | 1.0243e-06
1290 | feeder2_line22 | 2 | 99 | 2.3722 | 2.3722 | 2.3962 | 2.3962
1290 | feeder2_line22 | 3 | 99 | 5.7327e-07 | 1.0161e-06 | 5.7907e-07 | 1.0263e-06
1290 | feeder2_line23 | 1 | 99 | 5.7213e-07 | 9.4926e-07 | 5.7791e-07 | 9.5884e-07
1290 | feeder2_line23 | 2 | 99 | 5.7055e-07 | 9.4665e-07 | 5.7632e-07 | 9.5622e-07
1290 | feeder2_line23 | 3 | 99 | 1.9275 | 1.9275 | 1.947 | 1.947
1290 | feeder2_line24 | 1 | 354.6 | 39.9011 | 39.9083 | 11.2524 | 11.2545
1290 | feeder2_line24 | 2 | 354.6 | 35.2513 | 35.2583 | 9.9411 | 9.9431
1290 | feeder2_line24 | 3 | 354.6 | 58.4406 | 58.4282 | 16.4807 | 16.4772
1290 | feeder2_line25 | 1 | 99 | 2.3727 | 2.3727 | 2.3967 | 2.3967
1290 | feeder2_line25 | 2 | 99 | 4.9958e-08 | 6.8827e-07 | 5.0462e-08 | 6.9522e-07
1290 | feeder2_line25 | 3 | 99 | 4.9437e-08 | 6.9173e-07 | 4.9937e-08 | 6.9872e-07
1290 | feeder2_line26 | 1 | 99 | 1.3718 | 1.3718 | 1.3857 | 1.3857
1290 | feeder2_line26 | 2 | 99 | 5.4559e-07 | 8.5272e-07 | 5.5111e-07 | 8.6134e-07
1290 | feeder2_line26 | 3 | 99 | 5.4876e-07 | 8.5701e-07 | 5.543e-07 | 8.6567e-07
1290 | feeder2_line27 | 1 | 354.6 | 43.5184 | 43.5257 | 12.2725 | 12.2746
1290 | feeder2_line27 | 2 | 354.6 | 35.2513 | 35.2583 | 9.9411 | 9.9431
1290 | feeder2_line27 | 3 | 354.6 | 58.4406 | 58.4282 | 16.4807 | 16.4772
1290 | feeder2_line28 | 1 | 99 | 2.5379e-06 | 7.1008e-07 | 2.5635e-06 | 7.1726e-07
1290 | feeder2_line28 | 2 | 99 | 0.76319 | 0.76317 | 0.7709 | 0.77087
1290 | feeder2_line28 | 3 | 99 | 2.5478e-06 | 7.118e-07 | 2.5735e-06 | 7.1899e-07
1290 | feeder2_line29 | 1 | 354.6 | 43.5184 | 43.5257 | 12.2725 | 12.2746
1290 | feeder2_line29 | 2 | 354.6 | 35.5372 | 35.5441 | 10.0218 | 10.0237
1290 | feeder2_line29 | 3 | 354.6 | 58.4406 | 58.4282 | 16.4807 | 16.4772
1290 | feeder2_line30 | 1 | 266.4 | 6.5773 | 6.5773 | 2.469 | 2.4689
1290 | feeder2_line30 | 2 | 266.4 | 8.7517 | 8.7517 | 3.2852 | 3.2852
1290 | feeder2_line30 | 3 | 266.4 | 2.7937 | 2.7933 | 1.0487 | 1.0485
1290 | feeder2_line31 | 1 | 354.6 | 49.7737 | 49.7809 | 14.0366 | 14.0386
1290 | feeder2_line31 | 2 | 354.6 | 42.4447 | 42.4507 | 11.9697 | 11.9714
1290 | feeder2_line31 | 3 | 354.6 | 61.2224 | 61.2096 | 17.2652 | 17.2616
1290 | feeder2_line32 | 1 | 354.6 | 49.7737 | 49.7809 | 14.0366 | 14.0386
1290 | feeder2_line32 | 2 | 354.6 | 43.6852 | 43.6912 | 12.3196 | 12.3213
1290 | feeder2_line32 | 3 | 354.6 | 61.2224 | 61.2096 | 17.2652 | 17.2616
1290 | feeder2_line33 | 1 | 99 | 4.9914e-08 | 6.8553e-07 | 5.0419e-08 | 6.9246e-07
1290 | feeder2_line33 | 2 | 99 | 1.2656 | 1.2656 | 1.2783 | 1.2783
1290 | feeder2_line33 | 3 | 99 | 4.9398e-08 | 6.8754e-07 | 4.9897e-08 | 6.9448e-07
1290 | feeder2_line34 | 1 | 354.6 | 49.7737 | 49.7809 | 14.0366 | 14.0386
1290 | feeder2_line34 | 2 | 354.6 | 43.6852 | 43.6912 | 12.3196 | 12.3213
1290 | feeder2_line34 | 3 | 354.6 | 61.4959 | 61.483 | 17.3423 | 17.3387
1290 | feeder2_line35 | 1 | 99 | 2.9891e-07 | 7.5923e-07 | 3.0193e-07 | 7.6689e-07
1290 | feeder2_line35 | 2 | 99 | 2.9792e-07 | 7.565e-07 | 3.0093e-07 | 7.6414e-07
1290 | feeder2_line35 | 3 | 99 | 0.27542 | 0.27541 | 0.27821 | 0.2782
1290 | feeder2_line36 | 1 | 354.6 | 51.1599 | 51.1673 | 14.4275 | 14.4296
1290 | feeder2_line36 | 2 | 354.6 | 43.6852 | 43.6912 | 12.3196 | 12.3213
1290 | feeder2_line36 | 3 | 354.6 | 61.4958 | 61.483 | 17.3423 | 17.3387
1290 | feeder2_line37 | 1 | 99 | 1.3949 | 1.3951 | 1.409 | 1.4092
1290 | feeder2_line37 | 2 | 99 | 2.9794e-07 | 8.3711e-07 | 3.0095e-07 | 8.4556e-07
1290 | feeder2_line37 | 3 | 99 | 2.9972e-07 | 8.4277e-07 | 3.0275e-07 | 8.5129e-07
1290 | feeder2_line38 | 1 | 99 | 3.2373e-07 | 7.7491e-07 | 3.27e-07 | 7.8274e-07
1290 | feeder2_line38 | 2 | 99 | 2.0856 | 2.0857 | 2.1067 | 2.1067
1290 | feeder2_line38 | 3 | 99 | 3.2419e-07 | 7.7709e-07 | 3.2746e-07 | 7.8494e-07
1290 | feeder2_line39 | 1 | 266.4 | 6.5773 | 6.5773 | 2.469 | 2.4689
1290 | feeder2_line39 | 2 | 266.4 | 6.6854 | 6.6854 | 2.5095 | 2.5095
1290 | feeder2_line39 | 3 | 266.4 | 2.7937 | 2.7933 | 1.0487 | 1.0485
1290 | feeder2_line40 | 1 | 354.6 | 53.4784 | 53.4857 | 15.0813 | 15.0834
1290 | feeder2_line40 | 2 | 354.6 | 43.6852 | 43.6912 | 12.3196 | 12.3213
1290 | feeder2_line40 | 3 | 354.6 | 61.4959 | 61.483 | 17.3423 | 17.3387
1290 | feeder2_line41 | 1 | 99 | 2.3729 | 2.3729 | 2.3968 | 2.3968
1290 | feeder2_line41 | 2 | 99 | 5.0116e-08 | 7.3151e-07 | 5.0622e-08 | 7.389e-07
1290 | feeder2_line41 | 3 | 99 | 4.9392e-08 | 7.3652e-07 | 4.9891e-08 | 7.4396e-07
1290 | feeder2_line42 | 1 | 99 | 2.9878e-07 | 7.4794e-07 | 3.018e-07 | 7.555e-07
1290 | feeder2_line42 | 2 | 99 | 2.9781e-07 | 7.4534e-07 | 3.0082e-07 | 7.5287e-07
1290 | feeder2_line42 | 3 | 99 | 0.1899 | 0.18989 | 0.19182 | 0.19181
1290 | feeder2_line43 | 1 | 266.4 | 6.5772 | 6.5773 | 2.4689 | 2.4689
1290 | feeder2_line43 | 2 | 266.4 | 6.6854 | 6.6854 | 2.5095 | 2.5095
1290 | feeder2_line43 | 3 | 266.4 | 2.6037 | 2.6034 | 0.97736 | 0.97725
1290 | feeder2_line44 | 1 | 354.6 | 53.4784 | 53.4857 | 15.0813 | 15.0834
1290 | feeder2_line44 | 2 | 354.6 | 43.6853 | 43.6912 | 12.3196 | 12.3213
1290 | feeder2_line44 | 3 | 354.6 | 63.1209 | 63.108 | 17.8006 | 17.797
1290 | feeder2_line45 | 1 | 99 | 4.9949e-08 | 5.7907e-07 | 5.0453e-08 | 5.8492e-07
1290 | feeder2_line45 | 2 | 99 | 5.0129e-08 | 5.7691e-07 | 5.0635e-08 | 5.8274e-07
1290 | feeder2_line45 | 3 | 99 | 1.6309 | 1.6308 | 1.6474 | 1.6473
1290 | feeder2_line46 | 1 | 99 | 5.726e-07 | 1.3559e-06 | 5.7839e-07 | 1.3696e-06
1290 | feeder2_line46 | 2 | 99 | 5.706e-07 | 1.3512e-06 | 5.7637e-07 | 1.3648e-06
1290 | feeder2_line46 | 3 | 99 | 0.16252 | 0.16248 | 0.16416 | 0.16412
1290 | feeder2_line47 | 1 | 266.4 | 6.5773 | 6.5773 | 2.4689 | 2.4689
1290 | feeder2_line47 | 2 | 266.4 | 6.6855 | 6.6854 | 2.5096 | 2.5095
1290 | feeder2_line47 | 3 | 266.4 | 2.4412 | 2.4409 | 0.91637 | 0.91627
1290 | feeder2_line48 | 1 | 99 | 1.7023 | 1.7022 | 1.7194 | 1.7194
1290 | feeder2_line48 | 2 | 99 | 5.0057e-08 | 7.2747e-07 | 5.0563e-08 | 7.3481e-07
1290 | feeder2_line48 | 3 | 99 | 4.9395e-08 | 7.321e-07 | 4.9894e-08 | 7.395e-07
1290 | feeder2_line49 | 1 | 266.4 | 4.9146 | 4.9146 | 1.8448 | 1.8448
1290 | feeder2_line49 | 2 | 266.4 | 6.6855 | 6.6854 | 2.5096 | 2.5095
1290 | feeder2_line49 | 3 | 266.4 | 2.4412 | 2.4409 | 0.91636 | 0.91627
1290 | feeder2_line50 | 1 | 99 | 5.7257e-07 | 1.2339e-06 | 5.7836e-07 | 1.2463e-06
1290 | feeder2_line50 | 2 | 99 | 3.6865 | 3.6866 | 3.7237 | 3.7238
1290 | feeder2_line50 | 3 | 99 | 5.7425e-07 | 1.2374e-06 | 5.8005e-07 | 1.2499e-06
1290 | feeder2_line51 | 1 | 99 | 0.09028 | 0.09042 | 0.091192 | 0.091334
1290 | feeder2_line51 | 2 | 99 | 5.7057e-07 | 1.3349e-06 | 5.7634e-07 | 1.3483e-06
1290 | feeder2_line51 | 3 | 99 | 5.7426e-07 | 1.3434e-06 | 5.8006e-07 | 1.357e-06
1290 | feeder2_line52 | 1 | 266.4 | 4.8315 | 4.8314 | 1.8136 | 1.8136
1290 | feeder2_line52 | 2 | 266.4 | 3.0033 | 3.0033 | 1.1274 | 1.1274
1290 | feeder2_line52 | 3 | 266.4 | 2.441 | 2.4409 | 0.91631 | 0.91627
1290 | feeder2_line53 | 1 | 99 | 5.4763e-07 | 7.5306e-07 | 5.5316e-07 | 7.6067e-07
1290 | feeder2_line53 | 2 | 99 | 3.0033 | 3.0033 | 3.0337 | 3.0337
1290 | feeder2_line53 | 3 | 99 | 5.4956e-07 | 7.5523e-07 | 5.5511e-07 | 7.6286e-07
1290 | feeder2_line54 | 1 | 266.4 | 4.8313 | 4.8314 | 1.8136 | 1.8136
1290 | feeder2_line54 | 2 | 266.4 | 8.5172e-05 | 4.604e-06 | 3.1971e-05 | 1.7282e-06
1290 | feeder2_line54 | 3 | 266.4 | 2.4409 | 2.4409 | 0.91624 | 0.91627
1290 | feeder2_line55 | 1 | 99 | 1.4419 | 1.4419 | 1.4565 | 1.4565
1290 | feeder2_line55 | 2 | 99 | 5.0167e-08 | 7.2694e-07 | 5.0674e-08 | 7.3429e-07
1290 | feeder2_line55 | 3 | 99 | 4.9385e-08 | 7.3227e-07 | 4.9884e-08 | 7.3966e-07
1290 | feeder2_line56 | 1 | 354.6 | 54.8897 | 54.897 | 15.4793 | 15.4814
1290 | feeder2_line56 | 2 | 354.6 | 43.6853 | 43.6912 | 12.3196 | 12.3213
1290 | feeder2_line56 | 3 | 354.6 | 63.121 | 63.108 | 17.8006 | 17.797
1290 | feeder2_line57 | 1 | 99 | 7.4837e-07 | 1.5425e-06 | 7.5593e-07 | 1.5581e-06
1290 | feeder2_line57 | 2 | 99 | 7.5081e-07 | 1.5371e-06 | 7.584e-07 | 1.5527e-06
1290 | feeder2_line57 | 3 | 99 | 2.4409 | 2.4409 | 2.4656 | 2.4656
1290 | feeder2_line58 | 1 | 266.4 | 4.8314 | 4.8314 | 1.8136 | 1.8136
1290 | feeder2_line58 | 2 | 266.4 | 1.884e-05 | 2.6731e-06 | 7.0722e-06 | 1.0034e-06
1290 | feeder2_line58 | 3 | 266.4 | 1.8988e-05 | 2.6894e-06 | 7.1278e-06 | 1.0095e-06
1290 | feeder2_line59 | 1 | 99 | 4.9894e-08 | 5.3618e-07 | 5.0398e-08 | 5.4159e-07
1290 | feeder2_line59 | 2 | 99 | 5.0062e-08 | 5.3433e-07 | 5.0568e-08 | 5.3972e-07
1290 | feeder2_line59 | 3 | 99 | 1.0291 | 1.0291 | 1.0395 | 1.0395
1290 | feeder2_line60 | 1 | 99 | 2.9875e-07 | 8.1034e-07 | 3.0177e-07 | 8.1852e-07
1290 | feeder2_line60 | 2 | 99 | 2.978e-07 | 8.0753e-07 | 3.0081e-07 | 8.1569e-07
1290 | feeder2_line60 | 3 | 99 | 1.4121 | 1.4121 | 1.4264 | 1.4264
1290 | feeder2_line61 | 1 | 266.4 | 1.9787 | 1.9789 | 0.74275 | 0.74282
1290 | feeder2_line61 | 2 | 266.4 | 3.9021 | 3.9023 | 1.4648 | 1.4648
1290 | feeder2_line61 | 3 | 266.4 | 4.9172 | 4.9173 | 1.8458 | 1.8458
1290 | feeder2_line62 | 1 | 354.6 | 56.8535 | 56.861 | 16.0331 | 16.0353
1290 | feeder2_line62 | 2 | 354.6 | 47.3832 | 47.3892 | 13.3624 | 13.3641
1290 | feeder2_line62 | 3 | 354.6 | 67.888 | 67.8752 | 19.145 | 19.1413
1290 | feeder2_line63 | 1 | 99 | 2.6784 | 2.6784 | 2.7054 | 2.7054
1290 | feeder2_line63 | 2 | 99 | 5.7057e-07 | 1.2141e-06 | 5.7633e-07 | 1.2264e-06
1290 | feeder2_line63 | 3 | 99 | 5.7426e-07 | 1.2219e-06 | 5.8006e-07 | 1.2342e-06
1290 | feeder2_line64 | 1 | 99 | 2.2218 | 2.2218 | 2.2442 | 2.2442
1290 | feeder2_line64 | 2 | 99 | 9.3881e-12 | 3.1981e-07 | 9.4829e-12 | 3.2304e-07
1290 | feeder2_line64 | 3 | 99 | 2.0924e-12 | 3.2186e-07 | 2.1136e-12 | 3.2511e-07
1290 | feeder2_line65 | 1 | 99 | 5.0013e-08 | 6.414e-07 | 5.0518e-08 | 6.4788e-07
1290 | feeder2_line65 | 2 | 99 | 1.0877 | 1.0877 | 1.0987 | 1.0987
1290 | feeder2_line65 | 3 | 99 | 4.9375e-08 | 6.4374e-07 | 4.9874e-08 | 6.5024e-07
1290 | feeder2_line66 | 1 | 354.6 | 56.8534 | 56.861 | 16.0331 | 16.0353
1290 | feeder2_line66 | 2 | 354.6 | 48.4613 | 48.4673 | 13.6665 | 13.6682
1290 | feeder2_line66 | 3 | 354.6 | 67.888 | 67.8752 | 19.1449 | 19.1413
1290 | feeder2_line67 | 1 | 99 | 2.4994e-08 | 3.6249e-07 | 2.5246e-08 | 3.6615e-07
1290 | feeder2_line67 | 2 | 99 | 2.5104e-08 | 3.6099e-07 | 2.5357e-08 | 3.6463e-07
1290 | feeder2_line67 | 3 | 99 | 2.3738 | 2.3738 | 2.3977 | 2.3977
1290 | feeder2_line68 | 1 | 266.4 | 1.9787 | 1.9789 | 0.74276 | 0.74282
1290 | feeder2_line68 | 2 | 266.4 | 3.9022 | 3.9023 | 1.4648 | 1.4648
1290 | feeder2_line68 | 3 | 266.4 | 2.5609 | 2.561 | 0.9613 | 0.96133
1290 | feeder2_line69 | 1 | 99 | 12.5968 | 12.5965 | 12.724 | 12.7238
1290 | feeder2_line69 | 2 | 99 | 2.5296e-06 | 6.6304e-07 | 2.5551e-06 | 6.6974e-07
1290 | feeder2_line69 | 3 | 99 | 2.5587e-06 | 6.6841e-07 | 2.5845e-06 | 6.7517e-07
1290 | feeder2_line70 | 1 | 354.6 | 69.1475 | 69.1551 | 19.5001 | 19.5023
1290 | feeder2_line70 | 2 | 354.6 | 48.4612 | 48.4673 | 13.6664 | 13.6682
1290 | feeder2_line70 | 3 | 354.6 | 67.8879 | 67.8752 | 19.1449 | 19.1413
1290 | feeder2_line71 | 1 | 99 | 5.0025e-08 | 7.1576e-07 | 5.053e-08 | 7.2299e-07
1290 | feeder2_line71 | 2 | 99 | 3.0877 | 3.0878 | 3.1189 | 3.119
1290 | feeder2_line71 | 3 | 99 | 4.9373e-08 | 7.1842e-07 | 4.9872e-08 | 7.2568e-07
1290 | feeder2_line72 | 1 | 354.6 | 69.1476 | 69.1551 | 19.5002 | 19.5023
1290 | feeder2_line72 | 2 | 354.6 | 51.2393 | 51.2453 | 14.4499 | 14.4516
1290 | feeder2_line72 | 3 | 354.6 | 67.888 | 67.8752 | 19.145 | 19.1413
1290 | feeder2_line73 | 1 | 99 | 5.9844e-07 | 1.5346e-06 | 6.0449e-07 | 1.5501e-06
1290 | feeder2_line73 | 2 | 99 | 1.2655 | 1.2655 | 1.2783 | 1.2783
1290 | feeder2_line73 | 3 | 99 | 6.0015e-07 | 1.5399e-06 | 6.0622e-07 | 1.5555e-06
1290 | feeder2_line74 | 1 | 99 | 4.9984e-08 | 4.5771e-07 | 5.0489e-08 | 4.6233e-07
1290 | feeder2_line74 | 2 | 99 | 2.5692 | 2.5692 | 2.5951 | 2.5952
1290 | feeder2_line74 | 3 | 99 | 4.938e-08 | 4.5929e-07 | 4.9879e-08 | 4.6393e-07
1290 | feeder2_line75 | 1 | 266.4 | 1.9788 | 1.9789 | 0.7428 | 0.74282
1290 | feeder2_line75 | 2 | 266.4 | 0.090247 | 0.090282 | 0.033876 | 0.03389
1290 | feeder2_line75 | 3 | 266.4 | 2.561 | 2.561 | 0.96134 | 0.96133
1290 | feeder2_line76 | 1 | 99 | 1.9789 | 1.9789 | 1.9988 | 1.9989
1290 | feeder2_line76 | 2 | 99 | 8.4404e-07 | 1.5765e-06 | 8.5256e-07 | 1.5924e-06
1290 | feeder2_line76 | 3 | 99 | 8.5084e-07 | 1.5885e-06 | 8.5943e-07 | 1.6045e-06
1290 | feeder2_line77 | 1 | 99 | 2.4994e-08 | 5.7518e-07 | 2.5247e-08 | 5.8099e-07
1290 | feeder2_line77 | 2 | 99 | 2.5097e-08 | 5.7279e-07 | 2.5351e-08 | 5.7858e-07
1290 | feeder2_line77 | 3 | 99 | 2.561 | 2.561 | 2.5869 | 2.5868
1290 | feeder2_line78 | 1 | 266.4 | 1.0506e-11 | 9.54e-07 | 3.9435e-12 | 3.5811e-07
1290 | feeder2_line78 | 2 | 266.4 | 0.090279 | 0.090282 | 0.033888 | 0.03389
1290 | feeder2_line78 | 3 | 266.4 | 6.5009e-12 | 9.5681e-07 | 2.4403e-12 | 3.5916e-07
1290 | feeder2_line79 | 1 | 354.6 | 16.1352 | 16.1346 | 4.5503 | 4.5501
1290 | feeder2_line79 | 2 | 354.6 | 20.203 | 20.2025 | 5.6974 | 5.6973
1290 | feeder2_line79 | 3 | 354.6 | 20.685 | 20.6847 | 5.8333 | 5.8332
1290 | feeder2_line80 | 1 | 354.6 | 85.0133 | 85.0201 | 23.9744 | 23.9763
1290 | feeder2_line80 | 2 | 354.6 | 70.7463 | 70.7511 | 19.951 | 19.9524
1290 | feeder2_line80 | 3 | 354.6 | 87.7861 | 87.773 | 24.7564 | 24.7527
1290 | feeder2_line81 | 1 | 354.6 | 85.0133 | 85.0201 | 23.9744 | 23.9763
1290 | feeder2_line81 | 2 | 354.6 | 70.7462 | 70.7511 | 19.951 | 19.9524
1290 | feeder2_line81 | 3 | 354.6 | 89.2087 | 89.1956 | 25.1576 | 25.1539
1290 | feeder2_line82 | 1 | 354.6 | 3.1016e-11 | 7.3459e-07 | 8.7467e-12 | 2.0716e-07
1290 | feeder2_line82 | 2 | 354.6 | 6.3162e-12 | 7.3118e-07 | 1.7812e-12 | 2.062e-07
1290 | feeder2_line82 | 3 | 354.6 | 1.4231 | 1.4231 | 0.40133 | 0.40133
1290 | feeder2_line83 | 1 | 354.6 | 85.0134 | 85.0201 | 23.9745 | 23.9763
1290 | feeder2_line83 | 2 | 354.6 | 73.2517 | 73.2564 | 20.6576 | 20.6589
1290 | feeder2_line83 | 3 | 354.6 | 89.2089 | 89.1956 | 25.1576 | 25.1539
1290 | feeder2_line84 | 1 | 354.6 | 8.0031e-12 | 1.2985e-06 | 2.2569e-12 | 3.6618e-07
1290 | feeder2_line84 | 2 | 354.6 | 2.5982 | 2.5983 | 0.73273 | 0.73274
1290 | feeder2_line84 | 3 | 354.6 | 1.306e-11 | 1.3028e-06 | 3.6831e-12 | 3.6739e-07
1290 | feeder2_line85 | 1 | 99 | 2.0871 | 2.0872 | 2.1082 | 2.1083
1290 | feeder2_line85 | 2 | 99 | 5.035e-08 | 4.6114e-07 | 5.0859e-08 | 4.658e-07
1290 | feeder2_line85 | 3 | 99 | 4.9384e-08 | 4.6519e-07 | 4.9883e-08 | 4.6989e-07
1290 | feeder2_line86 | 1 | 354.6 | 86.7731 | 86.7798 | 24.4707 | 24.4726
1290 | feeder2_line86 | 2 | 354.6 | 73.2518 | 73.2564 | 20.6576 | 20.6589
1290 | feeder2_line86 | 3 | 354.6 | 89.209 | 89.1956 | 25.1576 | 25.1539
1290 | feeder2_line87 | 1 | 354.6 | 86.7733 | 86.7798 | 24.4708 | 24.4726
1290 | feeder2_line87 | 2 | 354.6 | 77.0765 | 77.081 | 21.7362 | 21.7374
1290 | feeder2_line87 | 3 | 354.6 | 92.6549 | 92.6413 | 26.1294 | 26.1256
1290 | feeder2_line88 | 1 | 354.6 | 0.00011266 | 3.366e-06 | 3.177e-05 | 9.4924e-07
1290 | feeder2_line88 | 2 | 354.6 | 4.0288 | 4.0289 | 1.1361 | 1.1362
1290 | feeder2_line88 | 3 | 354.6 | 3.9107 | 3.9106 | 1.1028 | 1.1028
1290 | feeder2_line89 | 1 | 354.6 | 86.771 | 86.7798 | 24.4701 | 24.4726
1290 | feeder2_line89 | 2 | 354.6 | 81.4408 | 81.4475 | 22.9669 | 22.9689
1290 | feeder2_line89 | 3 | 354.6 | 92.6526 | 92.6413 | 26.1288 | 26.1256
1290 | feeder2_line90 | 1 | 354.6 | 0.00072371 | 2.0338e-06 | 0.00020409 | 5.7354e-07
1290 | feeder2_line90 | 2 | 354.6 | 4.5345 | 4.5349 | 1.2788 | 1.2789
1290 | feeder2_line90 | 3 | 354.6 | 0.00072992 | 2.0401e-06 | 0.00020584 | 5.7534e-07
1290 | feeder2_line91 | 1 | 354.6 | 86.7709 | 86.7798 | 24.4701 | 24.4726
1290 | feeder2_line91 | 2 | 354.6 | 81.4407 | 81.4475 | 22.9669 | 22.9689
1290 | feeder2_line91 | 3 | 354.6 | 94.0671 | 94.0558 | 26.5277 | 26.5245
1290 | feeder2_line92 | 1 | 354.6 | 1.0238e-11 | 1.0253e-06 | 2.8873e-12 | 2.8915e-07
1290 | feeder2_line92 | 2 | 354.6 | 7.6631e-12 | 1.0202e-06 | 2.1611e-12 | 2.8771e-07
1290 | feeder2_line92 | 3 | 354.6 | 1.4157 | 1.4157 | 0.39925 | 0.39925
1290 | feeder2_line93 | 1 | 99 | 2.505e-08 | 3.4222e-07 | 2.5303e-08 | 3.4568e-07
1290 | feeder2_line93 | 2 | 99 | 2.5977 | 2.5978 | 2.6239 | 2.624
1290 | feeder2_line93 | 3 | 99 | 2.4699e-08 | 3.4355e-07 | 2.4948e-08 | 3.4702e-07
1290 | feeder2_line94 | 1 | 354.6 | 2.505e-06 | 1.6662e-06 | 7.0643e-07 | 4.6989e-07
1290 | feeder2_line94 | 2 | 354.6 | 1.9408 | 1.9408 | 0.54731 | 0.54733
1290 | feeder2_line94 | 3 | 354.6 | 2.4698e-06 | 1.672e-06 | 6.9651e-07 | 4.7151e-07
1290 | feeder2_line95 | 1 | 99 | 3.5724e-06 | 2.6103e-06 | 3.6085e-06 | 2.6367e-06
1290 | feeder2_line95 | 2 | 99 | 4.0287 | 4.0289 | 4.0694 | 4.0696
1290 | feeder2_line95 | 3 | 99 | 3.5856e-06 | 2.6202e-06 | 3.6218e-06 | 2.6467e-06
1290 | feeder2_line96 | 1 | 354.6 | 0.0001211 | 6.2213e-07 | 3.4152e-05 | 1.7545e-07
1290 | feeder2_line96 | 2 | 354.6 | 0.00012048 | 6.1928e-07 | 3.3975e-05 | 1.7464e-07
1290 | feeder2_line96 | 3 | 354.6 | 3.9107 | 3.9106 | 1.1028 | 1.1028
1290 | feeder2_line97 | 1 | 354.6 | 87.6057 | 87.6145 | 24.7055 | 24.708
1290 | feeder2_line97 | 2 | 354.6 | 81.4408 | 81.4475 | 22.9669 | 22.9689
1290 | feeder2_line97 | 3 | 354.6 | 94.0673 | 94.0558 | 26.5277 | 26.5245
1290 | feeder2_line98 | 1 | 354.6 | 1.3562 | 1.3553 | 0.38245 | 0.38221
1290 | feeder2_line98 | 2 | 354.6 | 0.0016923 | 6.188e-07 | 0.00047726 | 1.7451e-07
1290 | feeder2_line98 | 3 | 354.6 | 0.0017222 | 6.24e-07 | 0.00048567 | 1.7597e-07
1290 | feeder2_line99 | 1 | 99 | 2.5042e-08 | 4.4734e-07 | 2.5295e-08 | 4.5186e-07
1290 | feeder2_line99 | 2 | 99 | 2.5191e-08 | 4.4506e-07 | 2.5445e-08 | 4.4955e-07
1290 | feeder2_line99 | 3 | 99 | 3.9106 | 3.9106 | 3.9501 | 3.9501
1290 | feeder2_line100 | 1 | 99 | 1.3553 | 1.3553 | 1.369 | 1.369
1290 | feeder2_line100 | 2 | 99 | 2.5216e-08 | 6.1121e-07 | 2.547e-08 | 6.1738e-07
1290 | feeder2_line100 | 3 | 99 | 2.47e-08 | 6.1687e-07 | 2.495e-08 | 6.231e-07
1290 | feeder2_line101 | 1 | 354.6 | 1.9411 | 1.9408 | 0.54741 | 0.54731
1290 | feeder2_line101 | 2 | 354.6 | 20.203 | 20.2025 | 5.6974 | 5.6973
1290 | feeder2_line101 | 3 | 354.6 | 20.6849 | 20.6847 | 5.8333 | 5.8332
1290 | feeder2_line102 | 1 | 99 | 14.2388 | 14.2385 | 14.3826 | 14.3824
1290 | feeder2_line102 | 2 | 99 | 2.32e-06 | 8.7371e-07 | 2.3434e-06 | 8.8254e-07
1290 | feeder2_line102 | 3 | 99 | 2.3527e-06 | 8.8112e-07 | 2.3764e-06 | 8.9002e-07
1290 | feeder2_line103 | 1 | 99 | 5.491e-07 | 8.0364e-07 | 5.5465e-07 | 8.1176e-07
1290 | feeder2_line103 | 2 | 99 | 13.831 | 13.8308 | 13.9707 | 13.9705
1290 | feeder2_line103 | 3 | 99 | 5.5144e-07 | 8.0642e-07 | 5.5701e-07 | 8.1456e-07
1290 | feeder2_line104 | 1 | 354.6 | 1.941 | 1.9408 | 0.54739 | 0.54731
1290 | feeder2_line104 | 2 | 354.6 | 6.5599 | 6.5597 | 1.8499 | 1.8499
1290 | feeder2_line104 | 3 | 354.6 | 20.6849 | 20.6847 | 5.8333 | 5.8332
1290 | feeder2_line105 | 1 | 99 | 2.5456e-06 | 7.3947e-07 | 2.5713e-06 | 7.4694e-07
1290 | feeder2_line105 | 2 | 99 | 2.5293e-06 | 7.358e-07 | 2.5549e-06 | 7.4323e-07
1290 | feeder2_line105 | 3 | 99 | 1.5246 | 1.5245 | 1.54 | 1.5399
1290 | feeder2_line106 | 1 | 354.6 | 1.941 | 1.9408 | 0.54737 | 0.54731
1290 | feeder2_line106 | 2 | 354.6 | 6.5598 | 6.5597 | 1.8499 | 1.8499
1290 | feeder2_line106 | 3 | 354.6 | 19.2725 | 19.2725 | 5.435 | 5.435
1290 | feeder2_line107 | 1 | 99 | 3.2456e-07 | 9.0117e-07 | 3.2784e-07 | 9.1028e-07
1290 | feeder2_line107 | 2 | 99 | 2.1487 | 2.1488 | 2.1704 | 2.1705
1290 | feeder2_line107 | 3 | 99 | 3.2504e-07 | 9.0402e-07 | 3.2832e-07 | 9.1315e-07
1290 | feeder2_line108 | 1 | 354.6 | 1.941 | 1.9408 | 0.54737 | 0.54731
1290 | feeder2_line108 | 2 | 354.6 | 4.4436 | 4.4434 | 1.2531 | 1.2531
1290 | feeder2_line108 | 3 | 354.6 | 19.2725 | 19.2725 | 5.435 | 5.435
1290 | feeder2_line109 | 1 | 354.6 | 88.7811 | 88.7887 | 25.037 | 25.0391
1290 | feeder2_line109 | 2 | 354.6 | 81.442 | 81.4475 | 22.9673 | 22.9689
1290 | feeder2_line109 | 3 | 354.6 | 94.0685 | 94.0558 | 26.5281 | 26.5245
1290 | feeder2_line110 | 1 | 99 | 1.5431 | 1.5425 | 1.5587 | 1.5581
1290 | feeder2_line110 | 2 | 99 | 0.00079875 | 9.0431e-07 | 0.00080681 | 9.1344e-07
1290 | feeder2_line110 | 3 | 99 | 0.00081044 | 9.1325e-07 | 0.00081863 | 9.2248e-07
1290 | feeder2_line111 | 1 | 99 | 2.5034e-08 | 3.8206e-07 | 2.5287e-08 | 3.8592e-07
1290 | feeder2_line111 | 2 | 99 | 2.4571 | 2.4572 | 2.482 | 2.482
1290 | feeder2_line111 | 3 | 99 | 2.4695e-08 | 3.8351e-07 | 2.4944e-08 | 3.8738e-07
1290 | feeder2_line112 | 1 | 99 | 3.2487e-07 | 9.1811e-07 | 3.2815e-07 | 9.2738e-07
1290 | feeder2_line112 | 2 | 99 | 1.6705 | 1.6706 | 1.6873 | 1.6875
1290 | feeder2_line112 | 3 | 99 | 3.2547e-07 | 9.2159e-07 | 3.2876e-07 | 9.309e-07
1290 | feeder2_line113 | 1 | 99 | 1.4715 | 1.4715 | 1.4863 | 1.4863
1290 | feeder2_line113 | 2 | 99 | 3.2396e-07 | 9.0142e-07 | 3.2723e-07 | 9.1052e-07
1290 | feeder2_line113 | 3 | 99 | 3.2589e-07 | 9.099e-07 | 3.2918e-07 | 9.1909e-07
1290 | feeder2_line114 | 1 | 99 | 13.8874 | 13.8871 | 14.0276 | 14.0274
1290 | feeder2_line114 | 2 | 99 | 2.5144e-08 | 4.3445e-07 | 2.5398e-08 | 4.3884e-07
1290 | feeder2_line114 | 3 | 99 | 2.4682e-08 | 4.3814e-07 | 2.4931e-08 | 4.4257e-07
1290 | feeder2_line115 | 1 | 99 | 2.4987e-08 | 5.6239e-07 | 2.5239e-08 | 5.6807e-07
1290 | feeder2_line115 | 2 | 99 | 2.3597 | 2.3597 | 2.3836 | 2.3835
1290 | feeder2_line115 | 3 | 99 | 2.4705e-08 | 5.6403e-07 | 2.4954e-08 | 5.6973e-07
1290 | feeder2_line116 | 1 | 354.6 | 1.941 | 1.9408 | 0.54738 | 0.54731
1290 | feeder2_line116 | 2 | 354.6 | 2.1108 | 2.1106 | 0.59527 | 0.59521
1290 | feeder2_line116 | 3 | 354.6 | 19.2725 | 19.2725 | 5.435 | 5.435
1290 | feeder2_line117 | 1 | 99 | 5.0169e-08 | 6.436e-07 | 5.0675e-08 | 6.5011e-07
1290 | feeder2_line117 | 2 | 99 | 0.16268 | 0.16276 | 0.16432 | 0.1644
1290 | feeder2_line117 | 3 | 99 | 4.9424e-08 | 6.4626e-07 | 4.9923e-08 | 6.5278e-07
1290 | feeder2_line118 | 1 | 354.6 | 88.7811 | 88.7887 | 25.037 | 25.0391
1290 | feeder2_line118 | 2 | 354.6 | 81.6047 | 81.6103 | 23.0132 | 23.0148
1290 | feeder2_line118 | 3 | 354.6 | 94.0685 | 94.0558 | 26.5281 | 26.5245
1290 | feeder2_line119 | 1 | 99 | 2.498e-08 | 6.0517e-07 | 2.5232e-08 | 6.1128e-07
1290 | feeder2_line119 | 2 | 99 | 2.514e-08 | 6.0215e-07 | 2.5394e-08 | 6.0823e-07
1290 | feeder2_line119 | 3 | 99 | 2.5795 | 2.5794 | 2.6055 | 2.6055
1290 | feeder2_line120 | 1 | 354.6 | 1.941 | 1.9408 | 0.54738 | 0.54731
1290 | feeder2_line120 | 2 | 354.6 | 2.1108 | 2.1106 | 0.59527 | 0.59521
1290 | feeder2_line120 | 3 | 354.6 | 16.7309 | 16.7309 | 4.7182 | 4.7182
1290 | feeder2_line121 | 1 | 99 | 3.2454e-07 | 9.3713e-07 | 3.2782e-07 | 9.466e-07
1290 | feeder2_line121 | 2 | 99 | 1.9502 | 1.9502 | 1.9699 | 1.9699
1290 | feeder2_line121 | 3 | 99 | 3.2488e-07 | 9.394e-07 | 3.2816e-07 | 9.4888e-07
1290 | feeder2_line122 | 1 | 354.6 | 1.941 | 1.9408 | 0.54737 | 0.54731
1290 | feeder2_line122 | 2 | 354.6 | 0.17979 | 0.17956 | 0.050704 | 0.050638
1290 | feeder2_line122 | 3 | 354.6 | 16.7309 | 16.7309 | 4.7182 | 4.7182
1290 | feeder2_line123 | 1 | 99 | 5.7417e-07 | 9.7109e-07 | 5.7997e-07 | 9.809e-07
1290 | feeder2_line123 | 2 | 99 | 5.7134e-07 | 9.6633e-07 | 5.7711e-07 | 9.7609e-07
1290 | feeder2_line123 | 3 | 99 | 0.76466 | 0.76464 | 0.77238 | 0.77236
1290 | feeder2_line124 | 1 | 354.6 | 1.9409 | 1.9408 | 0.54736 | 0.54731
1290 | feeder2_line124 | 2 | 354.6 | 0.1797 | 0.17956 | 0.050678 | 0.050638
1290 | feeder2_line124 | 3 | 354.6 | 16.1191 | 16.1192 | 4.5457 | 4.5457
1290 | feeder2_line125 | 1 | 99 | 5.7417e-07 | 9.0272e-07 | 5.7997e-07 | 9.1184e-07
1290 | feeder2_line125 | 2 | 99 | 5.7135e-07 | 8.9831e-07 | 5.7712e-07 | 9.0739e-07
1290 | feeder2_line125 | 3 | 99 | 1.3561 | 1.3561 | 1.3698 | 1.3698
1290 | feeder2_line126 | 1 | 354.6 | 1.9411 | 1.9408 | 0.5474 | 0.54731
1290 | feeder2_line126 | 2 | 354.6 | 0.17986 | 0.17956 | 0.050722 | 0.050638
1290 | feeder2_line126 | 3 | 354.6 | 15.0921 | 15.0921 | 4.2561 | 4.2561
1290 | feeder2_line127 | 1 | 99 | 5.7415e-07 | 1.0807e-06 | 5.7995e-07 | 1.0916e-06
1290 | feeder2_line127 | 2 | 99 | 5.7135e-07 | 1.0755e-06 | 5.7712e-07 | 1.0863e-06
1290 | feeder2_line127 | 3 | 99 | 11.4842 | 11.4846 | 11.6002 | 11.6006
1290 | feeder2_line128 | 1 | 354.6 | 1.941 | 1.9408 | 0.54738 | 0.54731
1290 | feeder2_line128 | 2 | 354.6 | 0.17978 | 0.17956 | 0.050699 | 0.050638
1290 | feeder2_line128 | 3 | 354.6 | 4.0354 | 4.0352 | 1.138 | 1.138
1290 | feeder2_line129 | 1 | 99 | 5.492e-07 | 8.763e-07 | 5.5475e-07 | 8.8515e-07
1290 | feeder2_line129 | 2 | 99 | 0.17956 | 0.17956 | 0.18137 | 0.18137
1290 | feeder2_line129 | 3 | 99 | 5.5068e-07 | 8.7816e-07 | 5.5624e-07 | 8.8703e-07
1290 | feeder2_line130 | 1 | 354.6 | 1.9411 | 1.9408 | 0.54739 | 0.54731
1290 | feeder2_line130 | 2 | 354.6 | 0.00030685 | 4.6157e-06 | 8.6533e-05 | 1.3017e-06
1290 | feeder2_line130 | 3 | 354.6 | 4.0355 | 4.0352 | 1.138 | 1.138
1290 | feeder2_line131 | 1 | 99 | 5.7416e-07 | 9.7122e-07 | 5.7996e-07 | 9.8103e-07
1290 | feeder2_line131 | 2 | 99 | 5.7137e-07 | 9.6654e-07 | 5.7714e-07 | 9.763e-07
1290 | feeder2_line131 | 3 | 99 | 1.9477 | 1.9477 | 1.9674 | 1.9674
1290 | feeder2_line132 | 1 | 354.6 | 1.9409 | 1.9408 | 0.54734 | 0.54731
1290 | feeder2_line132 | 2 | 354.6 | 0.00012489 | 2.902e-06 | 3.522e-05 | 8.184e-07
1290 | feeder2_line132 | 3 | 354.6 | 2.088 | 2.0879 | 0.58883 | 0.58881
1290 | feeder2_line133 | 1 | 99 | 1.9408 | 1.9408 | 1.9604 | 1.9604
1290 | feeder2_line133 | 2 | 99 | 2.9825e-07 | 9.7426e-07 | 3.0126e-07 | 9.841e-07
1290 | feeder2_line133 | 3 | 99 | 3.0006e-07 | 9.8104e-07 | 3.031e-07 | 9.9095e-07
1290 | feeder2_line134 | 1 | 354.6 | 3.3102e-12 | 1.7853e-06 | 9.3351e-13 | 5.0346e-07
1290 | feeder2_line134 | 2 | 354.6 | 1.1868e-11 | 1.7772e-06 | 3.347e-12 | 5.0118e-07
1290 | feeder2_line134 | 3 | 354.6 | 2.0879 | 2.0879 | 0.5888 | 0.58881
1290 | feeder2_line135 | 1 | 99 | 3.0781 | 3.0782 | 3.1092 | 3.1093
1290 | feeder2_line135 | 2 | 99 | 5.055e-08 | 5.8347e-07 | 5.1061e-08 | 5.8936e-07
1290 | feeder2_line135 | 3 | 99 | 4.9436e-08 | 5.892e-07 | 4.9935e-08 | 5.9515e-07
1290 | feeder2_line136 | 1 | 354.6 | 91.7046 | 91.7123 | 25.8614 | 25.8636
1290 | feeder2_line136 | 2 | 354.6 | 81.6047 | 81.6103 | 23.0132 | 23.0148
1290 | feeder2_line136 | 3 | 354.6 | 94.0685 | 94.0558 | 26.5281 | 26.5245
1290 | feeder2_line137 | 1 | 99 | 1.7342 | 1.7342 | 1.7517 | 1.7517
1290 | feeder2_line137 | 2 | 99 | 8.4657e-07 | 1.5716e-06 | 8.5512e-07 | 1.5875e-06
1290 | feeder2_line137 | 3 | 99 | 8.5543e-07 | 1.5871e-06 | 8.6407e-07 | 1.6032e-06
1290 | feeder2_line138 | 1 | 354.6 | 93.3407 | 93.3483 | 26.3228 | 26.325
1290 | feeder2_line138 | 2 | 354.6 | 81.6047 | 81.6103 | 23.0132 | 23.0148
1290 | feeder2_line138 | 3 | 354.6 | 94.0685 | 94.0558 | 26.5281 | 26.5245
1290 | feeder2_line139 | 1 | 99 | 5.0211e-08 | 4.9253e-07 | 5.0718e-08 | 4.975e-07
1290 | feeder2_line139 | 2 | 99 | 5.0576e-08 | 4.8974e-07 | 5.1087e-08 | 4.9468e-07
1290 | feeder2_line139 | 3 | 99 | 0.97808 | 0.97765 | 0.98796 | 0.98753
1290 | feeder2_line140 | 1 | 354.6 | 93.3408 | 93.3483 | 26.3228 | 26.325
1290 | feeder2_line140 | 2 | 354.6 | 81.6048 | 81.6103 | 23.0132 | 23.0148
1290 | feeder2_line140 | 3 | 354.6 | 94.7209 | 94.7073 | 26.7121 | 26.7082
1290 | feeder2_line141 | 1 | 99 | 2.5299e-06 | 4.8728e-07 | 2.5555e-06 | 4.922e-07
1290 | feeder2_line141 | 2 | 99 | 0.18994 | 0.18994 | 0.19186 | 0.19186
1290 | feeder2_line141 | 3 | 99 | 2.5477e-06 | 4.8933e-07 | 2.5734e-06 | 4.9428e-07
1290 | feeder2_line142 | 1 | 354.6 | 93.3406 | 93.3483 | 26.3228 | 26.325
1290 | feeder2_line142 | 2 | 354.6 | 81.7946 | 81.8002 | 23.0667 | 23.0683
1290 | feeder2_line142 | 3 | 354.6 | 94.7208 | 94.7073 | 26.712 | 26.7082
1290 | feeder2_line143 | 1 | 99 | 8.5195e-07 | 1.7316e-06 | 8.6056e-07 | 1.7491e-06
1290 | feeder2_line143 | 2 | 99 | 2.1476 | 2.1477 | 2.1693 | 2.1694
1290 | feeder2_line143 | 3 | 99 | 8.5588e-07 | 1.7389e-06 | 8.6452e-07 | 1.7565e-06
1290 | feeder2_line144 | 1 | 354.6 | 93.3404 | 93.3483 | 26.3227 | 26.325
1290 | feeder2_line144 | 2 | 354.6 | 83.6638 | 83.6696 | 23.5939 | 23.5955
1290 | feeder2_line144 | 3 | 354.6 | 94.7206 | 94.7073 | 26.7119 | 26.7082
1290 | feeder2_line145 | 1 | 99 | 2.5118e-08 | 4.8557e-07 | 2.5372e-08 | 4.9047e-07
1290 | feeder2_line145 | 2 | 99 | 1.4235 | 1.4236 | 1.4379 | 1.4379
1290 | feeder2_line145 | 3 | 99 | 2.4729e-08 | 4.8763e-07 | 2.4979e-08 | 4.9255e-07
1290 | feeder2_line146 | 1 | 354.6 | 93.3403 | 93.3483 | 26.3227 | 26.325
1290 | feeder2_line146 | 2 | 354.6 | 85.0872 | 85.0932 | 23.9953 | 23.997
1290 | feeder2_line146 | 3 | 354.6 | 94.7205 | 94.7073 | 26.7119 | 26.7082
1290 | feeder2_line147 | 1 | 99 | 0.10779 | 0.1078 | 0.10888 | 0.10888
1290 | feeder2_line147 | 2 | 99 | 1.1462e-06 | 2.2269e-06 | 1.1578e-06 | 2.2494e-06
1290 | feeder2_line147 | 3 | 99 | 1.1579e-06 | 2.2493e-06 | 1.1696e-06 | 2.272e-06
1290 | feeder2_line148 | 1 | 99 | 1.3703 | 1.3703 | 1.3841 | 1.3842
1290 | feeder2_line148 | 2 | 99 | 5.9841e-07 | 1.4922e-06 | 6.0445e-07 | 1.5072e-06
1290 | feeder2_line148 | 3 | 99 | 6.0367e-07 | 1.5072e-06 | 6.0977e-07 | 1.5224e-06
1290 | feeder2_line149 | 1 | 354.6 | 94.8174 | 94.8253 | 26.7393 | 26.7415
1290 | feeder2_line149 | 2 | 354.6 | 85.0874 | 85.0932 | 23.9953 | 23.997
1290 | feeder2_line149 | 3 | 354.6 | 94.7206 | 94.7073 | 26.712 | 26.7082
1290 | feeder2_line150 | 1 | 354.6 | 94.8175 | 94.8253 | 26.7393 | 26.7415
1290 | feeder2_line150 | 2 | 354.6 | 99.0001 | 99.0055 | 27.9188 | 27.9203
1290 | feeder2_line150 | 3 | 354.6 | 94.7207 | 94.7073 | 26.712 | 26.7082
1290 | feeder2_line151 | 1 | 99 | 9.774e-06 | 1.7831e-06 | 9.8728e-06 | 1.8011e-06
1290 | feeder2_line151 | 2 | 99 | 13.9435 | 13.9432 | 14.0843 | 14.0841
1290 | feeder2_line151 | 3 | 99 | 9.8585e-06 | 1.7906e-06 | 9.9581e-06 | 1.8087e-06
1290 | feeder2_line152 | 1 | 354.6 | 3.7526e-12 | 1.1887e-06 | 1.0583e-12 | 3.3521e-07
1290 | feeder2_line152 | 2 | 354.6 | 3.7526e-12 | 1.1821e-06 | 1.0583e-12 | 3.3336e-07
1290 | feeder2_line152 | 3 | 354.6 | 0.076221 | 0.076212 | 0.021495 | 0.021492
1290 | feeder2_line153 | 1 | 99 | 1.9477 | 1.9477 | 1.9674 | 1.9674
1290 | feeder2_line153 | 2 | 99 | 5.0668e-08 | 5.912e-07 | 5.118e-08 | 5.9717e-07
1290 | feeder2_line153 | 3 | 99 | 4.9499e-08 | 5.972e-07 | 4.9999e-08 | 6.0324e-07
1290 | feeder2_line154 | 1 | 99 | 5.7702e-07 | 8.849e-07 | 5.8285e-07 | 8.9384e-07
1290 | feeder2_line154 | 2 | 99 | 5.7362e-07 | 8.7972e-07 | 5.7942e-07 | 8.8861e-07
1290 | feeder2_line154 | 3 | 99 | 2.8641 | 2.864 | 2.893 | 2.8929
1290 | feeder2_line155 | 1 | 99 | 96.5629 | 96.5709 | 97.5383 | 97.5463
1290 | feeder2_line155 | 2 | 99 | 99 | 99.0055 | 100 | 100.0055
1290 | feeder2_line155 | 3 | 99 | 97.5172 | 97.5038 | 98.5022 | 98.4887
1290 | feeder2_line156 | 1 | 99 | 6.0186e-07 | 1.1643e-06 | 6.0794e-07 | 1.1761e-06
1290 | feeder2_line156 | 2 | 99 | 13.8544 | 13.8541 | 13.9943 | 13.994
1290 | feeder2_line156 | 3 | 99 | 6.0396e-07 | 1.1693e-06 | 6.1006e-07 | 1.1811e-06
1290 | feeder2_line157 | 1 | 99 | 2.5128e-08 | 2.5278e-07 | 2.5382e-08 | 2.5533e-07
1290 | feeder2_line157 | 2 | 99 | 0.090059 | 0.090064 | 0.090969 | 0.090974
1290 | feeder2_line157 | 3 | 99 | 2.4736e-08 | 2.5385e-07 | 2.4986e-08 | 2.5641e-07
1320 | feeder2_line1 | 1 | 354.6 | 31.5153 | 31.5128 | 8.8876 | 8.8868
1320 | feeder2_line1 | 2 | 354.6 | 47.4899 | 47.48 | 13.3925 | 13.3897
1320 | feeder2_line1 | 3 | 354.6 | 49.1786 | 49.1916 | 13.8688 | 13.8724
1320 | feeder2_line2 | 1 | 354.6 | 34.9491 | 34.9463 | 9.8559 | 9.8551
1320 | feeder2_line2 | 2 | 354.6 | 47.49 | 47.48 | 13.3926 | 13.3897
1320 | feeder2_line2 | 3 | 354.6 | 49.1788 | 49.1916 | 13.8688 | 13.8724
1320 | feeder2_line3 | 1 | 80.1 | 3.5426 | 3.5426 | 4.4227 | 4.4227
1320 | feeder2_line3 | 2 | 80.1 | 5.7164e-07 | 1.0564e-06 | 7.1366e-07 | 1.3188e-06
1320 | feeder2_line3 | 3 | 80.1 | 5.7185e-07 | 1.0568e-06 | 7.1392e-07 | 1.3193e-06
1320 | feeder2_line4 | 1 | 354.6 | 34.9493 | 34.9463 | 9.856 | 9.8551
1320 | feeder2_line4 | 2 | 354.6 | 48.1731 | 48.163 | 13.5852 | 13.5823
1320 | feeder2_line4 | 3 | 354.6 | 49.1789 | 49.1916 | 13.8688 | 13.8724
1320 | feeder2_line5 | 1 | 80.1 | 5.7154e-07 | 9.9729e-07 | 7.1353e-07 | 1.2451e-06
1320 | feeder2_line5 | 2 | 80.1 | 1.5291 | 1.5291 | 1.9089 | 1.909
1320 | feeder2_line5 | 3 | 80.1 | 5.7189e-07 | 9.979e-07 | 7.1397e-07 | 1.2458e-06
1320 | feeder2_line6 | 1 | 80.1 | 5.7157e-07 | 1.1732e-06 | 7.1357e-07 | 1.4647e-06
1320 | feeder2_line6 | 2 | 80.1 | 5.7172e-07 | 1.1735e-06 | 7.1376e-07 | 1.4651e-06
1320 | feeder2_line6 | 3 | 80.1 | 1.2638 | 1.2638 | 1.5777 | 1.5777
1320 | feeder2_line7 | 1 | 354.6 | 34.9494 | 34.9463 | 9.856 | 9.8551
1320 | feeder2_line7 | 2 | 354.6 | 48.1732 | 48.163 | 13.5852 | 13.5823
1320 | feeder2_line7 | 3 | 354.6 | 50.4385 | 50.4511 | 14.2241 | 14.2276
1320 | feeder2_line8 | 1 | 80.1 | 0.75772 | 0.75772 | 0.94597 | 0.94597
1320 | feeder2_line8 | 2 | 80.1 | 5.7185e-07 | 1.1318e-06 | 7.1392e-07 | 1.413e-06
1320 | feeder2_line8 | 3 | 80.1 | 5.7205e-07 | 1.1322e-06 | 7.1417e-07 | 1.4135e-06
1320 | feeder2_line9 | 1 | 354.6 | 35.7072 | 35.704 | 10.0697 | 10.0688
1320 | feeder2_line9 | 2 | 354.6 | 48.1733 | 48.163 | 13.5852 | 13.5823
1320 | feeder2_line9 | 3 | 354.6 | 50.4386 | 50.4511 | 14.2241 | 14.2276
1320 | feeder2_line10 | 1 | 80.1 | 8.4505e-07 | 1.494e-06 | 1.055e-06 | 1.8651e-06
1320 | feeder2_line10 | 2 | 80.1 | 0.758 | 0.758 | 0.94631 | 0.94632
1320 | feeder2_line10 | 3 | 80.1 | 8.4565e-07 | 1.495e-06 | 1.0557e-06 | 1.8665e-06
1320 | feeder2_line11 | 1 | 354.6 | 35.7072 | 35.704 | 10.0697 | 10.0688
1320 | feeder2_line11 | 2 | 354.6 | 48.9019 | 48.8916 | 13.7907 | 13.7878
1320 | feeder2_line11 | 3 | 354.6 | 50.4386 | 50.4511 | 14.2241 | 14.2276
1320 | feeder2_line12 | 1 | 80.1 | 5.4681e-07 | 9.9105e-07 | 6.8266e-07 | 1.2373e-06
1320 | feeder2_line12 | 2 | 80.1 | 5.4712e-07 | 9.9142e-07 | 6.8304e-07 | 1.2377e-06
1320 | feeder2_line12 | 3 | 80.1 | 1.4956 | 1.4956 | 1.8672 | 1.8672
1320 | feeder2_line13 | 1 | 354.6 | 35.7071 | 35.704 | 10.0697 | 10.0688
1320 | feeder2_line13 | 2 | 354.6 | 48.9019 | 48.8916 | 13.7907 | 13.7878
1320 | feeder2_line13 | 3 | 354.6 | 51.7552 | 51.7678 | 14.5954 | 14.5989
1320 | feeder2_line14 | 1 | 80.1 | 0.27522 | 0.27522 | 0.3436 | 0.34359
1320 | feeder2_line14 | 2 | 80.1 | 2.9839e-07 | 6.4654e-07 | 3.7252e-07 | 8.0717e-07
1320 | feeder2_line14 | 3 | 80.1 | 2.9854e-07 | 6.4678e-07 | 3.7271e-07 | 8.0746e-07
1320 | feeder2_line15 | 1 | 354.6 | 35.9824 | 35.9792 | 10.1473 | 10.1464
1320 | feeder2_line15 | 2 | 354.6 | 48.9019 | 48.8916 | 13.7907 | 13.7878
1320 | feeder2_line15 | 3 | 354.6 | 51.7553 | 51.7678 | 14.5954 | 14.5989
1320 | feeder2_line16 | 1 | 80.1 | 5.7177e-07 | 1.0301e-06 | 7.1382e-07 | 1.286e-06
1320 | feeder2_line16 | 2 | 80.1 | 7.5467 | 7.5468 | 9.4217 | 9.4217
1320 | feeder2_line16 | 3 | 80.1 | 5.7223e-07 | 1.0309e-06 | 7.1439e-07 | 1.287e-06
1320 | feeder2_line17 | 1 | 354.6 | 35.9824 | 35.9792 | 10.1473 | 10.1464
1320 | feeder2_line17 | 2 | 354.6 | 56.1944 | 56.1841 | 15.8473 | 15.8444
1320 | feeder2_line17 | 3 | 354.6 | 51.7553 | 51.7678 | 14.5954 | 14.5989
1320 | feeder2_line18 | 1 | 80.1 | 5.4706e-07 | 7.3761e-07 | 6.8297e-07 | 9.2086e-07
1320 | feeder2_line18 | 2 | 80.1 | 5.4768e-07 | 7.3824e-07 | 6.8375e-07 | 9.2165e-07
1320 | feeder2_line18 | 3 | 80.1 | 0.49139 | 0.49141 | 0.61347 | 0.6135
1320 | feeder2_line19 | 1 | 354.6 | 35.9824 | 35.9792 | 10.1473 | 10.1464
1320 | feeder2_line19 | 2 | 354.6 | 56.1944 | 56.1841 | 15.8473 | 15.8444
1320 | feeder2_line19 | 3 | 354.6 | 52.2428 | 52.2553 | 14.7329 | 14.7364
1320 | feeder2_line20 | 1 | 99 | 5.4712e-07 | 8.8446e-07 | 5.5265e-07 | 8.9339e-07
1320 | feeder2_line20 | 2 | 99 | 5.4784e-07 | 8.8536e-07 | 5.5338e-07 | 8.943e-07
1320 | feeder2_line20 | 3 | 99 | 0.35651 | 0.35653 | 0.36011 | 0.36013
1320 | feeder2_line21 | 1 | 354.6 | 35.9825 | 35.9792 | 10.1474 | 10.1464
1320 | feeder2_line21 | 2 | 354.6 | 56.1945 | 56.1841 | 15.8473 | 15.8444
1320 | feeder2_line21 | 3 | 354.6 | 52.5974 | 52.6099 | 14.8329 | 14.8364
1320 | feeder2_line22 | 1 | 99 | 5.7209e-07 | 1.014e-06 | 5.7787e-07 | 1.0242e-06
1320 | feeder2_line22 | 2 | 99 | 2.5131 | 2.5131 | 2.5385 | 2.5385
1320 | feeder2_line22 | 3 | 99 | 5.7275e-07 | 1.0152e-06 | 5.7853e-07 | 1.0254e-06
1320 | feeder2_line23 | 1 | 99 | 5.7206e-07 | 9.4916e-07 | 5.7783e-07 | 9.5875e-07
1320 | feeder2_line23 | 2 | 99 | 5.7271e-07 | 9.5022e-07 | 5.785e-07 | 9.5982e-07
1320 | feeder2_line23 | 3 | 99 | 19.5211 | 19.5207 | 19.7183 | 19.7179
1320 | feeder2_line24 | 1 | 354.6 | 35.9825 | 35.9792 | 10.1474 | 10.1464
1320 | feeder2_line24 | 2 | 354.6 | 58.6008 | 58.5904 | 16.5259 | 16.5229
1320 | feeder2_line24 | 3 | 354.6 | 72.0065 | 72.0186 | 20.3064 | 20.3098
1320 | feeder2_line25 | 1 | 99 | 2.5128 | 2.5128 | 2.5381 | 2.5381
1320 | feeder2_line25 | 2 | 99 | 4.9574e-08 | 6.9104e-07 | 5.0074e-08 | 6.9802e-07
1320 | feeder2_line25 | 3 | 99 | 4.9913e-08 | 6.9116e-07 | 5.0418e-08 | 6.9814e-07
1320 | feeder2_line26 | 1 | 99 | 1.5675 | 1.5675 | 1.5833 | 1.5833
1320 | feeder2_line26 | 2 | 99 | 5.4811e-07 | 8.5615e-07 | 5.5364e-07 | 8.648e-07
1320 | feeder2_line26 | 3 | 99 | 5.4802e-07 | 8.563e-07 | 5.5356e-07 | 8.6495e-07
1320 | feeder2_line27 | 1 | 354.6 | 40.0581 | 40.0547 | 11.2967 | 11.2957
1320 | feeder2_line27 | 2 | 354.6 | 58.6008 | 58.5904 | 16.5259 | 16.5229
1320 | feeder2_line27 | 3 | 354.6 | 72.0066 | 72.0186 | 20.3064 | 20.3098
1320 | feeder2_line28 | 1 | 99 | 2.5366e-06 | 7.0992e-07 | 2.5622e-06 | 7.1709e-07
1320 | feeder2_line28 | 2 | 99 | 1.2635 | 1.2635 | 1.2763 | 1.2763
1320 | feeder2_line28 | 3 | 99 | 2.5423e-06 | 7.1128e-07 | 2.5679e-06 | 7.1846e-07
1320 | feeder2_line29 | 1 | 354.6 | 40.0581 | 40.0547 | 11.2967 | 11.2957
1320 | feeder2_line29 | 2 | 354.6 | 59.1694 | 59.159 | 16.6863 | 16.6833
1320 | feeder2_line29 | 3 | 354.6 | 72.0066 | 72.0186 | 20.3064 | 20.3098
1320 | feeder2_line30 | 1 | 266.4 | 5.245 | 5.2447 | 1.9689 | 1.9687
1320 | feeder2_line30 | 2 | 266.4 | 5.2521 | 5.2518 | 1.9715 | 1.9714
1320 | feeder2_line30 | 3 | 266.4 | 4.775 | 4.775 | 1.7924 | 1.7924
1320 | feeder2_line31 | 1 | 354.6 | 45.2564 | 45.2526 | 12.7627 | 12.7616
1320 | feeder2_line31 | 2 | 354.6 | 64.1287 | 64.1179 | 18.0848 | 18.0817
1320 | feeder2_line31 | 3 | 354.6 | 76.0973 | 76.109 | 21.46 | 21.4633
1320 | feeder2_line32 | 1 | 354.6 | 45.2564 | 45.2526 | 12.7627 | 12.7616
1320 | feeder2_line32 | 2 | 354.6 | 65.5692 | 65.5583 | 18.491 | 18.488
1320 | feeder2_line32 | 3 | 354.6 | 76.0973 | 76.109 | 21.46 | 21.4633
1320 | feeder2_line33 | 1 | 99 | 5.0059e-08 | 6.8521e-07 | 5.0565e-08 | 6.9213e-07
1320 | feeder2_line33 | 2 | 99 | 1.462 | 1.462 | 1.4768 | 1.4768
1320 | feeder2_line33 | 3 | 99 | 4.9958e-08 | 6.8718e-07 | 5.0463e-08 | 6.9412e-07
1320 | feeder2_line34 | 1 | 354.6 | 45.2564 | 45.2526 | 12.7627 | 12.7616
1320 | feeder2_line34 | 2 | 354.6 | 65.5692 | 65.5583 | 18.491 | 18.488
1320 | feeder2_line34 | 3 | 354.6 | 76.8914 | 76.9031 | 21.684 | 21.6873
1320 | feeder2_line35 | 1 | 99 | 2.9881e-07 | 7.5885e-07 | 3.0182e-07 | 7.6651e-07
1320 | feeder2_line35 | 2 | 99 | 2.9932e-07 | 7.605e-07 | 3.0234e-07 | 7.6819e-07
1320 | feeder2_line35 | 3 | 99 | 0.79515 | 0.79514 | 0.80318 | 0.80318
1320 | feeder2_line36 | 1 | 354.6 | 46.4106 | 46.4068 | 13.0882 | 13.0871
1320 | feeder2_line36 | 2 | 354.6 | 65.5691 | 65.5583 | 18.491 | 18.488
1320 | feeder2_line36 | 3 | 354.6 | 76.8913 | 76.9031 | 21.684 | 21.6873
1320 | feeder2_line37 | 1 | 99 | 1.1571 | 1.157 | 1.1688 | 1.1687
1320 | feeder2_line37 | 2 | 99 | 2.9937e-07 | 8.4164e-07 | 3.024e-07 | 8.5014e-07
1320 | feeder2_line37 | 3 | 99 | 2.9973e-07 | 8.4241e-07 | 3.0276e-07 | 8.5092e-07
1320 | feeder2_line38 | 1 | 99 | 3.2372e-07 | 7.7461e-07 | 3.2699e-07 | 7.8243e-07
1320 | feeder2_line38 | 2 | 99 | 1.701 | 1.701 | 1.7182 | 1.7182
1320 | feeder2_line38 | 3 | 99 | 3.244e-07 | 7.766e-07 | 3.2768e-07 | 7.8445e-07
1320 | feeder2_line39 | 1 | 266.4 | 5.2451 | 5.2447 | 1.9689 | 1.9687
1320 | feeder2_line39 | 2 | 266.4 | 3.5819 | 3.5817 | 1.3446 | 1.3445
1320 | feeder2_line39 | 3 | 266.4 | 4.775 | 4.775 | 1.7924 | 1.7924
1320 | feeder2_line40 | 1 | 354.6 | 48.9214 | 48.9175 | 13.7962 | 13.7951
1320 | feeder2_line40 | 2 | 354.6 | 65.5692 | 65.5583 | 18.491 | 18.488
1320 | feeder2_line40 | 3 | 354.6 | 76.8914 | 76.9031 | 21.684 | 21.6873
1320 | feeder2_line41 | 1 | 99 | 2.5128 | 2.5128 | 2.5382 | 2.5382
1320 | feeder2_line41 | 2 | 99 | 4.9582e-08 | 7.3551e-07 | 5.0082e-08 | 7.4294e-07
1320 | feeder2_line41 | 3 | 99 | 4.9975e-08 | 7.3622e-07 | 5.048e-08 | 7.4366e-07
1320 | feeder2_line42 | 1 | 99 | 2.987e-07 | 7.4764e-07 | 3.0171e-07 | 7.5519e-07
1320 | feeder2_line42 | 2 | 99 | 2.9915e-07 | 7.491e-07 | 3.0217e-07 | 7.5666e-07
1320 | feeder2_line42 | 3 | 99 | 0.75804 | 0.75804 | 0.76569 | 0.7657
1320 | feeder2_line43 | 1 | 266.4 | 5.245 | 5.2447 | 1.9688 | 1.9687
1320 | feeder2_line43 | 2 | 266.4 | 3.5819 | 3.5817 | 1.3445 | 1.3445
1320 | feeder2_line43 | 3 | 266.4 | 4.1223 | 4.1224 | 1.5474 | 1.5474
1320 | feeder2_line44 | 1 | 354.6 | 48.9214 | 48.9175 | 13.7962 | 13.7951
1320 | feeder2_line44 | 2 | 354.6 | 65.5692 | 65.5583 | 18.491 | 18.488
1320 | feeder2_line44 | 3 | 354.6 | 77.248 | 77.2597 | 21.7846 | 21.7879
1320 | feeder2_line45 | 1 | 99 | 5.0124e-08 | 5.7873e-07 | 5.063e-08 | 5.8458e-07
1320 | feeder2_line45 | 2 | 99 | 4.9585e-08 | 5.8011e-07 | 5.0086e-08 | 5.8597e-07
1320 | feeder2_line45 | 3 | 99 | 0.35681 | 0.35685 | 0.36042 | 0.36046
1320 | feeder2_line46 | 1 | 99 | 5.7238e-07 | 1.3553e-06 | 5.7816e-07 | 1.369e-06
1320 | feeder2_line46 | 2 | 99 | 5.735e-07 | 1.358e-06 | 5.793e-07 | 1.3717e-06
1320 | feeder2_line46 | 3 | 99 | 1.5281 | 1.5281 | 1.5435 | 1.5435
1320 | feeder2_line47 | 1 | 266.4 | 5.245 | 5.2447 | 1.9689 | 1.9687
1320 | feeder2_line47 | 2 | 266.4 | 3.5819 | 3.5817 | 1.3446 | 1.3445
1320 | feeder2_line47 | 3 | 266.4 | 2.7123 | 2.7122 | 1.0181 | 1.0181
1320 | feeder2_line48 | 1 | 99 | 2.5218 | 2.5218 | 2.5473 | 2.5473
1320 | feeder2_line48 | 2 | 99 | 4.9571e-08 | 7.3114e-07 | 5.0072e-08 | 7.3853e-07
1320 | feeder2_line48 | 3 | 99 | 4.994e-08 | 7.3162e-07 | 5.0445e-08 | 7.3901e-07
1320 | feeder2_line49 | 1 | 266.4 | 2.7929 | 2.7926 | 1.0484 | 1.0483
1320 | feeder2_line49 | 2 | 266.4 | 3.5819 | 3.5817 | 1.3446 | 1.3445
1320 | feeder2_line49 | 3 | 266.4 | 2.7123 | 2.7122 | 1.0181 | 1.0181
1320 | feeder2_line50 | 1 | 99 | 5.7235e-07 | 1.2334e-06 | 5.7813e-07 | 1.2459e-06
1320 | feeder2_line50 | 2 | 99 | 1.2648 | 1.2647 | 1.2775 | 1.2775
1320 | feeder2_line50 | 3 | 99 | 5.7385e-07 | 1.2366e-06 | 5.7965e-07 | 1.2491e-06
1320 | feeder2_line51 | 1 | 99 | 0.090316 | 0.09031 | 0.091228 | 0.091222
1320 | feeder2_line51 | 2 | 99 | 5.7349e-07 | 1.3416e-06 | 5.7929e-07 | 1.3552e-06
1320 | feeder2_line51 | 3 | 99 | 5.7385e-07 | 1.3425e-06 | 5.7965e-07 | 1.3561e-06
1320 | feeder2_line52 | 1 | 266.4 | 2.7045 | 2.7044 | 1.0152 | 1.0152
1320 | feeder2_line52 | 2 | 266.4 | 2.3886 | 2.3885 | 0.89661 | 0.89659
1320 | feeder2_line52 | 3 | 266.4 | 2.7122 | 2.7122 | 1.0181 | 1.0181
1320 | feeder2_line53 | 1 | 99 | 5.4734e-07 | 7.5278e-07 | 5.5286e-07 | 7.6038e-07
1320 | feeder2_line53 | 2 | 99 | 2.3885 | 2.3885 | 2.4127 | 2.4127
1320 | feeder2_line53 | 3 | 99 | 5.4888e-07 | 7.5474e-07 | 5.5442e-07 | 7.6236e-07
1320 | feeder2_line54 | 1 | 266.4 | 2.7043 | 2.7044 | 1.0151 | 1.0152
1320 | feeder2_line54 | 2 | 266.4 | 8.552e-05 | 4.6266e-06 | 3.2102e-05 | 1.7367e-06
1320 | feeder2_line54 | 3 | 266.4 | 2.7121 | 2.7122 | 1.0181 | 1.0181
1320 | feeder2_line55 | 1 | 99 | 0.18087 | 0.18086 | 0.18269 | 0.18269
1320 | feeder2_line55 | 2 | 99 | 4.9592e-08 | 7.3122e-07 | 5.0093e-08 | 7.386e-07
1320 | feeder2_line55 | 3 | 99 | 5e-08 | 7.3208e-07 | 5.0505e-08 | 7.3948e-07
1320 | feeder2_line56 | 1 | 354.6 | 49.1022 | 49.0983 | 13.8472 | 13.8461
1320 | feeder2_line56 | 2 | 354.6 | 65.5693 | 65.5583 | 18.491 | 18.488
1320 | feeder2_line56 | 3 | 354.6 | 77.2481 | 77.2597 | 21.7846 | 21.7879
1320 | feeder2_line57 | 1 | 99 | 7.5037e-07 | 1.5419e-06 | 7.5795e-07 | 1.5575e-06
1320 | feeder2_line57 | 2 | 99 | 7.4349e-07 | 1.5449e-06 | 7.51e-07 | 1.5606e-06
1320 | feeder2_line57 | 3 | 99 | 2.7122 | 2.7122 | 2.7396 | 2.7396
1320 | feeder2_line58 | 1 | 266.4 | 2.7044 | 2.7044 | 1.0151 | 1.0152
1320 | feeder2_line58 | 2 | 266.4 | 1.8959e-05 | 2.6861e-06 | 7.1168e-06 | 1.0083e-06
1320 | feeder2_line58 | 3 | 266.4 | 1.8972e-05 | 2.688e-06 | 7.1216e-06 | 1.009e-06
1320 | feeder2_line59 | 1 | 99 | 5.003e-08 | 5.3598e-07 | 5.0536e-08 | 5.4139e-07
1320 | feeder2_line59 | 2 | 99 | 4.9567e-08 | 5.3704e-07 | 5.0067e-08 | 5.4246e-07
1320 | feeder2_line59 | 3 | 99 | 1.22 | 1.22 | 1.2323 | 1.2323
1320 | feeder2_line60 | 1 | 99 | 2.9868e-07 | 8.1003e-07 | 3.0169e-07 | 8.1821e-07
1320 | feeder2_line60 | 2 | 99 | 2.9914e-07 | 8.1162e-07 | 3.0216e-07 | 8.1982e-07
1320 | feeder2_line60 | 3 | 99 | 1.4929 | 1.4929 | 1.508 | 1.508
1320 | feeder2_line61 | 1 | 266.4 | 1.7174 | 1.7176 | 0.64466 | 0.64473
1320 | feeder2_line61 | 2 | 266.4 | 6.1253 | 6.1254 | 2.2993 | 2.2993
1320 | feeder2_line61 | 3 | 266.4 | 5.9805 | 5.9807 | 2.2449 | 2.245
1320 | feeder2_line62 | 1 | 354.6 | 50.8178 | 50.8141 | 14.331 | 14.33
1320 | feeder2_line62 | 2 | 354.6 | 70.8856 | 70.8749 | 19.9903 | 19.9873
1320 | feeder2_line62 | 3 | 354.6 | 83.0591 | 83.0711 | 23.4233 | 23.4267
1320 | feeder2_line63 | 1 | 99 | 0.35975 | 0.35975 | 0.36339 | 0.36338
1320 | feeder2_line63 | 2 | 99 | 5.735e-07 | 1.2203e-06 | 5.7929e-07 | 1.2326e-06
1320 | feeder2_line63 | 3 | 99 | 5.7385e-07 | 1.221e-06 | 5.7964e-07 | 1.2334e-06
1320 | feeder2_line64 | 1 | 99 | 2.3446 | 2.3446 | 2.3683 | 2.3683
1320 | feeder2_line64 | 2 | 99 | 4.5524e-12 | 3.2145e-07 | 4.5984e-12 | 3.247e-07
1320 | feeder2_line64 | 3 | 99 | 1.3392e-11 | 3.2165e-07 | 1.3527e-11 | 3.249e-07
1320 | feeder2_line65 | 1 | 99 | 5.0261e-08 | 6.4084e-07 | 5.0769e-08 | 6.4732e-07
1320 | feeder2_line65 | 2 | 99 | 1.5317 | 1.5317 | 1.5472 | 1.5472
1320 | feeder2_line65 | 3 | 99 | 5.003e-08 | 6.4372e-07 | 5.0535e-08 | 6.5022e-07
1320 | feeder2_line66 | 1 | 354.6 | 50.8177 | 50.8141 | 14.331 | 14.33
1320 | feeder2_line66 | 2 | 354.6 | 71.7937 | 71.7831 | 20.2464 | 20.2434
1320 | feeder2_line66 | 3 | 354.6 | 83.059 | 83.0711 | 23.4233 | 23.4267
1320 | feeder2_line67 | 1 | 99 | 2.5103e-08 | 3.6222e-07 | 2.5357e-08 | 3.6588e-07
1320 | feeder2_line67 | 2 | 99 | 2.4797e-08 | 3.6319e-07 | 2.5047e-08 | 3.6686e-07
1320 | feeder2_line67 | 3 | 99 | 2.5139 | 2.5139 | 2.5393 | 2.5393
1320 | feeder2_line68 | 1 | 266.4 | 1.7174 | 1.7176 | 0.64468 | 0.64473
1320 | feeder2_line68 | 2 | 266.4 | 6.1254 | 6.1254 | 2.2993 | 2.2993
1320 | feeder2_line68 | 3 | 266.4 | 3.5093 | 3.5095 | 1.3173 | 1.3174
1320 | feeder2_line69 | 1 | 99 | 15.0425 | 15.0427 | 15.1944 | 15.1947
1320 | feeder2_line69 | 2 | 99 | 2.5526e-06 | 6.6738e-07 | 2.5784e-06 | 6.7412e-07
1320 | feeder2_line69 | 3 | 99 | 2.5543e-06 | 6.6842e-07 | 2.5801e-06 | 6.7517e-07
1320 | feeder2_line70 | 1 | 354.6 | 65.8472 | 65.8438 | 18.5694 | 18.5685
1320 | feeder2_line70 | 2 | 354.6 | 71.7936 | 71.7831 | 20.2464 | 20.2434
1320 | feeder2_line70 | 3 | 354.6 | 83.059 | 83.0711 | 23.4233 | 23.4267
1320 | feeder2_line71 | 1 | 99 | 5.0293e-08 | 7.1509e-07 | 5.0801e-08 | 7.2231e-07
1320 | feeder2_line71 | 2 | 99 | 2.3016 | 2.3015 | 2.3249 | 2.3248
1320 | feeder2_line71 | 3 | 99 | 5.004e-08 | 7.1846e-07 | 5.0545e-08 | 7.2571e-07
1320 | feeder2_line72 | 1 | 354.6 | 65.8473 | 65.8438 | 18.5695 | 18.5685
1320 | feeder2_line72 | 2 | 354.6 | 74.0836 | 74.0729 | 20.8922 | 20.8891
1320 | feeder2_line72 | 3 | 354.6 | 83.0591 | 83.0711 | 23.4233 | 23.4267
1320 | feeder2_line73 | 1 | 99 | 5.9812e-07 | 1.5335e-06 | 6.0416e-07 | 1.549e-06
1320 | feeder2_line73 | 2 | 99 | 1.4617 | 1.4617 | 1.4764 | 1.4764
1320 | feeder2_line73 | 3 | 99 | 6.0034e-07 | 1.5396e-06 | 6.064e-07 | 1.5552e-06
1320 | feeder2_line74 | 1 | 99 | 5.0198e-08 | 4.5737e-07 | 5.0705e-08 | 4.6199e-07
1320 | feeder2_line74 | 2 | 99 | 3.5097 | 3.5096 | 3.5451 | 3.545
1320 | feeder2_line74 | 3 | 99 | 5.0016e-08 | 4.592e-07 | 5.0521e-08 | 4.6384e-07
1320 | feeder2_line75 | 1 | 266.4 | 1.7175 | 1.7176 | 0.64472 | 0.64473
1320 | feeder2_line75 | 2 | 266.4 | 1.4792 | 1.4793 | 0.55527 | 0.55529
1320 | feeder2_line75 | 3 | 266.4 | 3.5094 | 3.5095 | 1.3174 | 1.3174
1320 | feeder2_line76 | 1 | 99 | 1.7176 | 1.7176 | 1.7349 | 1.7349
1320 | feeder2_line76 | 2 | 99 | 8.4946e-07 | 1.5861e-06 | 8.5804e-07 | 1.6021e-06
1320 | feeder2_line76 | 3 | 99 | 8.5048e-07 | 1.5882e-06 | 8.5907e-07 | 1.6042e-06
1320 | feeder2_line77 | 1 | 99 | 2.5106e-08 | 5.7475e-07 | 2.5359e-08 | 5.8056e-07
1320 | feeder2_line77 | 2 | 99 | 2.4798e-08 | 5.7629e-07 | 2.5048e-08 | 5.8211e-07
1320 | feeder2_line77 | 3 | 99 | 3.5095 | 3.5095 | 3.5449 | 3.545
1320 | feeder2_line78 | 1 | 266.4 | 3.259e-12 | 9.5346e-07 | 1.2233e-12 | 3.579e-07
1320 | feeder2_line78 | 2 | 266.4 | 1.4793 | 1.4793 | 0.55529 | 0.55529
1320 | feeder2_line78 | 3 | 266.4 | 1.9009e-11 | 9.5702e-07 | 7.1354e-12 | 3.5924e-07
1320 | feeder2_line79 | 1 | 354.6 | 2.9488 | 2.9484 | 0.83158 | 0.83148
1320 | feeder2_line79 | 2 | 354.6 | 5.8283 | 5.8277 | 1.6436 | 1.6435
1320 | feeder2_line79 | 3 | 354.6 | 10.6723 | 10.6721 | 3.0097 | 3.0096
1320 | feeder2_line80 | 1 | 354.6 | 68.7804 | 68.7764 | 19.3966 | 19.3955
1320 | feeder2_line80 | 2 | 354.6 | 79.8885 | 79.8771 | 22.5292 | 22.526
1320 | feeder2_line80 | 3 | 354.6 | 93.5124 | 93.524 | 26.3712 | 26.3745
1320 | feeder2_line81 | 1 | 354.6 | 68.7804 | 68.7764 | 19.3966 | 19.3955
1320 | feeder2_line81 | 2 | 354.6 | 79.8884 | 79.8771 | 22.5292 | 22.526
1320 | feeder2_line81 | 3 | 354.6 | 94.7914 | 94.803 | 26.7319 | 26.7352
1320 | feeder2_line82 | 1 | 354.6 | 7.6986e-12 | 7.3389e-07 | 2.1711e-12 | 2.0696e-07
1320 | feeder2_line82 | 2 | 354.6 | 7.6987e-12 | 7.3588e-07 | 2.1711e-12 | 2.0752e-07
1320 | feeder2_line82 | 3 | 354.6 | 1.5156 | 1.5156 | 0.42742 | 0.42741
1320 | feeder2_line83 | 1 | 354.6 | 68.7805 | 68.7764 | 19.3967 | 19.3955
1320 | feeder2_line83 | 2 | 354.6 | 82.886 | 82.8746 | 23.3745 | 23.3713
1320 | feeder2_line83 | 3 | 354.6 | 94.7915 | 94.803 | 26.732 | 26.7352
1320 | feeder2_line84 | 1 | 354.6 | 1.3844e-11 | 1.2972e-06 | 3.9041e-12 | 3.6582e-07
1320 | feeder2_line84 | 2 | 354.6 | 3.6247 | 3.6246 | 1.0222 | 1.0222
1320 | feeder2_line84 | 3 | 354.6 | 7.2801e-12 | 1.3035e-06 | 2.0531e-12 | 3.6759e-07
1320 | feeder2_line85 | 1 | 99 | 1.6994 | 1.6994 | 1.7166 | 1.7166
1320 | feeder2_line85 | 2 | 99 | 4.9647e-08 | 4.6441e-07 | 5.0149e-08 | 4.691e-07
1320 | feeder2_line85 | 3 | 99 | 5.0085e-08 | 4.6529e-07 | 5.0591e-08 | 4.6999e-07
1320 | feeder2_line86 | 1 | 354.6 | 70.478 | 70.4738 | 19.8754 | 19.8742
1320 | feeder2_line86 | 2 | 354.6 | 82.8862 | 82.8746 | 23.3746 | 23.3713
1320 | feeder2_line86 | 3 | 354.6 | 94.7917 | 94.803 | 26.732 | 26.7352
1320 | feeder2_line87 | 1 | 354.6 | 70.4782 | 70.4738 | 19.8754 | 19.8742
1320 | feeder2_line87 | 2 | 354.6 | 87.9295 | 87.9176 | 24.7968 | 24.7935
1320 | feeder2_line87 | 3 | 354.6 | 95.0543 | 95.0655 | 26.8061 | 26.8092
1320 | feeder2_line88 | 1 | 354.6 | 0.00011309 | 3.3617e-06 | 3.1892e-05 | 9.4801e-07
1320 | feeder2_line88 | 2 | 354.6 | 6.1012 | 6.101 | 1.7206 | 1.7205
1320 | feeder2_line88 | 3 | 354.6 | 0.26264 | 0.26258 | 0.074066 | 0.07405
1320 | feeder2_line89 | 1 | 354.6 | 70.476 | 70.4738 | 19.8748 | 19.8742
1320 | feeder2_line89 | 2 | 354.6 | 92.4908 | 92.4812 | 26.0831 | 26.0804
1320 | feeder2_line89 | 3 | 354.6 | 95.052 | 95.0655 | 26.8054 | 26.8092
1320 | feeder2_line90 | 1 | 354.6 | 0.00072218 | 2.029e-06 | 0.00020366 | 5.7218e-07
1320 | feeder2_line90 | 2 | 354.6 | 5.1585 | 5.1585 | 1.4547 | 1.4547
1320 | feeder2_line90 | 3 | 354.6 | 0.00072747 | 2.0411e-06 | 0.00020515 | 5.7561e-07
1320 | feeder2_line91 | 1 | 354.6 | 70.4759 | 70.4738 | 19.8747 | 19.8742
1320 | feeder2_line91 | 2 | 354.6 | 92.4907 | 92.4812 | 26.0831 | 26.0804
1320 | feeder2_line91 | 3 | 354.6 | 96.4441 | 96.4578 | 27.198 | 27.2019
1320 | feeder2_line92 | 1 | 354.6 | 5.817e-12 | 1.024e-06 | 1.6404e-12 | 2.8879e-07
1320 | feeder2_line92 | 2 | 354.6 | 1.808e-11 | 1.0272e-06 | 5.0988e-12 | 2.8967e-07
1320 | feeder2_line92 | 3 | 354.6 | 1.4872 | 1.4872 | 0.41939 | 0.4194
1320 | feeder2_line93 | 1 | 99 | 2.522e-08 | 3.4175e-07 | 2.5475e-08 | 3.452e-07
1320 | feeder2_line93 | 2 | 99 | 3.6239 | 3.6238 | 3.6605 | 3.6604
1320 | feeder2_line93 | 3 | 99 | 2.5056e-08 | 3.4364e-07 | 2.5309e-08 | 3.4711e-07
1320 | feeder2_line94 | 1 | 354.6 | 2.5218e-06 | 1.6642e-06 | 7.1116e-07 | 4.6932e-07
1320 | feeder2_line94 | 2 | 354.6 | 1.5477 | 1.5476 | 0.43646 | 0.43644
1320 | feeder2_line94 | 3 | 354.6 | 2.5055e-06 | 1.673e-06 | 7.0658e-07 | 4.7179e-07
1320 | feeder2_line95 | 1 | 99 | 3.5605e-06 | 2.6069e-06 | 3.5965e-06 | 2.6333e-06
1320 | feeder2_line95 | 2 | 99 | 6.1012 | 6.101 | 6.1628 | 6.1626
1320 | feeder2_line95 | 3 | 99 | 3.5863e-06 | 2.6209e-06 | 3.6225e-06 | 2.6474e-06
1320 | feeder2_line96 | 1 | 354.6 | 0.00012095 | 6.2129e-07 | 3.4108e-05 | 1.7521e-07
1320 | feeder2_line96 | 2 | 354.6 | 0.00012145 | 6.2354e-07 | 3.4249e-05 | 1.7584e-07
1320 | feeder2_line96 | 3 | 354.6 | 0.26262 | 0.26258 | 0.074061 | 0.07405
1320 | feeder2_line97 | 1 | 354.6 | 72.4807 | 72.4785 | 20.4401 | 20.4395
1320 | feeder2_line97 | 2 | 354.6 | 92.4909 | 92.4812 | 26.0832 | 26.0804
1320 | feeder2_line97 | 3 | 354.6 | 96.4443 | 96.4578 | 27.198 | 27.2019
1320 | feeder2_line98 | 1 | 354.6 | 2.0064 | 2.0048 | 0.56582 | 0.56536
1320 | feeder2_line98 | 2 | 354.6 | 0.0017154 | 6.2244e-07 | 0.00048376 | 1.7553e-07
1320 | feeder2_line98 | 3 | 354.6 | 0.0017053 | 6.2682e-07 | 0.00048091 | 1.7677e-07
1320 | feeder2_line99 | 1 | 99 | 2.5197e-08 | 4.4677e-07 | 2.5452e-08 | 4.5128e-07
1320 | feeder2_line99 | 2 | 99 | 2.4821e-08 | 4.4824e-07 | 2.5072e-08 | 4.5277e-07
1320 | feeder2_line99 | 3 | 99 | 0.26253 | 0.26258 | 0.26518 | 0.26523
1320 | feeder2_line100 | 1 | 99 | 2.0047 | 2.0048 | 2.025 | 2.025
1320 | feeder2_line100 | 2 | 99 | 2.4841e-08 | 6.1575e-07 | 2.5092e-08 | 6.2197e-07
1320 | feeder2_line100 | 3 | 99 | 2.5061e-08 | 6.1703e-07 | 2.5314e-08 | 6.2327e-07
1320 | feeder2_line101 | 1 | 354.6 | 1.5491 | 1.5487 | 0.43685 | 0.43676
1320 | feeder2_line101 | 2 | 354.6 | 5.8283 | 5.8277 | 1.6436 | 1.6435
1320 | feeder2_line101 | 3 | 354.6 | 10.6723 | 10.6721 | 3.0097 | 3.0096
1320 | feeder2_line102 | 1 | 99 | 1.4744 | 1.4744 | 1.4893 | 1.4893
1320 | feeder2_line102 | 2 | 99 | 2.346e-06 | 8.7993e-07 | 2.3697e-06 | 8.8881e-07
1320 | feeder2_line102 | 3 | 99 | 2.3411e-06 | 8.8135e-07 | 2.3648e-06 | 8.9025e-07
1320 | feeder2_line103 | 1 | 99 | 5.484e-07 | 8.0288e-07 | 5.5394e-07 | 8.1099e-07
1320 | feeder2_line103 | 2 | 99 | 0.65683 | 0.65683 | 0.66347 | 0.66346
1320 | feeder2_line103 | 3 | 99 | 5.5124e-07 | 8.0667e-07 | 5.5681e-07 | 8.1482e-07
1320 | feeder2_line104 | 1 | 354.6 | 1.549 | 1.5487 | 0.43683 | 0.43676
1320 | feeder2_line104 | 2 | 354.6 | 5.178 | 5.1776 | 1.4602 | 1.4601
1320 | feeder2_line104 | 3 | 354.6 | 10.6722 | 10.6721 | 3.0097 | 3.0096
1320 | feeder2_line105 | 1 | 99 | 2.5408e-06 | 7.3877e-07 | 2.5664e-06 | 7.4623e-07
1320 | feeder2_line105 | 2 | 99 | 2.5544e-06 | 7.4106e-07 | 2.5802e-06 | 7.4855e-07
1320 | feeder2_line105 | 3 | 99 | 0.49282 | 0.49287 | 0.4978 | 0.49784
1320 | feeder2_line106 | 1 | 354.6 | 1.549 | 1.5487 | 0.43682 | 0.43676
1320 | feeder2_line106 | 2 | 354.6 | 5.178 | 5.1776 | 1.4602 | 1.4601
1320 | feeder2_line106 | 3 | 354.6 | 10.188 | 10.1879 | 2.8731 | 2.8731
1320 | feeder2_line107 | 1 | 99 | 3.2451e-07 | 9.0029e-07 | 3.2779e-07 | 9.0939e-07
1320 | feeder2_line107 | 2 | 99 | 1.9263 | 1.9262 | 1.9457 | 1.9456
1320 | feeder2_line107 | 3 | 99 | 3.2566e-07 | 9.0441e-07 | 3.2895e-07 | 9.1355e-07
1320 | feeder2_line108 | 1 | 354.6 | 1.549 | 1.5487 | 0.43682 | 0.43676
1320 | feeder2_line108 | 2 | 354.6 | 3.2542 | 3.2539 | 0.91771 | 0.91763
1320 | feeder2_line108 | 3 | 354.6 | 10.188 | 10.1879 | 2.8731 | 2.8731
1320 | feeder2_line109 | 1 | 354.6 | 72.9348 | 72.9314 | 20.5682 | 20.5672
1320 | feeder2_line109 | 2 | 354.6 | 92.4921 | 92.4812 | 26.0835 | 26.0804
1320 | feeder2_line109 | 3 | 354.6 | 96.4455 | 96.4578 | 27.1984 | 27.2019
1320 | feeder2_line110 | 1 | 99 | 0.46307 | 0.46227 | 0.46775 | 0.46694
1320 | feeder2_line110 | 2 | 99 | 0.00080797 | 9.1196e-07 | 0.00081613 | 9.2118e-07
1320 | feeder2_line110 | 3 | 99 | 0.00080872 | 9.1347e-07 | 0.00081688 | 9.227e-07
1320 | feeder2_line111 | 1 | 99 | 2.5192e-08 | 3.8156e-07 | 2.5447e-08 | 3.8541e-07
1320 | feeder2_line111 | 2 | 99 | 2.4109 | 2.4109 | 2.4353 | 2.4353
1320 | feeder2_line111 | 3 | 99 | 2.5047e-08 | 3.8361e-07 | 2.53e-08 | 3.8748e-07
1320 | feeder2_line112 | 1 | 99 | 3.2472e-07 | 9.169e-07 | 3.28e-07 | 9.2616e-07
1320 | feeder2_line112 | 2 | 99 | 3.6933 | 3.6931 | 3.7306 | 3.7304
1320 | feeder2_line112 | 3 | 99 | 3.2606e-07 | 9.2182e-07 | 3.2935e-07 | 9.3114e-07
1320 | feeder2_line113 | 1 | 99 | 0.35411 | 0.35411 | 0.35769 | 0.35769
1320 | feeder2_line113 | 2 | 99 | 3.2555e-07 | 9.0823e-07 | 3.2884e-07 | 9.1741e-07
1320 | feeder2_line113 | 3 | 99 | 3.265e-07 | 9.1016e-07 | 3.298e-07 | 9.1935e-07
1320 | feeder2_line114 | 1 | 99 | 0.65723 | 0.65723 | 0.66387 | 0.66387
1320 | feeder2_line114 | 2 | 99 | 2.4821e-08 | 4.3755e-07 | 2.5072e-08 | 4.4197e-07
1320 | feeder2_line114 | 3 | 99 | 2.5036e-08 | 4.3826e-07 | 2.5289e-08 | 4.4269e-07
1320 | feeder2_line115 | 1 | 99 | 2.5151e-08 | 5.6183e-07 | 2.5405e-08 | 5.6751e-07
1320 | feeder2_line115 | 2 | 99 | 1.1013 | 1.1013 | 1.1124 | 1.1124
1320 | feeder2_line115 | 3 | 99 | 2.5042e-08 | 5.6434e-07 | 2.5295e-08 | 5.7004e-07
1320 | feeder2_line116 | 1 | 354.6 | 1.549 | 1.5487 | 0.43682 | 0.43676
1320 | feeder2_line116 | 2 | 354.6 | 2.153 | 2.1527 | 0.60717 | 0.60709
1320 | feeder2_line116 | 3 | 354.6 | 10.188 | 10.1879 | 2.8731 | 2.8731
1320 | feeder2_line117 | 1 | 99 | 5.0551e-08 | 6.4241e-07 | 5.1062e-08 | 6.489e-07
1320 | feeder2_line117 | 2 | 99 | 1.5315 | 1.5314 | 1.5469 | 1.5469
1320 | feeder2_line117 | 3 | 99 | 5.016e-08 | 6.4645e-07 | 5.0667e-08 | 6.5298e-07
1320 | feeder2_line118 | 1 | 354.6 | 72.9348 | 72.9314 | 20.5682 | 20.5672
1320 | feeder2_line118 | 2 | 354.6 | 93.4612 | 93.4502 | 26.3568 | 26.3537
1320 | feeder2_line118 | 3 | 354.6 | 96.4455 | 96.4578 | 27.1984 | 27.2019
1320 | feeder2_line119 | 1 | 99 | 2.5145e-08 | 6.0456e-07 | 2.5399e-08 | 6.1066e-07
1320 | feeder2_line119 | 2 | 99 | 2.4809e-08 | 6.0642e-07 | 2.5059e-08 | 6.1255e-07
1320 | feeder2_line119 | 3 | 99 | 2.361 | 2.361 | 2.3848 | 2.3848
1320 | feeder2_line120 | 1 | 354.6 | 1.549 | 1.5487 | 0.43682 | 0.43676
1320 | feeder2_line120 | 2 | 354.6 | 2.153 | 2.1527 | 0.60717 | 0.60709
1320 | feeder2_line120 | 3 | 354.6 | 7.867 | 7.8669 | 2.2186 | 2.2185
1320 | feeder2_line121 | 1 | 99 | 3.245e-07 | 9.3617e-07 | 3.2778e-07 | 9.4563e-07
1320 | feeder2_line121 | 2 | 99 | 1.8176 | 1.8176 | 1.8359 | 1.8359
1320 | feeder2_line121 | 3 | 99 | 3.2558e-07 | 9.4015e-07 | 3.2887e-07 | 9.4964e-07
1320 | feeder2_line122 | 1 | 354.6 | 1.5489 | 1.5487 | 0.43681 | 0.43676
1320 | feeder2_line122 | 2 | 354.6 | 0.33597 | 0.33572 | 0.094747 | 0.094675
1320 | feeder2_line122 | 3 | 354.6 | 7.867 | 7.8669 | 2.2186 | 2.2185
1320 | feeder2_line123 | 1 | 99 | 5.7357e-07 | 9.701e-07 | 5.7937e-07 | 9.799e-07
1320 | feeder2_line123 | 2 | 99 | 5.7539e-07 | 9.7312e-07 | 5.8121e-07 | 9.8295e-07
1320 | feeder2_line123 | 3 | 99 | 1.265 | 1.2649 | 1.2778 | 1.2777
1320 | feeder2_line124 | 1 | 354.6 | 1.5489 | 1.5487 | 0.43681 | 0.43676
1320 | feeder2_line124 | 2 | 354.6 | 0.33588 | 0.33572 | 0.09472 | 0.094675
1320 | feeder2_line124 | 3 | 354.6 | 6.8989 | 6.8988 | 1.9455 | 1.9455
1320 | feeder2_line125 | 1 | 99 | 5.7357e-07 | 9.0179e-07 | 5.7936e-07 | 9.109e-07
1320 | feeder2_line125 | 2 | 99 | 5.754e-07 | 9.0463e-07 | 5.8121e-07 | 9.1376e-07
1320 | feeder2_line125 | 3 | 99 | 1.9984 | 1.9985 | 2.0186 | 2.0187
1320 | feeder2_line126 | 1 | 354.6 | 1.5491 | 1.5487 | 0.43685 | 0.43676
1320 | feeder2_line126 | 2 | 354.6 | 0.33603 | 0.33572 | 0.094764 | 0.094675
1320 | feeder2_line126 | 3 | 354.6 | 4.9165 | 4.9162 | 1.3865 | 1.3864
1320 | feeder2_line127 | 1 | 99 | 5.7356e-07 | 1.0796e-06 | 5.7935e-07 | 1.0905e-06
1320 | feeder2_line127 | 2 | 99 | 5.754e-07 | 1.083e-06 | 5.8121e-07 | 1.0939e-06
1320 | feeder2_line127 | 3 | 99 | 3.1032 | 3.1032 | 3.1346 | 3.1346
1320 | feeder2_line128 | 1 | 354.6 | 1.549 | 1.5487 | 0.43683 | 0.43676
1320 | feeder2_line128 | 2 | 354.6 | 0.33595 | 0.33572 | 0.09474 | 0.094675
1320 | feeder2_line128 | 3 | 354.6 | 1.8666 | 1.8663 | 0.52639 | 0.52632
1320 | feeder2_line129 | 1 | 99 | 5.4842e-07 | 8.7539e-07 | 5.5396e-07 | 8.8423e-07
1320 | feeder2_line129 | 2 | 99 | 0.33573 | 0.33572 | 0.33912 | 0.33911
1320 | feeder2_line129 | 3 | 99 | 5.509e-07 | 8.7902e-07 | 5.5647e-07 | 8.879e-07
1320 | feeder2_line130 | 1 | 354.6 | 1.549 | 1.5487 | 0.43684 | 0.43676
1320 | feeder2_line130 | 2 | 354.6 | 0.00030863 | 4.6466e-06 | 8.7037e-05 | 1.3104e-06
1320 | feeder2_line130 | 3 | 354.6 | 1.8666 | 1.8663 | 0.52639 | 0.52632
1320 | feeder2_line131 | 1 | 99 | 5.7356e-07 | 9.7022e-07 | 5.7935e-07 | 9.8002e-07
1320 | feeder2_line131 | 2 | 99 | 5.7541e-07 | 9.733e-07 | 5.8122e-07 | 9.8313e-07
1320 | feeder2_line131 | 3 | 99 | 0.16251 | 0.16252 | 0.16415 | 0.16416
1320 | feeder2_line132 | 1 | 354.6 | 1.5489 | 1.5487 | 0.43679 | 0.43676
1320 | feeder2_line132 | 2 | 354.6 | 0.00012604 | 2.9213e-06 | 3.5544e-05 | 8.2383e-07
1320 | feeder2_line132 | 3 | 354.6 | 1.7039 | 1.7038 | 0.48052 | 0.48049
1320 | feeder2_line133 | 1 | 99 | 1.5487 | 1.5487 | 1.5644 | 1.5644
1320 | feeder2_line133 | 2 | 99 | 3.001e-07 | 9.8106e-07 | 3.0313e-07 | 9.9097e-07
1320 | feeder2_line133 | 3 | 99 | 3.005e-07 | 9.8202e-07 | 3.0353e-07 | 9.9194e-07
1320 | feeder2_line134 | 1 | 354.6 | 9.2833e-12 | 1.7838e-06 | 2.618e-12 | 5.0306e-07
1320 | feeder2_line134 | 2 | 354.6 | 8.0737e-12 | 1.7887e-06 | 2.2769e-12 | 5.0443e-07
1320 | feeder2_line134 | 3 | 354.6 | 1.7039 | 1.7038 | 0.4805 | 0.48049
1320 | feeder2_line135 | 1 | 99 | 2.3041 | 2.3041 | 2.3274 | 2.3274
1320 | feeder2_line135 | 2 | 99 | 4.9705e-08 | 5.8811e-07 | 5.0207e-08 | 5.9405e-07
1320 | feeder2_line135 | 3 | 99 | 5.0181e-08 | 5.894e-07 | 5.0688e-08 | 5.9535e-07
1320 | feeder2_line136 | 1 | 354.6 | 75.2368 | 75.2335 | 21.2174 | 21.2164
1320 | feeder2_line136 | 2 | 354.6 | 93.4612 | 93.4502 | 26.3568 | 26.3537
1320 | feeder2_line136 | 3 | 354.6 | 96.4455 | 96.4578 | 27.1984 | 27.2019
1320 | feeder2_line137 | 1 | 99 | 0.085809 | 0.085851 | 0.086676 | 0.086718
1320 | feeder2_line137 | 2 | 99 | 8.5374e-07 | 1.5842e-06 | 8.6237e-07 | 1.6002e-06
1320 | feeder2_line137 | 3 | 99 | 8.555e-07 | 1.5877e-06 | 8.6414e-07 | 1.6037e-06
1320 | feeder2_line138 | 1 | 354.6 | 75.3222 | 75.3188 | 21.2415 | 21.2405
1320 | feeder2_line138 | 2 | 354.6 | 93.4612 | 93.4502 | 26.3568 | 26.3537
1320 | feeder2_line138 | 3 | 354.6 | 96.4455 | 96.4578 | 27.1984 | 27.2019
1320 | feeder2_line139 | 1 | 99 | 5.0639e-08 | 4.9144e-07 | 5.1151e-08 | 4.964e-07
1320 | feeder2_line139 | 2 | 99 | 4.9714e-08 | 4.9369e-07 | 5.0217e-08 | 4.9868e-07
1320 | feeder2_line139 | 3 | 99 | 1.3353 | 1.3359 | 1.3488 | 1.3494
1320 | feeder2_line140 | 1 | 354.6 | 75.3223 | 75.3188 | 21.2415 | 21.2405
1320 | feeder2_line140 | 2 | 354.6 | 93.4613 | 93.4502 | 26.3568 | 26.3537
1320 | feeder2_line140 | 3 | 354.6 | 97.3231 | 97.336 | 27.4459 | 27.4495
1320 | feeder2_line141 | 1 | 99 | 2.5202e-06 | 4.8616e-07 | 2.5457e-06 | 4.9108e-07
1320 | feeder2_line141 | 2 | 99 | 0.76048 | 0.76048 | 0.76816 | 0.76817
1320 | feeder2_line141 | 3 | 99 | 2.5434e-06 | 4.8952e-07 | 2.5691e-06 | 4.9446e-07
1320 | feeder2_line142 | 1 | 354.6 | 75.3221 | 75.3188 | 21.2414 | 21.2405
1320 | feeder2_line142 | 2 | 354.6 | 94.2215 | 94.2105 | 26.5712 | 26.5681
1320 | feeder2_line142 | 3 | 354.6 | 97.3229 | 97.336 | 27.4458 | 27.4495
1320 | feeder2_line143 | 1 | 99 | 8.4982e-07 | 1.7276e-06 | 8.584e-07 | 1.745e-06
1320 | feeder2_line143 | 2 | 99 | 1.9273 | 1.9273 | 1.9468 | 1.9467
1320 | feeder2_line143 | 3 | 99 | 8.5597e-07 | 1.7396e-06 | 8.6462e-07 | 1.7572e-06
1320 | feeder2_line144 | 1 | 354.6 | 75.322 | 75.3188 | 21.2414 | 21.2405
1320 | feeder2_line144 | 2 | 354.6 | 96.1473 | 96.1365 | 27.1143 | 27.1112
1320 | feeder2_line144 | 3 | 354.6 | 97.3227 | 97.336 | 27.4458 | 27.4495
1320 | feeder2_line145 | 1 | 99 | 2.5335e-08 | 4.8443e-07 | 2.5591e-08 | 4.8932e-07
1320 | feeder2_line145 | 2 | 99 | 1.5168 | 1.5168 | 1.5321 | 1.5321
1320 | feeder2_line145 | 3 | 99 | 2.5105e-08 | 4.8782e-07 | 2.5358e-08 | 4.9275e-07
1320 | feeder2_line146 | 1 | 354.6 | 75.3218 | 75.3188 | 21.2414 | 21.2405
1320 | feeder2_line146 | 2 | 354.6 | 97.4331 | 97.4224 | 27.4769 | 27.4739
1320 | feeder2_line146 | 3 | 354.6 | 97.3226 | 97.336 | 27.4457 | 27.4495
1320 | feeder2_line147 | 1 | 99 | 0.10811 | 0.1081 | 0.1092 | 0.1092
1320 | feeder2_line147 | 2 | 99 | 1.1557e-06 | 2.2452e-06 | 1.1674e-06 | 2.2679e-06
1320 | feeder2_line147 | 3 | 99 | 1.1583e-06 | 2.2502e-06 | 1.17e-06 | 2.2729e-06
1320 | feeder2_line148 | 1 | 99 | 1.5661 | 1.5661 | 1.582 | 1.582
1320 | feeder2_line148 | 2 | 99 | 6.0273e-07 | 1.5044e-06 | 6.0881e-07 | 1.5196e-06
1320 | feeder2_line148 | 3 | 99 | 6.0425e-07 | 1.5078e-06 | 6.1035e-07 | 1.523e-06
1320 | feeder2_line149 | 1 | 354.6 | 76.9925 | 76.9893 | 21.7125 | 21.7116
1320 | feeder2_line149 | 2 | 354.6 | 97.4333 | 97.4224 | 27.477 | 27.4739
1320 | feeder2_line149 | 3 | 354.6 | 97.3227 | 97.336 | 27.4458 | 27.4495
1320 | feeder2_line150 | 1 | 354.6 | 76.9926 | 76.9893 | 21.7125 | 21.7116
1320 | feeder2_line150 | 2 | 354.6 | 99.0001 | 98.9892 | 27.9188 | 27.9157
1320 | feeder2_line150 | 3 | 354.6 | 97.3228 | 97.336 | 27.4458 | 27.4495
1320 | feeder2_line151 | 1 | 99 | 9.7336e-06 | 1.7785e-06 | 9.8319e-06 | 1.7965e-06
1320 | feeder2_line151 | 2 | 99 | 1.8878 | 1.8878 | 1.9068 | 1.9069
1320 | feeder2_line151 | 3 | 99 | 9.8305e-06 | 1.7915e-06 | 9.9298e-06 | 1.8096e-06
1320 | feeder2_line152 | 1 | 354.6 | 6.9893e-12 | 1.1858e-06 | 1.971e-12 | 3.3439e-07
1320 | feeder2_line152 | 2 | 354.6 | 2.7498e-11 | 1.1913e-06 | 7.7547e-12 | 3.3595e-07
1320 | feeder2_line152 | 3 | 354.6 | 0.076338 | 0.076347 | 0.021528 | 0.021531
1320 | feeder2_line153 | 1 | 99 | 1.8203 | 1.8203 | 1.8387 | 1.8387
1320 | feeder2_line153 | 2 | 99 | 4.9739e-08 | 5.9618e-07 | 5.0241e-08 | 6.0221e-07
1320 | feeder2_line153 | 3 | 99 | 5.0253e-08 | 5.975e-07 | 5.0761e-08 | 6.0354e-07
1320 | feeder2_line154 | 1 | 99 | 5.7542e-07 | 8.8247e-07 | 5.8123e-07 | 8.9138e-07
1320 | feeder2_line154 | 2 | 99 | 5.7852e-07 | 8.8714e-07 | 5.8436e-07 | 8.961e-07
1320 | feeder2_line154 | 3 | 99 | 1.5072 | 1.5072 | 1.5224 | 1.5224
1320 | feeder2_line155 | 1 | 99 | 78.8115 | 78.8084 | 79.6076 | 79.6044
1320 | feeder2_line155 | 2 | 99 | 99 | 98.9892 | 100 | 99.9891
1320 | feeder2_line155 | 3 | 99 | 98.9039 | 98.9171 | 99.9029 | 99.9163
1320 | feeder2_line156 | 1 | 99 | 6.0062e-07 | 1.1613e-06 | 6.0669e-07 | 1.1731e-06
1320 | feeder2_line156 | 2 | 99 | 0.65648 | 0.65647 | 0.66311 | 0.6631
1320 | feeder2_line156 | 3 | 99 | 6.046e-07 | 1.1698e-06 | 6.1071e-07 | 1.1816e-06
1320 | feeder2_line157 | 1 | 99 | 2.5361e-08 | 2.5211e-07 | 2.5617e-08 | 2.5466e-07
1320 | feeder2_line157 | 2 | 99 | 1.4827 | 1.4827 | 1.4976 | 1.4977
1320 | feeder2_line157 | 3 | 99 | 2.5119e-08 | 2.5396e-07 | 2.5372e-08 | 2.5653e-07
1350 | feeder2_line1 | 1 | 354.6 | 48.5017 | 48.4984 | 13.6779 | 13.6769
1350 | feeder2_line1 | 2 | 354.6 | 49.4102 | 49.4196 | 13.9341 | 13.9367
1350 | feeder2_line1 | 3 | 354.6 | 50.9758 | 50.9719 | 14.3756 | 14.3745
1350 | feeder2_line2 | 1 | 354.6 | 51.7687 | 51.7651 | 14.5992 | 14.5982
1350 | feeder2_line2 | 2 | 354.6 | 49.4104 | 49.4196 | 13.9341 | 13.9367
1350 | feeder2_line2 | 3 | 354.6 | 50.976 | 50.9719 | 14.3756 | 14.3745
1350 | feeder2_line3 | 1 | 80.1 | 3.4627 | 3.4627 | 4.323 | 4.323
1350 | feeder2_line3 | 2 | 80.1 | 5.7195e-07 | 1.0569e-06 | 7.1404e-07 | 1.3195e-06
1350 | feeder2_line3 | 3 | 80.1 | 5.72e-07 | 1.057e-06 | 7.1411e-07 | 1.3197e-06
1350 | feeder2_line4 | 1 | 354.6 | 51.7688 | 51.7651 | 14.5992 | 14.5982
1350 | feeder2_line4 | 2 | 354.6 | 49.6894 | 49.6985 | 14.0128 | 14.0154
1350 | feeder2_line4 | 3 | 354.6 | 50.9761 | 50.9719 | 14.3757 | 14.3745
1350 | feeder2_line5 | 1 | 80.1 | 5.7188e-07 | 9.9788e-07 | 7.1396e-07 | 1.2458e-06
1350 | feeder2_line5 | 2 | 80.1 | 0.27929 | 0.27929 | 0.34867 | 0.34868
1350 | feeder2_line5 | 3 | 80.1 | 5.7204e-07 | 9.9815e-07 | 7.1415e-07 | 1.2461e-06
1350 | feeder2_line6 | 1 | 80.1 | 5.7193e-07 | 1.174e-06 | 7.1402e-07 | 1.4657e-06
1350 | feeder2_line6 | 2 | 80.1 | 5.7202e-07 | 1.1742e-06 | 7.1413e-07 | 1.4659e-06
1350 | feeder2_line6 | 3 | 80.1 | 2.0588 | 2.0588 | 2.5702 | 2.5702
1350 | feeder2_line7 | 1 | 354.6 | 51.7689 | 51.7651 | 14.5992 | 14.5982
1350 | feeder2_line7 | 2 | 354.6 | 49.6895 | 49.6985 | 14.0128 | 14.0154
1350 | feeder2_line7 | 3 | 354.6 | 52.6907 | 52.6864 | 14.8592 | 14.858
1350 | feeder2_line8 | 1 | 80.1 | 0.99231 | 0.99231 | 1.2388 | 1.2388
1350 | feeder2_line8 | 2 | 80.1 | 5.7215e-07 | 1.1324e-06 | 7.143e-07 | 1.4138e-06
1350 | feeder2_line8 | 3 | 80.1 | 5.7224e-07 | 1.1326e-06 | 7.144e-07 | 1.414e-06
1350 | feeder2_line9 | 1 | 354.6 | 52.7611 | 52.7572 | 14.879 | 14.878
1350 | feeder2_line9 | 2 | 354.6 | 49.6896 | 49.6985 | 14.0129 | 14.0154
1350 | feeder2_line9 | 3 | 354.6 | 52.6908 | 52.6864 | 14.8592 | 14.858
1350 | feeder2_line10 | 1 | 80.1 | 8.4569e-07 | 1.4951e-06 | 1.0558e-06 | 1.8665e-06
1350 | feeder2_line10 | 2 | 80.1 | 0.99238 | 0.99238 | 1.2389 | 1.2389
1350 | feeder2_line10 | 3 | 80.1 | 8.4595e-07 | 1.4955e-06 | 1.0561e-06 | 1.8671e-06
1350 | feeder2_line11 | 1 | 354.6 | 52.761 | 52.7572 | 14.879 | 14.878
1350 | feeder2_line11 | 2 | 354.6 | 50.6813 | 50.6902 | 14.2925 | 14.295
1350 | feeder2_line11 | 3 | 354.6 | 52.6907 | 52.6864 | 14.8592 | 14.858
1350 | feeder2_line12 | 1 | 80.1 | 5.4726e-07 | 9.9183e-07 | 6.8322e-07 | 1.2382e-06
1350 | feeder2_line12 | 2 | 80.1 | 5.4735e-07 | 9.9195e-07 | 6.8333e-07 | 1.2384e-06
1350 | feeder2_line12 | 3 | 80.1 | 2.9741 | 2.9741 | 3.713 | 3.713
1350 | feeder2_line13 | 1 | 354.6 | 52.761 | 52.7572 | 14.879 | 14.878
1350 | feeder2_line13 | 2 | 354.6 | 50.6813 | 50.6902 | 14.2925 | 14.295
1350 | feeder2_line13 | 3 | 354.6 | 55.6599 | 55.6556 | 15.6965 | 15.6953
1350 | feeder2_line14 | 1 | 80.1 | 0.27525 | 0.27525 | 0.34364 | 0.34364
1350 | feeder2_line14 | 2 | 80.1 | 2.9858e-07 | 6.4689e-07 | 3.7276e-07 | 8.076e-07
1350 | feeder2_line14 | 3 | 80.1 | 2.9862e-07 | 6.4701e-07 | 3.7281e-07 | 8.0775e-07
1350 | feeder2_line15 | 1 | 354.6 | 53.0356 | 53.0318 | 14.9565 | 14.9554
1350 | feeder2_line15 | 2 | 354.6 | 50.6813 | 50.6902 | 14.2925 | 14.295
1350 | feeder2_line15 | 3 | 354.6 | 55.66 | 55.6556 | 15.6966 | 15.6953
1350 | feeder2_line16 | 1 | 80.1 | 5.7228e-07 | 1.031e-06 | 7.1446e-07 | 1.2871e-06
1350 | feeder2_line16 | 2 | 80.1 | 0.25438 | 0.25438 | 0.31758 | 0.31758
1350 | feeder2_line16 | 3 | 80.1 | 5.7247e-07 | 1.0313e-06 | 7.147e-07 | 1.2876e-06
1350 | feeder2_line17 | 1 | 354.6 | 53.0356 | 53.0318 | 14.9565 | 14.9554
1350 | feeder2_line17 | 2 | 354.6 | 50.935 | 50.9439 | 14.3641 | 14.3666
1350 | feeder2_line17 | 3 | 354.6 | 55.66 | 55.6556 | 15.6966 | 15.6953
1350 | feeder2_line18 | 1 | 80.1 | 5.4773e-07 | 7.3847e-07 | 6.838e-07 | 9.2194e-07
1350 | feeder2_line18 | 2 | 80.1 | 5.4777e-07 | 7.3851e-07 | 6.8385e-07 | 9.2198e-07
1350 | feeder2_line18 | 3 | 80.1 | 1.4347 | 1.4347 | 1.7911 | 1.7911
1350 | feeder2_line19 | 1 | 354.6 | 53.0356 | 53.0318 | 14.9565 | 14.9554
1350 | feeder2_line19 | 2 | 354.6 | 50.9351 | 50.9439 | 14.3641 | 14.3666
1350 | feeder2_line19 | 3 | 354.6 | 57.0878 | 57.0833 | 16.0992 | 16.098
1350 | feeder2_line20 | 1 | 99 | 5.4786e-07 | 8.8559e-07 | 5.5339e-07 | 8.9453e-07
1350 | feeder2_line20 | 2 | 99 | 5.4788e-07 | 8.8561e-07 | 5.5341e-07 | 8.9456e-07
1350 | feeder2_line20 | 3 | 99 | 1.5844 | 1.5844 | 1.6004 | 1.6004
1350 | feeder2_line21 | 1 | 354.6 | 53.0358 | 53.0318 | 14.9565 | 14.9554
1350 | feeder2_line21 | 2 | 354.6 | 50.9352 | 50.9439 | 14.3641 | 14.3666
1350 | feeder2_line21 | 3 | 354.6 | 58.1487 | 58.1441 | 16.3984 | 16.3971
1350 | feeder2_line22 | 1 | 99 | 5.7285e-07 | 1.0154e-06 | 5.7864e-07 | 1.0256e-06
1350 | feeder2_line22 | 2 | 99 | 3.5351 | 3.5351 | 3.5708 | 3.5708
1350 | feeder2_line22 | 3 | 99 | 5.7315e-07 | 1.0159e-06 | 5.7894e-07 | 1.0261e-06
1350 | feeder2_line23 | 1 | 99 | 5.7286e-07 | 9.5047e-07 | 5.7865e-07 | 9.6007e-07
1350 | feeder2_line23 | 2 | 99 | 5.7286e-07 | 9.5048e-07 | 5.7865e-07 | 9.6008e-07
1350 | feeder2_line23 | 3 | 99 | 0.5668 | 0.56681 | 0.57252 | 0.57254
1350 | feeder2_line24 | 1 | 354.6 | 53.0358 | 53.0318 | 14.9565 | 14.9554
1350 | feeder2_line24 | 2 | 354.6 | 54.4536 | 54.4624 | 15.3564 | 15.3588
1350 | feeder2_line24 | 3 | 354.6 | 58.6775 | 58.6728 | 16.5475 | 16.5462
1350 | feeder2_line25 | 1 | 99 | 3.535 | 3.535 | 3.5707 | 3.5707
1350 | feeder2_line25 | 2 | 99 | 4.9849e-08 | 6.9119e-07 | 5.0352e-08 | 6.9817e-07
1350 | feeder2_line25 | 3 | 99 | 4.978e-08 | 6.9157e-07 | 5.0283e-08 | 6.9856e-07
1350 | feeder2_line26 | 1 | 99 | 1.6988 | 1.6988 | 1.716 | 1.716
1350 | feeder2_line26 | 2 | 99 | 5.4809e-07 | 8.5634e-07 | 5.5362e-07 | 8.6499e-07
1350 | feeder2_line26 | 3 | 99 | 5.4844e-07 | 8.5682e-07 | 5.5398e-07 | 8.6547e-07
1350 | feeder2_line27 | 1 | 354.6 | 58.2426 | 58.2386 | 16.4249 | 16.4237
1350 | feeder2_line27 | 2 | 354.6 | 54.4537 | 54.4624 | 15.3564 | 15.3588
1350 | feeder2_line27 | 3 | 354.6 | 58.6775 | 58.6728 | 16.5475 | 16.5462
1350 | feeder2_line28 | 1 | 99 | 2.5421e-06 | 7.1116e-07 | 2.5677e-06 | 7.1835e-07
1350 | feeder2_line28 | 2 | 99 | 0.10865 | 0.10865 | 0.10975 | 0.10975
1350 | feeder2_line28 | 3 | 99 | 2.5444e-06 | 7.1159e-07 | 2.5701e-06 | 7.1878e-07
1350 | feeder2_line29 | 1 | 354.6 | 58.2426 | 58.2386 | 16.4249 | 16.4237
1350 | feeder2_line29 | 2 | 354.6 | 54.5618 | 54.5705 | 15.3869 | 15.3893
1350 | feeder2_line29 | 3 | 354.6 | 58.6775 | 58.6728 | 16.5475 | 16.5462
1350 | feeder2_line30 | 1 | 266.4 | 13.2855 | 13.2852 | 4.9871 | 4.9869
1350 | feeder2_line30 | 2 | 266.4 | 3.9856 | 3.9854 | 1.4961 | 1.496
1350 | feeder2_line30 | 3 | 266.4 | 6.9407 | 6.9405 | 2.6054 | 2.6053
1350 | feeder2_line31 | 1 | 354.6 | 71.4995 | 71.4951 | 20.1634 | 20.1622
1350 | feeder2_line31 | 2 | 354.6 | 58.4366 | 58.445 | 16.4796 | 16.482
1350 | feeder2_line31 | 3 | 354.6 | 65.2382 | 65.2332 | 18.3977 | 18.3963
1350 | feeder2_line32 | 1 | 354.6 | 71.4995 | 71.4951 | 20.1634 | 20.1622
1350 | feeder2_line32 | 2 | 354.6 | 60.7157 | 60.7241 | 17.1223 | 17.1247
1350 | feeder2_line32 | 3 | 354.6 | 65.2383 | 65.2332 | 18.3977 | 18.3963
1350 | feeder2_line33 | 1 | 99 | 4.993e-08 | 6.8688e-07 | 5.0435e-08 | 6.9382e-07
1350 | feeder2_line33 | 2 | 99 | 2.2798 | 2.2799 | 2.3029 | 2.3029
1350 | feeder2_line33 | 3 | 99 | 4.9832e-08 | 6.8726e-07 | 5.0335e-08 | 6.942e-07
1350 | feeder2_line34 | 1 | 354.6 | 71.4995 | 71.4951 | 20.1634 | 20.1622
1350 | feeder2_line34 | 2 | 354.6 | 60.7157 | 60.7241 | 17.1223 | 17.1247
1350 | feeder2_line34 | 3 | 354.6 | 65.9047 | 65.8997 | 18.5857 | 18.5842
1350 | feeder2_line35 | 1 | 99 | 2.9952e-07 | 7.6081e-07 | 3.0254e-07 | 7.685e-07
1350 | feeder2_line35 | 2 | 99 | 2.9939e-07 | 7.6047e-07 | 3.0242e-07 | 7.6815e-07
1350 | feeder2_line35 | 3 | 99 | 0.66665 | 0.66665 | 0.67338 | 0.67339
1350 | feeder2_line36 | 1 | 354.6 | 72.9964 | 72.992 | 20.5856 | 20.5843
1350 | feeder2_line36 | 2 | 354.6 | 60.7156 | 60.7241 | 17.1223 | 17.1247
1350 | feeder2_line36 | 3 | 354.6 | 65.9047 | 65.8997 | 18.5856 | 18.5842
1350 | feeder2_line37 | 1 | 99 | 1.8091 | 1.8091 | 1.8274 | 1.8274
1350 | feeder2_line37 | 2 | 99 | 2.9945e-07 | 8.4157e-07 | 3.0247e-07 | 8.5007e-07
1350 | feeder2_line37 | 3 | 99 | 2.9971e-07 | 8.4242e-07 | 3.0273e-07 | 8.5093e-07
1350 | feeder2_line38 | 1 | 99 | 3.2426e-07 | 7.7625e-07 | 3.2753e-07 | 7.8409e-07
1350 | feeder2_line38 | 2 | 99 | 1.5416 | 1.5416 | 1.5572 | 1.5572
1350 | feeder2_line38 | 3 | 99 | 3.2437e-07 | 7.7677e-07 | 3.2765e-07 | 7.8461e-07
1350 | feeder2_line39 | 1 | 266.4 | 13.2856 | 13.2852 | 4.9871 | 4.9869
1350 | feeder2_line39 | 2 | 266.4 | 2.5444 | 2.5443 | 0.9551 | 0.95507
1350 | feeder2_line39 | 3 | 266.4 | 6.9407 | 6.9405 | 2.6054 | 2.6053
1350 | feeder2_line40 | 1 | 354.6 | 76.5208 | 76.5163 | 21.5795 | 21.5782
1350 | feeder2_line40 | 2 | 354.6 | 60.7157 | 60.7241 | 17.1223 | 17.1247
1350 | feeder2_line40 | 3 | 354.6 | 65.9047 | 65.8997 | 18.5857 | 18.5842
1350 | feeder2_line41 | 1 | 99 | 3.5339 | 3.5339 | 3.5696 | 3.5695
1350 | feeder2_line41 | 2 | 99 | 5.0003e-08 | 7.3544e-07 | 5.0508e-08 | 7.4286e-07
1350 | feeder2_line41 | 3 | 99 | 4.9853e-08 | 7.3621e-07 | 5.0356e-08 | 7.4364e-07
1350 | feeder2_line42 | 1 | 99 | 2.9926e-07 | 7.4915e-07 | 3.0228e-07 | 7.5672e-07
1350 | feeder2_line42 | 2 | 99 | 2.9926e-07 | 7.4919e-07 | 3.0228e-07 | 7.5676e-07
1350 | feeder2_line42 | 3 | 99 | 1.5563 | 1.5563 | 1.572 | 1.572
1350 | feeder2_line43 | 1 | 266.4 | 13.2855 | 13.2852 | 4.987 | 4.9869
1350 | feeder2_line43 | 2 | 266.4 | 2.5444 | 2.5443 | 0.95509 | 0.95507
1350 | feeder2_line43 | 3 | 266.4 | 5.4709 | 5.4708 | 2.0537 | 2.0536
1350 | feeder2_line44 | 1 | 354.6 | 76.5208 | 76.5163 | 21.5795 | 21.5782
1350 | feeder2_line44 | 2 | 354.6 | 60.7157 | 60.7241 | 17.1223 | 17.1247
1350 | feeder2_line44 | 3 | 354.6 | 67.0329 | 67.0278 | 18.9038 | 18.9024
1350 | feeder2_line45 | 1 | 99 | 4.9945e-08 | 5.8042e-07 | 5.0449e-08 | 5.8628e-07
1350 | feeder2_line45 | 2 | 99 | 5.0019e-08 | 5.8003e-07 | 5.0524e-08 | 5.8589e-07
1350 | feeder2_line45 | 3 | 99 | 1.5856 | 1.5856 | 1.6016 | 1.6016
1350 | feeder2_line46 | 1 | 99 | 5.7354e-07 | 1.3581e-06 | 5.7933e-07 | 1.3718e-06
1350 | feeder2_line46 | 2 | 99 | 5.7357e-07 | 1.3582e-06 | 5.7936e-07 | 1.3719e-06
1350 | feeder2_line46 | 3 | 99 | 0.95764 | 0.95765 | 0.96731 | 0.96732
1350 | feeder2_line47 | 1 | 266.4 | 13.2855 | 13.2852 | 4.987 | 4.9869
1350 | feeder2_line47 | 2 | 266.4 | 2.5444 | 2.5443 | 0.95512 | 0.95507
1350 | feeder2_line47 | 3 | 266.4 | 4.7127 | 4.7125 | 1.769 | 1.7689
1350 | feeder2_line48 | 1 | 99 | 0.13636 | 0.13636 | 0.13774 | 0.13774
1350 | feeder2_line48 | 2 | 99 | 4.9902e-08 | 7.3125e-07 | 5.0406e-08 | 7.3864e-07
1350 | feeder2_line48 | 3 | 99 | 4.9818e-08 | 7.3176e-07 | 5.0322e-08 | 7.3915e-07
1350 | feeder2_line49 | 1 | 266.4 | 13.1519 | 13.1516 | 4.9369 | 4.9368
1350 | feeder2_line49 | 2 | 266.4 | 2.5444 | 2.5443 | 0.95512 | 0.95508
1350 | feeder2_line49 | 3 | 266.4 | 4.7127 | 4.7125 | 1.769 | 1.7689
1350 | feeder2_line50 | 1 | 99 | 5.7347e-07 | 1.2358e-06 | 5.7926e-07 | 1.2483e-06
1350 | feeder2_line50 | 2 | 99 | 2.0584 | 2.0585 | 2.0792 | 2.0792
1350 | feeder2_line50 | 3 | 99 | 5.7397e-07 | 1.2369e-06 | 5.7976e-07 | 1.2494e-06
1350 | feeder2_line51 | 1 | 99 | 0.89627 | 0.89616 | 0.90532 | 0.90521
1350 | feeder2_line51 | 2 | 99 | 5.7357e-07 | 1.3418e-06 | 5.7937e-07 | 1.3554e-06
1350 | feeder2_line51 | 3 | 99 | 5.7396e-07 | 1.3427e-06 | 5.7976e-07 | 1.3563e-06
1350 | feeder2_line52 | 1 | 266.4 | 12.2558 | 12.2558 | 4.6005 | 4.6005
1350 | feeder2_line52 | 2 | 266.4 | 0.59317 | 0.59305 | 0.22266 | 0.22262
1350 | feeder2_line52 | 3 | 266.4 | 4.7125 | 4.7125 | 1.769 | 1.7689
1350 | feeder2_line53 | 1 | 99 | 5.4849e-07 | 7.5423e-07 | 5.5404e-07 | 7.6184e-07
1350 | feeder2_line53 | 2 | 99 | 0.59304 | 0.59305 | 0.59903 | 0.59904
1350 | feeder2_line53 | 3 | 99 | 5.4905e-07 | 7.5487e-07 | 5.546e-07 | 7.625e-07
1350 | feeder2_line54 | 1 | 266.4 | 12.2556 | 12.2558 | 4.6005 | 4.6005
1350 | feeder2_line54 | 2 | 266.4 | 8.5566e-05 | 4.6278e-06 | 3.2119e-05 | 1.7372e-06
1350 | feeder2_line54 | 3 | 266.4 | 4.7124 | 4.7125 | 1.7689 | 1.7689
1350 | feeder2_line55 | 1 | 99 | 0.18108 | 0.18108 | 0.18291 | 0.18291
1350 | feeder2_line55 | 2 | 99 | 5.0073e-08 | 7.3103e-07 | 5.0579e-08 | 7.3841e-07
1350 | feeder2_line55 | 3 | 99 | 4.9884e-08 | 7.3194e-07 | 5.0388e-08 | 7.3933e-07
1350 | feeder2_line56 | 1 | 354.6 | 76.7018 | 76.6973 | 21.6305 | 21.6292
1350 | feeder2_line56 | 2 | 354.6 | 60.7158 | 60.7241 | 17.1223 | 17.1247
1350 | feeder2_line56 | 3 | 354.6 | 67.033 | 67.0278 | 18.9038 | 18.9024
1350 | feeder2_line57 | 1 | 99 | 7.4906e-07 | 1.5448e-06 | 7.5662e-07 | 1.5604e-06
1350 | feeder2_line57 | 2 | 99 | 7.4838e-07 | 1.5452e-06 | 7.5594e-07 | 1.5608e-06
1350 | feeder2_line57 | 3 | 99 | 4.7125 | 4.7125 | 4.7601 | 4.7601
1350 | feeder2_line58 | 1 | 266.4 | 12.2557 | 12.2558 | 4.6005 | 4.6005
1350 | feeder2_line58 | 2 | 266.4 | 1.8956e-05 | 2.6869e-06 | 7.1155e-06 | 1.0086e-06
1350 | feeder2_line58 | 3 | 266.4 | 1.8974e-05 | 2.6885e-06 | 7.1223e-06 | 1.0092e-06
1350 | feeder2_line59 | 1 | 99 | 4.9936e-08 | 5.3699e-07 | 5.044e-08 | 5.4241e-07
1350 | feeder2_line59 | 2 | 99 | 4.9889e-08 | 5.3713e-07 | 5.0393e-08 | 5.4256e-07
1350 | feeder2_line59 | 3 | 99 | 1.7968 | 1.7968 | 1.815 | 1.815
1350 | feeder2_line60 | 1 | 99 | 2.992e-07 | 8.1155e-07 | 3.0222e-07 | 8.1975e-07
1350 | feeder2_line60 | 2 | 99 | 2.9927e-07 | 8.1177e-07 | 3.0229e-07 | 8.1996e-07
1350 | feeder2_line60 | 3 | 99 | 2.9786 | 2.9786 | 3.0087 | 3.0087
1350 | feeder2_line61 | 1 | 266.4 | 2.1869 | 2.1871 | 0.82092 | 0.82099
1350 | feeder2_line61 | 2 | 266.4 | 5.9856 | 5.9859 | 2.2469 | 2.247
1350 | feeder2_line61 | 3 | 266.4 | 7.142 | 7.1422 | 2.6809 | 2.681
1350 | feeder2_line62 | 1 | 354.6 | 78.5103 | 78.506 | 22.1405 | 22.1393
1350 | feeder2_line62 | 2 | 354.6 | 66.7008 | 66.7095 | 18.8102 | 18.8126
1350 | feeder2_line62 | 3 | 354.6 | 74.1742 | 74.1693 | 20.9177 | 20.9163
1350 | feeder2_line63 | 1 | 99 | 0.35991 | 0.3599 | 0.36354 | 0.36354
1350 | feeder2_line63 | 2 | 99 | 5.736e-07 | 1.2205e-06 | 5.7939e-07 | 1.2328e-06
1350 | feeder2_line63 | 3 | 99 | 5.7397e-07 | 1.2213e-06 | 5.7977e-07 | 1.2336e-06
1350 | feeder2_line64 | 1 | 99 | 11.8958 | 11.8959 | 12.016 | 12.0161
1350 | feeder2_line64 | 2 | 99 | 1.9251e-12 | 3.215e-07 | 1.9446e-12 | 3.2475e-07
1350 | feeder2_line64 | 3 | 99 | 2.8531e-12 | 3.2171e-07 | 2.8819e-12 | 3.2496e-07
1350 | feeder2_line65 | 1 | 99 | 4.997e-08 | 6.4343e-07 | 5.0474e-08 | 6.4993e-07
1350 | feeder2_line65 | 2 | 99 | 0.27942 | 0.27943 | 0.28224 | 0.28225
1350 | feeder2_line65 | 3 | 99 | 4.9922e-08 | 6.4344e-07 | 5.0426e-08 | 6.4994e-07
1350 | feeder2_line66 | 1 | 354.6 | 78.5102 | 78.506 | 22.1405 | 22.1393
1350 | feeder2_line66 | 2 | 354.6 | 66.9801 | 66.9889 | 18.8889 | 18.8914
1350 | feeder2_line66 | 3 | 354.6 | 74.1742 | 74.1693 | 20.9177 | 20.9163
1350 | feeder2_line67 | 1 | 99 | 2.4978e-08 | 3.6355e-07 | 2.523e-08 | 3.6723e-07
1350 | feeder2_line67 | 2 | 99 | 2.5065e-08 | 3.6307e-07 | 2.5318e-08 | 3.6674e-07
1350 | feeder2_line67 | 3 | 99 | 3.5329 | 3.5329 | 3.5686 | 3.5686
1350 | feeder2_line68 | 1 | 266.4 | 2.187 | 2.1871 | 0.82094 | 0.82099
1350 | feeder2_line68 | 2 | 266.4 | 5.9857 | 5.9859 | 2.2469 | 2.247
1350 | feeder2_line68 | 3 | 266.4 | 3.6131 | 3.6132 | 1.3563 | 1.3563
1350 | feeder2_line69 | 1 | 99 | 4.222 | 4.2219 | 4.2646 | 4.2646
1350 | feeder2_line69 | 2 | 99 | 2.5474e-06 | 6.6705e-07 | 2.5731e-06 | 6.7379e-07
1350 | feeder2_line69 | 3 | 99 | 2.5536e-06 | 6.681e-07 | 2.5794e-06 | 6.7485e-07
1350 | feeder2_line70 | 1 | 354.6 | 82.7321 | 82.7279 | 23.3311 | 23.3299
1350 | feeder2_line70 | 2 | 354.6 | 66.98 | 66.9889 | 18.8889 | 18.8914
1350 | feeder2_line70 | 3 | 354.6 | 74.1741 | 74.1693 | 20.9177 | 20.9163
1350 | feeder2_line71 | 1 | 99 | 4.9977e-08 | 7.1814e-07 | 5.0481e-08 | 7.254e-07
1350 | feeder2_line71 | 2 | 99 | 3.2223 | 3.2223 | 3.2548 | 3.2549
1350 | feeder2_line71 | 3 | 99 | 4.9937e-08 | 7.1808e-07 | 5.0441e-08 | 7.2534e-07
1350 | feeder2_line72 | 1 | 354.6 | 82.7322 | 82.7279 | 23.3311 | 23.3299
1350 | feeder2_line72 | 2 | 354.6 | 70.0087 | 70.0174 | 19.743 | 19.7455
1350 | feeder2_line72 | 3 | 354.6 | 74.1742 | 74.1693 | 20.9177 | 20.9163
1350 | feeder2_line73 | 1 | 99 | 6.0012e-07 | 1.5391e-06 | 6.0618e-07 | 1.5547e-06
1350 | feeder2_line73 | 2 | 99 | 2.2793 | 2.2794 | 2.3024 | 2.3024
1350 | feeder2_line73 | 3 | 99 | 6.0011e-07 | 1.5392e-06 | 6.0617e-07 | 1.5547e-06
1350 | feeder2_line74 | 1 | 99 | 4.9953e-08 | 4.5905e-07 | 5.0457e-08 | 4.6368e-07
1350 | feeder2_line74 | 2 | 99 | 3.617 | 3.6171 | 3.6535 | 3.6536
1350 | feeder2_line74 | 3 | 99 | 4.9896e-08 | 4.5907e-07 | 5.04e-08 | 4.637e-07
1350 | feeder2_line75 | 1 | 266.4 | 2.1871 | 2.1871 | 0.82098 | 0.82099
1350 | feeder2_line75 | 2 | 266.4 | 0.089748 | 0.089785 | 0.033689 | 0.033703
1350 | feeder2_line75 | 3 | 266.4 | 3.6132 | 3.6132 | 1.3563 | 1.3563
1350 | feeder2_line76 | 1 | 99 | 2.1871 | 2.1871 | 2.2092 | 2.2092
1350 | feeder2_line76 | 2 | 99 | 8.49e-07 | 1.5855e-06 | 8.5758e-07 | 1.6015e-06
1350 | feeder2_line76 | 3 | 99 | 8.5026e-07 | 1.5877e-06 | 8.5884e-07 | 1.6037e-06
1350 | feeder2_line77 | 1 | 99 | 2.4971e-08 | 5.7687e-07 | 2.5223e-08 | 5.8269e-07
1350 | feeder2_line77 | 2 | 99 | 2.5057e-08 | 5.7609e-07 | 2.531e-08 | 5.8191e-07
1350 | feeder2_line77 | 3 | 99 | 3.6132 | 3.6132 | 3.6497 | 3.6497
1350 | feeder2_line78 | 1 | 266.4 | 3.0286e-12 | 9.5667e-07 | 1.1368e-12 | 3.5911e-07
1350 | feeder2_line78 | 2 | 266.4 | 0.08978 | 0.089785 | 0.033701 | 0.033703
1350 | feeder2_line78 | 3 | 266.4 | 8.4593e-12 | 9.5668e-07 | 3.1754e-12 | 3.5911e-07
1350 | feeder2_line79 | 1 | 354.6 | 3.1975 | 3.1971 | 0.90173 | 0.90161
1350 | feeder2_line79 | 2 | 354.6 | 18.7719 | 18.7714 | 5.2938 | 5.2937
1350 | feeder2_line79 | 3 | 354.6 | 15.0837 | 15.0834 | 4.2537 | 4.2536
1350 | feeder2_line80 | 1 | 354.6 | 85.8775 | 85.8726 | 24.2181 | 24.2168
1350 | feeder2_line80 | 2 | 354.6 | 88.6554 | 88.6636 | 25.0015 | 25.0038
1350 | feeder2_line80 | 3 | 354.6 | 89.2419 | 89.2365 | 25.1669 | 25.1654
1350 | feeder2_line81 | 1 | 354.6 | 85.8774 | 85.8726 | 24.2181 | 24.2168
1350 | feeder2_line81 | 2 | 354.6 | 88.6554 | 88.6636 | 25.0015 | 25.0038
1350 | feeder2_line81 | 3 | 354.6 | 90.1711 | 90.1658 | 25.429 | 25.4275
1350 | feeder2_line82 | 1 | 354.6 | 4.6628e-12 | 7.3699e-07 | 1.3149e-12 | 2.0784e-07
1350 | feeder2_line82 | 2 | 354.6 | 4.6628e-12 | 7.3572e-07 | 1.3149e-12 | 2.0748e-07
1350 | feeder2_line82 | 3 | 354.6 | 0.92956 | 0.92956 | 0.26214 | 0.26214
1350 | feeder2_line83 | 1 | 354.6 | 85.8776 | 85.8726 | 24.2182 | 24.2168
1350 | feeder2_line83 | 2 | 354.6 | 88.7703 | 88.7783 | 25.0339 | 25.0362
1350 | feeder2_line83 | 3 | 354.6 | 90.1713 | 90.1658 | 25.429 | 25.4275
1350 | feeder2_line84 | 1 | 354.6 | 1.3053e-11 | 1.3028e-06 | 3.681e-12 | 3.674e-07
1350 | feeder2_line84 | 2 | 354.6 | 0.11617 | 0.1162 | 0.03276 | 0.032769
1350 | feeder2_line84 | 3 | 354.6 | 2.526e-11 | 1.3026e-06 | 7.1237e-12 | 3.6734e-07
1350 | feeder2_line85 | 1 | 99 | 1.546 | 1.546 | 1.5616 | 1.5616
1350 | feeder2_line85 | 2 | 99 | 5.0276e-08 | 4.6415e-07 | 5.0783e-08 | 4.6884e-07
1350 | feeder2_line85 | 3 | 99 | 4.9988e-08 | 4.6498e-07 | 5.0493e-08 | 4.6967e-07
1350 | feeder2_line86 | 1 | 354.6 | 87.4177 | 87.4126 | 24.6525 | 24.651
1350 | feeder2_line86 | 2 | 354.6 | 88.7704 | 88.7783 | 25.034 | 25.0362
1350 | feeder2_line86 | 3 | 354.6 | 90.1714 | 90.1658 | 25.429 | 25.4275
1350 | feeder2_line87 | 1 | 354.6 | 87.4179 | 87.4126 | 24.6525 | 24.651
1350 | feeder2_line87 | 2 | 354.6 | 91.1408 | 91.1486 | 25.7024 | 25.7046
1350 | feeder2_line87 | 3 | 354.6 | 92.2225 | 92.2166 | 26.0075 | 26.0058
1350 | feeder2_line88 | 1 | 354.6 | 0.00011437 | 3.3778e-06 | 3.2254e-05 | 9.5257e-07
1350 | feeder2_line88 | 2 | 354.6 | 2.3705 | 2.3705 | 0.6685 | 0.6685
1350 | feeder2_line88 | 3 | 354.6 | 2.0555 | 2.0554 | 0.57967 | 0.57964
1350 | feeder2_line89 | 1 | 354.6 | 87.4156 | 87.4126 | 24.6519 | 24.651
1350 | feeder2_line89 | 2 | 354.6 | 93.639 | 93.6491 | 26.4069 | 26.4098
1350 | feeder2_line89 | 3 | 354.6 | 92.2202 | 92.2166 | 26.0068 | 26.0058
1350 | feeder2_line90 | 1 | 354.6 | 0.00072721 | 2.041e-06 | 0.00020508 | 5.7559e-07
1350 | feeder2_line90 | 2 | 354.6 | 2.5536 | 2.5541 | 0.72014 | 0.72027
1350 | feeder2_line90 | 3 | 354.6 | 0.00072758 | 2.0392e-06 | 0.00020518 | 5.7507e-07
1350 | feeder2_line91 | 1 | 354.6 | 87.4155 | 87.4126 | 24.6519 | 24.651
1350 | feeder2_line91 | 2 | 354.6 | 93.6389 | 93.6491 | 26.4069 | 26.4098
1350 | feeder2_line91 | 3 | 354.6 | 95.205 | 95.2016 | 26.8486 | 26.8476
1350 | feeder2_line92 | 1 | 354.6 | 1.0839e-11 | 1.0287e-06 | 3.0566e-12 | 2.9011e-07
1350 | feeder2_line92 | 2 | 354.6 | 1.0839e-11 | 1.0269e-06 | 3.0566e-12 | 2.896e-07
1350 | feeder2_line92 | 3 | 354.6 | 2.9865 | 2.9865 | 0.84223 | 0.84223
1350 | feeder2_line93 | 1 | 99 | 2.5032e-08 | 3.4341e-07 | 2.5285e-08 | 3.4688e-07
1350 | feeder2_line93 | 2 | 99 | 0.11609 | 0.11613 | 0.11727 | 0.1173
1350 | feeder2_line93 | 3 | 99 | 2.5012e-08 | 3.4338e-07 | 2.5264e-08 | 3.4685e-07
1350 | feeder2_line94 | 1 | 354.6 | 2.5031e-06 | 1.6718e-06 | 7.059e-07 | 4.7146e-07
1350 | feeder2_line94 | 2 | 354.6 | 2.446 | 2.446 | 0.68979 | 0.6898
1350 | feeder2_line94 | 3 | 354.6 | 2.501e-06 | 1.6717e-06 | 7.0529e-07 | 4.7143e-07
1350 | feeder2_line95 | 1 | 99 | 3.583e-06 | 2.6194e-06 | 3.6192e-06 | 2.6458e-06
1350 | feeder2_line95 | 2 | 99 | 2.3704 | 2.3705 | 2.3943 | 2.3945
1350 | feeder2_line95 | 3 | 99 | 3.5807e-06 | 2.619e-06 | 3.6168e-06 | 2.6455e-06
1350 | feeder2_line96 | 1 | 354.6 | 0.00012157 | 6.2433e-07 | 3.4282e-05 | 1.7607e-07
1350 | feeder2_line96 | 2 | 354.6 | 0.00012131 | 6.2346e-07 | 3.4209e-05 | 1.7582e-07
1350 | feeder2_line96 | 3 | 354.6 | 2.0555 | 2.0554 | 0.57966 | 0.57964
1350 | feeder2_line97 | 1 | 354.6 | 87.88 | 87.8769 | 24.7829 | 24.782
1350 | feeder2_line97 | 2 | 354.6 | 93.639 | 93.6491 | 26.4069 | 26.4098
1350 | feeder2_line97 | 3 | 354.6 | 95.2052 | 95.2016 | 26.8486 | 26.8476
1350 | feeder2_line98 | 1 | 354.6 | 0.46895 | 0.46719 | 0.13225 | 0.13175
1350 | feeder2_line98 | 2 | 354.6 | 0.0017035 | 6.222e-07 | 0.00048041 | 1.7546e-07
1350 | feeder2_line98 | 3 | 354.6 | 0.0017126 | 6.24e-07 | 0.00048298 | 1.7597e-07
1350 | feeder2_line99 | 1 | 99 | 2.5017e-08 | 4.4889e-07 | 2.527e-08 | 4.5342e-07
1350 | feeder2_line99 | 2 | 99 | 2.5141e-08 | 4.4802e-07 | 2.5395e-08 | 4.5254e-07
1350 | feeder2_line99 | 3 | 99 | 2.0554 | 2.0554 | 2.0762 | 2.0762
1350 | feeder2_line100 | 1 | 99 | 0.46725 | 0.46719 | 0.47197 | 0.47191
1350 | feeder2_line100 | 2 | 99 | 2.5163e-08 | 6.1542e-07 | 2.5417e-08 | 6.2163e-07
1350 | feeder2_line100 | 3 | 99 | 2.5017e-08 | 6.1656e-07 | 2.5269e-08 | 6.2279e-07
1350 | feeder2_line101 | 1 | 354.6 | 2.4471 | 2.4467 | 0.69009 | 0.68999
1350 | feeder2_line101 | 2 | 354.6 | 18.7719 | 18.7714 | 5.2938 | 5.2937
1350 | feeder2_line101 | 3 | 354.6 | 15.0837 | 15.0834 | 4.2537 | 4.2536
1350 | feeder2_line102 | 1 | 99 | 0.77294 | 0.77291 | 0.78075 | 0.78071
1350 | feeder2_line102 | 2 | 99 | 2.3353e-06 | 8.7923e-07 | 2.3589e-06 | 8.8811e-07
1350 | feeder2_line102 | 3 | 99 | 2.3449e-06 | 8.8079e-07 | 2.3686e-06 | 8.8968e-07
1350 | feeder2_line103 | 1 | 99 | 5.5124e-07 | 8.0657e-07 | 5.5681e-07 | 8.1472e-07
1350 | feeder2_line103 | 2 | 99 | 0.096548 | 0.096553 | 0.097523 | 0.097528
1350 | feeder2_line103 | 3 | 99 | 5.5093e-07 | 8.0614e-07 | 5.565e-07 | 8.1429e-07
1350 | feeder2_line104 | 1 | 354.6 | 2.447 | 2.4467 | 0.69007 | 0.68999
1350 | feeder2_line104 | 2 | 354.6 | 18.6784 | 18.678 | 5.2675 | 5.2674
1350 | feeder2_line104 | 3 | 354.6 | 15.0836 | 15.0834 | 4.2537 | 4.2536
1350 | feeder2_line105 | 1 | 99 | 2.5565e-06 | 7.4217e-07 | 2.5823e-06 | 7.4967e-07
1350 | feeder2_line105 | 2 | 99 | 2.5475e-06 | 7.4038e-07 | 2.5732e-06 | 7.4786e-07
1350 | feeder2_line105 | 3 | 99 | 1.4331 | 1.4331 | 1.4476 | 1.4476
1350 | feeder2_line106 | 1 | 354.6 | 2.4469 | 2.4467 | 0.69006 | 0.68999
1350 | feeder2_line106 | 2 | 354.6 | 18.6784 | 18.678 | 5.2674 | 5.2674
1350 | feeder2_line106 | 3 | 354.6 | 13.6513 | 13.6511 | 3.8498 | 3.8497
1350 | feeder2_line107 | 1 | 99 | 3.2558e-07 | 9.0448e-07 | 3.2886e-07 | 9.1362e-07
1350 | feeder2_line107 | 2 | 99 | 2.2929 | 2.293 | 2.3161 | 2.3161
1350 | feeder2_line107 | 3 | 99 | 3.2538e-07 | 9.0381e-07 | 3.2867e-07 | 9.1294e-07
1350 | feeder2_line108 | 1 | 354.6 | 2.4469 | 2.4467 | 0.69006 | 0.68999
1350 | feeder2_line108 | 2 | 354.6 | 16.3889 | 16.3886 | 4.6218 | 4.6217
1350 | feeder2_line108 | 3 | 354.6 | 13.6512 | 13.6511 | 3.8498 | 3.8497
1350 | feeder2_line109 | 1 | 354.6 | 89.0917 | 89.0874 | 25.1246 | 25.1233
1350 | feeder2_line109 | 2 | 354.6 | 93.6403 | 93.6491 | 26.4073 | 26.4098
1350 | feeder2_line109 | 3 | 354.6 | 95.2064 | 95.2016 | 26.849 | 26.8476
1350 | feeder2_line110 | 1 | 99 | 1.6029 | 1.6023 | 1.6191 | 1.6184
1350 | feeder2_line110 | 2 | 99 | 0.00080561 | 9.1121e-07 | 0.00081375 | 9.2042e-07
1350 | feeder2_line110 | 3 | 99 | 0.00080821 | 9.1284e-07 | 0.00081638 | 9.2206e-07
1350 | feeder2_line111 | 1 | 99 | 2.5012e-08 | 3.8337e-07 | 2.5265e-08 | 3.8724e-07
1350 | feeder2_line111 | 2 | 99 | 1.3499 | 1.35 | 1.3636 | 1.3636
1350 | feeder2_line111 | 3 | 99 | 2.4999e-08 | 3.8333e-07 | 2.5252e-08 | 3.872e-07
1350 | feeder2_line112 | 1 | 99 | 3.2585e-07 | 9.2128e-07 | 3.2914e-07 | 9.3058e-07
1350 | feeder2_line112 | 2 | 99 | 1.0205 | 1.0205 | 1.0308 | 1.0309
1350 | feeder2_line112 | 3 | 99 | 3.2579e-07 | 9.2116e-07 | 3.2908e-07 | 9.3047e-07
1350 | feeder2_line113 | 1 | 99 | 1.5338 | 1.5338 | 1.5493 | 1.5493
1350 | feeder2_line113 | 2 | 99 | 3.2588e-07 | 9.0772e-07 | 3.2917e-07 | 9.1689e-07
1350 | feeder2_line113 | 3 | 99 | 3.262e-07 | 9.0943e-07 | 3.295e-07 | 9.1862e-07
1350 | feeder2_line114 | 1 | 99 | 0.096354 | 0.096352 | 0.097327 | 0.097325
1350 | feeder2_line114 | 2 | 99 | 2.5132e-08 | 4.372e-07 | 2.5386e-08 | 4.4162e-07
1350 | feeder2_line114 | 3 | 99 | 2.4981e-08 | 4.3798e-07 | 2.5234e-08 | 4.4241e-07
1350 | feeder2_line115 | 1 | 99 | 2.4958e-08 | 5.6448e-07 | 2.521e-08 | 5.7018e-07
1350 | feeder2_line115 | 2 | 99 | 11.1262 | 11.126 | 11.2386 | 11.2384
1350 | feeder2_line115 | 3 | 99 | 2.4974e-08 | 5.6395e-07 | 2.5226e-08 | 5.6965e-07
1350 | feeder2_line116 | 1 | 354.6 | 2.447 | 2.4467 | 0.69006 | 0.68999
1350 | feeder2_line116 | 2 | 354.6 | 5.5511 | 5.5509 | 1.5655 | 1.5654
1350 | feeder2_line116 | 3 | 354.6 | 13.6513 | 13.6511 | 3.8498 | 3.8497
1350 | feeder2_line117 | 1 | 99 | 5.014e-08 | 6.4578e-07 | 5.0646e-08 | 6.5231e-07
1350 | feeder2_line117 | 2 | 99 | 0.95848 | 0.95854 | 0.96816 | 0.96822
1350 | feeder2_line117 | 3 | 99 | 5.0074e-08 | 6.4592e-07 | 5.0579e-08 | 6.5244e-07
1350 | feeder2_line118 | 1 | 354.6 | 89.0917 | 89.0874 | 25.1246 | 25.1233
1350 | feeder2_line118 | 2 | 354.6 | 94.2963 | 94.3052 | 26.5923 | 26.5948
1350 | feeder2_line118 | 3 | 354.6 | 95.2064 | 95.2016 | 26.849 | 26.8476
1350 | feeder2_line119 | 1 | 99 | 2.495e-08 | 6.0741e-07 | 2.5203e-08 | 6.1355e-07
1350 | feeder2_line119 | 2 | 99 | 2.5138e-08 | 6.0568e-07 | 2.5392e-08 | 6.118e-07
1350 | feeder2_line119 | 3 | 99 | 0.546 | 0.54599 | 0.55151 | 0.5515
1350 | feeder2_line120 | 1 | 354.6 | 2.447 | 2.4467 | 0.69006 | 0.68999
1350 | feeder2_line120 | 2 | 354.6 | 5.5511 | 5.5509 | 1.5654 | 1.5654
1350 | feeder2_line120 | 3 | 354.6 | 13.1064 | 13.1063 | 3.6961 | 3.6961
1350 | feeder2_line121 | 1 | 99 | 3.2557e-07 | 9.4062e-07 | 3.2886e-07 | 9.5012e-07
1350 | feeder2_line121 | 2 | 99 | 2.0047 | 2.0047 | 2.0249 | 2.0249
1350 | feeder2_line121 | 3 | 99 | 3.2527e-07 | 9.3941e-07 | 3.2855e-07 | 9.4889e-07
1350 | feeder2_line122 | 1 | 354.6 | 2.4469 | 2.4467 | 0.69005 | 0.68999
1350 | feeder2_line122 | 2 | 354.6 | 3.7706 | 3.7704 | 1.0633 | 1.0633
1350 | feeder2_line122 | 3 | 354.6 | 13.1064 | 13.1063 | 3.6961 | 3.6961
1350 | feeder2_line123 | 1 | 99 | 5.7633e-07 | 9.7472e-07 | 5.8215e-07 | 9.8457e-07
1350 | feeder2_line123 | 2 | 99 | 5.7463e-07 | 9.7188e-07 | 5.8044e-07 | 9.817e-07
1350 | feeder2_line123 | 3 | 99 | 0.10834 | 0.10834 | 0.10943 | 0.10943
1350 | feeder2_line124 | 1 | 354.6 | 2.4469 | 2.4467 | 0.69004 | 0.68999
1350 | feeder2_line124 | 2 | 354.6 | 3.7706 | 3.7704 | 1.0633 | 1.0633
1350 | feeder2_line124 | 3 | 354.6 | 13.0008 | 13.0007 | 3.6663 | 3.6663
1350 | feeder2_line125 | 1 | 99 | 5.7633e-07 | 9.061e-07 | 5.8215e-07 | 9.1525e-07
1350 | feeder2_line125 | 2 | 99 | 5.7463e-07 | 9.0347e-07 | 5.8043e-07 | 9.1259e-07
1350 | feeder2_line125 | 3 | 99 | 0.46845 | 0.46846 | 0.47319 | 0.47319
1350 | feeder2_line126 | 1 | 354.6 | 2.447 | 2.4467 | 0.69008 | 0.68999
1350 | feeder2_line126 | 2 | 354.6 | 3.7707 | 3.7704 | 1.0634 | 1.0633
1350 | feeder2_line126 | 3 | 354.6 | 12.5418 | 12.5415 | 3.5369 | 3.5368
1350 | feeder2_line127 | 1 | 99 | 5.7632e-07 | 1.0847e-06 | 5.8214e-07 | 1.0957e-06
1350 | feeder2_line127 | 2 | 99 | 5.7462e-07 | 1.0816e-06 | 5.8042e-07 | 1.0925e-06
1350 | feeder2_line127 | 3 | 99 | 10.1211 | 10.1212 | 10.2233 | 10.2234
1350 | feeder2_line128 | 1 | 354.6 | 2.447 | 2.4467 | 0.69006 | 0.68999
1350 | feeder2_line128 | 2 | 354.6 | 3.7707 | 3.7704 | 1.0634 | 1.0633
1350 | feeder2_line128 | 3 | 354.6 | 2.532 | 2.5317 | 0.71404 | 0.71397
1350 | feeder2_line129 | 1 | 99 | 5.514e-07 | 8.7958e-07 | 5.5697e-07 | 8.8846e-07
1350 | feeder2_line129 | 2 | 99 | 3.7704 | 3.7704 | 3.8085 | 3.8085
1350 | feeder2_line129 | 3 | 99 | 5.5044e-07 | 8.7823e-07 | 5.56e-07 | 8.871e-07
1350 | feeder2_line130 | 1 | 354.6 | 2.447 | 2.4467 | 0.69007 | 0.68999
1350 | feeder2_line130 | 2 | 354.6 | 0.00030886 | 4.6415e-06 | 8.7101e-05 | 1.3089e-06
1350 | feeder2_line130 | 3 | 354.6 | 2.532 | 2.5317 | 0.71405 | 0.71397
1350 | feeder2_line131 | 1 | 99 | 5.7633e-07 | 9.7487e-07 | 5.8215e-07 | 9.8471e-07
1350 | feeder2_line131 | 2 | 99 | 5.7463e-07 | 9.7203e-07 | 5.8043e-07 | 9.8185e-07
1350 | feeder2_line131 | 3 | 99 | 1.3195 | 1.3196 | 1.3329 | 1.3329
1350 | feeder2_line132 | 1 | 354.6 | 2.4468 | 2.4467 | 0.69002 | 0.68999
1350 | feeder2_line132 | 2 | 354.6 | 0.00012568 | 2.9184e-06 | 3.5443e-05 | 8.23e-07
1350 | feeder2_line132 | 3 | 354.6 | 1.5445 | 1.5444 | 0.43556 | 0.43554
1350 | feeder2_line133 | 1 | 99 | 2.4467 | 2.4467 | 2.4714 | 2.4714
1350 | feeder2_line133 | 2 | 99 | 2.9987e-07 | 9.7979e-07 | 3.029e-07 | 9.8969e-07
1350 | feeder2_line133 | 3 | 99 | 3.0021e-07 | 9.8113e-07 | 3.0324e-07 | 9.9104e-07
1350 | feeder2_line134 | 1 | 354.6 | 9.0199e-12 | 1.7918e-06 | 2.5437e-12 | 5.0529e-07
1350 | feeder2_line134 | 2 | 354.6 | 6.3736e-12 | 1.787e-06 | 1.7974e-12 | 5.0396e-07
1350 | feeder2_line134 | 3 | 354.6 | 1.5444 | 1.5444 | 0.43554 | 0.43554
1350 | feeder2_line135 | 1 | 99 | 3.2185 | 3.2184 | 3.251 | 3.2509
1350 | feeder2_line135 | 2 | 99 | 5.0408e-08 | 5.8772e-07 | 5.0917e-08 | 5.9366e-07
1350 | feeder2_line135 | 3 | 99 | 5.0097e-08 | 5.8888e-07 | 5.0603e-08 | 5.9483e-07
1350 | feeder2_line136 | 1 | 354.6 | 92.1514 | 92.147 | 25.9874 | 25.9862
1350 | feeder2_line136 | 2 | 354.6 | 94.2963 | 94.3052 | 26.5923 | 26.5948
1350 | feeder2_line136 | 3 | 354.6 | 95.2064 | 95.2016 | 26.849 | 26.8476
1350 | feeder2_line137 | 1 | 99 | 1.1923 | 1.1923 | 1.2044 | 1.2043
1350 | feeder2_line137 | 2 | 99 | 8.5295e-07 | 1.5832e-06 | 8.6156e-07 | 1.5992e-06
1350 | feeder2_line137 | 3 | 99 | 8.5475e-07 | 1.5863e-06 | 8.6339e-07 | 1.6023e-06
1350 | feeder2_line138 | 1 | 354.6 | 92.8928 | 92.8884 | 26.1965 | 26.1953
1350 | feeder2_line138 | 2 | 354.6 | 94.2964 | 94.3052 | 26.5923 | 26.5948
1350 | feeder2_line138 | 3 | 354.6 | 95.2064 | 95.2016 | 26.849 | 26.8476
1350 | feeder2_line139 | 1 | 99 | 5.02e-08 | 4.9417e-07 | 5.0707e-08 | 4.9916e-07
1350 | feeder2_line139 | 2 | 99 | 5.0424e-08 | 4.9336e-07 | 5.0934e-08 | 4.9834e-07
1350 | feeder2_line139 | 3 | 99 | 0.13662 | 0.13649 | 0.138 | 0.13787
1350 | feeder2_line140 | 1 | 354.6 | 92.8929 | 92.8884 | 26.1965 | 26.1953
1350 | feeder2_line140 | 2 | 354.6 | 94.2965 | 94.3052 | 26.5923 | 26.5948
1350 | feeder2_line140 | 3 | 354.6 | 95.3368 | 95.3316 | 26.8857 | 26.8843
1350 | feeder2_line141 | 1 | 99 | 2.5396e-06 | 4.8888e-07 | 2.5652e-06 | 4.9382e-07
1350 | feeder2_line141 | 2 | 99 | 1.5573 | 1.5573 | 1.573 | 1.573
1350 | feeder2_line141 | 3 | 99 | 2.5413e-06 | 4.8907e-07 | 2.5669e-06 | 4.9401e-07
1350 | feeder2_line142 | 1 | 354.6 | 92.8927 | 92.8884 | 26.1965 | 26.1953
1350 | feeder2_line142 | 2 | 354.6 | 95.5944 | 95.6033 | 26.9584 | 26.9609
1350 | feeder2_line142 | 3 | 354.6 | 95.3366 | 95.3316 | 26.8857 | 26.8843
1350 | feeder2_line143 | 1 | 99 | 8.5484e-07 | 1.7373e-06 | 8.6348e-07 | 1.7549e-06
1350 | feeder2_line143 | 2 | 99 | 2.2942 | 2.2943 | 2.3174 | 2.3175
1350 | feeder2_line143 | 3 | 99 | 8.5518e-07 | 1.738e-06 | 8.6382e-07 | 1.7555e-06
1350 | feeder2_line144 | 1 | 354.6 | 92.8925 | 92.8884 | 26.1964 | 26.1953
1350 | feeder2_line144 | 2 | 354.6 | 97.8876 | 97.8967 | 27.6051 | 27.6077
1350 | feeder2_line144 | 3 | 354.6 | 95.3365 | 95.3316 | 26.8856 | 26.8843
1350 | feeder2_line145 | 1 | 99 | 2.5113e-08 | 4.8718e-07 | 2.5367e-08 | 4.921e-07
1350 | feeder2_line145 | 2 | 99 | 0.92925 | 0.92927 | 0.93864 | 0.93866
1350 | feeder2_line145 | 3 | 99 | 2.5067e-08 | 4.8736e-07 | 2.532e-08 | 4.9228e-07
1350 | feeder2_line146 | 1 | 354.6 | 92.8924 | 92.8884 | 26.1964 | 26.1953
1350 | feeder2_line146 | 2 | 354.6 | 98.8161 | 98.8255 | 27.8669 | 27.8696
1350 | feeder2_line146 | 3 | 354.6 | 95.3363 | 95.3316 | 26.8856 | 26.8843
1350 | feeder2_line147 | 1 | 99 | 0.1075 | 0.10749 | 0.10858 | 0.10858
1350 | feeder2_line147 | 2 | 99 | 1.1549e-06 | 2.2436e-06 | 1.1665e-06 | 2.2663e-06
1350 | feeder2_line147 | 3 | 99 | 1.1572e-06 | 2.2481e-06 | 1.1689e-06 | 2.2708e-06
1350 | feeder2_line148 | 1 | 99 | 1.694 | 1.694 | 1.7111 | 1.7111
1350 | feeder2_line148 | 2 | 99 | 6.0265e-07 | 1.5034e-06 | 6.0874e-07 | 1.5186e-06
1350 | feeder2_line148 | 3 | 99 | 6.0366e-07 | 1.5064e-06 | 6.0976e-07 | 1.5216e-06
1350 | feeder2_line149 | 1 | 354.6 | 94.6923 | 94.6881 | 26.704 | 26.7028
1350 | feeder2_line149 | 2 | 354.6 | 98.8163 | 98.8255 | 27.867 | 27.8696
1350 | feeder2_line149 | 3 | 354.6 | 95.3365 | 95.3316 | 26.8856 | 26.8843
1350 | feeder2_line150 | 1 | 354.6 | 94.6924 | 94.6881 | 26.704 | 26.7028
1350 | feeder2_line150 | 2 | 354.6 | 99.0001 | 99.0092 | 27.9188 | 27.9214
1350 | feeder2_line150 | 3 | 354.6 | 95.3366 | 95.3316 | 26.8857 | 26.8843
1350 | feeder2_line151 | 1 | 99 | 9.8157e-06 | 1.7889e-06 | 9.9149e-06 | 1.807e-06
1350 | feeder2_line151 | 2 | 99 | 0.18546 | 0.18549 | 0.18734 | 0.18736
1350 | feeder2_line151 | 3 | 99 | 9.8257e-06 | 1.7897e-06 | 9.925e-06 | 1.8077e-06
1350 | feeder2_line152 | 1 | 354.6 | 1.8811e-11 | 1.1924e-06 | 5.3049e-12 | 3.3628e-07
1350 | feeder2_line152 | 2 | 354.6 | 1.8811e-11 | 1.1908e-06 | 5.3049e-12 | 3.3583e-07
1350 | feeder2_line152 | 3 | 354.6 | 1.1886 | 1.1886 | 0.33521 | 0.3352
1350 | feeder2_line153 | 1 | 99 | 1.9984 | 1.9984 | 2.0186 | 2.0186
1350 | feeder2_line153 | 2 | 99 | 5.0488e-08 | 5.9573e-07 | 5.0998e-08 | 6.0175e-07
1350 | feeder2_line153 | 3 | 99 | 5.0192e-08 | 5.9687e-07 | 5.0699e-08 | 6.0289e-07
1350 | feeder2_line154 | 1 | 99 | 5.7892e-07 | 8.878e-07 | 5.8477e-07 | 8.9677e-07
1350 | feeder2_line154 | 2 | 99 | 5.7805e-07 | 8.8648e-07 | 5.8389e-07 | 8.9543e-07
1350 | feeder2_line154 | 3 | 99 | 2.6241 | 2.6241 | 2.6506 | 2.6506
1350 | feeder2_line155 | 1 | 99 | 96.6901 | 96.6859 | 97.6667 | 97.6625
1350 | feeder2_line155 | 2 | 99 | 99 | 99.0092 | 100 | 100.0093
1350 | feeder2_line155 | 3 | 99 | 98.6963 | 98.6913 | 99.6932 | 99.6882
1350 | feeder2_line156 | 1 | 99 | 6.038e-07 | 1.1682e-06 | 6.099e-07 | 1.18e-06
1350 | feeder2_line156 | 2 | 99 | 0.096265 | 0.096272 | 0.097237 | 0.097244
1350 | feeder2_line156 | 3 | 99 | 6.0399e-07 | 1.1686e-06 | 6.1009e-07 | 1.1804e-06
1350 | feeder2_line157 | 1 | 99 | 2.5122e-08 | 2.536e-07 | 2.5376e-08 | 2.5617e-07
1350 | feeder2_line157 | 2 | 99 | 0.089363 | 0.08937 | 0.090266 | 0.090273
1350 | feeder2_line157 | 3 | 99 | 2.5085e-08 | 2.537e-07 | 2.5338e-08 | 2.5627e-07
1380 | feeder2_line1 | 1 | 354.6 | 59.6332 | 59.6358 | 16.817 | 16.8178
1380 | feeder2_line1 | 2 | 354.6 | 34.9461 | 34.9586 | 9.8551 | 9.8586
1380 | feeder2_line1 | 3 | 354.6 | 49.4974 | 49.4867 | 13.9587 | 13.9556
1380 | feeder2_line2 | 1 | 354.6 | 59.9642 | 59.9666 | 16.9104 | 16.9111
1380 | feeder2_line2 | 2 | 354.6 | 34.9463 | 34.9586 | 9.8551 | 9.8586
1380 | feeder2_line2 | 3 | 354.6 | 49.4976 | 49.4867 | 13.9587 | 13.9556
1380 | feeder2_line3 | 1 | 80.1 | 0.33974 | 0.33974 | 0.42415 | 0.42414
1380 | feeder2_line3 | 2 | 80.1 | 5.7095e-07 | 1.0551e-06 | 7.128e-07 | 1.3173e-06
1380 | feeder2_line3 | 3 | 80.1 | 5.7168e-07 | 1.0565e-06 | 7.1371e-07 | 1.3189e-06
1380 | feeder2_line4 | 1 | 354.6 | 59.9644 | 59.9666 | 16.9104 | 16.9111
1380 | feeder2_line4 | 2 | 354.6 | 35.2059 | 35.2181 | 9.9283 | 9.9318
1380 | feeder2_line4 | 3 | 354.6 | 49.4977 | 49.4867 | 13.9587 | 13.9556
1380 | feeder2_line5 | 1 | 80.1 | 5.7217e-07 | 9.9837e-07 | 7.1432e-07 | 1.2464e-06
1380 | feeder2_line5 | 2 | 80.1 | 0.27921 | 0.27921 | 0.34857 | 0.34858
1380 | feeder2_line5 | 3 | 80.1 | 5.7171e-07 | 9.9757e-07 | 7.1374e-07 | 1.2454e-06
1380 | feeder2_line6 | 1 | 80.1 | 5.722e-07 | 1.1746e-06 | 7.1436e-07 | 1.4664e-06
1380 | feeder2_line6 | 2 | 80.1 | 5.7093e-07 | 1.172e-06 | 7.1278e-07 | 1.4632e-06
1380 | feeder2_line6 | 3 | 80.1 | 11.4277 | 11.4278 | 14.2668 | 14.2669
1380 | feeder2_line7 | 1 | 354.6 | 59.9645 | 59.9666 | 16.9105 | 16.9111
1380 | feeder2_line7 | 2 | 354.6 | 35.206 | 35.2181 | 9.9284 | 9.9318
1380 | feeder2_line7 | 3 | 354.6 | 60.6845 | 60.6733 | 17.1135 | 17.1104
1380 | feeder2_line8 | 1 | 80.1 | 0.072571 | 0.072572 | 0.090601 | 0.090601
1380 | feeder2_line8 | 2 | 80.1 | 5.7095e-07 | 1.1301e-06 | 7.128e-07 | 1.4108e-06
1380 | feeder2_line8 | 3 | 80.1 | 5.7194e-07 | 1.132e-06 | 7.1404e-07 | 1.4132e-06
1380 | feeder2_line9 | 1 | 354.6 | 60.0361 | 60.0382 | 16.9307 | 16.9313
1380 | feeder2_line9 | 2 | 354.6 | 35.2061 | 35.2181 | 9.9284 | 9.9318
1380 | feeder2_line9 | 3 | 354.6 | 60.6845 | 60.6733 | 17.1135 | 17.1104
1380 | feeder2_line10 | 1 | 80.1 | 8.4624e-07 | 1.496e-06 | 1.0565e-06 | 1.8676e-06
1380 | feeder2_line10 | 2 | 80.1 | 0.072854 | 0.072855 | 0.090953 | 0.090955
1380 | feeder2_line10 | 3 | 80.1 | 8.4555e-07 | 1.4947e-06 | 1.0556e-06 | 1.8661e-06
1380 | feeder2_line11 | 1 | 354.6 | 60.0361 | 60.0382 | 16.9307 | 16.9313
1380 | feeder2_line11 | 2 | 354.6 | 35.2753 | 35.2873 | 9.9479 | 9.9513
1380 | feeder2_line11 | 3 | 354.6 | 60.6845 | 60.6733 | 17.1135 | 17.1104
1380 | feeder2_line12 | 1 | 80.1 | 5.4769e-07 | 9.9243e-07 | 6.8375e-07 | 1.239e-06
1380 | feeder2_line12 | 2 | 80.1 | 5.4597e-07 | 9.8975e-07 | 6.8161e-07 | 1.2356e-06
1380 | feeder2_line12 | 3 | 80.1 | 3.2347 | 3.2347 | 4.0383 | 4.0383
1380 | feeder2_line13 | 1 | 354.6 | 60.0361 | 60.0382 | 16.9307 | 16.9313
1380 | feeder2_line13 | 2 | 354.6 | 35.2753 | 35.2873 | 9.9479 | 9.9513
1380 | feeder2_line13 | 3 | 354.6 | 63.8682 | 63.857 | 18.0113 | 18.0082
1380 | feeder2_line14 | 1 | 80.1 | 1.5992 | 1.5991 | 1.9965 | 1.9964
1380 | feeder2_line14 | 2 | 80.1 | 2.9796e-07 | 6.4539e-07 | 3.7199e-07 | 8.0574e-07
1380 | feeder2_line14 | 3 | 80.1 | 2.9845e-07 | 6.467e-07 | 3.726e-07 | 8.0737e-07
1380 | feeder2_line15 | 1 | 354.6 | 60.83 | 60.8322 | 17.1545 | 17.1552
1380 | feeder2_line15 | 2 | 354.6 | 35.2753 | 35.2873 | 9.9479 | 9.9513
1380 | feeder2_line15 | 3 | 354.6 | 63.8682 | 63.857 | 18.0113 | 18.0082
1380 | feeder2_line16 | 1 | 80.1 | 5.7267e-07 | 1.0317e-06 | 7.1495e-07 | 1.288e-06
1380 | feeder2_line16 | 2 | 80.1 | 0.25402 | 0.25402 | 0.31713 | 0.31713
1380 | feeder2_line16 | 3 | 80.1 | 5.7223e-07 | 1.0309e-06 | 7.144e-07 | 1.287e-06
1380 | feeder2_line17 | 1 | 354.6 | 60.8301 | 60.8322 | 17.1546 | 17.1552
1380 | feeder2_line17 | 2 | 354.6 | 35.51 | 35.5219 | 10.0141 | 10.0175
1380 | feeder2_line17 | 3 | 354.6 | 63.8683 | 63.857 | 18.0114 | 18.0082
1380 | feeder2_line18 | 1 | 80.1 | 5.483e-07 | 7.3909e-07 | 6.8452e-07 | 9.2271e-07
1380 | feeder2_line18 | 2 | 80.1 | 5.4587e-07 | 7.3625e-07 | 6.8149e-07 | 9.1917e-07
1380 | feeder2_line18 | 3 | 80.1 | 2.0073 | 2.0073 | 2.506 | 2.506
1380 | feeder2_line19 | 1 | 354.6 | 60.8301 | 60.8322 | 17.1546 | 17.1552
1380 | feeder2_line19 | 2 | 354.6 | 35.51 | 35.522 | 10.0141 | 10.0175
1380 | feeder2_line19 | 3 | 354.6 | 65.5185 | 65.5073 | 18.4767 | 18.4736
1380 | feeder2_line20 | 1 | 99 | 5.4847e-07 | 8.8639e-07 | 5.5401e-07 | 8.9534e-07
1380 | feeder2_line20 | 2 | 99 | 5.4584e-07 | 8.8271e-07 | 5.5136e-07 | 8.9163e-07
1380 | feeder2_line20 | 3 | 99 | 0.35664 | 0.35661 | 0.36024 | 0.36022
1380 | feeder2_line21 | 1 | 354.6 | 60.8302 | 60.8322 | 17.1546 | 17.1552
1380 | feeder2_line21 | 2 | 354.6 | 35.5101 | 35.522 | 10.0141 | 10.0175
1380 | feeder2_line21 | 3 | 354.6 | 65.8719 | 65.8605 | 18.5764 | 18.5732
1380 | feeder2_line22 | 1 | 99 | 5.7341e-07 | 1.0163e-06 | 5.792e-07 | 1.0266e-06
1380 | feeder2_line22 | 2 | 99 | 0.094276 | 0.09428 | 0.095229 | 0.095232
1380 | feeder2_line22 | 3 | 99 | 5.7306e-07 | 1.0157e-06 | 5.7885e-07 | 1.026e-06
1380 | feeder2_line23 | 1 | 99 | 5.7341e-07 | 9.5136e-07 | 5.792e-07 | 9.6097e-07
1380 | feeder2_line23 | 2 | 99 | 5.7088e-07 | 9.4722e-07 | 5.7665e-07 | 9.5679e-07
1380 | feeder2_line23 | 3 | 99 | 3.5089 | 3.5088 | 3.5443 | 3.5442
1380 | feeder2_line24 | 1 | 354.6 | 60.8302 | 60.8322 | 17.1546 | 17.1552
1380 | feeder2_line24 | 2 | 354.6 | 35.5995 | 35.6112 | 10.0393 | 10.0427
1380 | feeder2_line24 | 3 | 354.6 | 68.121 | 68.1095 | 19.2107 | 19.2074
1380 | feeder2_line25 | 1 | 99 | 0.093752 | 0.093753 | 0.094699 | 0.0947
1380 | feeder2_line25 | 2 | 99 | 5.018e-08 | 6.8863e-07 | 5.0687e-08 | 6.9559e-07
1380 | feeder2_line25 | 3 | 99 | 4.9524e-08 | 6.9151e-07 | 5.0025e-08 | 6.985e-07
1380 | feeder2_line26 | 1 | 99 | 1.9051 | 1.9051 | 1.9244 | 1.9244
1380 | feeder2_line26 | 2 | 99 | 5.4578e-07 | 8.5318e-07 | 5.5129e-07 | 8.6179e-07
1380 | feeder2_line26 | 3 | 99 | 5.4853e-07 | 8.5674e-07 | 5.5407e-07 | 8.6539e-07
1380 | feeder2_line27 | 1 | 354.6 | 62.7956 | 62.7976 | 17.7089 | 17.7094
1380 | feeder2_line27 | 2 | 354.6 | 35.5995 | 35.6112 | 10.0393 | 10.0427
1380 | feeder2_line27 | 3 | 354.6 | 68.121 | 68.1095 | 19.2107 | 19.2074
1380 | feeder2_line28 | 1 | 99 | 2.5467e-06 | 7.1195e-07 | 2.5724e-06 | 7.1914e-07
1380 | feeder2_line28 | 2 | 99 | 0.4904 | 0.4904 | 0.49535 | 0.49535
1380 | feeder2_line28 | 3 | 99 | 2.5466e-06 | 7.1164e-07 | 2.5724e-06 | 7.1883e-07
1380 | feeder2_line29 | 1 | 354.6 | 62.7956 | 62.7976 | 17.7089 | 17.7094
1380 | feeder2_line29 | 2 | 354.6 | 36.0587 | 36.0704 | 10.1688 | 10.1721
1380 | feeder2_line29 | 3 | 354.6 | 68.121 | 68.1095 | 19.2107 | 19.2074
1380 | feeder2_line30 | 1 | 266.4 | 17.1204 | 17.1202 | 6.4266 | 6.4265
1380 | feeder2_line30 | 2 | 266.4 | 12.638 | 12.6375 | 4.744 | 4.7438
1380 | feeder2_line30 | 3 | 266.4 | 4.1426 | 4.1423 | 1.555 | 1.5549
1380 | feeder2_line31 | 1 | 354.6 | 79.2625 | 79.2642 | 22.3526 | 22.3531
1380 | feeder2_line31 | 2 | 354.6 | 48.0477 | 48.0587 | 13.5498 | 13.5529
1380 | feeder2_line31 | 3 | 354.6 | 72.1436 | 72.1318 | 20.3451 | 20.3417
1380 | feeder2_line32 | 1 | 354.6 | 79.2625 | 79.2642 | 22.3527 | 22.3531
1380 | feeder2_line32 | 2 | 354.6 | 49.9232 | 49.9342 | 14.0788 | 14.0818
1380 | feeder2_line32 | 3 | 354.6 | 72.1437 | 72.1318 | 20.3451 | 20.3417
1380 | feeder2_line33 | 1 | 99 | 4.9678e-08 | 6.8778e-07 | 5.018e-08 | 6.9472e-07
1380 | feeder2_line33 | 2 | 99 | 2.4039 | 2.4039 | 2.4282 | 2.4282
1380 | feeder2_line33 | 3 | 99 | 4.9473e-08 | 6.875e-07 | 4.9972e-08 | 6.9444e-07
1380 | feeder2_line34 | 1 | 354.6 | 79.2625 | 79.2642 | 22.3527 | 22.3531
1380 | feeder2_line34 | 2 | 354.6 | 49.9232 | 49.9342 | 14.0787 | 14.0818
1380 | feeder2_line34 | 3 | 354.6 | 73.575 | 73.563 | 20.7487 | 20.7454
1380 | feeder2_line35 | 1 | 99 | 2.9984e-07 | 7.6183e-07 | 3.0287e-07 | 7.6952e-07
1380 | feeder2_line35 | 2 | 99 | 2.9802e-07 | 7.5656e-07 | 3.0103e-07 | 7.642e-07
1380 | feeder2_line35 | 3 | 99 | 1.4354 | 1.4354 | 1.4499 | 1.4499
1380 | feeder2_line36 | 1 | 354.6 | 80.6857 | 80.6876 | 22.754 | 22.7545
1380 | feeder2_line36 | 2 | 354.6 | 49.9232 | 49.9342 | 14.0787 | 14.0818
1380 | feeder2_line36 | 3 | 354.6 | 73.5749 | 73.563 | 20.7487 | 20.7454
1380 | feeder2_line37 | 1 | 99 | 2.5913 | 2.5916 | 2.6175 | 2.6178
1380 | feeder2_line37 | 2 | 99 | 2.9804e-07 | 8.3714e-07 | 3.0105e-07 | 8.456e-07
1380 | feeder2_line37 | 3 | 99 | 2.9973e-07 | 8.4275e-07 | 3.0276e-07 | 8.5126e-07
1380 | feeder2_line38 | 1 | 99 | 3.2442e-07 | 7.7718e-07 | 3.277e-07 | 7.8503e-07
1380 | feeder2_line38 | 2 | 99 | 0.6066 | 0.6066 | 0.61273 | 0.61273
1380 | feeder2_line38 | 3 | 99 | 3.2421e-07 | 7.7703e-07 | 3.2748e-07 | 7.8488e-07
1380 | feeder2_line39 | 1 | 266.4 | 17.1204 | 17.1202 | 6.4266 | 6.4265
1380 | feeder2_line39 | 2 | 266.4 | 12.0536 | 12.0531 | 4.5246 | 4.5244
1380 | feeder2_line39 | 3 | 266.4 | 4.1426 | 4.1423 | 1.555 | 1.5549
1380 | feeder2_line40 | 1 | 354.6 | 80.7792 | 80.781 | 22.7804 | 22.7809
1380 | feeder2_line40 | 2 | 354.6 | 49.9232 | 49.9342 | 14.0787 | 14.0818
1380 | feeder2_line40 | 3 | 354.6 | 73.575 | 73.563 | 20.7487 | 20.7454
1380 | feeder2_line41 | 1 | 99 | 0.093522 | 0.093523 | 0.094467 | 0.094468
1380 | feeder2_line41 | 2 | 99 | 5.0482e-08 | 7.3152e-07 | 5.0992e-08 | 7.3891e-07
1380 | feeder2_line41 | 3 | 99 | 4.9477e-08 | 7.365e-07 | 4.9976e-08 | 7.4394e-07
1380 | feeder2_line42 | 1 | 99 | 2.9953e-07 | 7.5003e-07 | 3.0256e-07 | 7.5761e-07
1380 | feeder2_line42 | 2 | 99 | 2.9793e-07 | 7.4545e-07 | 3.0094e-07 | 7.5298e-07
1380 | feeder2_line42 | 3 | 99 | 0.1899 | 0.18989 | 0.19182 | 0.19181
1380 | feeder2_line43 | 1 | 266.4 | 17.1204 | 17.1202 | 6.4266 | 6.4265
1380 | feeder2_line43 | 2 | 266.4 | 12.0535 | 12.0531 | 4.5246 | 4.5244
1380 | feeder2_line43 | 3 | 266.4 | 3.9554 | 3.9552 | 1.4848 | 1.4847
1380 | feeder2_line44 | 1 | 354.6 | 80.7792 | 80.781 | 22.7804 | 22.7809
1380 | feeder2_line44 | 2 | 354.6 | 49.9233 | 49.9342 | 14.0788 | 14.0818
1380 | feeder2_line44 | 3 | 354.6 | 73.9308 | 73.9188 | 20.8491 | 20.8457
1380 | feeder2_line45 | 1 | 99 | 4.9675e-08 | 5.8126e-07 | 5.0177e-08 | 5.8713e-07
1380 | feeder2_line45 | 2 | 99 | 5.0505e-08 | 5.7691e-07 | 5.1015e-08 | 5.8273e-07
1380 | feeder2_line45 | 3 | 99 | 0.35698 | 0.35694 | 0.36058 | 0.36055
1380 | feeder2_line46 | 1 | 99 | 5.7422e-07 | 1.3597e-06 | 5.8002e-07 | 1.3734e-06
1380 | feeder2_line46 | 2 | 99 | 5.7068e-07 | 1.3514e-06 | 5.7644e-07 | 1.365e-06
1380 | feeder2_line46 | 3 | 99 | 0.16253 | 0.1625 | 0.16417 | 0.16414
1380 | feeder2_line47 | 1 | 266.4 | 17.1204 | 17.1202 | 6.4266 | 6.4265
1380 | feeder2_line47 | 2 | 266.4 | 12.0535 | 12.0531 | 4.5246 | 4.5244
1380 | feeder2_line47 | 3 | 266.4 | 3.7952 | 3.795 | 1.4246 | 1.4245
1380 | feeder2_line48 | 1 | 99 | 1.1287 | 1.1287 | 1.1401 | 1.1401
1380 | feeder2_line48 | 2 | 99 | 5.0348e-08 | 7.2757e-07 | 5.0856e-08 | 7.3492e-07
1380 | feeder2_line48 | 3 | 99 | 4.944e-08 | 7.3207e-07 | 4.9939e-08 | 7.3946e-07
1380 | feeder2_line49 | 1 | 266.4 | 16.3107 | 16.3105 | 6.1226 | 6.1226
1380 | feeder2_line49 | 2 | 266.4 | 12.0535 | 12.0531 | 4.5246 | 4.5244
1380 | feeder2_line49 | 3 | 266.4 | 3.7952 | 3.795 | 1.4246 | 1.4245
1380 | feeder2_line50 | 1 | 99 | 5.7412e-07 | 1.2372e-06 | 5.7992e-07 | 1.2497e-06
1380 | feeder2_line50 | 2 | 99 | 11.3895 | 11.3894 | 11.5046 | 11.5044
1380 | feeder2_line50 | 3 | 99 | 5.7421e-07 | 1.2374e-06 | 5.8001e-07 | 1.2499e-06
1380 | feeder2_line51 | 1 | 99 | 2.9803 | 2.9804 | 3.0104 | 3.0105
1380 | feeder2_line51 | 2 | 99 | 5.7062e-07 | 1.335e-06 | 5.7639e-07 | 1.3485e-06
1380 | feeder2_line51 | 3 | 99 | 5.7423e-07 | 1.3433e-06 | 5.8003e-07 | 1.3569e-06
1380 | feeder2_line52 | 1 | 266.4 | 13.331 | 13.3309 | 5.0041 | 5.0041
1380 | feeder2_line52 | 2 | 266.4 | 0.66708 | 0.66698 | 0.2504 | 0.25037
1380 | feeder2_line52 | 3 | 266.4 | 3.795 | 3.795 | 1.4246 | 1.4245
1380 | feeder2_line53 | 1 | 99 | 5.4928e-07 | 7.5508e-07 | 5.5483e-07 | 7.6271e-07
1380 | feeder2_line53 | 2 | 99 | 0.66697 | 0.66697 | 0.6737 | 0.67371
1380 | feeder2_line53 | 3 | 99 | 5.4952e-07 | 7.5521e-07 | 5.5507e-07 | 7.6284e-07
1380 | feeder2_line54 | 1 | 266.4 | 13.3308 | 13.3309 | 5.0041 | 5.0041
1380 | feeder2_line54 | 2 | 266.4 | 8.5203e-05 | 4.605e-06 | 3.1983e-05 | 1.7286e-06
1380 | feeder2_line54 | 3 | 266.4 | 3.7949 | 3.795 | 1.4245 | 1.4245
1380 | feeder2_line55 | 1 | 99 | 0.18121 | 0.18121 | 0.18304 | 0.18304
1380 | feeder2_line55 | 2 | 99 | 5.0578e-08 | 7.2689e-07 | 5.1089e-08 | 7.3423e-07
1380 | feeder2_line55 | 3 | 99 | 4.9483e-08 | 7.3229e-07 | 4.9983e-08 | 7.3968e-07
1380 | feeder2_line56 | 1 | 354.6 | 80.9595 | 80.9613 | 22.8312 | 22.8317
1380 | feeder2_line56 | 2 | 354.6 | 49.9233 | 49.9342 | 14.0788 | 14.0818
1380 | feeder2_line56 | 3 | 354.6 | 73.9309 | 73.9188 | 20.8491 | 20.8457
1380 | feeder2_line57 | 1 | 99 | 7.4555e-07 | 1.5466e-06 | 7.5309e-07 | 1.5622e-06
1380 | feeder2_line57 | 2 | 99 | 7.5508e-07 | 1.5374e-06 | 7.6271e-07 | 1.5529e-06
1380 | feeder2_line57 | 3 | 99 | 3.795 | 3.795 | 3.8333 | 3.8333
1380 | feeder2_line58 | 1 | 266.4 | 13.3309 | 13.3309 | 5.0041 | 5.0041
1380 | feeder2_line58 | 2 | 266.4 | 1.8841e-05 | 2.6737e-06 | 7.0724e-06 | 1.0036e-06
1380 | feeder2_line58 | 3 | 266.4 | 1.8981e-05 | 2.6894e-06 | 7.1249e-06 | 1.0095e-06
1380 | feeder2_line59 | 1 | 99 | 4.9707e-08 | 5.3759e-07 | 5.0209e-08 | 5.4302e-07
1380 | feeder2_line59 | 2 | 99 | 5.0332e-08 | 5.344e-07 | 5.084e-08 | 5.398e-07
1380 | feeder2_line59 | 3 | 99 | 0.7645 | 0.76447 | 0.77222 | 0.77219
1380 | feeder2_line60 | 1 | 99 | 2.9947e-07 | 8.1246e-07 | 3.0249e-07 | 8.2067e-07
1380 | feeder2_line60 | 2 | 99 | 2.979e-07 | 8.0764e-07 | 3.0091e-07 | 8.1579e-07
1380 | feeder2_line60 | 3 | 99 | 3.2387 | 3.2387 | 3.2714 | 3.2714
1380 | feeder2_line61 | 1 | 266.4 | 1.4369 | 1.4371 | 0.53937 | 0.53943
1380 | feeder2_line61 | 2 | 266.4 | 2.7545 | 2.7547 | 1.034 | 1.0341
1380 | feeder2_line61 | 3 | 266.4 | 0.38471 | 0.38485 | 0.14441 | 0.14446
1380 | feeder2_line62 | 1 | 354.6 | 82.3903 | 82.3923 | 23.2347 | 23.2353
1380 | feeder2_line62 | 2 | 354.6 | 52.2192 | 52.2303 | 14.7262 | 14.7294
1380 | feeder2_line62 | 3 | 354.6 | 74.3147 | 74.3029 | 20.9573 | 20.954
1380 | feeder2_line63 | 1 | 99 | 1.4818 | 1.4818 | 1.4967 | 1.4967
1380 | feeder2_line63 | 2 | 99 | 5.7065e-07 | 1.2143e-06 | 5.7642e-07 | 1.2266e-06
1380 | feeder2_line63 | 3 | 99 | 5.7425e-07 | 1.2218e-06 | 5.8005e-07 | 1.2342e-06
1380 | feeder2_line64 | 1 | 99 | 11.852 | 11.852 | 11.9717 | 11.9717
1380 | feeder2_line64 | 2 | 99 | 6.0905e-12 | 3.1988e-07 | 6.152e-12 | 3.2311e-07
1380 | feeder2_line64 | 3 | 99 | 5.5115e-12 | 3.2186e-07 | 5.5671e-12 | 3.2511e-07
1380 | feeder2_line65 | 1 | 99 | 4.9667e-08 | 6.4446e-07 | 5.0169e-08 | 6.5097e-07
1380 | feeder2_line65 | 2 | 99 | 0.27913 | 0.27914 | 0.28195 | 0.28196
1380 | feeder2_line65 | 3 | 99 | 4.9493e-08 | 6.4377e-07 | 4.9993e-08 | 6.5027e-07
1380 | feeder2_line66 | 1 | 354.6 | 82.3902 | 82.3923 | 23.2347 | 23.2353
1380 | feeder2_line66 | 2 | 354.6 | 52.4924 | 52.5035 | 14.8033 | 14.8064
1380 | feeder2_line66 | 3 | 354.6 | 74.3147 | 74.3029 | 20.9573 | 20.954
1380 | feeder2_line67 | 1 | 99 | 2.4833e-08 | 3.641e-07 | 2.5084e-08 | 3.6778e-07
1380 | feeder2_line67 | 2 | 99 | 2.5322e-08 | 3.6093e-07 | 2.5578e-08 | 3.6458e-07
1380 | feeder2_line67 | 3 | 99 | 0.093415 | 0.09341 | 0.094359 | 0.094353
1380 | feeder2_line68 | 1 | 266.4 | 1.4369 | 1.4371 | 0.53938 | 0.53943
1380 | feeder2_line68 | 2 | 266.4 | 2.7545 | 2.7547 | 1.034 | 1.0341
1380 | feeder2_line68 | 3 | 266.4 | 0.2914 | 0.2915 | 0.10938 | 0.10942
1380 | feeder2_line69 | 1 | 99 | 5.4069 | 5.4069 | 5.4615 | 5.4615
1380 | feeder2_line69 | 2 | 99 | 2.5257e-06 | 6.6289e-07 | 2.5512e-06 | 6.6959e-07
1380 | feeder2_line69 | 3 | 99 | 2.558e-06 | 6.6844e-07 | 2.5838e-06 | 6.7519e-07
1380 | feeder2_line70 | 1 | 354.6 | 87.4956 | 87.4977 | 24.6744 | 24.6751
1380 | feeder2_line70 | 2 | 354.6 | 52.4923 | 52.5035 | 14.8032 | 14.8064
1380 | feeder2_line70 | 3 | 354.6 | 74.3146 | 74.3029 | 20.9573 | 20.954
1380 | feeder2_line71 | 1 | 99 | 4.9668e-08 | 7.1933e-07 | 5.0169e-08 | 7.2659e-07
1380 | feeder2_line71 | 2 | 99 | 0.32304 | 0.32312 | 0.32631 | 0.32638
1380 | feeder2_line71 | 3 | 99 | 4.95e-08 | 7.1844e-07 | 5e-08 | 7.257e-07
1380 | feeder2_line72 | 1 | 354.6 | 87.4957 | 87.4977 | 24.6745 | 24.6751
1380 | feeder2_line72 | 2 | 354.6 | 52.8075 | 52.8187 | 14.8921 | 14.8953
1380 | feeder2_line72 | 3 | 354.6 | 74.3147 | 74.3029 | 20.9573 | 20.954
1380 | feeder2_line73 | 1 | 99 | 6.0086e-07 | 1.5415e-06 | 6.0693e-07 | 1.557e-06
1380 | feeder2_line73 | 2 | 99 | 2.404 | 2.4041 | 2.4283 | 2.4283
1380 | feeder2_line73 | 3 | 99 | 6.0026e-07 | 1.5401e-06 | 6.0632e-07 | 1.5556e-06
1380 | feeder2_line74 | 1 | 99 | 4.9671e-08 | 4.5975e-07 | 5.0173e-08 | 4.644e-07
1380 | feeder2_line74 | 2 | 99 | 0.29127 | 0.29132 | 0.29421 | 0.29426
1380 | feeder2_line74 | 3 | 99 | 4.9485e-08 | 4.5933e-07 | 4.9985e-08 | 4.6397e-07
1380 | feeder2_line75 | 1 | 266.4 | 1.437 | 1.4371 | 0.53942 | 0.53943
1380 | feeder2_line75 | 2 | 266.4 | 0.090359 | 0.090397 | 0.033919 | 0.033933
1380 | feeder2_line75 | 3 | 266.4 | 0.2915 | 0.2915 | 0.10942 | 0.10942
1380 | feeder2_line76 | 1 | 99 | 1.4371 | 1.4371 | 1.4516 | 1.4516
1380 | feeder2_line76 | 2 | 99 | 8.4378e-07 | 1.5762e-06 | 8.5231e-07 | 1.5922e-06
1380 | feeder2_line76 | 3 | 99 | 8.5091e-07 | 1.5887e-06 | 8.5951e-07 | 1.6047e-06
1380 | feeder2_line77 | 1 | 99 | 2.4829e-08 | 5.7775e-07 | 2.508e-08 | 5.8359e-07
1380 | feeder2_line77 | 2 | 99 | 2.5318e-08 | 5.7272e-07 | 2.5574e-08 | 5.7851e-07
1380 | feeder2_line77 | 3 | 99 | 0.29153 | 0.2915 | 0.29448 | 0.29445
1380 | feeder2_line78 | 1 | 266.4 | 1.2317e-11 | 9.5793e-07 | 4.6234e-12 | 3.5958e-07
1380 | feeder2_line78 | 2 | 266.4 | 0.090392 | 0.090397 | 0.033931 | 0.033933
1380 | feeder2_line78 | 3 | 266.4 | 1.2243e-11 | 9.5696e-07 | 4.5958e-12 | 3.5922e-07
1380 | feeder2_line79 | 1 | 354.6 | 4.5594 | 4.559 | 1.2858 | 1.2857
1380 | feeder2_line79 | 2 | 354.6 | 6.3035 | 6.3033 | 1.7776 | 1.7776
1380 | feeder2_line79 | 3 | 354.6 | 14.7766 | 14.7764 | 4.1671 | 4.1671
1380 | feeder2_line80 | 1 | 354.6 | 91.4116 | 91.4132 | 25.7788 | 25.7792
1380 | feeder2_line80 | 2 | 354.6 | 57.1601 | 57.1706 | 16.1196 | 16.1226
1380 | feeder2_line80 | 3 | 354.6 | 88.792 | 88.7799 | 25.0401 | 25.0366
1380 | feeder2_line81 | 1 | 354.6 | 91.4115 | 91.4132 | 25.7788 | 25.7792
1380 | feeder2_line81 | 2 | 354.6 | 57.1601 | 57.1706 | 16.1196 | 16.1226
1380 | feeder2_line81 | 3 | 354.6 | 89.8128 | 89.8006 | 25.3279 | 25.3245
1380 | feeder2_line82 | 1 | 354.6 | 3.1764e-11 | 7.3818e-07 | 8.9577e-12 | 2.0817e-07
1380 | feeder2_line82 | 2 | 354.6 | 3.92e-12 | 7.3104e-07 | 1.1055e-12 | 2.0616e-07
1380 | feeder2_line82 | 3 | 354.6 | 1.0208 | 1.0208 | 0.28788 | 0.28788
1380 | feeder2_line83 | 1 | 354.6 | 91.4117 | 91.4132 | 25.7788 | 25.7792
1380 | feeder2_line83 | 2 | 354.6 | 57.7362 | 57.7465 | 16.2821 | 16.285
1380 | feeder2_line83 | 3 | 354.6 | 89.813 | 89.8006 | 25.328 | 25.3245
1380 | feeder2_line84 | 1 | 354.6 | 2.5027e-11 | 1.305e-06 | 7.0577e-12 | 3.6801e-07
1380 | feeder2_line84 | 2 | 354.6 | 1.0513 | 1.0513 | 0.29647 | 0.29649
1380 | feeder2_line84 | 3 | 354.6 | 1.5066e-11 | 1.3029e-06 | 4.2486e-12 | 3.6743e-07
1380 | feeder2_line85 | 1 | 99 | 0.61009 | 0.61008 | 0.61625 | 0.61625
1380 | feeder2_line85 | 2 | 99 | 5.0889e-08 | 4.6088e-07 | 5.1403e-08 | 4.6553e-07
1380 | feeder2_line85 | 3 | 99 | 4.9513e-08 | 4.6521e-07 | 5.0013e-08 | 4.6991e-07
1380 | feeder2_line86 | 1 | 354.6 | 92.0072 | 92.0085 | 25.9467 | 25.9471
1380 | feeder2_line86 | 2 | 354.6 | 57.7363 | 57.7465 | 16.2821 | 16.285
1380 | feeder2_line86 | 3 | 354.6 | 89.8131 | 89.8006 | 25.328 | 25.3245
1380 | feeder2_line87 | 1 | 354.6 | 92.0073 | 92.0085 | 25.9468 | 25.9471
1380 | feeder2_line87 | 2 | 354.6 | 93.3671 | 93.376 | 26.3302 | 26.3328
1380 | feeder2_line87 | 3 | 354.6 | 91.6413 | 91.6286 | 25.8436 | 25.84
1380 | feeder2_line88 | 1 | 354.6 | 0.00011447 | 3.3844e-06 | 3.2281e-05 | 9.5443e-07
1380 | feeder2_line88 | 2 | 354.6 | 35.8227 | 35.8218 | 10.1023 | 10.102
1380 | feeder2_line88 | 3 | 354.6 | 2.0838 | 2.0837 | 0.58764 | 0.58761
1380 | feeder2_line89 | 1 | 354.6 | 92.005 | 92.0085 | 25.9461 | 25.9471
1380 | feeder2_line89 | 2 | 354.6 | 96.1524 | 96.1637 | 27.1157 | 27.1189
1380 | feeder2_line89 | 3 | 354.6 | 91.639 | 91.6286 | 25.8429 | 25.84
1380 | feeder2_line90 | 1 | 354.6 | 0.00072949 | 2.0431e-06 | 0.00020572 | 5.7617e-07
1380 | feeder2_line90 | 2 | 354.6 | 2.9359 | 2.9364 | 0.82796 | 0.82809
1380 | feeder2_line90 | 3 | 354.6 | 0.00072999 | 2.0397e-06 | 0.00020586 | 5.752e-07
1380 | feeder2_line91 | 1 | 354.6 | 92.0049 | 92.0085 | 25.9461 | 25.9471
1380 | feeder2_line91 | 2 | 354.6 | 96.1523 | 96.1637 | 27.1157 | 27.1189
1380 | feeder2_line91 | 3 | 354.6 | 94.8785 | 94.8682 | 26.7565 | 26.7536
1380 | feeder2_line92 | 1 | 354.6 | 2.58e-11 | 1.0306e-06 | 7.2757e-12 | 2.9062e-07
1380 | feeder2_line92 | 2 | 354.6 | 1.4296e-11 | 1.02e-06 | 4.0317e-12 | 2.8765e-07
1380 | feeder2_line92 | 3 | 354.6 | 3.2434 | 3.2434 | 0.91466 | 0.91467
1380 | feeder2_line93 | 1 | 99 | 2.4843e-08 | 3.4409e-07 | 2.5094e-08 | 3.4756e-07
1380 | feeder2_line93 | 2 | 99 | 1.0514 | 1.0514 | 1.062 | 1.0621
1380 | feeder2_line93 | 3 | 99 | 2.4769e-08 | 3.4354e-07 | 2.5019e-08 | 3.4701e-07
1380 | feeder2_line94 | 1 | 354.6 | 2.4845e-06 | 1.6747e-06 | 7.0065e-07 | 4.7229e-07
1380 | feeder2_line94 | 2 | 354.6 | 2.1586 | 2.1587 | 0.60875 | 0.60876
1380 | feeder2_line94 | 3 | 354.6 | 2.4767e-06 | 1.672e-06 | 6.9845e-07 | 4.7152e-07
1380 | feeder2_line95 | 1 | 99 | 3.5975e-06 | 2.6243e-06 | 3.6339e-06 | 2.6508e-06
1380 | feeder2_line95 | 2 | 99 | 35.8226 | 35.8218 | 36.1844 | 36.1836
1380 | feeder2_line95 | 3 | 99 | 3.581e-06 | 2.6201e-06 | 3.6172e-06 | 2.6465e-06
1380 | feeder2_line96 | 1 | 354.6 | 0.00012182 | 6.2564e-07 | 3.4355e-05 | 1.7644e-07
1380 | feeder2_line96 | 2 | 354.6 | 0.00012031 | 6.189e-07 | 3.3929e-05 | 1.7454e-07
1380 | feeder2_line96 | 3 | 354.6 | 2.0837 | 2.0837 | 0.58763 | 0.58761
1380 | feeder2_line97 | 1 | 354.6 | 92.1583 | 92.1617 | 25.9894 | 25.9903
1380 | feeder2_line97 | 2 | 354.6 | 96.1524 | 96.1637 | 27.1157 | 27.1189
1380 | feeder2_line97 | 3 | 354.6 | 94.8787 | 94.8682 | 26.7565 | 26.7536
1380 | feeder2_line98 | 1 | 354.6 | 0.15596 | 0.15422 | 0.043983 | 0.04349
1380 | feeder2_line98 | 2 | 354.6 | 0.0016806 | 6.1343e-07 | 0.00047394 | 1.7299e-07
1380 | feeder2_line98 | 3 | 354.6 | 0.0017281 | 6.2494e-07 | 0.00048733 | 1.7624e-07
1380 | feeder2_line99 | 1 | 99 | 2.4831e-08 | 4.4977e-07 | 2.5082e-08 | 4.5431e-07
1380 | feeder2_line99 | 2 | 99 | 2.5461e-08 | 4.4474e-07 | 2.5718e-08 | 4.4923e-07
1380 | feeder2_line99 | 3 | 99 | 2.0837 | 2.0837 | 2.1047 | 2.1047
1380 | feeder2_line100 | 1 | 99 | 0.15426 | 0.15422 | 0.15581 | 0.15577
1380 | feeder2_line100 | 2 | 99 | 2.5481e-08 | 6.1094e-07 | 2.5739e-08 | 6.1711e-07
1380 | feeder2_line100 | 3 | 99 | 2.4776e-08 | 6.1682e-07 | 2.5026e-08 | 6.2305e-07
1380 | feeder2_line101 | 1 | 354.6 | 2.1712 | 2.1707 | 0.61229 | 0.61217
1380 | feeder2_line101 | 2 | 354.6 | 6.3035 | 6.3033 | 1.7776 | 1.7776
1380 | feeder2_line101 | 3 | 354.6 | 14.7766 | 14.7764 | 4.1671 | 4.1671
1380 | feeder2_line102 | 1 | 99 | 2.8438 | 2.8438 | 2.8725 | 2.8725
1380 | feeder2_line102 | 2 | 99 | 2.3111e-06 | 8.7355e-07 | 2.3344e-06 | 8.8237e-07
1380 | feeder2_line102 | 3 | 99 | 2.3555e-06 | 8.8117e-07 | 2.3793e-06 | 8.9007e-07
1380 | feeder2_line103 | 1 | 99 | 5.5239e-07 | 8.0793e-07 | 5.5797e-07 | 8.1609e-07
1380 | feeder2_line103 | 2 | 99 | 1.257 | 1.2569 | 1.2697 | 1.2696
1380 | feeder2_line103 | 3 | 99 | 5.5141e-07 | 8.0648e-07 | 5.5698e-07 | 8.1463e-07
1380 | feeder2_line104 | 1 | 354.6 | 2.1711 | 2.1707 | 0.61226 | 0.61217
1380 | feeder2_line104 | 2 | 354.6 | 5.1004 | 5.1002 | 1.4384 | 1.4383
1380 | feeder2_line104 | 3 | 354.6 | 14.7765 | 14.7764 | 4.1671 | 4.1671
1380 | feeder2_line105 | 1 | 99 | 2.5635e-06 | 7.4341e-07 | 2.5894e-06 | 7.5092e-07
1380 | feeder2_line105 | 2 | 99 | 2.5256e-06 | 7.357e-07 | 2.5511e-06 | 7.4313e-07
1380 | feeder2_line105 | 3 | 99 | 2.0106 | 2.0105 | 2.0309 | 2.0309
1380 | feeder2_line106 | 1 | 354.6 | 2.171 | 2.1707 | 0.61225 | 0.61217
1380 | feeder2_line106 | 2 | 354.6 | 5.1004 | 5.1002 | 1.4383 | 1.4383
1380 | feeder2_line106 | 3 | 354.6 | 12.8838 | 12.8838 | 3.6333 | 3.6333
1380 | feeder2_line107 | 1 | 99 | 3.2581e-07 | 9.0596e-07 | 3.2911e-07 | 9.1511e-07
1380 | feeder2_line107 | 2 | 99 | 1.0532 | 1.0533 | 1.0639 | 1.0639
1380 | feeder2_line107 | 3 | 99 | 3.2519e-07 | 9.0415e-07 | 3.2847e-07 | 9.1329e-07
1380 | feeder2_line108 | 1 | 354.6 | 2.171 | 2.1707 | 0.61225 | 0.61217
1380 | feeder2_line108 | 2 | 354.6 | 4.1045 | 4.1043 | 1.1575 | 1.1575
1380 | feeder2_line108 | 3 | 354.6 | 12.8838 | 12.8838 | 3.6333 | 3.6333
1380 | feeder2_line109 | 1 | 354.6 | 93.0215 | 93.0237 | 26.2328 | 26.2334
1380 | feeder2_line109 | 2 | 354.6 | 96.1536 | 96.1637 | 27.1161 | 27.1189
1380 | feeder2_line109 | 3 | 354.6 | 94.8799 | 94.8682 | 26.7569 | 26.7536
1380 | feeder2_line110 | 1 | 99 | 0.8711 | 0.8703 | 0.8799 | 0.87909
1380 | feeder2_line110 | 2 | 99 | 0.00079702 | 9.0414e-07 | 0.00080507 | 9.1327e-07
1380 | feeder2_line110 | 3 | 99 | 0.00080991 | 9.1313e-07 | 0.00081809 | 9.2235e-07
1380 | feeder2_line111 | 1 | 99 | 2.4809e-08 | 3.8409e-07 | 2.506e-08 | 3.8797e-07
1380 | feeder2_line111 | 2 | 99 | 35.7815 | 35.7805 | 36.1429 | 36.142
1380 | feeder2_line111 | 3 | 99 | 2.4715e-08 | 3.8346e-07 | 2.4964e-08 | 3.8734e-07
1380 | feeder2_line112 | 1 | 99 | 3.2608e-07 | 9.2301e-07 | 3.2937e-07 | 9.3233e-07
1380 | feeder2_line112 | 2 | 99 | 0.041183 | 0.041325 | 0.041599 | 0.041742
1380 | feeder2_line112 | 3 | 99 | 3.2548e-07 | 9.215e-07 | 3.2877e-07 | 9.3081e-07
1380 | feeder2_line113 | 1 | 99 | 0.76624 | 0.76625 | 0.77398 | 0.77399
1380 | feeder2_line113 | 2 | 99 | 3.2423e-07 | 9.011e-07 | 3.275e-07 | 9.102e-07
1380 | feeder2_line113 | 3 | 99 | 3.2596e-07 | 9.0978e-07 | 3.2925e-07 | 9.1897e-07
1380 | feeder2_line114 | 1 | 99 | 1.2629 | 1.2628 | 1.2756 | 1.2756
1380 | feeder2_line114 | 2 | 99 | 2.5405e-08 | 4.3439e-07 | 2.5661e-08 | 4.3877e-07
1380 | feeder2_line114 | 3 | 99 | 2.4761e-08 | 4.3817e-07 | 2.5011e-08 | 4.4259e-07
1380 | feeder2_line115 | 1 | 99 | 2.4798e-08 | 5.6537e-07 | 2.5049e-08 | 5.7108e-07
1380 | feeder2_line115 | 2 | 99 | 2.8059 | 2.8059 | 2.8342 | 2.8342
1380 | feeder2_line115 | 3 | 99 | 2.4777e-08 | 5.6415e-07 | 2.5027e-08 | 5.6985e-07
1380 | feeder2_line116 | 1 | 354.6 | 2.171 | 2.1707 | 0.61225 | 0.61217
1380 | feeder2_line116 | 2 | 354.6 | 1.421 | 1.4209 | 0.40074 | 0.40071
1380 | feeder2_line116 | 3 | 354.6 | 12.8838 | 12.8838 | 3.6333 | 3.6333
1380 | feeder2_line117 | 1 | 99 | 4.9756e-08 | 6.4712e-07 | 5.0259e-08 | 6.5365e-07
1380 | feeder2_line117 | 2 | 99 | 0.16272 | 0.16281 | 0.16437 | 0.16445
1380 | feeder2_line117 | 3 | 99 | 4.9601e-08 | 6.4613e-07 | 5.0102e-08 | 6.5265e-07
1380 | feeder2_line118 | 1 | 354.6 | 93.0216 | 93.0237 | 26.2328 | 26.2334
1380 | feeder2_line118 | 2 | 354.6 | 96.3162 | 96.3263 | 27.1619 | 27.1648
1380 | feeder2_line118 | 3 | 354.6 | 94.88 | 94.8682 | 26.7569 | 26.7536
1380 | feeder2_line119 | 1 | 99 | 2.4795e-08 | 6.0837e-07 | 2.5046e-08 | 6.1452e-07
1380 | feeder2_line119 | 2 | 99 | 2.5393e-08 | 6.0205e-07 | 2.5649e-08 | 6.0813e-07
1380 | feeder2_line119 | 3 | 99 | 1.7292 | 1.7292 | 1.7467 | 1.7467
1380 | feeder2_line120 | 1 | 354.6 | 2.171 | 2.1707 | 0.61225 | 0.61217
1380 | feeder2_line120 | 2 | 354.6 | 1.421 | 1.4209 | 0.40074 | 0.40071
1380 | feeder2_line120 | 3 | 354.6 | 11.5314 | 11.5314 | 3.2519 | 3.2519
1380 | feeder2_line121 | 1 | 99 | 3.258e-07 | 9.4211e-07 | 3.2909e-07 | 9.5163e-07
1380 | feeder2_line121 | 2 | 99 | 1.3115 | 1.3115 | 1.3247 | 1.3248
1380 | feeder2_line121 | 3 | 99 | 3.2508e-07 | 9.3975e-07 | 3.2836e-07 | 9.4924e-07
1380 | feeder2_line122 | 1 | 354.6 | 2.171 | 2.1707 | 0.61224 | 0.61217
1380 | feeder2_line122 | 2 | 354.6 | 0.17985 | 0.17963 | 0.050721 | 0.050656
1380 | feeder2_line122 | 3 | 354.6 | 11.5314 | 11.5314 | 3.2519 | 3.2519
1380 | feeder2_line123 | 1 | 99 | 5.7725e-07 | 9.7625e-07 | 5.8308e-07 | 9.8611e-07
1380 | feeder2_line123 | 2 | 99 | 5.712e-07 | 9.6613e-07 | 5.7697e-07 | 9.7589e-07
1380 | feeder2_line123 | 3 | 99 | 0.49208 | 0.49208 | 0.49705 | 0.49705
1380 | feeder2_line124 | 1 | 354.6 | 2.1709 | 2.1707 | 0.61222 | 0.61217
1380 | feeder2_line124 | 2 | 354.6 | 0.17976 | 0.17963 | 0.050695 | 0.050656
1380 | feeder2_line124 | 3 | 354.6 | 11.0393 | 11.0394 | 3.1132 | 3.1132
1380 | feeder2_line125 | 1 | 99 | 5.7725e-07 | 9.0752e-07 | 5.8308e-07 | 9.1669e-07
1380 | feeder2_line125 | 2 | 99 | 5.7121e-07 | 8.9812e-07 | 5.7698e-07 | 9.072e-07
1380 | feeder2_line125 | 3 | 99 | 0.15472 | 0.15468 | 0.15628 | 0.15625
1380 | feeder2_line126 | 1 | 354.6 | 2.1711 | 2.1707 | 0.61226 | 0.61217
1380 | feeder2_line126 | 2 | 354.6 | 0.17992 | 0.17963 | 0.050739 | 0.050656
1380 | feeder2_line126 | 3 | 354.6 | 10.8868 | 10.8868 | 3.0702 | 3.0702
1380 | feeder2_line127 | 1 | 99 | 5.7723e-07 | 1.0864e-06 | 5.8306e-07 | 1.0974e-06
1380 | feeder2_line127 | 2 | 99 | 5.712e-07 | 1.0752e-06 | 5.7697e-07 | 1.0861e-06
1380 | feeder2_line127 | 3 | 99 | 10.1381 | 10.1384 | 10.2405 | 10.2408
1380 | feeder2_line128 | 1 | 354.6 | 2.171 | 2.1707 | 0.61224 | 0.61217
1380 | feeder2_line128 | 2 | 354.6 | 0.17984 | 0.17963 | 0.050716 | 0.050656
1380 | feeder2_line128 | 3 | 354.6 | 0.76693 | 0.76673 | 0.21628 | 0.21622
1380 | feeder2_line129 | 1 | 99 | 5.5247e-07 | 8.8095e-07 | 5.5805e-07 | 8.8985e-07
1380 | feeder2_line129 | 2 | 99 | 0.17962 | 0.17962 | 0.18143 | 0.18144
1380 | feeder2_line129 | 3 | 99 | 5.509e-07 | 8.7858e-07 | 5.5646e-07 | 8.8746e-07
1380 | feeder2_line130 | 1 | 354.6 | 2.171 | 2.1707 | 0.61224 | 0.61217
1380 | feeder2_line130 | 2 | 354.6 | 0.00030739 | 4.6153e-06 | 8.6688e-05 | 1.3016e-06
1380 | feeder2_line130 | 3 | 354.6 | 0.76694 | 0.76673 | 0.21628 | 0.21622
1380 | feeder2_line131 | 1 | 99 | 5.7724e-07 | 9.7638e-07 | 5.8307e-07 | 9.8625e-07
1380 | feeder2_line131 | 2 | 99 | 5.7122e-07 | 9.6632e-07 | 5.7699e-07 | 9.7608e-07
1380 | feeder2_line131 | 3 | 99 | 0.16255 | 0.16254 | 0.16419 | 0.16418
1380 | feeder2_line132 | 1 | 354.6 | 2.1709 | 2.1707 | 0.6122 | 0.61217
1380 | feeder2_line132 | 2 | 354.6 | 0.00012472 | 2.9018e-06 | 3.5172e-05 | 8.1833e-07
1380 | feeder2_line132 | 3 | 354.6 | 0.60934 | 0.60929 | 0.17184 | 0.17182
1380 | feeder2_line133 | 1 | 99 | 2.1708 | 2.1707 | 2.1927 | 2.1927
1380 | feeder2_line133 | 2 | 99 | 2.983e-07 | 9.7403e-07 | 3.0132e-07 | 9.8387e-07
1380 | feeder2_line133 | 3 | 99 | 3.0024e-07 | 9.8154e-07 | 3.0327e-07 | 9.9146e-07
1380 | feeder2_line134 | 1 | 354.6 | 4.0357e-12 | 1.7942e-06 | 1.1381e-12 | 5.0598e-07
1380 | feeder2_line134 | 2 | 354.6 | 7.6855e-12 | 1.7773e-06 | 2.1674e-12 | 5.012e-07
1380 | feeder2_line134 | 3 | 354.6 | 0.60929 | 0.60929 | 0.17182 | 0.17182
1380 | feeder2_line135 | 1 | 99 | 0.32506 | 0.32502 | 0.32834 | 0.32831
1380 | feeder2_line135 | 2 | 99 | 5.104e-08 | 5.8343e-07 | 5.1555e-08 | 5.8932e-07
1380 | feeder2_line135 | 3 | 99 | 4.9632e-08 | 5.8904e-07 | 5.0134e-08 | 5.9499e-07
1380 | feeder2_line136 | 1 | 354.6 | 93.3461 | 93.3482 | 26.3243 | 26.3249
1380 | feeder2_line136 | 2 | 354.6 | 96.3162 | 96.3263 | 27.1619 | 27.1648
1380 | feeder2_line136 | 3 | 354.6 | 94.8799 | 94.8682 | 26.7569 | 26.7536
1380 | feeder2_line137 | 1 | 99 | 0.085039 | 0.085001 | 0.085898 | 0.085859
1380 | feeder2_line137 | 2 | 99 | 8.4639e-07 | 1.5716e-06 | 8.5494e-07 | 1.5874e-06
1380 | feeder2_line137 | 3 | 99 | 8.5513e-07 | 1.5867e-06 | 8.6377e-07 | 1.6027e-06
1380 | feeder2_line138 | 1 | 354.6 | 93.4312 | 93.4332 | 26.3483 | 26.3489
1380 | feeder2_line138 | 2 | 354.6 | 96.3162 | 96.3263 | 27.1619 | 27.1648
1380 | feeder2_line138 | 3 | 354.6 | 94.88 | 94.8682 | 26.7569 | 26.7536
1380 | feeder2_line139 | 1 | 99 | 4.9801e-08 | 4.9518e-07 | 5.0304e-08 | 5.0018e-07
1380 | feeder2_line139 | 2 | 99 | 5.1053e-08 | 4.8974e-07 | 5.1568e-08 | 4.9469e-07
1380 | feeder2_line139 | 3 | 99 | 0.13654 | 0.13588 | 0.13792 | 0.13725
1380 | feeder2_line140 | 1 | 354.6 | 93.4313 | 93.4332 | 26.3484 | 26.3489
1380 | feeder2_line140 | 2 | 354.6 | 96.3163 | 96.3263 | 27.162 | 27.1648
1380 | feeder2_line140 | 3 | 354.6 | 95.0125 | 95 | 26.7943 | 26.7907
1380 | feeder2_line141 | 1 | 99 | 2.5486e-06 | 4.8991e-07 | 2.5743e-06 | 4.9486e-07
1380 | feeder2_line141 | 2 | 99 | 0.18995 | 0.18995 | 0.19187 | 0.19187
1380 | feeder2_line141 | 3 | 99 | 2.5454e-06 | 4.8918e-07 | 2.5711e-06 | 4.9412e-07
1380 | feeder2_line142 | 1 | 354.6 | 93.4311 | 93.4332 | 26.3483 | 26.3489
1380 | feeder2_line142 | 2 | 354.6 | 96.506 | 96.5162 | 27.2155 | 27.2183
1380 | feeder2_line142 | 3 | 354.6 | 95.0123 | 95 | 26.7942 | 26.7907
1380 | feeder2_line143 | 1 | 99 | 8.5676e-07 | 1.7409e-06 | 8.6542e-07 | 1.7585e-06
1380 | feeder2_line143 | 2 | 99 | 1.0539 | 1.054 | 1.0646 | 1.0646
1380 | feeder2_line143 | 3 | 99 | 8.5554e-07 | 1.7384e-06 | 8.6418e-07 | 1.7559e-06
1380 | feeder2_line144 | 1 | 354.6 | 93.4309 | 93.4332 | 26.3483 | 26.3489
1380 | feeder2_line144 | 2 | 354.6 | 97.1447 | 97.1551 | 27.3956 | 27.3985
1380 | feeder2_line144 | 3 | 354.6 | 95.0121 | 95 | 26.7942 | 26.7907
1380 | feeder2_line145 | 1 | 99 | 2.491e-08 | 4.8818e-07 | 2.5162e-08 | 4.9311e-07
1380 | feeder2_line145 | 2 | 99 | 1.0245 | 1.0245 | 1.0348 | 1.0349
1380 | feeder2_line145 | 3 | 99 | 2.4834e-08 | 4.8747e-07 | 2.5085e-08 | 4.9239e-07
1380 | feeder2_line146 | 1 | 354.6 | 93.4308 | 93.4332 | 26.3482 | 26.3489
1380 | feeder2_line146 | 2 | 354.6 | 98.169 | 98.1796 | 27.6844 | 27.6874
1380 | feeder2_line146 | 3 | 354.6 | 95.012 | 95 | 26.7941 | 26.7907
1380 | feeder2_line147 | 1 | 99 | 0.10722 | 0.10722 | 0.10831 | 0.10831
1380 | feeder2_line147 | 2 | 99 | 1.1463e-06 | 2.2271e-06 | 1.1579e-06 | 2.2496e-06
1380 | feeder2_line147 | 3 | 99 | 1.1575e-06 | 2.2486e-06 | 1.1692e-06 | 2.2713e-06
1380 | feeder2_line148 | 1 | 99 | 1.8941 | 1.8941 | 1.9132 | 1.9132
1380 | feeder2_line148 | 2 | 99 | 5.9868e-07 | 1.4923e-06 | 6.0473e-07 | 1.5074e-06
1380 | feeder2_line148 | 3 | 99 | 6.0357e-07 | 1.5067e-06 | 6.0967e-07 | 1.5219e-06
1380 | feeder2_line149 | 1 | 354.6 | 95.431 | 95.4333 | 26.9123 | 26.9129
1380 | feeder2_line149 | 2 | 354.6 | 98.1692 | 98.1796 | 27.6845 | 27.6874
1380 | feeder2_line149 | 3 | 354.6 | 95.0122 | 95 | 26.7942 | 26.7907
1380 | feeder2_line150 | 1 | 354.6 | 95.4311 | 95.4333 | 26.9123 | 26.9129
1380 | feeder2_line150 | 2 | 354.6 | 99.0001 | 99.0104 | 27.9188 | 27.9217
1380 | feeder2_line150 | 3 | 354.6 | 95.0123 | 95 | 26.7942 | 26.7907
1380 | feeder2_line151 | 1 | 99 | 9.8501e-06 | 1.7926e-06 | 9.9495e-06 | 1.8107e-06
1380 | feeder2_line151 | 2 | 99 | 1.3116 | 1.3115 | 1.3248 | 1.3248
1380 | feeder2_line151 | 3 | 99 | 9.8497e-06 | 1.79e-06 | 9.9492e-06 | 1.8081e-06
1380 | feeder2_line152 | 1 | 354.6 | 1.2502e-11 | 1.1946e-06 | 3.5255e-12 | 3.3688e-07
1380 | feeder2_line152 | 2 | 354.6 | 1.0899e-11 | 1.1826e-06 | 3.0737e-12 | 3.335e-07
1380 | feeder2_line152 | 3 | 354.6 | 0.076297 | 0.076288 | 0.021516 | 0.021514
1380 | feeder2_line153 | 1 | 99 | 1.3217 | 1.3217 | 1.3351 | 1.3351
1380 | feeder2_line153 | 2 | 99 | 5.1128e-08 | 5.9132e-07 | 5.1644e-08 | 5.9729e-07
1380 | feeder2_line153 | 3 | 99 | 4.9724e-08 | 5.9697e-07 | 5.0226e-08 | 6.03e-07
1380 | feeder2_line154 | 1 | 99 | 5.8012e-07 | 8.896e-07 | 5.8598e-07 | 8.9859e-07
1380 | feeder2_line154 | 2 | 99 | 5.7372e-07 | 8.799e-07 | 5.7952e-07 | 8.8879e-07
1380 | feeder2_line154 | 3 | 99 | 2.4212 | 2.4212 | 2.4457 | 2.4456
1380 | feeder2_line155 | 1 | 99 | 96.1466 | 96.1489 | 97.1177 | 97.1201
1380 | feeder2_line155 | 2 | 99 | 99 | 99.0104 | 100 | 100.0105
1380 | feeder2_line155 | 3 | 99 | 97.5096 | 97.4973 | 98.4946 | 98.4822
1380 | feeder2_line156 | 1 | 99 | 6.0479e-07 | 1.1706e-06 | 6.109e-07 | 1.1824e-06
1380 | feeder2_line156 | 2 | 99 | 1.2583 | 1.2583 | 1.271 | 1.271
1380 | feeder2_line156 | 3 | 99 | 6.0389e-07 | 1.1689e-06 | 6.0998e-07 | 1.1807e-06
1380 | feeder2_line157 | 1 | 99 | 2.4934e-08 | 2.5412e-07 | 2.5186e-08 | 2.5669e-07
1380 | feeder2_line157 | 2 | 99 | 0.090128 | 0.090136 | 0.091038 | 0.091046
1380 | feeder2_line157 | 3 | 99 | 2.4851e-08 | 2.5375e-07 | 2.5102e-08 | 2.5632e-07
1410 | feeder2_line1 | 1 | 354.6 | 53.1169 | 53.1127 | 14.9794 | 14.9782
1410 | feeder2_line1 | 2 | 354.6 | 71.9415 | 71.9316 | 20.2881 | 20.2853
1410 | feeder2_line1 | 3 | 354.6 | 60.0203 | 60.0364 | 16.9262 | 16.9307
1410 | feeder2_line2 | 1 | 354.6 | 53.4531 | 53.4488 | 15.0742 | 15.073
1410 | feeder2_line2 | 2 | 354.6 | 71.9417 | 71.9316 | 20.2881 | 20.2853
1410 | feeder2_line2 | 3 | 354.6 | 60.0204 | 60.0364 | 16.9262 | 16.9307
1410 | feeder2_line3 | 1 | 80.1 | 0.33964 | 0.33964 | 0.42401 | 0.42402
1410 | feeder2_line3 | 2 | 80.1 | 5.7233e-07 | 1.0576e-06 | 7.1452e-07 | 1.3204e-06
1410 | feeder2_line3 | 3 | 80.1 | 5.7187e-07 | 1.0568e-06 | 7.1394e-07 | 1.3194e-06
1410 | feeder2_line4 | 1 | 354.6 | 53.4532 | 53.4488 | 15.0742 | 15.073
1410 | feeder2_line4 | 2 | 354.6 | 72.2169 | 72.2067 | 20.3657 | 20.3629
1410 | feeder2_line4 | 3 | 354.6 | 60.0206 | 60.0364 | 16.9263 | 16.9307
1410 | feeder2_line5 | 1 | 80.1 | 5.7172e-07 | 9.9761e-07 | 7.1376e-07 | 1.2455e-06
1410 | feeder2_line5 | 2 | 80.1 | 0.27932 | 0.27932 | 0.34872 | 0.34872
1410 | feeder2_line5 | 3 | 80.1 | 5.719e-07 | 9.9792e-07 | 7.1398e-07 | 1.2458e-06
1410 | feeder2_line6 | 1 | 80.1 | 5.7175e-07 | 1.1736e-06 | 7.138e-07 | 1.4652e-06
1410 | feeder2_line6 | 2 | 80.1 | 5.7245e-07 | 1.175e-06 | 7.1467e-07 | 1.467e-06
1410 | feeder2_line6 | 3 | 80.1 | 1.9987 | 1.9987 | 2.4953 | 2.4953
1410 | feeder2_line7 | 1 | 354.6 | 53.4534 | 53.4488 | 15.0743 | 15.073
1410 | feeder2_line7 | 2 | 354.6 | 72.217 | 72.2067 | 20.3658 | 20.3629
1410 | feeder2_line7 | 3 | 354.6 | 61.9975 | 62.0133 | 17.4838 | 17.4882
1410 | feeder2_line8 | 1 | 80.1 | 0.072683 | 0.072683 | 0.090741 | 0.09074
1410 | feeder2_line8 | 2 | 80.1 | 5.7268e-07 | 1.1334e-06 | 7.1495e-07 | 1.415e-06
1410 | feeder2_line8 | 3 | 80.1 | 5.7208e-07 | 1.1323e-06 | 7.1421e-07 | 1.4136e-06
1410 | feeder2_line9 | 1 | 354.6 | 53.5259 | 53.5212 | 15.0947 | 15.0934
1410 | feeder2_line9 | 2 | 354.6 | 72.2171 | 72.2067 | 20.3658 | 20.3629
1410 | feeder2_line9 | 3 | 354.6 | 61.9976 | 62.0133 | 17.4838 | 17.4882
1410 | feeder2_line10 | 1 | 80.1 | 8.4538e-07 | 1.4945e-06 | 1.0554e-06 | 1.8658e-06
1410 | feeder2_line10 | 2 | 80.1 | 0.072523 | 0.072522 | 0.090541 | 0.090539
1410 | feeder2_line10 | 3 | 80.1 | 8.4568e-07 | 1.4951e-06 | 1.0558e-06 | 1.8666e-06
1410 | feeder2_line11 | 1 | 354.6 | 53.5259 | 53.5212 | 15.0947 | 15.0934
1410 | feeder2_line11 | 2 | 354.6 | 72.2891 | 72.2787 | 20.3861 | 20.3832
1410 | feeder2_line11 | 3 | 354.6 | 61.9976 | 62.0133 | 17.4838 | 17.4882
1410 | feeder2_line12 | 1 | 80.1 | 5.4703e-07 | 9.9144e-07 | 6.8293e-07 | 1.2377e-06
1410 | feeder2_line12 | 2 | 80.1 | 5.4798e-07 | 9.9293e-07 | 6.8412e-07 | 1.2396e-06
1410 | feeder2_line12 | 3 | 80.1 | 3.2208 | 3.2208 | 4.021 | 4.0209
1410 | feeder2_line13 | 1 | 354.6 | 53.5258 | 53.5212 | 15.0947 | 15.0934
1410 | feeder2_line13 | 2 | 354.6 | 72.2891 | 72.2787 | 20.3861 | 20.3832
1410 | feeder2_line13 | 3 | 354.6 | 65.1729 | 65.1886 | 18.3793 | 18.3837
1410 | feeder2_line14 | 1 | 80.1 | 0.27524 | 0.27523 | 0.34361 | 0.34361
1410 | feeder2_line14 | 2 | 80.1 | 2.9884e-07 | 6.4756e-07 | 3.7309e-07 | 8.0843e-07
1410 | feeder2_line14 | 3 | 80.1 | 2.9858e-07 | 6.4683e-07 | 3.7276e-07 | 8.0753e-07
1410 | feeder2_line15 | 1 | 354.6 | 53.7984 | 53.7937 | 15.1716 | 15.1703
1410 | feeder2_line15 | 2 | 354.6 | 72.2891 | 72.2787 | 20.3861 | 20.3832
1410 | feeder2_line15 | 3 | 354.6 | 65.173 | 65.1886 | 18.3793 | 18.3837
1410 | feeder2_line16 | 1 | 80.1 | 5.7203e-07 | 1.0305e-06 | 7.1414e-07 | 1.2866e-06
1410 | feeder2_line16 | 2 | 80.1 | 0.25457 | 0.25456 | 0.31781 | 0.31781
1410 | feeder2_line16 | 3 | 80.1 | 5.723e-07 | 1.0311e-06 | 7.1449e-07 | 1.2872e-06
1410 | feeder2_line17 | 1 | 354.6 | 53.7984 | 53.7937 | 15.1716 | 15.1703
1410 | feeder2_line17 | 2 | 354.6 | 72.539 | 72.5286 | 20.4566 | 20.4537
1410 | feeder2_line17 | 3 | 354.6 | 65.173 | 65.1886 | 18.3793 | 18.3837
1410 | feeder2_line18 | 1 | 80.1 | 5.4736e-07 | 7.3802e-07 | 6.8334e-07 | 9.2137e-07
1410 | feeder2_line18 | 2 | 80.1 | 5.4873e-07 | 7.396e-07 | 6.8506e-07 | 9.2334e-07
1410 | feeder2_line18 | 3 | 80.1 | 1.6536 | 1.6536 | 2.0644 | 2.0645
1410 | feeder2_line19 | 1 | 354.6 | 53.7984 | 53.7937 | 15.1716 | 15.1703
1410 | feeder2_line19 | 2 | 354.6 | 72.5391 | 72.5286 | 20.4566 | 20.4537
1410 | feeder2_line19 | 3 | 354.6 | 66.81 | 66.8256 | 18.8409 | 18.8454
1410 | feeder2_line20 | 1 | 99 | 5.4744e-07 | 8.8499e-07 | 5.5297e-07 | 8.9393e-07
1410 | feeder2_line20 | 2 | 99 | 5.4893e-07 | 8.8705e-07 | 5.5448e-07 | 8.9601e-07
1410 | feeder2_line20 | 3 | 99 | 0.35652 | 0.35655 | 0.36012 | 0.36015
1410 | feeder2_line21 | 1 | 354.6 | 53.7985 | 53.7937 | 15.1716 | 15.1703
1410 | feeder2_line21 | 2 | 354.6 | 72.5392 | 72.5286 | 20.4566 | 20.4537
1410 | feeder2_line21 | 3 | 354.6 | 67.1623 | 67.1779 | 18.9403 | 18.9447
1410 | feeder2_line22 | 1 | 99 | 5.7245e-07 | 1.0146e-06 | 5.7823e-07 | 1.0249e-06
1410 | feeder2_line22 | 2 | 99 | 0.093698 | 0.093695 | 0.094644 | 0.094642
1410 | feeder2_line22 | 3 | 99 | 5.7295e-07 | 1.0155e-06 | 5.7874e-07 | 1.0258e-06
1410 | feeder2_line23 | 1 | 99 | 5.7245e-07 | 9.4979e-07 | 5.7823e-07 | 9.5938e-07
1410 | feeder2_line23 | 2 | 99 | 5.7386e-07 | 9.521e-07 | 5.7965e-07 | 9.6172e-07
1410 | feeder2_line23 | 3 | 99 | 0.84045 | 0.84045 | 0.84894 | 0.84894
1410 | feeder2_line24 | 1 | 354.6 | 53.7986 | 53.7937 | 15.1716 | 15.1703
1410 | feeder2_line24 | 2 | 354.6 | 72.6322 | 72.6216 | 20.4828 | 20.4799
1410 | feeder2_line24 | 3 | 354.6 | 67.6263 | 67.6418 | 19.0712 | 19.0755
1410 | feeder2_line25 | 1 | 99 | 0.093972 | 0.093971 | 0.094921 | 0.09492
1410 | feeder2_line25 | 2 | 99 | 4.9606e-08 | 6.9246e-07 | 5.0107e-08 | 6.9945e-07
1410 | feeder2_line25 | 3 | 99 | 5.0006e-08 | 6.9134e-07 | 5.0511e-08 | 6.9832e-07
1410 | feeder2_line26 | 1 | 99 | 1.7105 | 1.7105 | 1.7278 | 1.7278
1410 | feeder2_line26 | 2 | 99 | 5.4927e-07 | 8.5791e-07 | 5.5482e-07 | 8.6657e-07
1410 | feeder2_line26 | 3 | 99 | 5.4812e-07 | 8.5652e-07 | 5.5366e-07 | 8.6517e-07
1410 | feeder2_line27 | 1 | 354.6 | 55.5927 | 55.5878 | 15.6776 | 15.6762
1410 | feeder2_line27 | 2 | 354.6 | 72.6322 | 72.6216 | 20.4828 | 20.4799
1410 | feeder2_line27 | 3 | 354.6 | 67.6263 | 67.6418 | 19.0712 | 19.0755
1410 | feeder2_line28 | 1 | 99 | 2.5389e-06 | 7.1051e-07 | 2.5646e-06 | 7.1769e-07
1410 | feeder2_line28 | 2 | 99 | 2.4676 | 2.4676 | 2.4925 | 2.4925
1410 | feeder2_line28 | 3 | 99 | 2.5418e-06 | 7.1134e-07 | 2.5675e-06 | 7.1853e-07
1410 | feeder2_line29 | 1 | 354.6 | 55.5927 | 55.5878 | 15.6776 | 15.6762
1410 | feeder2_line29 | 2 | 354.6 | 74.2317 | 74.2212 | 20.9339 | 20.931
1410 | feeder2_line29 | 3 | 354.6 | 67.6264 | 67.6418 | 19.0712 | 19.0755
1410 | feeder2_line30 | 1 | 266.4 | 25.5272 | 25.5268 | 9.5823 | 9.5822
1410 | feeder2_line30 | 2 | 266.4 | 5.138 | 5.1377 | 1.9287 | 1.9286
1410 | feeder2_line30 | 3 | 266.4 | 3.6829 | 3.6825 | 1.3825 | 1.3823
1410 | feeder2_line31 | 1 | 354.6 | 80.8905 | 80.8851 | 22.8118 | 22.8102
1410 | feeder2_line31 | 2 | 354.6 | 79.0975 | 79.0866 | 22.3061 | 22.3031
1410 | feeder2_line31 | 3 | 354.6 | 71.2755 | 71.2906 | 20.1002 | 20.1045
1410 | feeder2_line32 | 1 | 354.6 | 80.8905 | 80.8851 | 22.8118 | 22.8102
1410 | feeder2_line32 | 2 | 354.6 | 81.6599 | 81.649 | 23.0287 | 23.0257
1410 | feeder2_line32 | 3 | 354.6 | 71.2755 | 71.2906 | 20.1003 | 20.1045
1410 | feeder2_line33 | 1 | 99 | 5.0039e-08 | 6.861e-07 | 5.0544e-08 | 6.9303e-07
1410 | feeder2_line33 | 2 | 99 | 2.5896 | 2.5896 | 2.6157 | 2.6157
1410 | feeder2_line33 | 3 | 99 | 5.0116e-08 | 6.8696e-07 | 5.0622e-08 | 6.939e-07
1410 | feeder2_line34 | 1 | 354.6 | 80.8905 | 80.8851 | 22.8118 | 22.8102
1410 | feeder2_line34 | 2 | 354.6 | 81.6599 | 81.649 | 23.0287 | 23.0257
1410 | feeder2_line34 | 3 | 354.6 | 72.543 | 72.5581 | 20.4577 | 20.4619
1410 | feeder2_line35 | 1 | 99 | 2.9921e-07 | 7.5994e-07 | 3.0223e-07 | 7.6762e-07
1410 | feeder2_line35 | 2 | 99 | 3.0008e-07 | 7.6248e-07 | 3.0311e-07 | 7.7018e-07
1410 | feeder2_line35 | 3 | 99 | 1.2786 | 1.2786 | 1.2915 | 1.2915
1410 | feeder2_line36 | 1 | 354.6 | 82.0317 | 82.0262 | 23.1336 | 23.132
1410 | feeder2_line36 | 2 | 354.6 | 81.6598 | 81.649 | 23.0287 | 23.0257
1410 | feeder2_line36 | 3 | 354.6 | 72.5429 | 72.5581 | 20.4577 | 20.4619
1410 | feeder2_line37 | 1 | 99 | 1.5758 | 1.5756 | 1.5918 | 1.5915
1410 | feeder2_line37 | 2 | 99 | 3.0015e-07 | 8.4387e-07 | 3.0319e-07 | 8.524e-07
1410 | feeder2_line37 | 3 | 99 | 2.9963e-07 | 8.4199e-07 | 3.0265e-07 | 8.505e-07
1410 | feeder2_line38 | 1 | 99 | 3.2398e-07 | 7.7528e-07 | 3.2725e-07 | 7.8311e-07
1410 | feeder2_line38 | 2 | 99 | 1.9444 | 1.9444 | 1.964 | 1.964
1410 | feeder2_line38 | 3 | 99 | 3.2447e-07 | 7.7652e-07 | 3.2775e-07 | 7.8437e-07
1410 | feeder2_line39 | 1 | 266.4 | 25.5272 | 25.5268 | 9.5823 | 9.5822
1410 | feeder2_line39 | 2 | 266.4 | 3.4162 | 3.4158 | 1.2824 | 1.2822
1410 | feeder2_line39 | 3 | 266.4 | 3.6829 | 3.6825 | 1.3825 | 1.3823
1410 | feeder2_line40 | 1 | 354.6 | 82.1256 | 82.12 | 23.1601 | 23.1585
1410 | feeder2_line40 | 2 | 354.6 | 81.6599 | 81.649 | 23.0287 | 23.0257
1410 | feeder2_line40 | 3 | 354.6 | 72.543 | 72.5581 | 20.4577 | 20.4619
1410 | feeder2_line41 | 1 | 99 | 0.093835 | 0.093833 | 0.094783 | 0.094781
1410 | feeder2_line41 | 2 | 99 | 4.9643e-08 | 7.3749e-07 | 5.0144e-08 | 7.4494e-07
1410 | feeder2_line41 | 3 | 99 | 5.0165e-08 | 7.3582e-07 | 5.0672e-08 | 7.4325e-07
1410 | feeder2_line42 | 1 | 99 | 2.9889e-07 | 7.4812e-07 | 3.019e-07 | 7.5568e-07
1410 | feeder2_line42 | 2 | 99 | 2.9987e-07 | 7.5098e-07 | 3.029e-07 | 7.5856e-07
1410 | feeder2_line42 | 3 | 99 | 0.18992 | 0.18992 | 0.19183 | 0.19184
1410 | feeder2_line43 | 1 | 266.4 | 25.5271 | 25.5268 | 9.5822 | 9.5822
1410 | feeder2_line43 | 2 | 266.4 | 3.4161 | 3.4158 | 1.2823 | 1.2822
1410 | feeder2_line43 | 3 | 266.4 | 3.4929 | 3.4926 | 1.3111 | 1.311
1410 | feeder2_line44 | 1 | 354.6 | 82.1256 | 82.12 | 23.1601 | 23.1585
1410 | feeder2_line44 | 2 | 354.6 | 81.66 | 81.649 | 23.0288 | 23.0257
1410 | feeder2_line44 | 3 | 354.6 | 72.8966 | 72.9117 | 20.5574 | 20.5617
1410 | feeder2_line45 | 1 | 99 | 5.006e-08 | 5.7977e-07 | 5.0566e-08 | 5.8563e-07
1410 | feeder2_line45 | 2 | 99 | 4.9648e-08 | 5.817e-07 | 5.015e-08 | 5.8757e-07
1410 | feeder2_line45 | 3 | 99 | 0.35671 | 0.35676 | 0.36031 | 0.36037
1410 | feeder2_line46 | 1 | 99 | 5.7274e-07 | 1.3562e-06 | 5.7852e-07 | 1.3699e-06
1410 | feeder2_line46 | 2 | 99 | 5.7496e-07 | 1.3614e-06 | 5.8076e-07 | 1.3751e-06
1410 | feeder2_line46 | 3 | 99 | 0.16259 | 0.16263 | 0.16423 | 0.16427
1410 | feeder2_line47 | 1 | 266.4 | 25.5271 | 25.5268 | 9.5822 | 9.5822
1410 | feeder2_line47 | 2 | 266.4 | 3.4161 | 3.4158 | 1.2823 | 1.2822
1410 | feeder2_line47 | 3 | 266.4 | 3.3303 | 3.33 | 1.2501 | 1.25
1410 | feeder2_line48 | 1 | 99 | 0.13651 | 0.13651 | 0.13789 | 0.13789
1410 | feeder2_line48 | 2 | 99 | 4.9568e-08 | 7.33e-07 | 5.0069e-08 | 7.404e-07
1410 | feeder2_line48 | 3 | 99 | 5.0064e-08 | 7.316e-07 | 5.057e-08 | 7.3899e-07
1410 | feeder2_line49 | 1 | 266.4 | 25.3937 | 25.3935 | 9.5322 | 9.5321
1410 | feeder2_line49 | 2 | 266.4 | 3.4161 | 3.4158 | 1.2823 | 1.2822
1410 | feeder2_line49 | 3 | 266.4 | 3.3303 | 3.33 | 1.2501 | 1.25
1410 | feeder2_line50 | 1 | 99 | 5.726e-07 | 1.234e-06 | 5.7839e-07 | 1.2464e-06
1410 | feeder2_line50 | 2 | 99 | 1.9947 | 1.9946 | 2.0148 | 2.0148
1410 | feeder2_line50 | 3 | 99 | 5.7383e-07 | 1.2366e-06 | 5.7963e-07 | 1.2491e-06
1410 | feeder2_line51 | 1 | 99 | 13.7175 | 13.7175 | 13.8561 | 13.856
1410 | feeder2_line51 | 2 | 99 | 5.7493e-07 | 1.345e-06 | 5.8073e-07 | 1.3586e-06
1410 | feeder2_line51 | 3 | 99 | 5.7381e-07 | 1.3424e-06 | 5.7961e-07 | 1.356e-06
1410 | feeder2_line52 | 1 | 266.4 | 11.6762 | 11.6762 | 4.383 | 4.3829
1410 | feeder2_line52 | 2 | 266.4 | 1.4213 | 1.4212 | 0.53353 | 0.53349
1410 | feeder2_line52 | 3 | 266.4 | 3.3301 | 3.33 | 1.2501 | 1.25
1410 | feeder2_line53 | 1 | 99 | 5.4756e-07 | 7.531e-07 | 5.5309e-07 | 7.607e-07
1410 | feeder2_line53 | 2 | 99 | 1.4212 | 1.4212 | 1.4356 | 1.4356
1410 | feeder2_line53 | 3 | 99 | 5.488e-07 | 7.5472e-07 | 5.5435e-07 | 7.6235e-07
1410 | feeder2_line54 | 1 | 266.4 | 11.676 | 11.6762 | 4.3829 | 4.3829
1410 | feeder2_line54 | 2 | 266.4 | 8.5723e-05 | 4.6383e-06 | 3.2178e-05 | 1.7411e-06
1410 | feeder2_line54 | 3 | 266.4 | 3.33 | 3.33 | 1.25 | 1.25
1410 | feeder2_line55 | 1 | 99 | 0.181 | 0.181 | 0.18283 | 0.18282
1410 | feeder2_line55 | 2 | 99 | 4.9667e-08 | 7.3332e-07 | 5.0168e-08 | 7.4072e-07
1410 | feeder2_line55 | 3 | 99 | 5.0228e-08 | 7.3146e-07 | 5.0735e-08 | 7.3884e-07
1410 | feeder2_line56 | 1 | 354.6 | 82.3061 | 82.3004 | 23.211 | 23.2094
1410 | feeder2_line56 | 2 | 354.6 | 81.66 | 81.649 | 23.0288 | 23.0257
1410 | feeder2_line56 | 3 | 354.6 | 72.8967 | 72.9117 | 20.5574 | 20.5617
1410 | feeder2_line57 | 1 | 99 | 7.5101e-07 | 1.5425e-06 | 7.586e-07 | 1.5581e-06
1410 | feeder2_line57 | 2 | 99 | 7.4331e-07 | 1.5489e-06 | 7.5081e-07 | 1.5645e-06
1410 | feeder2_line57 | 3 | 99 | 3.33 | 3.33 | 3.3637 | 3.3636
1410 | feeder2_line58 | 1 | 266.4 | 11.6761 | 11.6762 | 4.3829 | 4.3829
1410 | feeder2_line58 | 2 | 266.4 | 1.9012e-05 | 2.6929e-06 | 7.1368e-06 | 1.0108e-06
1410 | feeder2_line58 | 3 | 266.4 | 1.8972e-05 | 2.6882e-06 | 7.1215e-06 | 1.0091e-06
1410 | feeder2_line59 | 1 | 99 | 5.0069e-08 | 5.3617e-07 | 5.0575e-08 | 5.4159e-07
1410 | feeder2_line59 | 2 | 99 | 4.9549e-08 | 5.3841e-07 | 5.005e-08 | 5.4385e-07
1410 | feeder2_line59 | 3 | 99 | 0.10823 | 0.10824 | 0.10932 | 0.10933
1410 | feeder2_line60 | 1 | 99 | 2.988e-07 | 8.1033e-07 | 3.0181e-07 | 8.1852e-07
1410 | feeder2_line60 | 2 | 99 | 2.9987e-07 | 8.137e-07 | 3.029e-07 | 8.2192e-07
1410 | feeder2_line60 | 3 | 99 | 3.2229 | 3.2229 | 3.2555 | 3.2554
1410 | feeder2_line61 | 1 | 266.4 | 1.3436 | 1.3438 | 0.50435 | 0.50441
1410 | feeder2_line61 | 2 | 266.4 | 3.9601 | 3.9602 | 1.4865 | 1.4866
1410 | feeder2_line61 | 3 | 266.4 | 0.38492 | 0.38515 | 0.14449 | 0.14457
1410 | feeder2_line62 | 1 | 354.6 | 83.6494 | 83.644 | 23.5898 | 23.5883
1410 | feeder2_line62 | 2 | 354.6 | 85.2607 | 85.2499 | 24.0442 | 24.0411
1410 | feeder2_line62 | 3 | 354.6 | 73.2791 | 73.2944 | 20.6653 | 20.6696
1410 | feeder2_line63 | 1 | 99 | 2.2993 | 2.2993 | 2.3226 | 2.3225
1410 | feeder2_line63 | 2 | 99 | 5.7498e-07 | 1.2234e-06 | 5.8079e-07 | 1.2358e-06
1410 | feeder2_line63 | 3 | 99 | 5.7385e-07 | 1.2211e-06 | 5.7964e-07 | 1.2334e-06
1410 | feeder2_line64 | 1 | 99 | 9.3768 | 9.3768 | 9.4715 | 9.4716
1410 | feeder2_line64 | 2 | 99 | 6.564e-12 | 3.2227e-07 | 6.6303e-12 | 3.2553e-07
1410 | feeder2_line64 | 3 | 99 | 4.4353e-12 | 3.2165e-07 | 4.4801e-12 | 3.249e-07
1410 | feeder2_line65 | 1 | 99 | 5.0108e-08 | 6.4262e-07 | 5.0614e-08 | 6.4911e-07
1410 | feeder2_line65 | 2 | 99 | 0.27961 | 0.2796 | 0.28243 | 0.28242
1410 | feeder2_line65 | 3 | 99 | 5.0312e-08 | 6.4286e-07 | 5.082e-08 | 6.4936e-07
1410 | feeder2_line66 | 1 | 354.6 | 83.6494 | 83.644 | 23.5898 | 23.5883
1410 | feeder2_line66 | 2 | 354.6 | 85.539 | 85.5282 | 24.1227 | 24.1196
1410 | feeder2_line66 | 3 | 354.6 | 73.279 | 73.2944 | 20.6653 | 20.6696
1410 | feeder2_line67 | 1 | 99 | 2.5052e-08 | 3.631e-07 | 2.5305e-08 | 3.6677e-07
1410 | feeder2_line67 | 2 | 99 | 2.485e-08 | 3.6429e-07 | 2.5101e-08 | 3.6797e-07
1410 | feeder2_line67 | 3 | 99 | 0.093711 | 0.09372 | 0.094658 | 0.094667
1410 | feeder2_line68 | 1 | 266.4 | 1.3436 | 1.3438 | 0.50437 | 0.50441
1410 | feeder2_line68 | 2 | 266.4 | 3.9602 | 3.9602 | 1.4866 | 1.4866
1410 | feeder2_line68 | 3 | 266.4 | 0.29132 | 0.29149 | 0.10935 | 0.10942
1410 | feeder2_line69 | 1 | 99 | 4.6758 | 4.6758 | 4.723 | 4.723
1410 | feeder2_line69 | 2 | 99 | 2.5611e-06 | 6.6948e-07 | 2.5869e-06 | 6.7625e-07
1410 | feeder2_line69 | 3 | 99 | 2.5481e-06 | 6.6746e-07 | 2.5739e-06 | 6.7421e-07
1410 | feeder2_line70 | 1 | 354.6 | 88.3008 | 88.2955 | 24.9015 | 24.9
1410 | feeder2_line70 | 2 | 354.6 | 85.5389 | 85.5282 | 24.1226 | 24.1196
1410 | feeder2_line70 | 3 | 354.6 | 73.2789 | 73.2944 | 20.6652 | 20.6696
1410 | feeder2_line71 | 1 | 99 | 5.012e-08 | 7.172e-07 | 5.0627e-08 | 7.2445e-07
1410 | feeder2_line71 | 2 | 99 | 0.32461 | 0.32453 | 0.32789 | 0.32781
1410 | feeder2_line71 | 3 | 99 | 5.0347e-08 | 7.1736e-07 | 5.0855e-08 | 7.2461e-07
1410 | feeder2_line72 | 1 | 354.6 | 88.3009 | 88.2955 | 24.9015 | 24.9
1410 | feeder2_line72 | 2 | 354.6 | 85.8615 | 85.8507 | 24.2136 | 24.2106
1410 | feeder2_line72 | 3 | 354.6 | 73.279 | 73.2944 | 20.6653 | 20.6696
1410 | feeder2_line73 | 1 | 99 | 5.9947e-07 | 1.5372e-06 | 6.0552e-07 | 1.5527e-06
1410 | feeder2_line73 | 2 | 99 | 2.5891 | 2.5891 | 2.6152 | 2.6152
1410 | feeder2_line73 | 3 | 99 | 5.9988e-07 | 1.5381e-06 | 6.0594e-07 | 1.5536e-06
1410 | feeder2_line74 | 1 | 99 | 5.0087e-08 | 4.5849e-07 | 5.0593e-08 | 4.6312e-07
1410 | feeder2_line74 | 2 | 99 | 0.29155 | 0.2915 | 0.2945 | 0.29444
1410 | feeder2_line74 | 3 | 99 | 5.0266e-08 | 4.5875e-07 | 5.0774e-08 | 4.6339e-07
1410 | feeder2_line75 | 1 | 266.4 | 1.3437 | 1.3438 | 0.5044 | 0.50441
1410 | feeder2_line75 | 2 | 266.4 | 1.4808 | 1.4808 | 0.55586 | 0.55587
1410 | feeder2_line75 | 3 | 266.4 | 0.29142 | 0.29149 | 0.10939 | 0.10942
1410 | feeder2_line76 | 1 | 99 | 1.3438 | 1.3438 | 1.3573 | 1.3573
1410 | feeder2_line76 | 2 | 99 | 8.5204e-07 | 1.5908e-06 | 8.6065e-07 | 1.6069e-06
1410 | feeder2_line76 | 3 | 99 | 8.4957e-07 | 1.5866e-06 | 8.5815e-07 | 1.6027e-06
1410 | feeder2_line77 | 1 | 99 | 2.5046e-08 | 5.7615e-07 | 2.5299e-08 | 5.8197e-07
1410 | feeder2_line77 | 2 | 99 | 2.4849e-08 | 5.7802e-07 | 2.51e-08 | 5.8386e-07
1410 | feeder2_line77 | 3 | 99 | 0.29145 | 0.29149 | 0.29439 | 0.29444
1410 | feeder2_line78 | 1 | 266.4 | 3.4396e-12 | 9.5563e-07 | 1.2911e-12 | 3.5872e-07
1410 | feeder2_line78 | 2 | 266.4 | 1.4808 | 1.4808 | 0.55587 | 0.55587
1410 | feeder2_line78 | 3 | 266.4 | 3.9144e-12 | 9.5627e-07 | 1.4694e-12 | 3.5896e-07
1410 | feeder2_line79 | 1 | 354.6 | 3.2469 | 3.2465 | 0.91565 | 0.91554
1410 | feeder2_line79 | 2 | 354.6 | 4.494 | 4.4936 | 1.2673 | 1.2672
1410 | feeder2_line79 | 3 | 354.6 | 17.3818 | 17.3812 | 4.9018 | 4.9016
1410 | feeder2_line80 | 1 | 354.6 | 91.4658 | 91.4598 | 25.7941 | 25.7924
1410 | feeder2_line80 | 2 | 354.6 | 89.6645 | 89.6531 | 25.2861 | 25.2829
1410 | feeder2_line80 | 3 | 354.6 | 89.7491 | 89.7637 | 25.3099 | 25.3141
1410 | feeder2_line81 | 1 | 354.6 | 91.4657 | 91.4598 | 25.7941 | 25.7924
1410 | feeder2_line81 | 2 | 354.6 | 89.6645 | 89.6531 | 25.2861 | 25.2829
1410 | feeder2_line81 | 3 | 354.6 | 90.7353 | 90.75 | 25.5881 | 25.5922
1410 | feeder2_line82 | 1 | 354.6 | 1.6606e-11 | 7.3612e-07 | 4.6831e-12 | 2.0759e-07
1410 | feeder2_line82 | 2 | 354.6 | 3.5773e-11 | 7.3827e-07 | 1.0088e-11 | 2.082e-07
1410 | feeder2_line82 | 3 | 354.6 | 0.9869 | 0.98693 | 0.27831 | 0.27832
1410 | feeder2_line83 | 1 | 354.6 | 91.4659 | 91.4598 | 25.7941 | 25.7924
1410 | feeder2_line83 | 2 | 354.6 | 89.78 | 89.7684 | 25.3187 | 25.3154
1410 | feeder2_line83 | 3 | 354.6 | 90.7355 | 90.75 | 25.5881 | 25.5922
1410 | feeder2_line84 | 1 | 354.6 | 1.7162e-11 | 1.3013e-06 | 4.8398e-12 | 3.6696e-07
1410 | feeder2_line84 | 2 | 354.6 | 0.11565 | 0.11559 | 0.032615 | 0.032596
1410 | feeder2_line84 | 3 | 354.6 | 1.461e-11 | 1.3013e-06 | 4.1201e-12 | 3.6697e-07
1410 | feeder2_line85 | 1 | 99 | 1.9444 | 1.9444 | 1.964 | 1.964
1410 | feeder2_line85 | 2 | 99 | 4.976e-08 | 4.6597e-07 | 5.0263e-08 | 4.7068e-07
1410 | feeder2_line85 | 3 | 99 | 5.0426e-08 | 4.644e-07 | 5.0935e-08 | 4.6909e-07
1410 | feeder2_line86 | 1 | 354.6 | 93.0438 | 93.0375 | 26.2391 | 26.2373
1410 | feeder2_line86 | 2 | 354.6 | 89.7801 | 89.7684 | 25.3187 | 25.3154
1410 | feeder2_line86 | 3 | 354.6 | 90.7356 | 90.75 | 25.5881 | 25.5922
1410 | feeder2_line87 | 1 | 354.6 | 93.044 | 93.0375 | 26.2391 | 26.2373
1410 | feeder2_line87 | 2 | 354.6 | 92.5098 | 92.4977 | 26.0885 | 26.0851
1410 | feeder2_line87 | 3 | 354.6 | 91.7854 | 91.7996 | 25.8842 | 25.8882
1410 | feeder2_line88 | 1 | 354.6 | 0.00011479 | 3.3733e-06 | 3.2373e-05 | 9.5129e-07
1410 | feeder2_line88 | 2 | 354.6 | 2.9077 | 2.9074 | 0.82 | 0.81991
1410 | feeder2_line88 | 3 | 354.6 | 1.05 | 1.0499 | 0.2961 | 0.29609
1410 | feeder2_line89 | 1 | 354.6 | 93.0417 | 93.0375 | 26.2385 | 26.2373
1410 | feeder2_line89 | 2 | 354.6 | 94.9449 | 94.935 | 26.7752 | 26.7724
1410 | feeder2_line89 | 3 | 354.6 | 91.7831 | 91.7996 | 25.8836 | 25.8882
1410 | feeder2_line90 | 1 | 354.6 | 0.00072626 | 2.0368e-06 | 0.00020481 | 5.744e-07
1410 | feeder2_line90 | 2 | 354.6 | 2.437 | 2.4374 | 0.68725 | 0.68736
1410 | feeder2_line90 | 3 | 354.6 | 0.00072475 | 2.0365e-06 | 0.00020439 | 5.7431e-07
1410 | feeder2_line91 | 1 | 354.6 | 93.0416 | 93.0375 | 26.2385 | 26.2373
1410 | feeder2_line91 | 2 | 354.6 | 94.9448 | 94.935 | 26.7752 | 26.7724
1410 | feeder2_line91 | 3 | 354.6 | 95.0027 | 95.0193 | 26.7915 | 26.7962
1410 | feeder2_line92 | 1 | 354.6 | 5.3833e-12 | 1.0276e-06 | 1.5181e-12 | 2.8978e-07
1410 | feeder2_line92 | 2 | 354.6 | 1.7407e-11 | 1.0306e-06 | 4.909e-12 | 2.9064e-07
1410 | feeder2_line92 | 3 | 354.6 | 3.2255 | 3.2254 | 0.90961 | 0.90959
1410 | feeder2_line93 | 1 | 99 | 2.5096e-08 | 3.4298e-07 | 2.535e-08 | 3.4645e-07
1410 | feeder2_line93 | 2 | 99 | 0.11558 | 0.11551 | 0.11675 | 0.11668
1410 | feeder2_line93 | 3 | 99 | 2.5235e-08 | 3.4292e-07 | 2.549e-08 | 3.4638e-07
1410 | feeder2_line94 | 1 | 354.6 | 2.5096e-06 | 1.6699e-06 | 7.0772e-07 | 4.7093e-07
1410 | feeder2_line94 | 2 | 354.6 | 2.3224 | 2.3224 | 0.65495 | 0.65493
1410 | feeder2_line94 | 3 | 354.6 | 2.5233e-06 | 1.6699e-06 | 7.1159e-07 | 4.7092e-07
1410 | feeder2_line95 | 1 | 99 | 3.574e-06 | 2.6161e-06 | 3.6101e-06 | 2.6425e-06
1410 | feeder2_line95 | 2 | 99 | 2.9076 | 2.9074 | 2.937 | 2.9368
1410 | feeder2_line95 | 3 | 99 | 3.5755e-06 | 2.6157e-06 | 3.6116e-06 | 2.6421e-06
1410 | feeder2_line96 | 1 | 354.6 | 0.00012142 | 6.2362e-07 | 3.4241e-05 | 1.7587e-07
1410 | feeder2_line96 | 2 | 354.6 | 0.00012185 | 6.2565e-07 | 3.4361e-05 | 1.7644e-07
1410 | feeder2_line96 | 3 | 354.6 | 1.0499 | 1.0499 | 0.29609 | 0.29609
1410 | feeder2_line97 | 1 | 354.6 | 93.1955 | 93.1913 | 26.2819 | 26.2807
1410 | feeder2_line97 | 2 | 354.6 | 94.945 | 94.935 | 26.7752 | 26.7724
1410 | feeder2_line97 | 3 | 354.6 | 95.0028 | 95.0193 | 26.7916 | 26.7962
1410 | feeder2_line98 | 1 | 354.6 | 0.15649 | 0.15482 | 0.044131 | 0.043659
1410 | feeder2_line98 | 2 | 354.6 | 0.0017157 | 6.2156e-07 | 0.00048383 | 1.7528e-07
1410 | feeder2_line98 | 3 | 354.6 | 0.0016991 | 6.2589e-07 | 0.00047917 | 1.7651e-07
1410 | feeder2_line99 | 1 | 99 | 2.5085e-08 | 4.4832e-07 | 2.5338e-08 | 4.5285e-07
1410 | feeder2_line99 | 2 | 99 | 2.4893e-08 | 4.4975e-07 | 2.5145e-08 | 4.543e-07
1410 | feeder2_line99 | 3 | 99 | 1.0499 | 1.0499 | 1.0605 | 1.0605
1410 | feeder2_line100 | 1 | 99 | 0.15478 | 0.15482 | 0.15634 | 0.15638
1410 | feeder2_line100 | 2 | 99 | 2.4907e-08 | 6.178e-07 | 2.5159e-08 | 6.2404e-07
1410 | feeder2_line100 | 3 | 99 | 2.5243e-08 | 6.157e-07 | 2.5498e-08 | 6.2192e-07
1410 | feeder2_line101 | 1 | 354.6 | 2.3205 | 2.3202 | 0.65441 | 0.6543
1410 | feeder2_line101 | 2 | 354.6 | 4.494 | 4.4936 | 1.2673 | 1.2672
1410 | feeder2_line101 | 3 | 354.6 | 17.3818 | 17.3812 | 4.9018 | 4.9016
1410 | feeder2_line102 | 1 | 99 | 1.0921 | 1.0921 | 1.1031 | 1.1031
1410 | feeder2_line102 | 2 | 99 | 2.3517e-06 | 8.8289e-07 | 2.3755e-06 | 8.9181e-07
1410 | feeder2_line102 | 3 | 99 | 2.3331e-06 | 8.7968e-07 | 2.3567e-06 | 8.8857e-07
1410 | feeder2_line103 | 1 | 99 | 5.5036e-07 | 8.0545e-07 | 5.5592e-07 | 8.1359e-07
1410 | feeder2_line103 | 2 | 99 | 0.09619 | 0.096184 | 0.097161 | 0.097156
1410 | feeder2_line103 | 3 | 99 | 5.4993e-07 | 8.051e-07 | 5.5549e-07 | 8.1323e-07
1410 | feeder2_line104 | 1 | 354.6 | 2.3204 | 2.3202 | 0.65438 | 0.6543
1410 | feeder2_line104 | 2 | 354.6 | 4.4158 | 4.4155 | 1.2453 | 1.2452
1410 | feeder2_line104 | 3 | 354.6 | 17.3817 | 17.3812 | 4.9018 | 4.9016
1410 | feeder2_line105 | 1 | 99 | 2.5514e-06 | 7.4112e-07 | 2.5772e-06 | 7.4861e-07
1410 | feeder2_line105 | 2 | 99 | 2.5635e-06 | 7.4357e-07 | 2.5894e-06 | 7.5108e-07
1410 | feeder2_line105 | 3 | 99 | 1.6534 | 1.6535 | 1.6701 | 1.6702
1410 | feeder2_line106 | 1 | 354.6 | 2.3204 | 2.3202 | 0.65437 | 0.6543
1410 | feeder2_line106 | 2 | 354.6 | 4.4157 | 4.4155 | 1.2453 | 1.2452
1410 | feeder2_line106 | 3 | 354.6 | 15.7845 | 15.784 | 4.4513 | 4.4512
1410 | feeder2_line107 | 1 | 99 | 3.2527e-07 | 9.0318e-07 | 3.2856e-07 | 9.123e-07
1410 | feeder2_line107 | 2 | 99 | 2.1344 | 2.1345 | 2.156 | 2.156
1410 | feeder2_line107 | 3 | 99 | 3.2534e-07 | 9.0257e-07 | 3.2862e-07 | 9.1169e-07
1410 | feeder2_line108 | 1 | 354.6 | 2.3204 | 2.3202 | 0.65436 | 0.6543
1410 | feeder2_line108 | 2 | 354.6 | 2.6584 | 2.6581 | 0.74969 | 0.74961
1410 | feeder2_line108 | 3 | 354.6 | 15.7845 | 15.784 | 4.4513 | 4.4512
1410 | feeder2_line109 | 1 | 354.6 | 94.3692 | 94.3637 | 26.6129 | 26.6113
1410 | feeder2_line109 | 2 | 354.6 | 94.9462 | 94.935 | 26.7756 | 26.7724
1410 | feeder2_line109 | 3 | 354.6 | 95.0041 | 95.0193 | 26.7919 | 26.7962
1410 | feeder2_line110 | 1 | 99 | 1.2041 | 1.2033 | 1.2162 | 1.2154
1410 | feeder2_line110 | 2 | 99 | 0.00081065 | 9.1494e-07 | 0.00081884 | 9.2418e-07
1410 | feeder2_line110 | 3 | 99 | 0.00080559 | 9.1155e-07 | 0.00081373 | 9.2076e-07
1410 | feeder2_line111 | 1 | 99 | 2.5088e-08 | 3.829e-07 | 2.5341e-08 | 3.8677e-07
1410 | feeder2_line111 | 2 | 99 | 2.8693 | 2.8692 | 2.8983 | 2.8982
1410 | feeder2_line111 | 3 | 99 | 2.5221e-08 | 3.8284e-07 | 2.5476e-08 | 3.8671e-07
1410 | feeder2_line112 | 1 | 99 | 3.2558e-07 | 9.2011e-07 | 3.2887e-07 | 9.2941e-07
1410 | feeder2_line112 | 2 | 99 | 0.040589 | 0.040424 | 0.040999 | 0.040832
1410 | feeder2_line112 | 3 | 99 | 3.2574e-07 | 9.1999e-07 | 3.2903e-07 | 9.2928e-07
1410 | feeder2_line113 | 1 | 99 | 1.1017 | 1.1017 | 1.1128 | 1.1128
1410 | feeder2_line113 | 2 | 99 | 3.2662e-07 | 9.1122e-07 | 3.2992e-07 | 9.2043e-07
1410 | feeder2_line113 | 3 | 99 | 3.2612e-07 | 9.0812e-07 | 3.2941e-07 | 9.1729e-07
1410 | feeder2_line114 | 1 | 99 | 0.096466 | 0.096463 | 0.09744 | 0.097438
1410 | feeder2_line114 | 2 | 99 | 2.4858e-08 | 4.3903e-07 | 2.5109e-08 | 4.4346e-07
1410 | feeder2_line114 | 3 | 99 | 2.5207e-08 | 4.3743e-07 | 2.5462e-08 | 4.4185e-07
1410 | feeder2_line115 | 1 | 99 | 2.5044e-08 | 5.6364e-07 | 2.5297e-08 | 5.6933e-07
1410 | feeder2_line115 | 2 | 99 | 2.0299 | 2.0299 | 2.0504 | 2.0504
1410 | feeder2_line115 | 3 | 99 | 2.5224e-08 | 5.6315e-07 | 2.5479e-08 | 5.6884e-07
1410 | feeder2_line116 | 1 | 354.6 | 2.3204 | 2.3202 | 0.65437 | 0.6543
1410 | feeder2_line116 | 2 | 354.6 | 0.85929 | 0.85912 | 0.24233 | 0.24228
1410 | feeder2_line116 | 3 | 354.6 | 15.7845 | 15.784 | 4.4513 | 4.4512
1410 | feeder2_line117 | 1 | 99 | 5.0257e-08 | 6.4505e-07 | 5.0765e-08 | 6.5157e-07
1410 | feeder2_line117 | 2 | 99 | 0.16235 | 0.16225 | 0.16399 | 0.16389
1410 | feeder2_line117 | 3 | 99 | 5.0538e-08 | 6.4494e-07 | 5.1048e-08 | 6.5145e-07
1410 | feeder2_line118 | 1 | 354.6 | 94.3692 | 94.3637 | 26.6129 | 26.6113
1410 | feeder2_line118 | 2 | 354.6 | 95.1084 | 95.097 | 26.8213 | 26.8181
1410 | feeder2_line118 | 3 | 354.6 | 95.0041 | 95.0193 | 26.7919 | 26.7962
1410 | feeder2_line119 | 1 | 99 | 2.5043e-08 | 6.0649e-07 | 2.5296e-08 | 6.1262e-07
1410 | feeder2_line119 | 2 | 99 | 2.4842e-08 | 6.0855e-07 | 2.5093e-08 | 6.147e-07
1410 | feeder2_line119 | 3 | 99 | 0.54543 | 0.54545 | 0.55094 | 0.55096
1410 | feeder2_line120 | 1 | 354.6 | 2.3204 | 2.3202 | 0.65437 | 0.6543
1410 | feeder2_line120 | 2 | 354.6 | 0.85929 | 0.85912 | 0.24233 | 0.24228
1410 | feeder2_line120 | 3 | 354.6 | 15.2561 | 15.2556 | 4.3023 | 4.3022
1410 | feeder2_line121 | 1 | 99 | 3.2525e-07 | 9.3917e-07 | 3.2854e-07 | 9.4865e-07
1410 | feeder2_line121 | 2 | 99 | 0.74339 | 0.7434 | 0.7509 | 0.7509
1410 | feeder2_line121 | 3 | 99 | 3.2519e-07 | 9.3797e-07 | 3.2848e-07 | 9.4745e-07
1410 | feeder2_line122 | 1 | 354.6 | 2.3204 | 2.3202 | 0.65436 | 0.6543
1410 | feeder2_line122 | 2 | 354.6 | 0.17937 | 0.17912 | 0.050583 | 0.050513
1410 | feeder2_line122 | 3 | 354.6 | 15.2561 | 15.2556 | 4.3023 | 4.3022
1410 | feeder2_line123 | 1 | 99 | 5.7542e-07 | 9.7319e-07 | 5.8124e-07 | 9.8302e-07
1410 | feeder2_line123 | 2 | 99 | 5.7745e-07 | 9.766e-07 | 5.8328e-07 | 9.8647e-07
1410 | feeder2_line123 | 3 | 99 | 2.4663 | 2.4662 | 2.4912 | 2.4911
1410 | feeder2_line124 | 1 | 354.6 | 2.3203 | 2.3202 | 0.65434 | 0.6543
1410 | feeder2_line124 | 2 | 354.6 | 0.17928 | 0.17912 | 0.050557 | 0.050513
1410 | feeder2_line124 | 3 | 354.6 | 13.0594 | 13.0589 | 3.6829 | 3.6827
1410 | feeder2_line125 | 1 | 99 | 5.7542e-07 | 9.0469e-07 | 5.8123e-07 | 9.1382e-07
1410 | feeder2_line125 | 2 | 99 | 5.7747e-07 | 9.0787e-07 | 5.833e-07 | 9.1704e-07
1410 | feeder2_line125 | 3 | 99 | 0.15522 | 0.15528 | 0.15679 | 0.15685
1410 | feeder2_line126 | 1 | 354.6 | 2.3204 | 2.3202 | 0.65438 | 0.6543
1410 | feeder2_line126 | 2 | 354.6 | 0.17943 | 0.17912 | 0.050602 | 0.050513
1410 | feeder2_line126 | 3 | 354.6 | 12.9138 | 12.9131 | 3.6418 | 3.6416
1410 | feeder2_line127 | 1 | 99 | 5.754e-07 | 1.083e-06 | 5.8122e-07 | 1.094e-06
1410 | feeder2_line127 | 2 | 99 | 5.7747e-07 | 1.0869e-06 | 5.833e-07 | 1.0979e-06
1410 | feeder2_line127 | 3 | 99 | 10.9709 | 10.9705 | 11.0817 | 11.0813
1410 | feeder2_line128 | 1 | 354.6 | 2.3203 | 2.3202 | 0.65436 | 0.6543
1410 | feeder2_line128 | 2 | 354.6 | 0.17935 | 0.17912 | 0.050578 | 0.050513
1410 | feeder2_line128 | 3 | 354.6 | 2.0837 | 2.0835 | 0.58763 | 0.58756
1410 | feeder2_line129 | 1 | 99 | 5.5039e-07 | 8.7819e-07 | 5.5595e-07 | 8.8706e-07
1410 | feeder2_line129 | 2 | 99 | 0.17913 | 0.17912 | 0.18094 | 0.18093
1410 | feeder2_line129 | 3 | 99 | 5.4927e-07 | 8.7686e-07 | 5.5481e-07 | 8.8572e-07
1410 | feeder2_line130 | 1 | 354.6 | 2.3204 | 2.3202 | 0.65436 | 0.6543
1410 | feeder2_line130 | 2 | 354.6 | 0.00031015 | 4.6632e-06 | 8.7465e-05 | 1.3151e-06
1410 | feeder2_line130 | 3 | 354.6 | 2.0838 | 2.0835 | 0.58764 | 0.58756
1410 | feeder2_line131 | 1 | 99 | 5.754e-07 | 9.7332e-07 | 5.8122e-07 | 9.8315e-07
1410 | feeder2_line131 | 2 | 99 | 5.7749e-07 | 9.7682e-07 | 5.8333e-07 | 9.8669e-07
1410 | feeder2_line131 | 3 | 99 | 0.16238 | 0.16239 | 0.16402 | 0.16403
1410 | feeder2_line132 | 1 | 354.6 | 2.3202 | 2.3202 | 0.65431 | 0.6543
1410 | feeder2_line132 | 2 | 354.6 | 0.00012654 | 2.9319e-06 | 3.5686e-05 | 8.2681e-07
1410 | feeder2_line132 | 3 | 354.6 | 1.9438 | 1.9437 | 0.54816 | 0.54813
1410 | feeder2_line133 | 1 | 99 | 2.3201 | 2.3202 | 2.3436 | 2.3436
1410 | feeder2_line133 | 2 | 99 | 3.0116e-07 | 9.8462e-07 | 3.042e-07 | 9.9456e-07
1410 | feeder2_line133 | 3 | 99 | 2.9988e-07 | 9.7961e-07 | 3.0291e-07 | 9.895e-07
1410 | feeder2_line134 | 1 | 354.6 | 7.3652e-12 | 1.7892e-06 | 2.077e-12 | 5.0456e-07
1410 | feeder2_line134 | 2 | 354.6 | 7.6794e-12 | 1.7951e-06 | 2.1656e-12 | 5.0623e-07
1410 | feeder2_line134 | 3 | 354.6 | 1.9437 | 1.9437 | 0.54813 | 0.54813
1410 | feeder2_line135 | 1 | 99 | 0.3245 | 0.32453 | 0.32777 | 0.3278
1410 | feeder2_line135 | 2 | 99 | 4.9889e-08 | 5.8998e-07 | 5.0393e-08 | 5.9594e-07
1410 | feeder2_line135 | 3 | 99 | 5.0571e-08 | 5.8794e-07 | 5.1082e-08 | 5.9388e-07
1410 | feeder2_line136 | 1 | 354.6 | 94.6933 | 94.6878 | 26.7042 | 26.7027
1410 | feeder2_line136 | 2 | 354.6 | 95.1083 | 95.097 | 26.8213 | 26.8181
1410 | feeder2_line136 | 3 | 354.6 | 95.0041 | 95.0193 | 26.7919 | 26.7962
1410 | feeder2_line137 | 1 | 99 | 0.83298 | 0.83295 | 0.84139 | 0.84136
1410 | feeder2_line137 | 2 | 99 | 8.5642e-07 | 1.5892e-06 | 8.6507e-07 | 1.6052e-06
1410 | feeder2_line137 | 3 | 99 | 8.5319e-07 | 1.5837e-06 | 8.6181e-07 | 1.5997e-06
1410 | feeder2_line138 | 1 | 354.6 | 95.1908 | 95.1853 | 26.8446 | 26.843
1410 | feeder2_line138 | 2 | 354.6 | 95.1084 | 95.097 | 26.8213 | 26.8181
1410 | feeder2_line138 | 3 | 354.6 | 95.0041 | 95.0193 | 26.7919 | 26.7962
1410 | feeder2_line139 | 1 | 99 | 5.0304e-08 | 4.9363e-07 | 5.0813e-08 | 4.9862e-07
1410 | feeder2_line139 | 2 | 99 | 4.99e-08 | 4.9523e-07 | 5.0404e-08 | 5.0024e-07
1410 | feeder2_line139 | 3 | 99 | 1.3338 | 1.3344 | 1.3473 | 1.3479
1410 | feeder2_line140 | 1 | 354.6 | 95.1909 | 95.1853 | 26.8446 | 26.843
1410 | feeder2_line140 | 2 | 354.6 | 95.1085 | 95.097 | 26.8213 | 26.8181
1410 | feeder2_line140 | 3 | 354.6 | 95.7978 | 95.8139 | 27.0157 | 27.0203
1410 | feeder2_line141 | 1 | 99 | 2.5357e-06 | 4.8836e-07 | 2.5613e-06 | 4.9329e-07
1410 | feeder2_line141 | 2 | 99 | 0.18985 | 0.18984 | 0.19177 | 0.19176
1410 | feeder2_line141 | 3 | 99 | 2.533e-06 | 4.8826e-07 | 2.5586e-06 | 4.9319e-07
1410 | feeder2_line142 | 1 | 354.6 | 95.1907 | 95.1853 | 26.8445 | 26.843
1410 | feeder2_line142 | 2 | 354.6 | 95.298 | 95.2867 | 26.8748 | 26.8716
1410 | feeder2_line142 | 3 | 354.6 | 95.7976 | 95.8139 | 27.0157 | 27.0203
1410 | feeder2_line143 | 1 | 99 | 8.5386e-07 | 1.7354e-06 | 8.6248e-07 | 1.753e-06
1410 | feeder2_line143 | 2 | 99 | 2.1372 | 2.1372 | 2.1588 | 2.1588
1410 | feeder2_line143 | 3 | 99 | 8.5359e-07 | 1.7351e-06 | 8.6222e-07 | 1.7526e-06
1410 | feeder2_line144 | 1 | 354.6 | 95.1906 | 95.1853 | 26.8445 | 26.843
1410 | feeder2_line144 | 2 | 354.6 | 96.4729 | 96.4618 | 27.2061 | 27.203
1410 | feeder2_line144 | 3 | 354.6 | 95.7975 | 95.8139 | 27.0156 | 27.0203
1410 | feeder2_line145 | 1 | 99 | 2.5159e-08 | 4.8665e-07 | 2.5413e-08 | 4.9156e-07
1410 | feeder2_line145 | 2 | 99 | 0.98381 | 0.98378 | 0.99375 | 0.99372
1410 | feeder2_line145 | 3 | 99 | 2.5305e-08 | 4.8654e-07 | 2.5561e-08 | 4.9146e-07
1410 | feeder2_line146 | 1 | 354.6 | 95.1904 | 95.1853 | 26.8445 | 26.843
1410 | feeder2_line146 | 2 | 354.6 | 97.4565 | 97.4454 | 27.4835 | 27.4804
1410 | feeder2_line146 | 3 | 354.6 | 95.7973 | 95.8139 | 27.0156 | 27.0203
1410 | feeder2_line147 | 1 | 99 | 0.10762 | 0.10761 | 0.1087 | 0.1087
1410 | feeder2_line147 | 2 | 99 | 1.1593e-06 | 2.2521e-06 | 1.171e-06 | 2.2748e-06
1410 | feeder2_line147 | 3 | 99 | 1.1552e-06 | 2.2443e-06 | 1.1669e-06 | 2.267e-06
1410 | feeder2_line148 | 1 | 99 | 1.7048 | 1.7048 | 1.722 | 1.722
1410 | feeder2_line148 | 2 | 99 | 6.046e-07 | 1.5091e-06 | 6.1071e-07 | 1.5243e-06
1410 | feeder2_line148 | 3 | 99 | 6.029e-07 | 1.5038e-06 | 6.0899e-07 | 1.519e-06
1410 | feeder2_line149 | 1 | 354.6 | 97.0024 | 96.9971 | 27.3554 | 27.3539
1410 | feeder2_line149 | 2 | 354.6 | 97.4567 | 97.4454 | 27.4835 | 27.4804
1410 | feeder2_line149 | 3 | 354.6 | 95.7975 | 95.8139 | 27.0157 | 27.0203
1410 | feeder2_line150 | 1 | 354.6 | 97.0025 | 96.9971 | 27.3555 | 27.3539
1410 | feeder2_line150 | 2 | 354.6 | 98.3915 | 98.3803 | 27.7472 | 27.744
1410 | feeder2_line150 | 3 | 354.6 | 95.7976 | 95.8139 | 27.0157 | 27.0203
1410 | feeder2_line151 | 1 | 99 | 9.8038e-06 | 1.787e-06 | 9.9029e-06 | 1.8051e-06
1410 | feeder2_line151 | 2 | 99 | 1.532 | 1.532 | 1.5474 | 1.5475
1410 | feeder2_line151 | 3 | 99 | 9.7861e-06 | 1.7866e-06 | 9.885e-06 | 1.8046e-06
1410 | feeder2_line152 | 1 | 354.6 | 1.8905e-11 | 1.1912e-06 | 5.3312e-12 | 3.3594e-07
1410 | feeder2_line152 | 2 | 354.6 | 1.1356e-11 | 1.1948e-06 | 3.2025e-12 | 3.3695e-07
1410 | feeder2_line152 | 3 | 354.6 | 0.076648 | 0.076659 | 0.021615 | 0.021618
1410 | feeder2_line153 | 1 | 99 | 0.74329 | 0.74329 | 0.7508 | 0.7508
1410 | feeder2_line153 | 2 | 99 | 4.9968e-08 | 5.9794e-07 | 5.0473e-08 | 6.0398e-07
1410 | feeder2_line153 | 3 | 99 | 5.0669e-08 | 5.9582e-07 | 5.118e-08 | 6.0184e-07
1410 | feeder2_line154 | 1 | 99 | 5.7829e-07 | 8.8684e-07 | 5.8414e-07 | 8.958e-07
1410 | feeder2_line154 | 2 | 99 | 5.8021e-07 | 8.8975e-07 | 5.8607e-07 | 8.9874e-07
1410 | feeder2_line154 | 3 | 99 | 3.5494 | 3.5495 | 3.5853 | 3.5854
1410 | feeder2_line155 | 1 | 99 | 97.4249 | 97.4195 | 98.409 | 98.4036
1410 | feeder2_line155 | 2 | 99 | 98.3914 | 98.3803 | 99.3853 | 99.374
1410 | feeder2_line155 | 3 | 99 | 99 | 99.0164 | 100 | 100.0166
1410 | feeder2_line156 | 1 | 99 | 6.0321e-07 | 1.1669e-06 | 6.0931e-07 | 1.1787e-06
1410 | feeder2_line156 | 2 | 99 | 0.095945 | 0.095937 | 0.096914 | 0.096906
1410 | feeder2_line156 | 3 | 99 | 6.0321e-07 | 1.1666e-06 | 6.093e-07 | 1.1784e-06
1410 | feeder2_line157 | 1 | 99 | 2.5173e-08 | 2.5332e-07 | 2.5428e-08 | 2.5588e-07
1410 | feeder2_line157 | 2 | 99 | 1.4841 | 1.4841 | 1.4991 | 1.4991
1410 | feeder2_line157 | 3 | 99 | 2.5323e-08 | 2.5327e-07 | 2.5578e-08 | 2.5583e-07
1440 | feeder2_line1 | 1 | 354.6 | 55.7032 | 55.7166 | 15.7087 | 15.7125
1440 | feeder2_line1 | 2 | 354.6 | 70.634 | 70.6181 | 19.9194 | 19.9149
1440 | feeder2_line1 | 3 | 354.6 | 54.6303 | 54.6366 | 15.4062 | 15.408
1440 | feeder2_line2 | 1 | 354.6 | 56.6424 | 56.6555 | 15.9736 | 15.9773
1440 | feeder2_line2 | 2 | 354.6 | 70.6342 | 70.6181 | 19.9194 | 19.9149
1440 | feeder2_line2 | 3 | 354.6 | 54.6304 | 54.6366 | 15.4062 | 15.408
1440 | feeder2_line3 | 1 | 80.1 | 1.5728 | 1.5728 | 1.9635 | 1.9635
1440 | feeder2_line3 | 2 | 80.1 | 5.7226e-07 | 1.0575e-06 | 7.1443e-07 | 1.3202e-06
1440 | feeder2_line3 | 3 | 80.1 | 5.7178e-07 | 1.0567e-06 | 7.1384e-07 | 1.3192e-06
1440 | feeder2_line4 | 1 | 354.6 | 56.6425 | 56.6555 | 15.9736 | 15.9773
1440 | feeder2_line4 | 2 | 354.6 | 70.9089 | 70.8926 | 19.9969 | 19.9923
1440 | feeder2_line4 | 3 | 354.6 | 54.6306 | 54.6366 | 15.4063 | 15.408
1440 | feeder2_line5 | 1 | 80.1 | 5.719e-07 | 9.9791e-07 | 7.1398e-07 | 1.2458e-06
1440 | feeder2_line5 | 2 | 80.1 | 0.27931 | 0.27931 | 0.34871 | 0.3487
1440 | feeder2_line5 | 3 | 80.1 | 5.7181e-07 | 9.9777e-07 | 7.1387e-07 | 1.2457e-06
1440 | feeder2_line6 | 1 | 80.1 | 5.7195e-07 | 1.174e-06 | 7.1405e-07 | 1.4657e-06
1440 | feeder2_line6 | 2 | 80.1 | 5.7237e-07 | 1.1749e-06 | 7.1457e-07 | 1.4668e-06
1440 | feeder2_line6 | 3 | 80.1 | 2.8186 | 2.8186 | 3.5189 | 3.5189
1440 | feeder2_line7 | 1 | 354.6 | 56.6426 | 56.6555 | 15.9737 | 15.9773
1440 | feeder2_line7 | 2 | 354.6 | 70.909 | 70.8926 | 19.9969 | 19.9923
1440 | feeder2_line7 | 3 | 354.6 | 57.1819 | 57.1878 | 16.1257 | 16.1274
1440 | feeder2_line8 | 1 | 80.1 | 0.072631 | 0.072633 | 0.090676 | 0.090678
1440 | feeder2_line8 | 2 | 80.1 | 5.7258e-07 | 1.1333e-06 | 7.1483e-07 | 1.4148e-06
1440 | feeder2_line8 | 3 | 80.1 | 5.7197e-07 | 1.1321e-06 | 7.1407e-07 | 1.4133e-06
1440 | feeder2_line9 | 1 | 354.6 | 56.7152 | 56.7281 | 15.9941 | 15.9978
1440 | feeder2_line9 | 2 | 354.6 | 70.9091 | 70.8926 | 19.9969 | 19.9923
1440 | feeder2_line9 | 3 | 354.6 | 57.1819 | 57.1878 | 16.1258 | 16.1274
1440 | feeder2_line10 | 1 | 80.1 | 8.4576e-07 | 1.4952e-06 | 1.0559e-06 | 1.8666e-06
1440 | feeder2_line10 | 2 | 80.1 | 0.072552 | 0.072549 | 0.090576 | 0.090573
1440 | feeder2_line10 | 3 | 80.1 | 8.4551e-07 | 1.4948e-06 | 1.0556e-06 | 1.8662e-06
1440 | feeder2_line11 | 1 | 354.6 | 56.7152 | 56.7281 | 15.9941 | 15.9978
1440 | feeder2_line11 | 2 | 354.6 | 70.981 | 70.9646 | 20.0172 | 20.0126
1440 | feeder2_line11 | 3 | 354.6 | 57.1819 | 57.1878 | 16.1258 | 16.1274
1440 | feeder2_line12 | 1 | 80.1 | 5.4732e-07 | 9.9187e-07 | 6.833e-07 | 1.2383e-06
1440 | feeder2_line12 | 2 | 80.1 | 5.4785e-07 | 9.9275e-07 | 6.8395e-07 | 1.2394e-06
1440 | feeder2_line12 | 3 | 80.1 | 3.7235 | 3.7235 | 4.6485 | 4.6486
1440 | feeder2_line13 | 1 | 354.6 | 56.7152 | 56.7281 | 15.9941 | 15.9978
1440 | feeder2_line13 | 2 | 354.6 | 70.981 | 70.9646 | 20.0172 | 20.0126
1440 | feeder2_line13 | 3 | 354.6 | 60.8874 | 60.8934 | 17.1707 | 17.1724
1440 | feeder2_line14 | 1 | 80.1 | 2.5961 | 2.5961 | 3.241 | 3.241
1440 | feeder2_line14 | 2 | 80.1 | 2.988e-07 | 6.4744e-07 | 3.7304e-07 | 8.0828e-07
1440 | feeder2_line14 | 3 | 80.1 | 2.9852e-07 | 6.4668e-07 | 3.7268e-07 | 8.0735e-07
1440 | feeder2_line15 | 1 | 354.6 | 58.1319 | 58.1447 | 16.3937 | 16.3973
1440 | feeder2_line15 | 2 | 354.6 | 70.981 | 70.9646 | 20.0172 | 20.0126
1440 | feeder2_line15 | 3 | 354.6 | 60.8875 | 60.8934 | 17.1707 | 17.1724
1440 | feeder2_line16 | 1 | 80.1 | 5.7232e-07 | 1.0311e-06 | 7.1451e-07 | 1.2872e-06
1440 | feeder2_line16 | 2 | 80.1 | 0.25452 | 0.25451 | 0.31775 | 0.31775
1440 | feeder2_line16 | 3 | 80.1 | 5.7217e-07 | 1.0308e-06 | 7.1431e-07 | 1.2869e-06
1440 | feeder2_line17 | 1 | 354.6 | 58.132 | 58.1447 | 16.3937 | 16.3973
1440 | feeder2_line17 | 2 | 354.6 | 71.2304 | 71.214 | 20.0875 | 20.0829
1440 | feeder2_line17 | 3 | 354.6 | 60.8875 | 60.8934 | 17.1708 | 17.1724
1440 | feeder2_line18 | 1 | 80.1 | 5.4783e-07 | 7.3855e-07 | 6.8393e-07 | 9.2203e-07
1440 | feeder2_line18 | 2 | 80.1 | 5.4853e-07 | 7.3941e-07 | 6.8481e-07 | 9.2311e-07
1440 | feeder2_line18 | 3 | 80.1 | 3.177 | 3.177 | 3.9663 | 3.9663
1440 | feeder2_line19 | 1 | 354.6 | 58.132 | 58.1447 | 16.3937 | 16.3973
1440 | feeder2_line19 | 2 | 354.6 | 71.2304 | 71.214 | 20.0875 | 20.0829
1440 | feeder2_line19 | 3 | 354.6 | 64.0432 | 64.0491 | 18.0607 | 18.0624
1440 | feeder2_line20 | 1 | 99 | 5.4797e-07 | 8.857e-07 | 5.5351e-07 | 8.9464e-07
1440 | feeder2_line20 | 2 | 99 | 5.4872e-07 | 8.868e-07 | 5.5426e-07 | 8.9576e-07
1440 | feeder2_line20 | 3 | 99 | 0.35647 | 0.35646 | 0.36007 | 0.36006
1440 | feeder2_line21 | 1 | 354.6 | 58.1321 | 58.1447 | 16.3937 | 16.3973
1440 | feeder2_line21 | 2 | 354.6 | 71.2306 | 71.214 | 20.0876 | 20.0829
1440 | feeder2_line21 | 3 | 354.6 | 64.3984 | 64.4042 | 18.1609 | 18.1625
1440 | feeder2_line22 | 1 | 99 | 5.7293e-07 | 1.0155e-06 | 5.7872e-07 | 1.0258e-06
1440 | feeder2_line22 | 2 | 99 | 0.093747 | 0.093742 | 0.094694 | 0.094689
1440 | feeder2_line22 | 3 | 99 | 5.7274e-07 | 1.0152e-06 | 5.7852e-07 | 1.0254e-06
1440 | feeder2_line23 | 1 | 99 | 5.7294e-07 | 9.5059e-07 | 5.7872e-07 | 9.6019e-07
1440 | feeder2_line23 | 2 | 99 | 5.7368e-07 | 9.5181e-07 | 5.7948e-07 | 9.6142e-07
1440 | feeder2_line23 | 3 | 99 | 0.84037 | 0.84038 | 0.84886 | 0.84887
1440 | feeder2_line24 | 1 | 354.6 | 58.1321 | 58.1447 | 16.3937 | 16.3973
1440 | feeder2_line24 | 2 | 354.6 | 71.3235 | 71.3068 | 20.1138 | 20.1091
1440 | feeder2_line24 | 3 | 354.6 | 64.9084 | 64.9142 | 18.3047 | 18.3063
1440 | feeder2_line25 | 1 | 99 | 0.093855 | 0.09386 | 0.094803 | 0.094808
1440 | feeder2_line25 | 2 | 99 | 4.9707e-08 | 6.9223e-07 | 5.0209e-08 | 6.9922e-07
1440 | feeder2_line25 | 3 | 99 | 5.0064e-08 | 6.9107e-07 | 5.0569e-08 | 6.9805e-07
1440 | feeder2_line26 | 1 | 99 | 1.7621 | 1.7621 | 1.7799 | 1.7799
1440 | feeder2_line26 | 2 | 99 | 5.4902e-07 | 8.5763e-07 | 5.5457e-07 | 8.6629e-07
1440 | feeder2_line26 | 3 | 99 | 5.4787e-07 | 8.5619e-07 | 5.534e-07 | 8.6484e-07
1440 | feeder2_line27 | 1 | 354.6 | 59.9828 | 59.9954 | 16.9156 | 16.9192
1440 | feeder2_line27 | 2 | 354.6 | 71.3235 | 71.3068 | 20.1138 | 20.1091
1440 | feeder2_line27 | 3 | 354.6 | 64.9084 | 64.9142 | 18.3047 | 18.3063
1440 | feeder2_line28 | 1 | 99 | 2.5431e-06 | 7.1126e-07 | 2.5688e-06 | 7.1845e-07
1440 | feeder2_line28 | 2 | 99 | 1.7397 | 1.7397 | 1.7573 | 1.7573
1440 | feeder2_line28 | 3 | 99 | 2.5401e-06 | 7.1104e-07 | 2.5658e-06 | 7.1822e-07
1440 | feeder2_line29 | 1 | 354.6 | 59.9828 | 59.9954 | 16.9156 | 16.9192
1440 | feeder2_line29 | 2 | 354.6 | 72.8311 | 72.8144 | 20.5389 | 20.5342
1440 | feeder2_line29 | 3 | 354.6 | 64.9084 | 64.9142 | 18.3047 | 18.3063
1440 | feeder2_line30 | 1 | 266.4 | 24.4982 | 24.4978 | 9.196 | 9.1959
1440 | feeder2_line30 | 2 | 266.4 | 6.0417 | 6.0414 | 2.2679 | 2.2678
1440 | feeder2_line30 | 3 | 266.4 | 6.0641 | 6.064 | 2.2763 | 2.2763
1440 | feeder2_line31 | 1 | 354.6 | 84.3055 | 84.3174 | 23.7748 | 23.7782
1440 | feeder2_line31 | 2 | 354.6 | 78.162 | 78.1447 | 22.0423 | 22.0374
1440 | feeder2_line31 | 3 | 354.6 | 70.4328 | 70.4384 | 19.8626 | 19.8642
1440 | feeder2_line32 | 1 | 354.6 | 84.3055 | 84.3174 | 23.7748 | 23.7782
1440 | feeder2_line32 | 2 | 354.6 | 80.4382 | 80.4208 | 22.6842 | 22.6793
1440 | feeder2_line32 | 3 | 354.6 | 70.4329 | 70.4384 | 19.8626 | 19.8642
1440 | feeder2_line33 | 1 | 99 | 4.9831e-08 | 6.8702e-07 | 5.0334e-08 | 6.9396e-07
1440 | feeder2_line33 | 2 | 99 | 2.2975 | 2.2975 | 2.3207 | 2.3207
1440 | feeder2_line33 | 3 | 99 | 5.0202e-08 | 6.8663e-07 | 5.0709e-08 | 6.9356e-07
1440 | feeder2_line34 | 1 | 354.6 | 84.3055 | 84.3174 | 23.7748 | 23.7782
1440 | feeder2_line34 | 2 | 354.6 | 80.4382 | 80.4208 | 22.6842 | 22.6793
1440 | feeder2_line34 | 3 | 354.6 | 71.6387 | 71.6442 | 20.2027 | 20.2042
1440 | feeder2_line35 | 1 | 99 | 2.9956e-07 | 7.6101e-07 | 3.0259e-07 | 7.6869e-07
1440 | feeder2_line35 | 2 | 99 | 2.9996e-07 | 7.621e-07 | 3.0299e-07 | 7.6979e-07
1440 | feeder2_line35 | 3 | 99 | 1.2071 | 1.2071 | 1.2193 | 1.2193
1440 | feeder2_line36 | 1 | 354.6 | 84.828 | 84.8403 | 23.9222 | 23.9256
1440 | feeder2_line36 | 2 | 354.6 | 80.4381 | 80.4208 | 22.6842 | 22.6793
1440 | feeder2_line36 | 3 | 354.6 | 71.6387 | 71.6442 | 20.2027 | 20.2042
1440 | feeder2_line37 | 1 | 99 | 0.52264 | 0.52298 | 0.52792 | 0.52826
1440 | feeder2_line37 | 2 | 99 | 3.0004e-07 | 8.4343e-07 | 3.0307e-07 | 8.5195e-07
1440 | feeder2_line37 | 3 | 99 | 2.9951e-07 | 8.4158e-07 | 3.0254e-07 | 8.5008e-07
1440 | feeder2_line38 | 1 | 99 | 3.242e-07 | 7.7627e-07 | 3.2747e-07 | 7.8411e-07
1440 | feeder2_line38 | 2 | 99 | 0.21252 | 0.21251 | 0.21467 | 0.21466
1440 | feeder2_line38 | 3 | 99 | 3.2438e-07 | 7.7613e-07 | 3.2766e-07 | 7.8397e-07
1440 | feeder2_line39 | 1 | 266.4 | 24.4982 | 24.4978 | 9.196 | 9.1959
1440 | feeder2_line39 | 2 | 266.4 | 5.8424 | 5.8422 | 2.1931 | 2.193
1440 | feeder2_line39 | 3 | 266.4 | 6.0641 | 6.064 | 2.2763 | 2.2763
1440 | feeder2_line40 | 1 | 354.6 | 84.9217 | 84.9339 | 23.9486 | 23.952
1440 | feeder2_line40 | 2 | 354.6 | 80.4382 | 80.4208 | 22.6842 | 22.6793
1440 | feeder2_line40 | 3 | 354.6 | 71.6387 | 71.6442 | 20.2027 | 20.2042
1440 | feeder2_line41 | 1 | 99 | 0.093653 | 0.09366 | 0.094599 | 0.094606
1440 | feeder2_line41 | 2 | 99 | 4.9795e-08 | 7.371e-07 | 5.0298e-08 | 7.4454e-07
1440 | feeder2_line41 | 3 | 99 | 5.0258e-08 | 7.3546e-07 | 5.0765e-08 | 7.4289e-07
1440 | feeder2_line42 | 1 | 99 | 2.9921e-07 | 7.4908e-07 | 3.0223e-07 | 7.5665e-07
1440 | feeder2_line42 | 2 | 99 | 2.9976e-07 | 7.5062e-07 | 3.0279e-07 | 7.582e-07
1440 | feeder2_line42 | 3 | 99 | 0.18992 | 0.18992 | 0.19184 | 0.19184
1440 | feeder2_line43 | 1 | 266.4 | 24.4981 | 24.4978 | 9.196 | 9.1959
1440 | feeder2_line43 | 2 | 266.4 | 5.8424 | 5.8422 | 2.1931 | 2.193
1440 | feeder2_line43 | 3 | 266.4 | 5.8883 | 5.8882 | 2.2103 | 2.2103
1440 | feeder2_line44 | 1 | 354.6 | 84.9218 | 84.9339 | 23.9486 | 23.952
1440 | feeder2_line44 | 2 | 354.6 | 80.4382 | 80.4208 | 22.6842 | 22.6793
1440 | feeder2_line44 | 3 | 354.6 | 71.9951 | 72.0006 | 20.3032 | 20.3047
1440 | feeder2_line45 | 1 | 99 | 4.983e-08 | 5.8064e-07 | 5.0333e-08 | 5.865e-07
1440 | feeder2_line45 | 2 | 99 | 4.9804e-08 | 5.8138e-07 | 5.0307e-08 | 5.8725e-07
1440 | feeder2_line45 | 3 | 99 | 0.35664 | 0.35661 | 0.36024 | 0.36022
1440 | feeder2_line46 | 1 | 99 | 5.7349e-07 | 1.358e-06 | 5.7928e-07 | 1.3717e-06
1440 | feeder2_line46 | 2 | 99 | 5.7467e-07 | 1.3607e-06 | 5.8047e-07 | 1.3745e-06
1440 | feeder2_line46 | 3 | 99 | 2.7442 | 2.7443 | 2.7719 | 2.772
1440 | feeder2_line47 | 1 | 266.4 | 24.4982 | 24.4978 | 9.196 | 9.1959
1440 | feeder2_line47 | 2 | 266.4 | 5.8425 | 5.8422 | 2.1931 | 2.193
1440 | feeder2_line47 | 3 | 266.4 | 3.8332 | 3.833 | 1.4389 | 1.4388
1440 | feeder2_line48 | 1 | 99 | 1.1995 | 1.1995 | 1.2116 | 1.2116
1440 | feeder2_line48 | 2 | 99 | 4.9702e-08 | 7.3264e-07 | 5.0204e-08 | 7.4004e-07
1440 | feeder2_line48 | 3 | 99 | 5.0146e-08 | 7.312e-07 | 5.0652e-08 | 7.3858e-07
1440 | feeder2_line49 | 1 | 266.4 | 23.6871 | 23.6867 | 8.8915 | 8.8914
1440 | feeder2_line49 | 2 | 266.4 | 5.8425 | 5.8422 | 2.1931 | 2.193
1440 | feeder2_line49 | 3 | 266.4 | 3.8332 | 3.833 | 1.4389 | 1.4388
1440 | feeder2_line50 | 1 | 99 | 5.7336e-07 | 1.2356e-06 | 5.7915e-07 | 1.248e-06
1440 | feeder2_line50 | 2 | 99 | 2.8101 | 2.81 | 2.8385 | 2.8384
1440 | feeder2_line50 | 3 | 99 | 5.7351e-07 | 1.2359e-06 | 5.7931e-07 | 1.2484e-06
1440 | feeder2_line51 | 1 | 99 | 12.4697 | 12.4698 | 12.5957 | 12.5957
1440 | feeder2_line51 | 2 | 99 | 5.7463e-07 | 1.3443e-06 | 5.8044e-07 | 1.3579e-06
1440 | feeder2_line51 | 3 | 99 | 5.7349e-07 | 1.3417e-06 | 5.7929e-07 | 1.3553e-06
1440 | feeder2_line52 | 1 | 266.4 | 11.2175 | 11.2171 | 4.2108 | 4.2106
1440 | feeder2_line52 | 2 | 266.4 | 3.0334 | 3.0333 | 1.1387 | 1.1386
1440 | feeder2_line52 | 3 | 266.4 | 3.8331 | 3.833 | 1.4388 | 1.4388
1440 | feeder2_line53 | 1 | 99 | 5.4842e-07 | 7.5408e-07 | 5.5396e-07 | 7.617e-07
1440 | feeder2_line53 | 2 | 99 | 3.0334 | 3.0333 | 3.064 | 3.064
1440 | feeder2_line53 | 3 | 99 | 5.4844e-07 | 7.5431e-07 | 5.5398e-07 | 7.6192e-07
1440 | feeder2_line54 | 1 | 266.4 | 11.2173 | 11.2171 | 4.2107 | 4.2106
1440 | feeder2_line54 | 2 | 266.4 | 8.5686e-05 | 4.6362e-06 | 3.2164e-05 | 1.7403e-06
1440 | feeder2_line54 | 3 | 266.4 | 3.8329 | 3.833 | 1.4388 | 1.4388
1440 | feeder2_line55 | 1 | 99 | 0.18112 | 0.18113 | 0.18295 | 0.18296
1440 | feeder2_line55 | 2 | 99 | 4.984e-08 | 7.3288e-07 | 5.0343e-08 | 7.4028e-07
1440 | feeder2_line55 | 3 | 99 | 5.0326e-08 | 7.3111e-07 | 5.0835e-08 | 7.385e-07
1440 | feeder2_line56 | 1 | 354.6 | 85.1028 | 85.1149 | 23.9996 | 24.0031
1440 | feeder2_line56 | 2 | 354.6 | 80.4383 | 80.4208 | 22.6842 | 22.6793
1440 | feeder2_line56 | 3 | 354.6 | 71.9952 | 72.0006 | 20.3032 | 20.3047
1440 | feeder2_line57 | 1 | 99 | 7.4796e-07 | 1.5445e-06 | 7.5551e-07 | 1.5601e-06
1440 | feeder2_line57 | 2 | 99 | 7.4531e-07 | 1.5481e-06 | 7.5284e-07 | 1.5637e-06
1440 | feeder2_line57 | 3 | 99 | 3.833 | 3.833 | 3.8717 | 3.8717
1440 | feeder2_line58 | 1 | 266.4 | 11.2174 | 11.2171 | 4.2107 | 4.2106
1440 | feeder2_line58 | 2 | 266.4 | 1.9003e-05 | 2.6916e-06 | 7.1334e-06 | 1.0104e-06
1440 | feeder2_line58 | 3 | 266.4 | 1.8953e-05 | 2.6867e-06 | 7.1146e-06 | 1.0085e-06
1440 | feeder2_line59 | 1 | 99 | 4.9865e-08 | 5.3689e-07 | 5.0368e-08 | 5.4231e-07
1440 | feeder2_line59 | 2 | 99 | 4.9688e-08 | 5.3814e-07 | 5.019e-08 | 5.4358e-07
1440 | feeder2_line59 | 3 | 99 | 0.1083 | 0.1083 | 0.10939 | 0.1094
1440 | feeder2_line60 | 1 | 99 | 2.9912e-07 | 8.1139e-07 | 3.0215e-07 | 8.1959e-07
1440 | feeder2_line60 | 2 | 99 | 2.9975e-07 | 8.1329e-07 | 3.0278e-07 | 8.215e-07
1440 | feeder2_line60 | 3 | 99 | 3.7258 | 3.7258 | 3.7634 | 3.7634
1440 | feeder2_line61 | 1 | 266.4 | 2.5554 | 2.5555 | 0.95922 | 0.95928
1440 | feeder2_line61 | 2 | 266.4 | 3.1815 | 3.1815 | 1.1942 | 1.1943
1440 | feeder2_line61 | 3 | 266.4 | 1.0445 | 1.0447 | 0.39207 | 0.39215
1440 | feeder2_line62 | 1 | 354.6 | 87.3498 | 87.3621 | 24.6333 | 24.6368
1440 | feeder2_line62 | 2 | 354.6 | 83.4489 | 83.4316 | 23.5333 | 23.5284
1440 | feeder2_line62 | 3 | 354.6 | 72.7961 | 72.8018 | 20.5291 | 20.5307
1440 | feeder2_line63 | 1 | 99 | 1.8207 | 1.8208 | 1.8391 | 1.8391
1440 | feeder2_line63 | 2 | 99 | 5.7468e-07 | 1.2228e-06 | 5.8049e-07 | 1.2351e-06
1440 | feeder2_line63 | 3 | 99 | 5.7352e-07 | 1.2204e-06 | 5.7932e-07 | 1.2327e-06
1440 | feeder2_line64 | 1 | 99 | 9.3966 | 9.3964 | 9.4916 | 9.4913
1440 | feeder2_line64 | 2 | 99 | 5.558e-12 | 3.221e-07 | 5.6141e-12 | 3.2536e-07
1440 | feeder2_line64 | 3 | 99 | 2.9594e-13 | 3.2147e-07 | 2.9893e-13 | 3.2472e-07
1440 | feeder2_line65 | 1 | 99 | 4.9836e-08 | 6.4379e-07 | 5.034e-08 | 6.5029e-07
1440 | feeder2_line65 | 2 | 99 | 0.27956 | 0.27954 | 0.28238 | 0.28237
1440 | feeder2_line65 | 3 | 99 | 5.042e-08 | 6.4257e-07 | 5.0929e-08 | 6.4906e-07
1440 | feeder2_line66 | 1 | 354.6 | 87.3498 | 87.3621 | 24.6333 | 24.6368
1440 | feeder2_line66 | 2 | 354.6 | 83.7267 | 83.7094 | 23.6116 | 23.6067
1440 | feeder2_line66 | 3 | 354.6 | 72.7961 | 72.8018 | 20.5291 | 20.5307
1440 | feeder2_line67 | 1 | 99 | 2.4914e-08 | 3.6372e-07 | 2.5166e-08 | 3.674e-07
1440 | feeder2_line67 | 2 | 99 | 2.4932e-08 | 3.6406e-07 | 2.5184e-08 | 3.6774e-07
1440 | feeder2_line67 | 3 | 99 | 0.093776 | 0.093779 | 0.094723 | 0.094727
1440 | feeder2_line68 | 1 | 266.4 | 2.5554 | 2.5555 | 0.95924 | 0.95928
1440 | feeder2_line68 | 2 | 266.4 | 3.1815 | 3.1815 | 1.1943 | 1.1943
1440 | feeder2_line68 | 3 | 266.4 | 0.97557 | 0.97573 | 0.3662 | 0.36626
1440 | feeder2_line69 | 1 | 99 | 0.2138 | 0.21391 | 0.21596 | 0.21607
1440 | feeder2_line69 | 2 | 99 | 2.5576e-06 | 6.69e-07 | 2.5835e-06 | 6.7576e-07
1440 | feeder2_line69 | 3 | 99 | 2.5461e-06 | 6.6716e-07 | 2.5718e-06 | 6.739e-07
1440 | feeder2_line70 | 1 | 354.6 | 87.5635 | 87.576 | 24.6936 | 24.6971
1440 | feeder2_line70 | 2 | 354.6 | 83.7267 | 83.7094 | 23.6116 | 23.6067
1440 | feeder2_line70 | 3 | 354.6 | 72.796 | 72.8018 | 20.529 | 20.5307
1440 | feeder2_line71 | 1 | 99 | 4.9837e-08 | 7.1856e-07 | 5.034e-08 | 7.2582e-07
1440 | feeder2_line71 | 2 | 99 | 2.715 | 2.7149 | 2.7424 | 2.7423
1440 | feeder2_line71 | 3 | 99 | 5.046e-08 | 7.1704e-07 | 5.097e-08 | 7.2429e-07
1440 | feeder2_line72 | 1 | 354.6 | 87.5636 | 87.576 | 24.6936 | 24.6971
1440 | feeder2_line72 | 2 | 354.6 | 85.297 | 85.2795 | 24.0544 | 24.0495
1440 | feeder2_line72 | 3 | 354.6 | 72.7961 | 72.8018 | 20.5291 | 20.5307
1440 | feeder2_line73 | 1 | 99 | 6.0032e-07 | 1.5398e-06 | 6.0638e-07 | 1.5553e-06
1440 | feeder2_line73 | 2 | 99 | 2.2964 | 2.2963 | 2.3196 | 2.3195
1440 | feeder2_line73 | 3 | 99 | 5.9966e-07 | 1.5374e-06 | 6.0572e-07 | 1.5529e-06
1440 | feeder2_line74 | 1 | 99 | 4.983e-08 | 4.5925e-07 | 5.0333e-08 | 4.6389e-07
1440 | feeder2_line74 | 2 | 99 | 0.97641 | 0.97639 | 0.98628 | 0.98625
1440 | feeder2_line74 | 3 | 99 | 5.0366e-08 | 4.5854e-07 | 5.0875e-08 | 4.6317e-07
1440 | feeder2_line75 | 1 | 266.4 | 2.5555 | 2.5555 | 0.95927 | 0.95928
1440 | feeder2_line75 | 2 | 266.4 | 0.089463 | 0.089487 | 0.033582 | 0.033591
1440 | feeder2_line75 | 3 | 266.4 | 0.97566 | 0.97573 | 0.36624 | 0.36627
1440 | feeder2_line76 | 1 | 99 | 2.5555 | 2.5555 | 2.5814 | 2.5813
1440 | feeder2_line76 | 2 | 99 | 8.5144e-07 | 1.5899e-06 | 8.6004e-07 | 1.6059e-06
1440 | feeder2_line76 | 3 | 99 | 8.4913e-07 | 1.5859e-06 | 8.577e-07 | 1.6019e-06
1440 | feeder2_line77 | 1 | 99 | 2.4917e-08 | 5.7712e-07 | 2.5169e-08 | 5.8295e-07
1440 | feeder2_line77 | 2 | 99 | 2.4931e-08 | 5.7766e-07 | 2.5183e-08 | 5.8349e-07
1440 | feeder2_line77 | 3 | 99 | 0.9757 | 0.97573 | 0.98555 | 0.98559
1440 | feeder2_line78 | 1 | 266.4 | 8.7948e-12 | 9.5701e-07 | 3.3014e-12 | 3.5924e-07
1440 | feeder2_line78 | 2 | 266.4 | 0.089495 | 0.089487 | 0.033594 | 0.033591
1440 | feeder2_line78 | 3 | 266.4 | 1.2444e-11 | 9.5593e-07 | 4.6712e-12 | 3.5883e-07
1440 | feeder2_line79 | 1 | 354.6 | 1.9399 | 1.9396 | 0.54707 | 0.54699
1440 | feeder2_line79 | 2 | 354.6 | 3.3505 | 3.35 | 0.94487 | 0.94472
1440 | feeder2_line79 | 3 | 354.6 | 18.2538 | 18.2533 | 5.1477 | 5.1476
1440 | feeder2_line80 | 1 | 354.6 | 89.5034 | 89.5154 | 25.2407 | 25.2441
1440 | feeder2_line80 | 2 | 354.6 | 88.2891 | 88.2709 | 24.8982 | 24.8931
1440 | feeder2_line80 | 3 | 354.6 | 90.6592 | 90.6644 | 25.5666 | 25.5681
1440 | feeder2_line81 | 1 | 354.6 | 89.5034 | 89.5154 | 25.2407 | 25.2441
1440 | feeder2_line81 | 2 | 354.6 | 88.289 | 88.2709 | 24.8982 | 24.8931
1440 | feeder2_line81 | 3 | 354.6 | 90.9094 | 90.9147 | 25.6372 | 25.6387
1440 | feeder2_line82 | 1 | 354.6 | 2.1715e-11 | 7.3744e-07 | 6.1239e-12 | 2.0796e-07
1440 | feeder2_line82 | 2 | 354.6 | 4.3451e-11 | 7.3785e-07 | 1.2253e-11 | 2.0808e-07
1440 | feeder2_line82 | 3 | 354.6 | 0.25031 | 0.25031 | 0.070588 | 0.07059
1440 | feeder2_line83 | 1 | 354.6 | 89.5036 | 89.5154 | 25.2407 | 25.2441
1440 | feeder2_line83 | 2 | 354.6 | 89.522 | 89.5036 | 25.2459 | 25.2407
1440 | feeder2_line83 | 3 | 354.6 | 90.9096 | 90.9147 | 25.6372 | 25.6387
1440 | feeder2_line84 | 1 | 354.6 | 7.5118e-12 | 1.3036e-06 | 2.1184e-12 | 3.6762e-07
1440 | feeder2_line84 | 2 | 354.6 | 2.2754 | 2.2753 | 0.64168 | 0.64166
1440 | feeder2_line84 | 3 | 354.6 | 1.2558e-11 | 1.3009e-06 | 3.5415e-12 | 3.6686e-07
1440 | feeder2_line85 | 1 | 99 | 0.21255 | 0.21256 | 0.21469 | 0.2147
1440 | feeder2_line85 | 2 | 99 | 4.9981e-08 | 4.6561e-07 | 5.0485e-08 | 4.7031e-07
1440 | feeder2_line85 | 3 | 99 | 5.0545e-08 | 4.6423e-07 | 5.1055e-08 | 4.6892e-07
1440 | feeder2_line86 | 1 | 354.6 | 89.7162 | 89.728 | 25.3007 | 25.304
1440 | feeder2_line86 | 2 | 354.6 | 89.5221 | 89.5036 | 25.2459 | 25.2407
1440 | feeder2_line86 | 3 | 354.6 | 90.9097 | 90.9147 | 25.6373 | 25.6387
1440 | feeder2_line87 | 1 | 354.6 | 89.7164 | 89.728 | 25.3007 | 25.304
1440 | feeder2_line87 | 2 | 354.6 | 92.6216 | 92.6026 | 26.12 | 26.1147
1440 | feeder2_line87 | 3 | 354.6 | 92.5123 | 92.5171 | 26.0892 | 26.0906
1440 | feeder2_line88 | 1 | 354.6 | 0.00011579 | 3.3801e-06 | 3.2653e-05 | 9.5322e-07
1440 | feeder2_line88 | 2 | 354.6 | 4.2636 | 4.2633 | 1.2024 | 1.2023
1440 | feeder2_line88 | 3 | 354.6 | 1.8908 | 1.8907 | 0.53321 | 0.5332
1440 | feeder2_line89 | 1 | 354.6 | 89.7141 | 89.728 | 25.3001 | 25.304
1440 | feeder2_line89 | 2 | 354.6 | 95.443 | 95.4263 | 26.9157 | 26.911
1440 | feeder2_line89 | 3 | 354.6 | 92.51 | 92.5171 | 26.0886 | 26.0906
1440 | feeder2_line90 | 1 | 354.6 | 0.00072877 | 2.0408e-06 | 0.00020552 | 5.7553e-07
1440 | feeder2_line90 | 2 | 354.6 | 3.3744 | 3.3744 | 0.95161 | 0.95161
1440 | feeder2_line90 | 3 | 354.6 | 0.00072442 | 2.0346e-06 | 0.00020429 | 5.7377e-07
1440 | feeder2_line91 | 1 | 354.6 | 89.714 | 89.728 | 25.3001 | 25.304
1440 | feeder2_line91 | 2 | 354.6 | 95.4429 | 95.4263 | 26.9157 | 26.911
1440 | feeder2_line91 | 3 | 354.6 | 96.2375 | 96.2446 | 27.1397 | 27.1417
1440 | feeder2_line92 | 1 | 354.6 | 4.8904e-12 | 1.0294e-06 | 1.3791e-12 | 2.9029e-07
1440 | feeder2_line92 | 2 | 354.6 | 4.8906e-12 | 1.0299e-06 | 1.3792e-12 | 2.9044e-07
1440 | feeder2_line92 | 3 | 354.6 | 3.7294 | 3.7294 | 1.0517 | 1.0517
1440 | feeder2_line93 | 1 | 99 | 2.4948e-08 | 3.4365e-07 | 2.52e-08 | 3.4712e-07
1440 | feeder2_line93 | 2 | 99 | 2.2761 | 2.276 | 2.2991 | 2.299
1440 | feeder2_line93 | 3 | 99 | 2.529e-08 | 3.4282e-07 | 2.5545e-08 | 3.4628e-07
1440 | feeder2_line94 | 1 | 354.6 | 2.4949e-06 | 1.6729e-06 | 7.0358e-07 | 4.7176e-07
1440 | feeder2_line94 | 2 | 354.6 | 1.4913 | 1.4912 | 0.42055 | 0.42054
1440 | feeder2_line94 | 3 | 354.6 | 2.529e-06 | 1.6695e-06 | 7.132e-07 | 4.708e-07
1440 | feeder2_line95 | 1 | 99 | 3.5837e-06 | 2.6212e-06 | 3.6199e-06 | 2.6477e-06
1440 | feeder2_line95 | 2 | 99 | 4.2636 | 4.2633 | 4.3066 | 4.3064
1440 | feeder2_line95 | 3 | 99 | 3.5716e-06 | 2.6148e-06 | 3.6077e-06 | 2.6412e-06
1440 | feeder2_line96 | 1 | 354.6 | 0.0001217 | 6.249e-07 | 3.432e-05 | 1.7623e-07
1440 | feeder2_line96 | 2 | 354.6 | 0.00012171 | 6.2528e-07 | 3.4323e-05 | 1.7633e-07
1440 | feeder2_line96 | 3 | 354.6 | 1.8907 | 1.8907 | 0.5332 | 0.5332
1440 | feeder2_line97 | 1 | 354.6 | 90.5647 | 90.5786 | 25.54 | 25.5439
1440 | feeder2_line97 | 2 | 354.6 | 95.4431 | 95.4263 | 26.9157 | 26.911
1440 | feeder2_line97 | 3 | 354.6 | 96.2376 | 96.2446 | 27.1398 | 27.1417
1440 | feeder2_line98 | 1 | 354.6 | 1.3579 | 1.357 | 0.38293 | 0.38269
1440 | feeder2_line98 | 2 | 354.6 | 0.0017083 | 6.2283e-07 | 0.00048176 | 1.7564e-07
1440 | feeder2_line98 | 3 | 354.6 | 0.0017014 | 6.2213e-07 | 0.00047981 | 1.7545e-07
1440 | feeder2_line99 | 1 | 99 | 2.494e-08 | 4.492e-07 | 2.5191e-08 | 4.5374e-07
1440 | feeder2_line99 | 2 | 99 | 2.5e-08 | 4.494e-07 | 2.5253e-08 | 4.5394e-07
1440 | feeder2_line99 | 3 | 99 | 1.8907 | 1.8907 | 1.9098 | 1.9098
1440 | feeder2_line100 | 1 | 99 | 1.357 | 1.357 | 1.3707 | 1.3707
1440 | feeder2_line100 | 2 | 99 | 2.502e-08 | 6.1732e-07 | 2.5273e-08 | 6.2356e-07
1440 | feeder2_line100 | 3 | 99 | 2.5297e-08 | 6.1554e-07 | 2.5553e-08 | 6.2176e-07
1440 | feeder2_line101 | 1 | 354.6 | 1.4913 | 1.491 | 0.42056 | 0.42046
1440 | feeder2_line101 | 2 | 354.6 | 3.3505 | 3.35 | 0.94486 | 0.94472
1440 | feeder2_line101 | 3 | 354.6 | 18.2538 | 18.2533 | 5.1477 | 5.1476
1440 | feeder2_line102 | 1 | 99 | 0.44872 | 0.4488 | 0.45325 | 0.45333
1440 | feeder2_line102 | 2 | 99 | 2.3455e-06 | 8.8223e-07 | 2.3692e-06 | 8.9114e-07
1440 | feeder2_line102 | 3 | 99 | 2.3329e-06 | 8.793e-07 | 2.3564e-06 | 8.8818e-07
1440 | feeder2_line103 | 1 | 99 | 5.5165e-07 | 8.0704e-07 | 5.5722e-07 | 8.1519e-07
1440 | feeder2_line103 | 2 | 99 | 0.096271 | 0.096262 | 0.097243 | 0.097234
1440 | feeder2_line103 | 3 | 99 | 5.4962e-07 | 8.0475e-07 | 5.5517e-07 | 8.1288e-07
1440 | feeder2_line104 | 1 | 354.6 | 1.4912 | 1.491 | 0.42053 | 0.42046
1440 | feeder2_line104 | 2 | 354.6 | 3.2676 | 3.2672 | 0.92149 | 0.92137
1440 | feeder2_line104 | 3 | 354.6 | 18.2537 | 18.2533 | 5.1477 | 5.1476
1440 | feeder2_line105 | 1 | 99 | 2.559e-06 | 7.4259e-07 | 2.5849e-06 | 7.5009e-07
1440 | feeder2_line105 | 2 | 99 | 2.56e-06 | 7.4303e-07 | 2.5859e-06 | 7.5053e-07
1440 | feeder2_line105 | 3 | 99 | 3.1761 | 3.1761 | 3.2082 | 3.2081
1440 | feeder2_line106 | 1 | 354.6 | 1.4911 | 1.491 | 0.42051 | 0.42046
1440 | feeder2_line106 | 2 | 354.6 | 3.2676 | 3.2672 | 0.92148 | 0.92137
1440 | feeder2_line106 | 3 | 354.6 | 15.14 | 15.1397 | 4.2696 | 4.2695
1440 | feeder2_line107 | 1 | 99 | 3.2563e-07 | 9.0496e-07 | 3.2892e-07 | 9.141e-07
1440 | feeder2_line107 | 2 | 99 | 1.1999 | 1.1998 | 1.212 | 1.212
1440 | feeder2_line107 | 3 | 99 | 3.253e-07 | 9.0218e-07 | 3.2858e-07 | 9.1129e-07
1440 | feeder2_line108 | 1 | 354.6 | 1.4911 | 1.491 | 0.42051 | 0.42046
1440 | feeder2_line108 | 2 | 354.6 | 2.2824 | 2.282 | 0.64364 | 0.64356
1440 | feeder2_line108 | 3 | 354.6 | 15.14 | 15.1397 | 4.2696 | 4.2695
1440 | feeder2_line109 | 1 | 354.6 | 91.8788 | 91.8915 | 25.9106 | 25.9141
1440 | feeder2_line109 | 2 | 354.6 | 95.4443 | 95.4263 | 26.9161 | 26.911
1440 | feeder2_line109 | 3 | 354.6 | 96.2388 | 96.2446 | 27.1401 | 27.1417
1440 | feeder2_line110 | 1 | 99 | 1.3261 | 1.3253 | 1.3395 | 1.3387
1440 | feeder2_line110 | 2 | 99 | 0.0008093 | 9.1331e-07 | 0.00081747 | 9.2253e-07
1440 | feeder2_line110 | 3 | 99 | 0.00080511 | 9.1147e-07 | 0.00081324 | 9.2068e-07
1440 | feeder2_line111 | 1 | 99 | 2.4926e-08 | 3.8364e-07 | 2.5177e-08 | 3.8752e-07
1440 | feeder2_line111 | 2 | 99 | 2.0281 | 2.028 | 2.0486 | 2.0485
1440 | feeder2_line111 | 3 | 99 | 2.5279e-08 | 3.8271e-07 | 2.5535e-08 | 3.8658e-07
1440 | feeder2_line112 | 1 | 99 | 3.2592e-07 | 9.2192e-07 | 3.2921e-07 | 9.3123e-07
1440 | feeder2_line112 | 2 | 99 | 2.3949 | 2.3947 | 2.4191 | 2.4189
1440 | feeder2_line112 | 3 | 99 | 3.2573e-07 | 9.1967e-07 | 3.2902e-07 | 9.2896e-07
1440 | feeder2_line113 | 1 | 99 | 1.2219 | 1.222 | 1.2343 | 1.2343
1440 | feeder2_line113 | 2 | 99 | 3.2656e-07 | 9.1051e-07 | 3.2986e-07 | 9.1971e-07
1440 | feeder2_line113 | 3 | 99 | 3.2614e-07 | 9.0793e-07 | 3.2943e-07 | 9.171e-07
1440 | feeder2_line114 | 1 | 99 | 0.096293 | 0.0963 | 0.097266 | 0.097273
1440 | feeder2_line114 | 2 | 99 | 2.4966e-08 | 4.387e-07 | 2.5218e-08 | 4.4313e-07
1440 | feeder2_line114 | 3 | 99 | 2.5265e-08 | 4.3724e-07 | 2.5521e-08 | 4.4166e-07
1440 | feeder2_line115 | 1 | 99 | 2.4899e-08 | 5.6475e-07 | 2.515e-08 | 5.7046e-07
1440 | feeder2_line115 | 2 | 99 | 1.6553 | 1.6552 | 1.672 | 1.672
1440 | feeder2_line115 | 3 | 99 | 2.5284e-08 | 5.6291e-07 | 2.5539e-08 | 5.6859e-07
1440 | feeder2_line116 | 1 | 354.6 | 1.4911 | 1.491 | 0.42051 | 0.42046
1440 | feeder2_line116 | 2 | 354.6 | 0.85908 | 0.8589 | 0.24227 | 0.24222
1440 | feeder2_line116 | 3 | 354.6 | 15.14 | 15.1397 | 4.2696 | 4.2695
1440 | feeder2_line117 | 1 | 99 | 4.9968e-08 | 6.463e-07 | 5.0473e-08 | 6.5283e-07
1440 | feeder2_line117 | 2 | 99 | 2.7544 | 2.7544 | 2.7822 | 2.7822
1440 | feeder2_line117 | 3 | 99 | 5.0642e-08 | 6.4485e-07 | 5.1154e-08 | 6.5136e-07
1440 | feeder2_line118 | 1 | 354.6 | 91.8788 | 91.8915 | 25.9106 | 25.9141
1440 | feeder2_line118 | 2 | 354.6 | 97.1078 | 97.0896 | 27.3852 | 27.38
1440 | feeder2_line118 | 3 | 354.6 | 96.2388 | 96.2446 | 27.1401 | 27.1417
1440 | feeder2_line119 | 1 | 99 | 2.4893e-08 | 6.077e-07 | 2.5144e-08 | 6.1384e-07
1440 | feeder2_line119 | 2 | 99 | 2.4952e-08 | 6.081e-07 | 2.5204e-08 | 6.1424e-07
1440 | feeder2_line119 | 3 | 99 | 0.54528 | 0.54529 | 0.55079 | 0.5508
1440 | feeder2_line120 | 1 | 354.6 | 1.4911 | 1.491 | 0.42051 | 0.42046
1440 | feeder2_line120 | 2 | 354.6 | 0.85907 | 0.8589 | 0.24226 | 0.24222
1440 | feeder2_line120 | 3 | 354.6 | 14.6097 | 14.6093 | 4.12 | 4.1199
1440 | feeder2_line121 | 1 | 99 | 3.2562e-07 | 9.4105e-07 | 3.2891e-07 | 9.5055e-07
1440 | feeder2_line121 | 2 | 99 | 0.74301 | 0.74302 | 0.75052 | 0.75053
1440 | feeder2_line121 | 3 | 99 | 3.2516e-07 | 9.3758e-07 | 3.2845e-07 | 9.4705e-07
1440 | feeder2_line122 | 1 | 354.6 | 1.4911 | 1.491 | 0.42051 | 0.42046
1440 | feeder2_line122 | 2 | 354.6 | 0.17941 | 0.17916 | 0.050596 | 0.050524
1440 | feeder2_line122 | 3 | 354.6 | 14.6097 | 14.6093 | 4.12 | 4.1199
1440 | feeder2_line123 | 1 | 99 | 5.7659e-07 | 9.7515e-07 | 5.8241e-07 | 9.85e-07
1440 | feeder2_line123 | 2 | 99 | 5.7702e-07 | 9.7587e-07 | 5.8285e-07 | 9.8573e-07
1440 | feeder2_line123 | 3 | 99 | 1.7388 | 1.7388 | 1.7564 | 1.7563
1440 | feeder2_line124 | 1 | 354.6 | 1.491 | 1.491 | 0.42049 | 0.42046
1440 | feeder2_line124 | 2 | 354.6 | 0.17932 | 0.17916 | 0.05057 | 0.050524
1440 | feeder2_line124 | 3 | 354.6 | 12.8792 | 12.8789 | 3.632 | 3.6319
1440 | feeder2_line125 | 1 | 99 | 5.7659e-07 | 9.065e-07 | 5.8241e-07 | 9.1566e-07
1440 | feeder2_line125 | 2 | 99 | 5.7703e-07 | 9.0719e-07 | 5.8286e-07 | 9.1635e-07
1440 | feeder2_line125 | 3 | 99 | 1.3544 | 1.3544 | 1.3681 | 1.3681
1440 | feeder2_line126 | 1 | 354.6 | 1.4912 | 1.491 | 0.42053 | 0.42046
1440 | feeder2_line126 | 2 | 354.6 | 0.17948 | 0.17916 | 0.050615 | 0.050524
1440 | feeder2_line126 | 3 | 354.6 | 11.8166 | 11.8161 | 3.3324 | 3.3322
1440 | feeder2_line127 | 1 | 99 | 5.7657e-07 | 1.0852e-06 | 5.8239e-07 | 1.0962e-06
1440 | feeder2_line127 | 2 | 99 | 5.7702e-07 | 1.0861e-06 | 5.8285e-07 | 1.097e-06
1440 | feeder2_line127 | 3 | 99 | 10.6402 | 10.6401 | 10.7477 | 10.7476
1440 | feeder2_line128 | 1 | 354.6 | 1.4911 | 1.491 | 0.42051 | 0.42046
1440 | feeder2_line128 | 2 | 354.6 | 0.1794 | 0.17916 | 0.050591 | 0.050524
1440 | feeder2_line128 | 3 | 354.6 | 1.4605 | 1.4603 | 0.41188 | 0.41182
1440 | feeder2_line129 | 1 | 99 | 5.5171e-07 | 8.7996e-07 | 5.5728e-07 | 8.8885e-07
1440 | feeder2_line129 | 2 | 99 | 0.17917 | 0.17916 | 0.18098 | 0.18097
1440 | feeder2_line129 | 3 | 99 | 5.4897e-07 | 8.7651e-07 | 5.5452e-07 | 8.8536e-07
1440 | feeder2_line130 | 1 | 354.6 | 1.4911 | 1.491 | 0.42051 | 0.42046
1440 | feeder2_line130 | 2 | 354.6 | 0.0003103 | 4.66e-06 | 8.7507e-05 | 1.3142e-06
1440 | feeder2_line130 | 3 | 354.6 | 1.4606 | 1.4603 | 0.41189 | 0.41182
1440 | feeder2_line131 | 1 | 99 | 5.7658e-07 | 9.7529e-07 | 5.8241e-07 | 9.8514e-07
1440 | feeder2_line131 | 2 | 99 | 5.7705e-07 | 9.7608e-07 | 5.8288e-07 | 9.8593e-07
1440 | feeder2_line131 | 3 | 99 | 1.3177 | 1.3177 | 1.331 | 1.331
1440 | feeder2_line132 | 1 | 354.6 | 1.491 | 1.491 | 0.42046 | 0.42046
1440 | feeder2_line132 | 2 | 354.6 | 0.00012638 | 2.9298e-06 | 3.5641e-05 | 8.2623e-07
1440 | feeder2_line132 | 3 | 354.6 | 0.21257 | 0.2125 | 0.059947 | 0.059927
1440 | feeder2_line133 | 1 | 99 | 1.4909 | 1.491 | 1.506 | 1.506
1440 | feeder2_line133 | 2 | 99 | 3.0099e-07 | 9.8387e-07 | 3.0403e-07 | 9.9381e-07
1440 | feeder2_line133 | 3 | 99 | 2.9979e-07 | 9.7922e-07 | 3.0282e-07 | 9.8911e-07
1440 | feeder2_line134 | 1 | 354.6 | 1.1487e-11 | 1.7924e-06 | 3.2395e-12 | 5.0548e-07
1440 | feeder2_line134 | 2 | 354.6 | 8.5294e-12 | 1.7939e-06 | 2.4054e-12 | 5.0591e-07
1440 | feeder2_line134 | 3 | 354.6 | 0.2125 | 0.2125 | 0.059926 | 0.059927
1440 | feeder2_line135 | 1 | 99 | 2.7182 | 2.7182 | 2.7457 | 2.7456
1440 | feeder2_line135 | 2 | 99 | 5.0124e-08 | 5.8954e-07 | 5.0631e-08 | 5.955e-07
1440 | feeder2_line135 | 3 | 99 | 5.0666e-08 | 5.8791e-07 | 5.1178e-08 | 5.9385e-07
1440 | feeder2_line136 | 1 | 354.6 | 93.6741 | 93.6867 | 26.4168 | 26.4204
1440 | feeder2_line136 | 2 | 354.6 | 97.1078 | 97.0896 | 27.3852 | 27.38
1440 | feeder2_line136 | 3 | 354.6 | 96.2388 | 96.2446 | 27.1401 | 27.1417
1440 | feeder2_line137 | 1 | 99 | 1.9847 | 1.9847 | 2.0047 | 2.0047
1440 | feeder2_line137 | 2 | 99 | 8.5574e-07 | 1.5881e-06 | 8.6438e-07 | 1.6041e-06
1440 | feeder2_line137 | 3 | 99 | 8.5313e-07 | 1.5836e-06 | 8.6174e-07 | 1.5996e-06
1440 | feeder2_line138 | 1 | 354.6 | 94.8679 | 94.8806 | 26.7535 | 26.7571
1440 | feeder2_line138 | 2 | 354.6 | 97.1078 | 97.0896 | 27.3852 | 27.38
1440 | feeder2_line138 | 3 | 354.6 | 96.2389 | 96.2446 | 27.1401 | 27.1417
1440 | feeder2_line139 | 1 | 99 | 5.003e-08 | 4.9457e-07 | 5.0535e-08 | 4.9957e-07
1440 | feeder2_line139 | 2 | 99 | 5.0139e-08 | 4.9489e-07 | 5.0646e-08 | 4.9989e-07
1440 | feeder2_line139 | 3 | 99 | 0.13679 | 0.13678 | 0.13817 | 0.13816
1440 | feeder2_line140 | 1 | 354.6 | 94.8681 | 94.8806 | 26.7535 | 26.7571
1440 | feeder2_line140 | 2 | 354.6 | 97.1079 | 97.0896 | 27.3852 | 27.38
1440 | feeder2_line140 | 3 | 354.6 | 96.3694 | 96.3753 | 27.1769 | 27.1786
1440 | feeder2_line141 | 1 | 99 | 2.5433e-06 | 4.893e-07 | 2.569e-06 | 4.9424e-07
1440 | feeder2_line141 | 2 | 99 | 0.18986 | 0.18984 | 0.19178 | 0.19176
1440 | feeder2_line141 | 3 | 99 | 2.5323e-06 | 4.8825e-07 | 2.5579e-06 | 4.9319e-07
1440 | feeder2_line142 | 1 | 354.6 | 94.8679 | 94.8806 | 26.7535 | 26.7571
1440 | feeder2_line142 | 2 | 354.6 | 97.2974 | 97.2793 | 27.4386 | 27.4335
1440 | feeder2_line142 | 3 | 354.6 | 96.3692 | 96.3753 | 27.1769 | 27.1786
1440 | feeder2_line143 | 1 | 99 | 8.5562e-07 | 1.7388e-06 | 8.6426e-07 | 1.7564e-06
1440 | feeder2_line143 | 2 | 99 | 1.2011 | 1.201 | 1.2132 | 1.2131
1440 | feeder2_line143 | 3 | 99 | 8.5357e-07 | 1.7351e-06 | 8.6219e-07 | 1.7526e-06
1440 | feeder2_line144 | 1 | 354.6 | 94.8677 | 94.8806 | 26.7534 | 26.7571
1440 | feeder2_line144 | 2 | 354.6 | 98.0757 | 98.0576 | 27.6581 | 27.653
1440 | feeder2_line144 | 3 | 354.6 | 96.369 | 96.3753 | 27.1768 | 27.1786
1440 | feeder2_line145 | 1 | 99 | 2.5022e-08 | 4.8759e-07 | 2.5274e-08 | 4.9252e-07
1440 | feeder2_line145 | 2 | 99 | 0.25075 | 0.25073 | 0.25328 | 0.25327
1440 | feeder2_line145 | 3 | 99 | 2.5354e-08 | 4.8655e-07 | 2.561e-08 | 4.9146e-07
1440 | feeder2_line146 | 1 | 354.6 | 94.8676 | 94.8806 | 26.7534 | 26.7571
1440 | feeder2_line146 | 2 | 354.6 | 98.3261 | 98.3081 | 27.7287 | 27.7237
1440 | feeder2_line146 | 3 | 354.6 | 96.3689 | 96.3753 | 27.1768 | 27.1786
1440 | feeder2_line147 | 1 | 99 | 0.10738 | 0.1074 | 0.10847 | 0.10848
1440 | feeder2_line147 | 2 | 99 | 1.1585e-06 | 2.2506e-06 | 1.1702e-06 | 2.2734e-06
1440 | feeder2_line147 | 3 | 99 | 1.1552e-06 | 2.2443e-06 | 1.1669e-06 | 2.267e-06
1440 | feeder2_line148 | 1 | 99 | 1.7546 | 1.7547 | 1.7724 | 1.7724
1440 | feeder2_line148 | 2 | 99 | 6.0434e-07 | 1.5081e-06 | 6.1044e-07 | 1.5233e-06
1440 | feeder2_line148 | 3 | 99 | 6.0296e-07 | 1.5039e-06 | 6.0905e-07 | 1.5191e-06
1440 | feeder2_line149 | 1 | 354.6 | 96.7269 | 96.7398 | 27.2778 | 27.2814
1440 | feeder2_line149 | 2 | 354.6 | 98.3263 | 98.3081 | 27.7288 | 27.7237
1440 | feeder2_line149 | 3 | 354.6 | 96.3691 | 96.3753 | 27.1768 | 27.1786
1440 | feeder2_line150 | 1 | 354.6 | 96.727 | 96.7398 | 27.2778 | 27.2814
1440 | feeder2_line150 | 2 | 354.6 | 98.5096 | 98.4913 | 27.7805 | 27.7753
1440 | feeder2_line150 | 3 | 354.6 | 96.3692 | 96.3753 | 27.1769 | 27.1786
1440 | feeder2_line151 | 1 | 99 | 9.8356e-06 | 1.7905e-06 | 9.9349e-06 | 1.8086e-06
1440 | feeder2_line151 | 2 | 99 | 0.1849 | 0.18488 | 0.18677 | 0.18675
1440 | feeder2_line151 | 3 | 99 | 9.7852e-06 | 1.7867e-06 | 9.884e-06 | 1.8047e-06
1440 | feeder2_line152 | 1 | 354.6 | 9.9325e-12 | 1.1934e-06 | 2.8011e-12 | 3.3654e-07
1440 | feeder2_line152 | 2 | 354.6 | 9.9325e-12 | 1.1943e-06 | 2.8011e-12 | 3.3679e-07
1440 | feeder2_line152 | 3 | 354.6 | 0.076662 | 0.076666 | 0.021619 | 0.02162
1440 | feeder2_line153 | 1 | 99 | 0.74408 | 0.74406 | 0.75159 | 0.75157
1440 | feeder2_line153 | 2 | 99 | 5.021e-08 | 5.9758e-07 | 5.0717e-08 | 6.0362e-07
1440 | feeder2_line153 | 3 | 99 | 5.0768e-08 | 5.9588e-07 | 5.1281e-08 | 6.019e-07
1440 | feeder2_line154 | 1 | 99 | 5.7945e-07 | 8.8859e-07 | 5.853e-07 | 8.9757e-07
1440 | feeder2_line154 | 2 | 99 | 5.7987e-07 | 8.8922e-07 | 5.8572e-07 | 8.9821e-07
1440 | feeder2_line154 | 3 | 99 | 2.6593 | 2.6592 | 2.6861 | 2.6861
1440 | feeder2_line155 | 1 | 99 | 97.1876 | 97.2004 | 98.1693 | 98.1822
1440 | feeder2_line155 | 2 | 99 | 98.5095 | 98.4913 | 99.5045 | 99.4861
1440 | feeder2_line155 | 3 | 99 | 99 | 99.0062 | 100 | 100.0063
1440 | feeder2_line156 | 1 | 99 | 6.0422e-07 | 1.1692e-06 | 6.1033e-07 | 1.181e-06
1440 | feeder2_line156 | 2 | 99 | 0.096022 | 0.096009 | 0.096992 | 0.096979
1440 | feeder2_line156 | 3 | 99 | 6.0329e-07 | 1.1667e-06 | 6.0938e-07 | 1.1785e-06
1440 | feeder2_line157 | 1 | 99 | 2.5037e-08 | 2.5382e-07 | 2.529e-08 | 2.5638e-07
1440 | feeder2_line157 | 2 | 99 | 0.089043 | 0.08903 | 0.089943 | 0.089929
1440 | feeder2_line157 | 3 | 99 | 2.5372e-08 | 2.5328e-07 | 2.5629e-08 | 2.5584e-07

## SOC_audit
Time_sample | SOC_actual_pu | SOC_expected_from_previous_interval_pu | SOC_balance_error_pu | audit_note
30 | 0.5 | 0.5 | -2.2204e-16 | sampled_SOC_state
60 | 0.45875 | 0.45875 | 0 | sampled_SOC_state
90 | 0.41722 | 0.41722 | -1.6653e-16 | sampled_SOC_state
120 | 0.37539 | 0.37539 | 0 | sampled_SOC_state
150 | 0.33441 | 0.33441 | 7.2164e-16 | sampled_SOC_state
180 | 0.29273 | 0.29273 | 5.5511e-17 | sampled_SOC_state
210 | 0.25104 | 0.25104 | -1.3323e-15 | sampled_SOC_state
240 | 0.2092 | 0.2092 | 0 | sampled_SOC_state
270 | 0.20786 | 0.20786 | -3.0531e-16 | sampled_SOC_state
300 | 0.20228 | 0.20228 | 0 | sampled_SOC_state
330 | 0.18959 | 0.18959 | 5.5511e-17 | sampled_SOC_state
360 | 0.18959 | 0.18959 | 0 | sampled_SOC_state
390 | 0.18959 | 0.18959 | 0 | sampled_SOC_state
420 | 0.18959 | 0.18959 | 2.7756e-17 | sampled_SOC_state
450 | 0.1932 | 0.1932 | -1.1102e-16 | sampled_SOC_state
480 | 0.22317 | 0.22317 | 2.7756e-17 | sampled_SOC_state
510 | 0.25196 | 0.25196 | -1.6653e-16 | sampled_SOC_state
540 | 0.28924 | 0.28924 | 0 | sampled_SOC_state
570 | 0.33313 | 0.33313 | 1.0547e-15 | sampled_SOC_state
600 | 0.38382 | 0.38382 | 0 | sampled_SOC_state
630 | 0.40604 | 0.40604 | 0 | sampled_SOC_state
660 | 0.47566 | 0.47566 | 0 | sampled_SOC_state
690 | 0.54838 | 0.54838 | -1.1102e-15 | sampled_SOC_state
720 | 0.61941 | 0.61941 | 0 | sampled_SOC_state
750 | 0.64753 | 0.64753 | 4.4409e-16 | sampled_SOC_state
780 | 0.65299 | 0.65299 | 0 | sampled_SOC_state
810 | 0.65299 | 0.65299 | -2.4425e-15 | sampled_SOC_state
840 | 0.72057 | 0.72057 | 0 | sampled_SOC_state
870 | 0.78651 | 0.78651 | -1.3323e-15 | sampled_SOC_state
900 | 0.84967 | 0.84967 | -1.1102e-16 | sampled_SOC_state
930 | 0.89225 | 0.89225 | 2.2204e-16 | sampled_SOC_state
960 | 0.90718 | 0.90718 | 1.1102e-16 | sampled_SOC_state
990 | 0.95066 | 0.95066 | -2.2204e-16 | sampled_SOC_state
1020 | 0.97343 | 0.97343 | 0 | sampled_SOC_state
1050 | 0.95066 | 0.95066 | 0 | sampled_SOC_state
1080 | 0.91502 | 0.91502 | 0 | sampled_SOC_state
1110 | 0.88041 | 0.88041 | 1.1102e-16 | sampled_SOC_state
1140 | 0.83969 | 0.83969 | 0 | sampled_SOC_state
1170 | 0.81523 | 0.81523 | -4.4409e-16 | sampled_SOC_state
1200 | 0.8043 | 0.8043 | 0 | sampled_SOC_state
1230 | 0.80183 | 0.80183 | 2.2204e-16 | sampled_SOC_state
1260 | 0.80098 | 0.80098 | 1.1102e-16 | sampled_SOC_state
1290 | 0.7592 | 0.7592 | 4.4409e-16 | sampled_SOC_state
1320 | 0.71791 | 0.71791 | 0 | sampled_SOC_state
1350 | 0.67611 | 0.67611 | 7.7716e-16 | sampled_SOC_state
1380 | 0.63445 | 0.63445 | -1.1102e-16 | sampled_SOC_state
1410 | 0.59326 | 0.59326 | 1.2212e-15 | sampled_SOC_state
1440 | 0.55164 | 0.55164 | 0 | sampled_SOC_state
1440 | 0.51 | 0.51 | 0 | terminal_SOC_after_final_dispatch_interval